## Slide 1: Cascade Natural Gas Corporation Integrated Resource Plan Technical Advisory Group Meeting #4
Thursday, September 15th, 2016
Seattle-Tacoma International Airport Conference Center

## Slide 2: AGENDA
Safety and housekeeping items
Introductions
Cascade’s New Webpage
IRP Update
Distribution System Planning
SENDOUT Model
Scenarios, Sensitivities Planned
Avoided Costs Methodology
2016 IRP Timeline
Adjournment

## Slide 3: Cascade’s New IRP Webpage
https://www.cngc.com/rates-services/rates-tariffs/integrated-resource-plan

## Slide 4: Distribution System Planning
Chris Bolton, Engineer II
Technical Advisory Group
September 15th, 2016

## Slide 5: Outline
Company overview
Network Design Fundamentals
Interstate Pipeline Companies
Software Technology
Data Gathering
Data Analysis
System Enhancement Techniques
Future Planning Process Flow
Future Projects

## Slide 6: CNG System Overview
Pipeline:
Diameter – ½” to 20”
Material – Polyethylene and Steel
Operating Pressure - 20 psi to 900 psi
Washington – approx. 4,744 miles of distribution main
Oregon – approx. 1,604 miles of distribution main

## Slide 7
Facilities:
Regulator stations – Over 700
Valves – Over 1600
Also other equipment such as heaters, odorizers and compressors.

## Slide 8: Where do we get our gas?
Many interstate pipeline companies
Williams Northwest Pipeline (red)
Transcanada Pipelines (yellow)

## Slide 9: Network Design Fundamentals
Keys:
Gate station capacity
Reg station placement
Pipe size and grid

## Slide 10: GIS – Geographic Information System
-GIS system keeps an up to date record of pipe and facilities complete with all system attributes
Pipe Size (Dia.)
Material
Date of install
Operating Pressure
Work Order
Etc……

## Slide 11: System Modeling
…Using internal GIS environment and other input data CNG is able to create system models through the software – Synergi.
What is Synergi?
Software to theoretically model piping and facilities to represent current pressure and flow conditions while also predicting future events and growth.

## Slide 12: Model Ex.
HOW DO WE MAKE THIS MODEL ACCURATE?

## Slide 13: Data Gathering
CC&B (customer billing data)

## Slide 14: Data Gathering (cont.)
SCADA Data : Real time and historical flow characteristics at specific locations in the system.

## Slide 15: Data Gathering (cont.)
IRP Customer Growth
WASHINGTON |  |  |  |  |  |  |  |  |  |  | 
YEAR | MCCLEARY (ABERDEEN/HOQUIAM) | ACME | ARLINGTON | BREMERTON (SHELTON) | CASTLE ROCK | WALLA WALLA | DEMING | WENATCHEE | FINLEY | GRANDVIEW | ZILLAH (TOPPENISH)
2017 | 0.6% | 1.4% | 1.3% | 1.2% | 1.1% | 0.7% | 1.7% | 1.4% | 1.9% | 0.8% | 0.8%
2018 | 0.6% | 1.4% | 1.3% | 1.2% | 1.1% | 0.7% | 1.7% | 1.3% | 1.9% | 0.8% | 0.8%
2019 | 0.6% | 1.4% | 1.3% | 1.2% | 1.0% | 0.7% | 1.7% | 1.3% | 1.9% | 0.8% | 0.8%
2020 | 0.6% | 1.3% | 1.3% | 1.2% | 1.0% | 0.7% | 1.7% | 1.3% | 1.8% | 0.8% | 0.8%
2021 | 0.6% | 1.3% | 1.3% | 1.2% | 1.0% | 0.7% | 1.7% | 1.3% | 1.8% | 0.7% | 0.8%
2022 | 0.6% | 1.3% | 1.2% | 1.2% | 1.0% | 0.7% | 1.7% | 1.2% | 1.8% | 0.7% | 0.8%
2023 | 0.6% | 1.3% | 1.2% | 1.2% | 1.0% | 0.7% | 1.7% | 1.2% | 1.8% | 0.7% | 0.8%
2024 | 0.6% | 1.3% | 1.2% | 1.2% | 0.9% | 0.7% | 1.7% | 1.2% | 1.8% | 0.7% | 0.7%
2025 | 0.5% | 1.3% | 1.2% | 1.2% | 0.9% | 0.6% | 1.7% | 1.2% | 1.7% | 0.7% | 0.7%
2026 | 0.5% | 1.3% | 1.2% | 1.1% | 0.9% | 0.6% | 1.7% | 1.2% | 1.7% | 0.7% | 0.7%
2027 | 0.5% | 1.3% | 1.2% | 1.1% | 0.9% | 0.6% | 1.7% | 1.2% | 1.7% | 0.7% | 0.7%
2028 | 0.5% | 1.3% | 1.2% | 1.1% | 0.9% | 0.6% | 1.7% | 1.2% | 1.7% | 0.7% | 0.7%
2029 | 0.5% | 1.3% | 1.2% | 1.1% | 0.9% | 0.6% | 1.7% | 1.2% | 1.7% | 0.7% | 0.7%
2030 | 0.5% | 1.3% | 1.2% | 1.1% | 0.9% | 0.6% | 1.6% | 1.2% | 1.7% | 0.7% | 0.7%
2031 | 0.5% | 1.2% | 1.2% | 1.1% | 0.9% | 0.6% | 1.6% | 1.1% | 1.6% | 0.6% | 0.7%
2032 | 0.5% | 1.2% | 1.1% | 1.1% | 0.8% | 0.5% | 1.6% | 1.1% | 1.6% | 0.6% | 0.6%
2033 | 0.4% | 1.2% | 1.1% | 1.1% | 0.8% | 0.5% | 1.6% | 1.1% | 1.6% | 0.6% | 0.6%
2034 | 0.4% | 1.2% | 1.1% | 1.0% | 0.8% | 0.5% | 1.6% | 1.1% | 1.6% | 0.6% | 0.6%
2035 | 0.4% | 1.2% | 1.1% | 1.0% | 0.8% | 0.5% | 1.5% | 1.1% | 1.5% | 0.5% | 0.6%
2036 | 0.4% | 1.2% | 1.1% | 1.0% | 0.8% | 0.4% | 1.5% | 1.0% | 1.5% | 0.5% | 0.5%
Average Annual Growth | 0.5% | 1.3% | 1.2% | 1.1% | 0.9% | 0.6% | 1.6% | 1.2% | 1.7% | 0.7% | 0.7%

## Slide 16: Data Gathering (cont.)
Peak Heating Degree Day (HDD) in the CNG different weather zones
Uses historical weather data to determine which degree day matches which zone.

## Slide 17: CNG Weather Zones
System Peak Day | 12/21/90
System Peak HDD | 56
Zone 1 | 46
Zone 2 | 46
Zone 3 | 58
Zone 4 | 67
Zone 5 | 65
Zone 6 | 70.5
Zone 7 | 70.5

## Slide 18: Customer Management Module (CMM)
Software that compiles data from CC&B, HDD, and/or growth studies to manage customer loads.
Works directly with Synergi to input customer data and represent pressures and flows in the model.

## Slide 19: CMM  Synergi
Conversion can result in 3 model types:
            Calibrated model – model to represent a specific date and time.
            Design Day Model – Uses the peak HDD for selected areas to simulate a cold weather (worst case scenario).
            Growth model - Uses design day model along with growth data to predict future projects.

## Slide 20: Calibrated vs Degree Day
Different loads will be applied to each customer
Chart: Load vs Temperature
| 2 | 4 | 42 | 23 | 6 | 9 | 33 | 15 | 8 | 10 | 18 | 16 | 12 | 12 | 15 | 13 | 20 | 25 | 24 | 26 | 31 | 28 | 35 | 33 | 34 | 38 | 36 | 40 | 44 | 43 | 45 | 48 | 51
 | 0.1 | 0.23 | 0.63 | 0.35 | 0.1658 | 0.19 | 0.47 | 0.222 | 0.254 | 0.29 | 0.2994 | 0.32 | 0.3533 | 0.358 | 0.38 | 0.38 | 0.4444 | 0.48 | 0.53351 | 0.549 | 0.5555 | 0.56 | 0.62 | 0.654 | 0.68 | 0.6894 | 0.7766 | 0.789 | 0.88 | 0.75 | 0.79 | 0.83 | 0.85
heat
40 DD = 0.72 mcfh
58 DD = 0.99 mcfh
Peak DD
Calibrated DD
base

## Slide 21: System Modeling (cont.)
All customers are loaded based upon base and heat trend.
Growth model – works with design day model and customer growth numbers to simulate pressures and flows in the future.
Benefits of the models: - customer requests
- future planning
- system reliability
- optimizing potential reinforcement

## Slide 22: Synergi
Theoretical low pressure scenario

## Slide 23: Capacity Enhancement Options
Pipes:
- replacements
- reinforcements
- loops
Regulator Stations
Compressors

## Slide 24: Pipe Enhancements
Pros
Reliable capacity
Low maintenance
Permanent
Can be expensive
Potential land acquisition/permitting issues
Cons

## Slide 25: Reg Station Upgrades/Installs
Pros
Adds source pressure to alternate system location
Increases flow control
Increases pressure control
Long term regulator and valve maintenance
High installation/fabrication costs
Potential land acquisition issues
Cons

## Slide 26: Compressor Stations
Pros
Adding capacity at lower initial cost
Less land required
Situational operation
Continuous maintenance/training
Cost of fuel consumption
Emissions/permitting
Beneficial only on transmission type lines
Cons

## Slide 27: Synergi
Low pressure scenario
Compressor station infeasible
Other Solutions?
REGS?
PIPE?

## Slide 28: Synergi
Possible solutions – raising reg station set points

## Slide 29: Synergi
Reinforcement option #1

## Slide 30: Synergi
Reinforcement option #2


## Slide 31: Project Process Flow
Info & Data
Project & Schedules

## Slide 32: CNG Future Projects
Example upcoming growth projects
Location | 2017 | 2018 | 2019
Stanwood 4” Reinforcement | $116,130 |  | 
Manchester 4” Reinforcement |  | $245,870 | 
South Walla Walla Gate & HP Line |  | $3,356,259 | $2,190,610

## Slide 33: Stanwood 4” pe reinforcement
2017 project
1550’ of 4” PE
Anticipating low pressure
Allow for growth to the north and east
Potential Growth

## Slide 34: Stanwood 4” pe reinforcement
Design day pressure before/after

## Slide 35: Manchester 4” pe reinforcement
2018 project
5100’ of 4” PE
Low pressure at the end of system
Allow for growth to the north and east
Potential Growth
Potential Growth

## Slide 36: Manchester 4” pe reinforcement
Design day pressure before/after

## Slide 37: Walla Walla Gate & HP Line
2018 and 2019 project
Growth noted in SE Walla Walla
Upgrade will introduce much more capacity to the system
Potential Growth

## Slide 38: Walla Walla Gate & HP Line
Model pressure before/after project

## Slide 39: Conclusion
CNGC strives to use technology to gather data, analyze, plan, and design a reliable, safe and economical distribution system.
¿ QUESTIONS ?

## Slide 40: SENDOUT OPTIMIZATION MODELING
Mark Sellers-Vaughn, Manager Resource Planning
Brian Robertson, Senior Resource Planning Analyst
Devin McGreal, Resource Planning Analyst I
Technical Advisory Group
September 15th, 2016

## Slide 41: SENDOUT model
Cascade utilizes SENDOUT™ for resource optimization.
This model permits the Company to develop and analyze a variety of resource portfolios to help determine the type, size, and timing of resources best matched to forecast requirements.
SENDOUT™ is very powerful and complex. It operates by combining a series of existing and potential demand side and supply side resources and optimizes their utilization at the lowest net present cost over the entire planning period for a given demand forecast.

## Slide 42: SENDOUT model
SENDOUT™ utilizes a linear programming approach.
The model knows the exact load and price for every day of the planning period based on the analyst’s input and can therefore minimize costs in a way that would not be possible in the real world.
Therefore, it is important to acknowledge that linear programming analysis provides helpful but not perfect information to guide decisions.

## Slide 43: Modeling Transportation In SENDOUT® IS A BALANCING ACT OF REALITY AND SUBJECTIVE APPLICATION
79
Start with a point in time look at each jurisdiction’s resources.
We start with the Nov16-Oct17 PGA portfolio.
Contracts –Receipt and Delivery Points
We start with current transport contracts, using centralized receipts and approx. 66 delivery locations.
Rates
Current contractual, with CPI increase every 3 years
Contractual vs. Operational
Contractual can be overly restrictive.
Operational can be overly flexible.
Incorporating operational realities into our modeling can defer the need to acquire new resources.
Gas Supply’s job is to get gas from the supply basin to the pipeline citygate.
IRP focus is on the core.
Operations job is to take gas from the pipeline gate to our customers.
Operations focus is on the system, not just the core.
Limiting factor is receipt quantity –how much can you bring into the system?

## Slide 44: Modeling Challenges
Supply needs to get gas to the citygate.
Many of our transport agreements were entered into decades ago, based on demand projections at that point in time.
Sum of receipt quantity and aggregated delivery quantity can help identify resource deficiency depending on how you allocate the rights.
The aggregated look can mask individual city gate issues for looped sections, and the disaggregated look can create deficiencies where they don’t exist.
In many cases operational capacity is greater than contracted.
SENDOUT has perfect knowledge.

## Slide 47: Base Case Sendout Inputs
Supply
Storage
Transportation
Demand
Price Forecast
Weather

## Slide 48: Supply
Cascade can purchase gas at 3 markets; AECO, SUMAS, and OPAL.
At each market Cascade can purchase gas at different locations along the pipeline.
For the first year, Cascade uses all current contracts for Supply inputs.
For years 2-20, Cascade uses Base, Fixed, Winter base, Summer and Winter day gas, and Peak day incremental supplies as inputs.
The contracts for years 2-20 are renewed in November and April.

## Slide 49: Supply

## Slide 50: Supply Base and Fixed
Supply Base and Fixed are the baseline supply contracts that are contracted every 12 months.
A base contract has a basis rate. This is defined as the price of gas at a given market (ie, AECO base is the expected cost of gas at NYMEX plus the basis for AECO, for a given month).
A fixed contract has a fixed rate.
A penalty is applied to each contract when the contracted amount of gas is not taken for a day. This type of penalty forces these types of contracts to take the optimal amount of gas to serve the base demand.

## Slide 51: Supply Example

## Slide 52: Base Supply cont’d

## Slide 53: Winter base Supply
Winter base supply is contracted supply with a premium charge that is slightly higher than base gas.
The Maximum Daily Quantity (MDQ) is optimally set by SENDOUT.
Winter supply is renewed every November and completes at the end of March.
Winter Supply is additional baseline supply on top of the base or fixed supplies for the winter months.
There is a penalty associated to this contract to force SENDOUT to take the optimal amount of additional winter base gas.

## Slide 54: Winter base Supply cont’d

## Slide 55: Day Supply (Winter)
Winter Day supply is gas that is R-mixed at the beginning of November each year.
The R-mix function takes into account the fixed and variable costs of a resource to determine the proper amount to take in a given period.
Winter day gas has a MDQ cap but is not a must take supply.
If a winter day supply has an MDQ of 10000 dth then it can take anywhere from 0 to 10000 dth’s of gas on any given day in the winter.
Winter day supply has a slightly higher premium than winter base supply and it can be contracted from November to April.

## Slide 56: Day Supply (Winter) cont’d

## Slide 57: Day Supply (Summer)
Summer day supply is gas that is R-mixed at the beginning of April each year.
Summer day gas has a MDQ cap but is not a must take supply.
If a summer day supply has an MDQ of 10000 dth then it can take anywhere from 0 to 10000 dth’s of gas on any given day in the summer.
Summer day supply has a slightly lower cost than base supply and it can be contracted from April to November.

## Slide 58: Day Supply (Summer)

## Slide 59: Peak Supply
Peak supply is gas purchased on high demand days where base, index, winter base, or day supply cannot accommodate.
Peak supply has a slightly higher premium to buy than day supply.
As long as Cascade has the transport capacity, we can purchase as much peak supply as needed to meet peak demand.

## Slide 60: Total Supply

## Slide 61: Storage
Cascade leases storage at 2 locations: Jackson Prairie (JP) and Plymouth.
Cascade has 4 storage contracts with JP and 2 contracts with Plymouth.
Storage injections targets are set at 35% by the end of June, 80% by the end of August, and 100% by the end of September.
These targets are set by our Gas Supply Oversight Committee.
Cascade can withdrawal approximately 56,000 dth’s per day from JP and 78,000 dth’s per day from Plymouth for a total of approximately 134,000 dth’s per day.

## Slide 62: Storage Example

## Slide 63: Storage Example 2

## Slide 64: Transportation
Transportation contracts are the means of how Cascade gets the gas from the supplier to the end user.
Cascade has multiple types of transportation:
  A single delivery point.
  Multiple delivery points.
The multiple delivery point contracts gives Cascade the flexibility to move the gas where it’s most needed.
On NWP, transportation goes to the zone level because MDDO’s can be reallocated within a zone to the Citygate.
On GTN, transportation goes to the Citygate level as MDDO’s cannot be reallocated within the GTN zone.

## Slide 65: Transportation cont’d
Transportation has an MDQ, a D1 rate, a transportation rate, and a fuel loss percentage.
A maximum delivery quantity (MDQ) which is the maximum amount of gas Cascade can move on the pipeline on a single day.
A D1 rate which is the reservation rate to have the ability to move the MDQ amount on the pipeline.
A transportation rate which is the rate per dekatherm that is actually moved on the pipeline.
The fuel loss percentage is the statutory percent of gas based on the tariff from the pipeline that is lost and unaccounted for from the point of where the gas was purchased to the Citygate.

## Slide 66: Transport Example

## Slide 67: Transport Example

## Slide 68: Delivery Rights vs Receipt Rights
Cascade has more Delivery Rights than Receipt Rights.
Approximately 457,000 Dth of Delivery Rights.
Approximately 360,000 Dth of Receipt Rights.
The excess Delivery Rights allow Cascade to be flexible with the 360,000 Dth of Receipt gas.

## Slide 69: Example of delivery right flexibility
All of the following must be true

## Slide 70: Example of delivery right inflexibility
2.5 MDTs
1 MDT
0.5 MDTs

## Slide 71: Location of Zones

## Slide 72: Zone 26 on Peak Day for Transport 135558

## Slide 73: Zone 30-S on Peak Day for Transport 135558

## Slide 74: Zone 30-W on Peak Day for Transport 135558

## Slide 75: Transport Contract 135558 on Peak Day

## Slide 76: Example of delivery right flexibility

## Slide 77: Demand Behind the Gate
Cascade has strived over the last several years to make the IRP forecast and resource analysis to get to as granular a level as possible using the available data.
Attempts to forecast demand behind the gate using existing forecasting methodology has been challenging.
Customer billing data does not have daily meter reads for core customers making regression analysis on a use per HDD per customer difficult.
Given Cascade is not a contiguous system, DSM by gate is currently is an ongoing complication
  This year we have added the Climate Zone
  Future IRPs will try and address the gate station level
Some towns can be served by multiple pipelines and the mix can change over time.
As part of the rate case settlement, Cascade is committed to performing a robust citygate study.
Notes: AFTER INTRODUCTIONS REVIEW THE AGENDA
Ask: Are there any questions about the plan for the afternoon?

## Slide 78: Demand
Demand is forecasted at the Citygate level by rate schedule.
For NWP, each Citygate’s demand is associated with the zone.
For GTN, each Citygate’s demand is associated with it’s respective Citygate interconnect.
Demand Inputs
  Forecast type (Monthly amount or Regressions)
  Monthly projected customers for 20 years.
  Regression coefficients if using the Regression forecast type.
  If using a monthly number, it is the 2015 demand for that month with a growth factor.

## Slide 79: Demand Example

## Slide 80: Demand Example 2

## Slide 81: Weather
Weather inputs for SENDOUT include:
  Monte Carlo
  Historical
  Normal
Monte Carlo inputs include mean, standard deviation, max and minimum.
Historical data is used to build weather profiles for Monte Carlo.
Normal weather is the daily average of the 30-year most recent history (1986-2015).

## Slide 82: Weather Example – Monte Carlo

## Slide 83: Long Range Price Forecast
Cascade’s long term planning price forecast is based on a blend of current market pricing along with long term fundamental price forecasts.
The fundamental forecasts include Wood Mackenzie, the Energy Information Administration (EIA), the Northwest Power Planning Council, Bentek and the Financial Forecast Center’s long term price forecasts.
Market, particularly in near term is heavily influenced by Henry Hub prices.
While not a guarantee of where the market will ultimately finish, Henry Hub NYMEX is the most current information that provides some direction as to future market prices.

## Slide 85
Base Weights in Draft 2016 IRP Price Forecast

## Slide 87
Chart: 20 YEAR PRICE FORECAST - NORMAL

## Slide 88: Major resource issues on the horizon
Addition alternatives to be considered during IRP process
  NWP I-5 Expansion
  Realignment of MDDOs to citygates
  Palomar/Cross Cascades
  Pacific Connector
  Incremental Nova
  Incremental Foothills
  Incremental GTN (north to south)
  Biofuel
  Satellite LNG
  Mist Storage
  AECO Storage
  Wild Goose Storage
  Gill Ranch Storage
  Ryckman Creek Storage
Began discussions with Niska Partners to gather information to model AECO Hub Storage in the 2016 IRP. In addition, we will be considering Wild Goose, Gill Ranch, Mist and Ryckman Creek storage.
Working with GTN to develop a narrative to explain how our long path capacity can be used to meet peak day shortfalls.

## Slide 89: SENSITIVITIES ANALYSES
Scenario Name | Key Assumptions
High Growth | Strong Economic Growth result in High Load growth, Average Weather, Medium Gas Prices.
Low Growth | Economic Conditions result in Low Load growth, Average Weather, Medium Gas Prices.
Environmental Externalities Carbon 1 | Medium Load Growth, Average Weather, Assumes Carbon Adder Implemented in 2018 for CO2 emissions at $10/ton with adder increasing annually by 3% plus CPI (Consumer Price Index).
Environmental Externalities Carbon 2 | Medium Load Growth, Average Weather, Assumes Carbon Adder Implemented in 2016 for CO2 emissions at $20/ton with adder increasing annually by 3% plus CPI (Consumer Price Index).
Environmental Externalities Carbon 3 | Medium Load Growth, Average Weather, Assumes Carbon Adder Implemented in 2017 for CO2 emissions at $30/ton with adder increasing annually by 3% plus CPI (Consumer Price Index).

## Slide 90: Supply Side Alternatives Modeled

## Slide 100
Chart: Potential Unserved 2025
| DEM AbrdnHoq | DEM Acme | DEM Advensch | DEM AMRender | DEM Arlingtn | DEM Athena | DEM Baker | DEM BendLop | DEM BrBkHLop | DEM BrmShelt | DEM CastleRk | DEM Chem | DEM Dehandry | DEM Deming | DEM EStwdLop | DEM Finley | DEM Gilc | DEM Grdvew | DEM Hrmston | DEM Huntgton | DEM Kalama | DEM Kalama2 | DEM KnwckLop | DEM Lapi | DEM Lawrence | DEM LDSChurc | DEM Madr | DEM MilFree | DEM Mission | DEM MosLake | DEM Moxee | DEM NPasco | DEM NyssaOnt | DEM Othello | DEM Paterson | DEM Pendletn | DEM Prong | DEM Prosser | DEM Prvl | DEM Quincy | DEM Redm | DEM SedroLop | DEM SLongLop | DEM SmsSPLop | DEM StanTap | DEM Stea | DEM Sunside | DEM Topenish | DEM Umatilla | DEM Walla | DEM Wenatche | DEM Woodland | DEM YakChFrm | DEM YakFirCr | DEM YakmaLop
2025 Demand | 5816.6587 | 110.2513 | 21.2708 | 337.3962 | 6021.6991 | 509.8074 | 4480.9036 | 50520.3389 | 7669.5339 | 38647.6492 | 166.1612 | 60.5719 | 1.5436 | 210.2419 | 10470.8489 | 199.9758 | 309.5943 | 2051.7064 | 7927.6085 | 132.8069 | 1.0879 | 531.0338 | 32456.2289 | 694.7487 | 83.649 | 13.7713 | 3778.392 | 631.0493 | 624.7162 | 3063.883 | 1374.9556 | 7878.1516 | 6978.8618 | 2493.5421 | 122.7037 | 7829.2259 | 599.3399 | 1052.1655 | 4723.4268 | 654.7904 | 12449.7078 | 32593.8053 | 5634.6805 | 55228.9728 | 316.6839 | 6411.2611 | 3750.623 | 4370.2154 | 1450.6433 | 18653.7277 | 5207.5059 | 1451.6235 | 0.64049 | 421.3769 | 33559.0396
2025 Served | 5816.6587 | 110.2513 | 21.2708 | 337.3962 | 6021.6991 | 509.8074 | 4480.9036 | 40719.8834 | 7669.5339 | 38647.6492 | 166.1612 | 60.5719 | 1.5436 | 210.2419 | 10470.8489 | 199.9758 | 309.5943 | 2051.7064 | 7927.6085 | 132.8069 | 1.0879 | 531.0338 | 32456.2289 | 203.6528 | 83.649 | 13.7713 | 2408.9997 | 631.0493 | 624.7162 | 3063.883 | 293.2827 | 7878.1516 | 6978.8618 | 2493.5421 | 122.7037 | 7829.2259 | 599.3399 | 1052.1655 | 3810.9996 | 416.9412 | 12015.7762 | 32593.8053 | 5634.6805 | 55228.9728 | 232.0001 | 5375.598 | 3750.623 | 4370.2154 | 1450.6433 | 18653.7277 | 2861.0054 | 1451.6235 | 0.64049 | 421.3769 | 30132.2505
2025 Unserved | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9800.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 491.0959 | 0 | 0 | 1369.3923 | 0 | 0 | 0 | 1081.6729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912.4272 | 237.8491 | 433.9316 | 0 | 0 | 0 | 84.6838 | 1035.6631 | 0 | 0 | 0 | 0 | 2346.5005 | 0 | 0 | 0 | 3426.7892

## Slide 101: Net Present Value of 20 Year Portfolio

## Slide 102: Preliminary Scenario NPV

## Slide 103: 2016 IRP Timeline

## Slide 104: NEXT STEPS?

## Slide 105: Cascade Natural Gas Corporation Integrated Resource Plan Technical Advisory Group Meeting #4
Thursday, September 15th, 2016
Seattle-Tacoma International Airport Conference Center