EXHIBIT NO. ___(JAB-1T)
DOCKET NO. UE-141335
WITNESS:  JENNIFER A. BOYER

BEFORE THE

WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION

| In the Matter of the Petition of: King County, Washington; BNSF Railway; Frontier Communications Northwest, Inc.; Verizon Wireless; and New Cingular Wireless PCS, LLC. For a Declaratory Order |  | Docket No. UE-141335 |
| --- | --- | --- |

PREFILED DIRECT TESTIMONY (NONCONFIDENTIAL) OF 
JENNIFER A. BOYER
ON BEHALF OF PUGET SOUND ENERGY, INC.

NOVEMBER 19, 2014

PUGET SOUND ENERGY, INC.

PREFILED DIRECT TESTIMONY
(NONCONFIDENTIAL) OF JENNIFER A. BOYER

Q.	Please state your name, business address and position with Puget Sound Energy, Inc. (“PSE”).

A.	My name is Jennifer A. (“Jenny”) Boyer, my business address is 355 110th Street NE, Bellevue, Washington, 98009-5591.  I am Manager, Electric Operations, at PSE.

Q.	Have you prepared an exhibit describing your professional qualifications?

A.	Yes, I have.  It is Exhibit No. ___(JAB-2).

Q.	What is the nature of your prefiled direct testimony in this proceeding?

A.	This prefiled direct testimony describes the facilities known as the Maloney Ridge line.  I will also discuss the engineering issues and challenges related to serving the customers on the Maloney Ridge line, and I will discuss options for service that PSE has investigated.

Q.	Please describe the facilities known as the Maloney Ridge line.

A.	The Maloney Ridge line is a cable underground distribution line 8.5 miles long, located in a remote section of the Snoqualmie National Forest.  It was built in or around 1971 pursuant to an Agreement Relating to the Extension of Electrical Service, dated September 23, 1971, between PSE and the General Telephone Company of the Northwest, Inc. (“GTE”), wherein GTE requested PSE to extend single phase electric service to GTE’s microwave station.  Lynn F. Logen describes this agreement, and subsequent agreements, more fully in his Prefiled Direct Testimony, Exhibit No. ___(LFL-1T).

The Maloney Ridge line originates at a pole located at approximately 10004 Foss River Road NE, in Skykomish, Washington.  Skykomish substation has a 9.37 MVa transformer, which transforms the voltage from the transmission voltage of 115 kV three-phase to the distribution feeder voltage of 12.5 kV three-phase, and a 75 MVa, 12.5 kV, three phase regulator.  The Maloney Ridge line itself is a single phase (7.2 kV) jacketed underground cable.

Q.	Is this a typical system configuration for PSE?

A.	This was generally a normal cable construction for the time it was installed.  If constructed today, the line would be constructed differently.  For instance, the cable would be placed in conduit, the cable itself would be constructed of longer-lasting (more  modern) material, and PSE would install more junction boxes, which would allow smaller sections to be replaced as needed, should cable failure occur.

Q.	Please describe the terrain in the area of the Maloney Ridge line.

A.	The 8.5 miles containing the Maloney Ridge line is steep, rugged, mountainous terrain that includes boulders, creeks and rivers.  It is covered in heavy snowpack several months out of each year, and access is usually limited from early October through early July.  Photos of the terrain taken in the summer are provided in the Second Exhibit to the Prefiled Direct Testimony of Jason M. Sanders, Exhibit No. ___(JMS-3).

Q.	Please describe the current quality of electrical service on the Maloney Ridge line.

A.	The quality of service is subjective, but the line does experience frequent cable faults.  A summary of faults on the line is provided as Exhibit No. ___(JAB-3).  These faults are caused by several factors.  Primarily, the cable is simply reaching the end of its useful life.  Additionally, the cable was constructed with material that is no longer used because it is not as reliable as other products.  Over the years, PSE has installed splices to repair portions of the cable.  These splices add a potential for degradation of cable integrity.  Each time a fault occurs on the system, the cable experiences “fault current”, which can itself degrade the insulation over time, leading to additional faults.

Further, the terrain itself contributes to faults due to the movement of earth and rocky material.  Rockslides and other rock movement are common on the steep slopes of Maloney Ridge, and these can cause direct damage to, and degradation of, the cable.  Additionally, shifts in the terrain (including rock and landslides) expose the cable to dig-ins and rock damage.

Q.	Please describe how PSE currently responds to a fault or other maintenance issue on the line.

A.	Before resolving an outage on the Maloney Ridge line, PSE must assesses the current conditions affecting the safety of their personnel and the personnel of its contractor, Potelco.  For instance, in the winter months (after snowfall), PSE does not respond during the night because of visibility issues.  In these cases, the Maloney Ridge customers are able to use back-up generators, which they have.  PSE first responds by sending service linemen to the site to investigate the cause of the outage.  During the winter, this involves using special equipment like a snow cat.  Some of the equipment used to identify the location of a fault is audio.  Therefore, snow, rain or other weather conditions can impair a lineman’s ability to identify the location of the fault.

Once the fault is identified, a crew must dig to the location of the fault before repairing it.  This may involve a backhoe or hand-digging, if a backhoe cannot reach the location.  When faults have occurred in very steep or otherwise less accessible locations,  repair times are greatly extended.

Q.	Has PSE identified options to improve the service on the Maloney Ridge line?

A.	Yes, I was involved in identifying five different options presented to the Maloney Ridge line customers in March 2013.  These options include replacing portions of the line with new material and replacing the entire line.  The options are presented the in the Third Exhibit to the Prefiled Direct Testimony of Jason M. Sanders, Exhibit No. ___(JMS-4).

Q.	Has PSE looked at alternatives besides those provided to the Maloney Ridge customers?

A.	Yes, in response to WUTC Staff’s inquiry, PSE analyzed the feasibility of a photovoltaic installation.  PSE also considered wind installation and combustion generators at the point of delivery.  PSE also considered installing an overhead distribution line.

Q.	What did PSE conclude?

A.	There are several challenges with each.  With regard to a photovoltaic installation, PSE conducted a basic review of the site conditions and determined that currently it would not be economically feasible to install a solar array of sufficient size to provide the electrical needs for the Maloney Ridge customers.  Due to snow pack and animal encounters, a solar array would need to be mounted several feet above ground and tipped, but this would reduce solar exposure.  Others issues such as battery back-up during winter months, snow shading, steep and uneven terrain, and the need to physically clear snow off the solar array led PSE to the initial determination that photovoltaic installation will not be economically feasible.

Regarding overhead lines, PSE determined it would be not be feasible due to worse weather-related reliability and difficult installation.  Overhead installation would require the construction of new, widened, or improved roads, as well as extensive tree removal (and U.S. Forest Service permits).

Regarding wind installation, for context, PSE’s Wild Horse wind farm performs at a 32 percent capacity factor.  So if the Maloney Ridge site had the same favorable wind characteristics as Wild Horse, the site would need a roughly 46 kW wind turbine.  Most customer-owned wind turbines, however, operate at 4 percent capacity or less in the Puget Sound region, so a 367 kW wind turbine would be likely required for Maloney Ridge.  More study on wind resource could be a logical next step compared to solar.  However, since the Maloney Ridge line is located in a National Forest, the U.S. Forest Service would have to provide a permit for a large scale wind turbine operation.

PSE and the Maloney Ridge customers explored the option of supplying power to Maloney Ridge customers with combustion generators at the points of delivery (e.g., diesel or propane), but these were discussions only and there was no formal analysis of initial construction and startup and average annual maintenance costs for such power.  There would likely be logistical restrictions or emissions permitting restrictions that could affect the viability of the option of supplying power to Maloney Ridge customers with combustion generators, but these details were not studied

Q.	Does this conclude your prefiled direct testimony?

A.	Yes, it does.