2005

Qualifying Storm Events

December 2, 2005

# Table of Contents

Table of Contents	2

Event Description	3

Date of event	3

Event Type	3

Service Areas Affected	3

Number of Customers Affected	3

Summary of System Impacts	3

Mobilization Summary	3

Major Event Day – Qualification	5

Qualified Events - 2005	5

Current Event – Calculation Detail	5

Cumulative list of events that have qualified	5

Event Restoration – Cost Summary	6

Restoration Cost Detail for December 2, 2005	6

YTD Storm Restoration Cost Detail – Through December 2, 2005	6

Detail Documents	7

Restoration Cost Detail – Current Event	8

SAIDI, SAIFI, CAIDI – Summary Report	9

Detailed List of Distribution Circuits with Outages	10

Terms, Codes and Definitions Used on Detail Reports	13

Newsprint Media Coverage	15

# Event Description

### Date of event

December 2nd, 2005

### Event Type

This was a moderate snow event, impacting the southern portion of Puget Sound Energy’s (PSE) electric service territory. Snow began to fall late in the night on Thursday, December 1st and continued until around daybreak, Friday morning, December 2nd.  While snow covered much of the region, the greatest accumulations occurred in and south of Enumclaw, in Pierce and Thurston Counties.

### Service Areas Affected

The majority of storm damage occurred in Pierce and Thurston Counties; however PSE also experienced a significant, though lesser number of outages across all other parts of our service area.

### Number of Customers Affected

28,185 customers lost power during the event.

### Summary of System Impacts

| Total Number of Outages | 254 |
| --- | --- |
| Distribution Circuits Totally Out | 12 |
| Distribution Circuits Partially Out | 242 |

| Transmission Circuits Affected | 1 |
| --- | --- |
| Substations Totally Off-line | 0 |

### Mobilization Summary

#### Operating bases

| Base | Date Opened | Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
| Pierce | 12/2/05 | 6:30am | 12/2/05 | 11:00pm |
| Thurston | 12/2/05 | 7:15am | 12/2/05 | 10:30pm |

#### Emergency Operations Center

| EOC | Date Opened | #### Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
|  | - | - | - | - |

# Major Event Day – Qualification

- IEEE 1366 Method

IEEE 1366 was established to present a set of terms and definitions which can be used to foster uniformity in the development of distribution service reliability indices, to identify factors which affect the indices, and to aid in consistent reporting practices among utilities.  Also, it provides guidance for new personnel in the reliability area, and tools for internal as well as external comparisons.  The Major Event Day definition was created as part of IEEE 1366 to allow for consistent calculation of reliability metrics between utilities, and enable more valid comparisons with other utility reliability metrics.

IEEE Major Event Day Calculation (2.5 BETA METHOD) - A threshold on daily SAIDI is computed once a year, following year end. - Assemble the 5 most recent years of historical values of SAIDI/day. - Discard any days in the data set that has a SAIDI/day of zero. - Find the natural logarithm of each value in the data set. - Compute the average Alpha and the standard deviation (Beta) of the natural logarithms computed in step 3. - Compute the threshold Tmed where Tmed = exp(Alpha + 2.5 * Beta) - Any day in the next year with SAIDI > Tmed is a major event day.

Puget Sound Energy’s Major Event Threshold for 2005: 4.88 Minutes

# Qualified Events - 2005

### Current Event – Calculation Detail

| Event Date | Total Customer Minutes | Average Customer Count | Daily SAIDI – Customer Minutes /Customer Count |
| --- | --- | --- | --- |
| 12/2/2005 | 6,841,750 | 1,025,044 | 6.67 (T-med) |

### Cumulative list of events that have qualified

| Date(s) | T-med Score | O&M – Deferrable Accumulation |
| --- | --- | --- |
| 3/20/2005 | 28.85 | $928,453 |
| 12/2/2005 | 6.67 | $243,617 |

# Event Restoration – Cost Summary

### Restoration Cost Detail by Qualifying Event

| Date | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M – Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| 03/20/05* | $81,999 | $0 | $76,071 | $928,453 | $1,004,524 | $1,086,523 |
| 12/02/05 | $23,091 | $0 | $26,587 | $243,617 | $270,204 | $293,295 |

* Costs reported for this storm on the 2005 Qualifying Storm Events report filed in June 2005 have been adjusted to reflect current accounting information.

### YTD Storm Restoration Cost Detail – Through December 2, 2005

| Catastrophic Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| $0 | $105,090 | $0 | $102,658 | $1,172,070 | $1,274,728 | $1,379,818 |

# Detail Documents

- Restoration Cost Detail – Current Event

SAIDI, SAIFI, CAIDI – Summary Report

- Detailed List of Distribution Circuits with Outages

- Terms, Codes & Definitions Used on Detail Reports

- Newsprint Media Coverage

| Restoration Cost Detail – Current Event |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Puget Sound Energy |  |  |  |  |  |  |  |  |
|  | December 2, 2005 Storm Damage Repair Costs |  |  |  |  |  |  |  |  |
|  |  | Catastrophic Deferred Account | Capital | C&D Recoverable from Direct Billings (Costs Not Yet Billed) | O&M - Not Deferrable | O&M - Deferrable Accumulation | Total O&M | Total |  |
|  | Labor |  |  |  |  |  |  |  |  |
|  | ST |  | $0 |  |  | $6,679 | $6,679 | $6,679 |  |
|  | OT |  | $384 |  |  | $27,164 | $27,164 | $27,548 |  |
|  | Total Labor | $0 | $384 | $0 | $0 | $33,843 | $33,843 | $34,227 |  |
|  | Labor OH |  | $260 |  | $6,313 | $12,483 | $18,796 | $19,056 |  |
|  | Materials |  | $4,863 |  | $3,129 | $7,845 | $10,974 | $15,837 |  |
|  | Contractors |  | $14,178 |  | $796 | $187,882 | $188,678 | $202,856 |  |
|  | Other Direct Charges |  | $0 |  |  | $63 | $63 | $63 |  |
|  | Fleet |  | $143 |  | $9,409 | $2,628 | $12,037 | $12,180 |  |
|  | Other Assessments |  | $3,263 |  | $6,940 | ($1,127) | $5,813 | $9,076 |  |
|  |  | $0 | $23,091 | $0 | $26,587 | $243,617 | $270,204 | $293,295 |  |

### SAIDI, SAIFI, CAIDI – Summary Report

|  | SAIDI SAIFI CAIDI |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | December 2 MAJ |  |  |  |  |  |  |  |  |
|  | Outage Cause |  | COUNT | C/MIN | C/OUT | SAIDI | SAIFI | CAIDI |  |
|  | ACCIDENT OTHER, WITH FIRES |  | 2 | 2,272 | 3 | 0.0022 | 0 | 757.3333 |  |
|  | BIRD OR ANIMAL |  | 6 | 31,743 | 215 | 0.0309 | 0.0002 | 147.6419 |  |
|  | CAR/POLE ACCIDENT |  | 5 | 395,372 | 1,800 | 0.3854 | 0.0018 | 219.6511 |  |
|  | CUSTOMER REQUEST |  | 1 | 110 | 1 | 0.0001 | 0 | 110 |  |
|  | DIG UP UNDERGROUND |  | 3 | 832 | 4 | 0.0008 | 0 | 208 |  |
|  | EQUIPMENT FAILURE |  | 149 | 4,387,239 | 13,281 | 4.277 | 0.0129 | 330.3395 |  |
|  | ELECTRICAL OVERLOAD |  | 9 | 1,217,780 | 2,436 | 1.1872 | 0.0024 | 499.9097 |  |
|  | LIGHTNING |  | 1 | 1,775 | 5 | 0.0017 | 0 | 355 |  |
|  | OUTSIDE DISTURBANCE;BPA LINES DOWN |  | 1 | 4,792 | 8 | 0.0047 | 0 | 599 |  |
|  | PARTIAL OUTAGE |  | 4 | 990 | 4 | 0.001 | 0 | 247.5 |  |
|  | SCHEDULED OUTAGE, WAS WR- WORK REQUIRED |  | 4 | 12,002 | 38 | 0.0117 | 0 | 315.8421 |  |
|  | TREE - OFF RIGHT OF WAY |  | 478 | 53,755,098 | 82,661 | 52.4045 | 0.0806 | 650.3079 |  |
|  | TREE - ON RIGHT OF WAY |  | 531 | 75,873,278 | 136,861 | 73.967 | 0.1334 | 554.382 |  |
|  | UNKNOWN CAUSE (UNK EQUIP INVOLVED ONLY) |  | 22 | 3,091,853 | 5,898 | 3.0142 | 0.0057 | 524.2206 |  |
|  |  | TOTALS | 1,216 | 138,775,136 | 243,215 | 135.2885 | 0.2371 | 570.5863 |  |
|  | Average Customer Count Used = 1,025,772 |  |  |  |  |  |  |  |  |

### Detailed List of Distribution Circuits with Outages

| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| E867570394 | 12/2/2005 | 0:05:00 | YEL-26 | ECC | EF | OFC | 22 | 13,926 |
| E369151284 | 12/2/2005 | 0:05:00 | BON-16 | ECA | TF | OCO | 2,108 | 314,443 |
| E818477429 | 12/2/2005 | 0:12:00 | PLG-01 | ECC | TO | OCO | 4,600 | 969,253 |
| E291055651 | 12/2/2005 | 0:18:00 | FAL-15 | EBF | TF | OCO | 791 | 526,941 |
| E749765895 | 12/2/2005 | 0:19:00 | CHA-15 | ECC | TO | OFC | 5 | 3,685 |
| E792131495 | 12/2/2005 | 0:36:00 | TLN-0021 | EBD | EF | OCO | 3,887 | 409,846 |
| E919536997 | 12/2/2005 | 0:40:00 | SWI-17 | ECC | TF | OSV | 1 | 378 |
| E606081658 | 12/2/2005 | 0:50:00 | PRI-21 | ECC | TO | OCO | 101 | 13,837 |
| E729342520 | 12/2/2005 | 0:52:00 | MAP-15 | EBF | TF | OTF | 1 | 240 |
| E824406159 | 12/2/2005 | 0:53:00 | SHD-18 | EBI | TO | OCO | 90 | 65,859 |
| E270985801 | 12/2/2005 | 0:55:00 | SHA-13 | ECA | TF | OCO | 1,716 | 451,308 |
| E151651357 | 12/2/2005 | 0:56:00 | YEL-25 | ECC | TO | OFC | 372 | 340,008 |
| E700783066 | 12/2/2005 | 0:57:00 | FRG-25 | ECC | TO | OCO | 16 | 7,328 |
| E647469850 | 12/2/2005 | 0:59:00 | FRA-13 | ECD | TO | OCO | 1,262 | 61,838 |
| E522523174 | 12/2/2005 | 1:06:00 | BDI-13 | EBI | CP | OTR | 4 | 2,496 |
| E291237536 | 12/2/2005 | 1:09:00 | RHO-16 | ECA | TF | OCO | 2,319 | 333,936 |
| E965247293 | 12/2/2005 | 1:12:00 | ORT-23 | ECA | TF | CDH | 15 | 13,215 |
| E583906747 | 12/2/2005 | 1:31:00 | BEL-17 | EBJ | TO | OFU | 3 | 503 |
| E111437982 | 12/2/2005 | 1:38:00 | GAR-16 | ECA | TO | OSV | 5 | 2,715 |
| E545584463 | 12/2/2005 | 1:39:00 | LON-23 | ECC | TF | OFU | 16 | 13,776 |
| E493508734 | 12/2/2005 | 1:42:00 | OSC-26 | EBI | TO | OCO | 7 | 3,563 |
| E596897555 | 12/2/2005 | 1:42:00 | WLK-13 | ECA | TF | OCO | 963 | 201,267 |
| E958011970 | 12/2/2005 | 1:43:00 | MIR-17 | EBF | EF | OTF | 3 | 546 |
| E538361715 | 12/2/2005 | 1:50:00 | LWS-15 | EBJ | TF | OFU | 1 | 132 |
| E334924550 | 12/2/2005 | 1:59:00 | GRV-15 | ECA | TO | OFU | 8 | 5,528 |
| E562311232 | 12/2/2005 | 2:02:00 | PAT-17 | ECC | TO | OCO | 72 | 18,216 |
| E249342975 | 12/2/2005 | 2:08:00 | PRI-23 | ECC | TO | OCO | 72 | 29,736 |
| E174430875 | 12/2/2005 | 2:14:00 | YEL-27 | ECC | TO | OCO | 1,609 | 280,744 |
| E422650785 | 12/2/2005 | 2:16:00 | NBE-13 | EBF | EF | OCO | 1 | 269 |
| E161330258 | 12/2/2005 | 2:16:00 | WAB-13 | EBI | EF | OFU | 1 | 161 |
| E690364881 | 12/2/2005 | 2:20:00 | MCA-13 | ECC | TO | OFC | 19 | 6,876 |
| E742920565 | 12/2/2005 | 2:23:00 | OSC-22 | EBI | TO | OFU | 59 | 12,538 |
| E358361887 | 12/2/2005 | 2:25:00 | HEM-17 | ECA | TO | DNO | 1 | 474 |
| E153376198 | 12/2/2005 | 2:34:00 | MIR-15 | EBF | TF | OCO | 90 | 13,215 |
| E517959559 | 12/2/2005 | 2:36:00 | ROC-17 | ECC | TO | OCO | 9 | 1,746 |
| E839018194 | 12/2/2005 | 2:39:00 | SOO-25 | EBI | TF | OCO | 6 | 2,790 |
| E321395274 | 12/2/2005 | 2:41:00 | BLU-13 | ECC | TO | OCO | 17 | 8,993 |
| E826697428 | 12/2/2005 | 2:43:00 | AIR-23 | ECC | TF | OCO | 28 | 3,976 |
| E077353657 | 12/2/2005 | 2:44:00 | TOL-17 | EBD | TF | OCO | 18 | 6,498 |
| E814621758 | 12/2/2005 | 2:44:00 | LEA-13 | EBI | EF | OSV | 1 | 106 |
| E060827794 | 12/2/2005 | 2:48:00 | KAP-15 | ECA | TO | CDH | 1 | 1,068 |
| E312607828 | 12/2/2005 | 2:50:00 | FCH-24 | ECA | TO | OFU | 3 | 1,125 |
| E451939087 | 12/2/2005 | 2:51:00 | ORT-22 | ECA | TF | CDH | 29 | 10,614 |
| E355825563 | 12/2/2005 | 3:01:00 | SHA-15 | ECA | TO | OCO | 2,525 | 343,400 |
| E424554961 | 12/2/2005 | 3:03:00 | BUC-16 | ECA | TO | CDH | 8 | 11,576 |
| E825362263 | 12/2/2005 | 3:03:00 | MIR-16 | EBF | TF | OCO | 28 | 2,576 |
| E685030312 | 12/2/2005 | 3:06:00 | SWI-15 | ECC | TF | OCO | 43 | 27,520 |
| E244826761 | 12/2/2005 | 3:08:00 | KAP-16 | ECA | TF | CDH | 36 | 29,772 |
| E154728359 | 12/2/2005 | 3:24:00 | PAT-15 | ECC | TO | OCO | 8 | 5,168 |
| E395721089 | 12/2/2005 | 3:28:00 | PRI-21 | ECC | TF | OFU | 4 | 888 |

| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| E827637022 | 12/2/2005 | 3:30:00 | TOL-15 | EBD | EF | UPC | 4 | 2,852 |
| E766164094 | 12/2/2005 | 3:44:00 | ENU-18 | EBI | TF | OCO | 5 | 2,270 |
| E850713264 | 12/2/2005 | 3:44:00 | MKI-14 | ECC | TF | OSV | 1 | 321 |
| E280073361 | 12/2/2005 | 3:51:00 | SOO-26 | EBJ | EF | OFU | 25 | 2,086 |
| E944513231 | 12/2/2005 | 4:08:00 | LLT-16 | EBD | TF | OCO | 2 | 294 |
| E931264027 | 12/2/2005 | 4:17:00 | FRA-13 | ECD | TO | OFU | 1 | 408 |
| E719214445 | 12/2/2005 | 4:20:00 | LOL-21 | ECD | TO | OCO | 20 | 2,412 |
| E173908198 | 12/2/2005 | 4:23:00 | VAS-23 | EBL | TO | OCO | 57 | 19,893 |
| E334558585 | 12/2/2005 | 4:26:00 | MKI-17 | ECC | TF | OCO | 460 | 202,860 |
| E431444652 | 12/2/2005 | 4:39:00 | FRU-22 | ECA | TF | OSV | 2 | 522 |
| E764761946 | 12/2/2005 | 4:41:00 | FRA-12 | ECD | TO | OCO | 4 | 692 |
| E190482002 | 12/2/2005 | 4:46:00 | LON-22 | ECC | TO | OCO | 41 | 38,909 |
| E325140241 | 12/2/2005 | 5:12:00 | WLK-13 | ECA | TF | OCO | 978 | 2,853 |
| E219483731 | 12/2/2005 | 5:15:00 | WLK-13 | ECA | TF | OCO | 543 | 123,804 |
| E862882272 | 12/2/2005 | 5:18:00 | LOL-23 | ECD | EF | OTF | 7 | 518 |
| E839408041 | 12/2/2005 | 5:19:00 | SHA-13 | ECA | TF | OCO | 1,716 | 368,940 |
| E391868472 | 12/2/2005 | 5:36:00 | LON-26 | ECC | TO | OCO | 13 | 3,926 |
| E582452998 | 12/2/2005 | 5:45:00 | KAP-13 | ECA | TF | OFU | 7 | 6,174 |
| E103967909 | 12/2/2005 | 5:47:00 | BON-16 | ECA | TO | OTR | 4 | 1,724 |
| E675268559 | 12/2/2005 | 5:51:00 | SHD-17 | EBJ | TO | OCO | 1 | 507 |
| E515914790 | 12/2/2005 | 5:56:00 | SHD-17 | EBI | TO | OFU | 889 | 287,278 |
| E150851455 | 12/2/2005 | 6:02:00 | OSC-22 | EBI | TO | OTF | 1 | 27 |
| E736128325 | 12/2/2005 | 6:07:00 | PIP-23 | EBI | TO | OFU | 3 | 300 |
| E377824396 | 12/2/2005 | 6:13:00 | BLU-16 | ECC | TF | OCO | 85 | 45,390 |
| E664463356 | 12/2/2005 | 6:20:00 | AIR-23 | ECC | TO | OPO | 24 | 18,360 |
| E581060824 | 12/2/2005 | 6:34:00 | PAT-17 | ECC | UN | OCO | 363 | 112,893 |
| E702353514 | 12/2/2005 | 6:36:00 | OSC-22 | EBI | TO | OCO | 10 | 3,300 |
| E360629075 | 12/2/2005 | 6:38:00 | MIR-13 | EBF | EF | OTF | 2 | 584 |
| E878291770 | 12/2/2005 | 6:50:00 | BON-15 | ECA | TF | OCO | 6 | 942 |
| E932390026 | 12/2/2005 | 7:01:00 | ROC-16 | ECC | CP | OPO | 1 | 477 |
| E084073400 | 12/2/2005 | 7:09:00 | NBE-15 | EBF | TF | OCO | 824 | 51,912 |
| E204557154 | 12/2/2005 | 7:17:00 | YEL-27 | ECC | UN | OCO | 3 | 1,152 |
| E307973388 | 12/2/2005 | 7:42:00 | OSC-23 | EBI | TO | OFU | 2 | 156 |
| E534668966 | 12/2/2005 | 8:02:00 | LWS-15 | EBJ | TF | OSV | 5 | 1,490 |
| E043876057 | 12/2/2005 | 8:10:00 | LWS-15 | EBI | CP | OCO | 1 | 709 |
| E318502540 | 12/2/2005 | 8:11:00 | WLK-15 | ECA | TF | OCO | 7 | 2,275 |
| E148461343 | 12/2/2005 | 8:22:00 | HOB-17 | EBI | TO | OTF | 1 | 212 |
| E386774747 | 12/2/2005 | 8:31:00 | MIR-17 | EBF | EF | OCO | 3 | 312 |
| E093454724 | 12/2/2005 | 8:46:00 | GAR-13 | ECA | TO | OCO | 30 | 6,120 |
| E081619241 | 12/2/2005 | 8:47:00 | AIR-26 | ECC | TO | OCO | 6 | 708 |
| E829173712 | 12/2/2005 | 8:48:00 | AIR-22 | ECC | UN | OCO | 18 | 2,106 |
| E748333132 | 12/2/2005 | 8:52:00 | NBE-16 | EBF | TF | OSV | 1 | 528 |
| E906956033 | 12/2/2005 | 8:54:00 | BRS-13 | EAC | EF | OTR | 4 | 2,424 |
| E915296651 | 12/2/2005 | 8:59:00 | TOL-17 | EBD | TF | OCO | 17 | 3,842 |
| E021209908 | 12/2/2005 | 9:06:00 | ORT-22 | ECA | TO | CDH | 25 | 6,575 |
| E649378029 | 12/2/2005 | 9:10:00 | PRI-23 | ECC | TO | OCO | 52 | 19,136 |
| E672017803 | 12/2/2005 | 9:29:00 | LLT-17 | EBD | TF | OCO | 8 | 1,216 |
| 10612714 | 12/2/2005 | 9:30:00 | FAL-15 | EBF | EF | OCO | 15 | 420 |
| E971112807 | 12/2/2005 | 9:35:00 | SHA-13 | ECA | TF | OFU | 20 | 9,180 |
| E820226927 | 12/2/2005 | 9:52:00 | NBE-13 | EBF | EF | OTF | 4 | 472 |
| E478855523 | 12/2/2005 | 9:53:00 | BDI-12 | EBI | TO | OFU | 9 | 1,953 |
| E981498102 | 12/2/2005 | 10:08:00 | ENU-17 | EBI | TO | OFU | 5 | 580 |
| E591486632 | 12/2/2005 | 10:15:00 | WOO-27 | ECA | TF | OCO | 1 | 595 |
| E752994996 | 12/2/2005 | 10:28:00 | FRG-15 | ECC | TO | OTF | 6 | 1,272 |
| E307238845 | 12/2/2005 | 10:37:00 | BLA-13 | EAA | EF | OJU | 46 | 8,648 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E852312907 | 12/2/2005 | 10:44:00 | YEL-26 | ECC | TO | OCO | 348 | 147,552 |
| E062987741 | 12/2/2005 | 10:45:00 | WOL-25 | ECC | TF | OFU | 1 | 270 |
| E526040656 | 12/2/2005 | 10:46:00 | GAR-12 | ECA | TF | OTF | 2 | 538 |
| E385467192 | 12/2/2005 | 10:47:00 | TAN-13 | ECC | TF | OTR | 2 | 1,070 |
| E529351136 | 12/2/2005 | 11:24:00 | DUV-15 | EBD | TF | OCO | 5 | 605 |
| E535767706 | 12/2/2005 | 11:26:00 | HAS-12 | ECF | EF | OTF | 6 | 276 |
| E855405187 | 12/2/2005 | 11:50:00 | MCA-16 | ECC | TO | OFU | 3 | 648 |
| E324859448 | 12/2/2005 | 11:51:00 | BLU-13 | ECC | TF | OFU | 1 | 141 |
| E455224362 | 12/2/2005 | 11:54:00 | PGA-13 | ECE | EF | ORE | 5 | 55 |
| E881993730 | 12/2/2005 | 12:08:00 | ELD-25 | ECC | TF | OFU | 1 | 187 |
| E389335653 | 12/2/2005 | 12:08:00 | SWI-17 | ECC | TF | OCO | 3 | 690 |
| E103129934 | 12/2/2005 | 12:14:00 | RHO-17 | ECA | TF | OCO | 1,229 | 665,885 |
| E058491521 | 12/2/2005 | 12:16:00 | PAT-17 | ECC | TF | OCO | 7 | 196 |
| E280859468 | 12/2/2005 | 12:25:00 | LON-26 | ECC | TO | OFC | 15 | 3,825 |
| E149593768 | 12/2/2005 | 12:27:00 | MIR-17 | EBI | EF | OTF | 1 | 123 |
| E211622058 | 12/2/2005 | 12:40:00 | FWD-13 | EBJ | TF | OCO | 2 | 657 |
| E843682793 | 12/2/2005 | 12:43:00 | FRG-16 | ECC | TF | OSV | 3 | 228 |
| E505916765 | 12/2/2005 | 12:47:00 | HEM-16 | ECA | TF | OCO | 2 | 746 |
| E352435216 | 12/2/2005 | 12:49:00 | RHO-15 | ECA | TO | OFU | 6 | 1,248 |
| E485173329 | 12/2/2005 | 13:04:00 | PLU-24 | ECC | TF | OCO | 92 | 4,416 |
| E643686173 | 12/2/2005 | 13:28:00 | FCH-24 | ECA | TF | OTF | 3 | 675 |
| E504535306 | 12/2/2005 | 14:00:00 | OSC-22 | EBI | TO | OFU | 10 | 370 |
| E245989052 | 12/2/2005 | 14:01:00 | SHD-18 | EBI | TO | OTF | 115 | 21,965 |
| E976045820 | 12/2/2005 | 14:16:00 | GAR-13 | ECA | TF | OCO | 8 | 4,790 |
| E531996237 | 12/2/2005 | 14:23:00 | ORT-22 | ECA | TF | OCO | 3 | 1,761 |
| E076576076 | 12/2/2005 | 14:52:00 | GWR-13 | EBI | TF | OFU | 3 | 222 |
| E113824642 | 12/2/2005 | 15:15:00 | OSC-22 | EBI | TO | OFU | 6 | 694 |
| E336172209 | 12/2/2005 | 15:30:00 | EDG-13 | ECA | TO | OTF | 3 | 435 |
| E114593102 | 12/2/2005 | 15:39:00 | BLU-16 | ECC | TO | OFU | 8 | 568 |
| E648538954 | 12/2/2005 | 15:40:00 | SHD-17 | EBI | EF | OTF | 2 | 507 |
| E880198501 | 12/2/2005 | 15:42:00 | YEL-23 | ECC | TO | OFU | 2 | 126 |
| E264594225 | 12/2/2005 | 15:53:00 | ORT-23 | ECA | EF | OFU | 15 | 3,555 |
| E899996737 | 12/2/2005 | 16:08:00 | PRI-23 | ECC | TO | OTR | 2 | 670 |
| E303631410 | 12/2/2005 | 16:25:00 | ORT-23 | ECA | TF | OCO | 16 | 6,800 |
| E359172502 | 12/2/2005 | 16:55:00 | PAT-15 | ECC | TF | OSV | 3 | 771 |
| E394874640 | 12/2/2005 | 17:12:00 | GRI-15 | ECC | TO | OTR | 2 | 606 |
| E330613739 | 12/2/2005 | 17:54:00 | KAP-16 | ECA | EF | OSV | 3 | 1,478 |
| E707991212 | 12/2/2005 | 18:28:00 | BCH-12 | EAA | EF | OFU | 15 | 1,950 |
| E531363055 | 12/2/2005 | 18:39:00 | BLU-16 | ECC | TO | OCO | 2 | 178 |
| E396935770 | 12/2/2005 | 18:45:00 | FCH-24 | ECA | TF | OSV | 1 | 85 |
| E057763297 | 12/2/2005 | 18:54:00 | YEL-26 | ECC | TO | OCO | 2 | 178 |
| E599544102 | 12/2/2005 | 19:17:00 | CAP-15 | ECC | EF | OTF | 2 | 66 |
| E364457003 | 12/2/2005 | 19:18:00 | LAC-17 | ECC | TO | OAR | 42 | 2,604 |
| E636118694 | 12/2/2005 | 19:22:00 | BLA-12 | EAA | TF | UPC | 25 | 6,425 |
| E860459490 | 12/2/2005 | 19:34:00 | SIN-22 | ECD | EF | OTF | 3 | 177 |
| E529737847 | 12/2/2005 | 20:06:00 | MIR-17 | EBF | EF | OTF | 2 | 165 |
| E834092825 | 12/2/2005 | 20:34:00 | SHD-18 | EBI | TF | OTF | 2 | 408 |
| E390667577 | 12/2/2005 | 20:52:00 | YEL-26 | ECC | TO | OCO | 3 | 552 |
| E339963324 | 12/2/2005 | 21:17:00 | LON-22 | ECC | TO | OCO | 10 | 290 |
| E059113929 | 12/2/2005 | 22:17:00 | PAT-15 | ECC | EF | UPT | 3 | 1,202 |

### Terms, Codes and Definitions Used on Detail Reports

| #### Number | [Notification Number] A number assigned by SAP, identifying the outage record |  |
| --- | --- | --- |
| Date | The date of the outage |  |
| Time | The time of the outage |  |
| CKT | [Reference Circuit] The circuit identifier for the affected circuit |  |
| F/LOC | [Functional Location] The grid number where the outage occurred. If the grid number is not available, the Reference Circuit identifier occupies this field |  |
| EQT NBR | [Equipment Number] A number used to tie the equipment involved in the outage to the related information in SAP. This number does not represent the physical number of the equipment |  |
| MPG | [Maintenance Planner Group] A code representing the energy, region and service center |  |
|  | EAA – Bellingham | EBJ – South King |
|  | EAB – Lynden | EBK – Southwest King |
|  | EAC – Skagit | EBL – Vashon |
|  | EAD – Whidbey | ECA – Puyallup |
|  | EBD – Redmond | ECC – Olympia |
|  | EBE – Factoria | ECD – Port Orchard |
|  | EBF – Snoqualmie | ECE – Poulsbo |
|  | EBI – Enumclaw | ECF – Port Townsend |

| CAZ | Cause of Outage |  |
| --- | --- | --- |
|  | AO – Accident Other | EF – Equipment Failure |
|  | BA – Bird or Animal | EO – Electrical Overload |
|  | CP – Car Pole | TF – Tree Off Right-of-Way |
|  | CR – Customer Request | TO – Tree On Right-of-Way |
|  | DU – Dig-up Underground | UN – Unknown |
|  | SO – Scheduled Outage |  |

| EQT | [Equipment] Affected by, or involved in the outage |  |
| --- | --- | --- |
|  | OCN – Connector | OSW – Overhead Switch |
|  | OCO – Overhead Conductor | OTF – Overhead Transformer Fuse |
|  | OCR – Crossarm | OTR – Overhead Transformer |
|  | OFC – Overhead Cut-out | OUP – OH to UG Primary |
|  | OFS – Overhead Fire Signal | OUS – OH to UG Secondary Service |
|  | OFU – Fuse Link/OH Line Fuse | SBF – High-side Bank Fuse |
|  | OGS – Span Guy | SCB – Power Circuit Breaker |
|  | OHR – Overhead Recloser | UOT – Underground Outdoor Term |
|  | OIN – Insulator | UPC – Underground Primary Cable |
|  | OJU- Jump Wire | UPT – Padmount Transformer |
|  | OPO – Pole | USV – Underground Service |
|  | OSV – Overhead Service | UTC – Underground Terminal Fuse |
|  | ORE – Regulator | UTR – Submersible Transformer |

#### Codes, Definitions – Continued

| C/OUT | [Customer Out] The number of customers without power for any given outage record |
| --- | --- |
| C/MIN | [Customer Minutes] The total number of minutes customers were without power for any given record |

| CODE | [Storm Code] An event descriptor |
| --- | --- |
|  | NON – Non Storm / Normal Conditions |
|  | WTH – Weather Related (eg: wind storm, showers, etc) |
|  | MAJ – Major event |

### Newsprint Media Coverage

No articles for this event.