2005

Qualifying Storm Events

December 25, 2005

# Table of Contents

Table of Contents	2

Event Description	3

Date of event	3

Event Type	3

Service Areas Affected	3

Number of Customers Affected	3

Summary of System Impacts	3

Mobilization Summary	3

Major Event Day – Qualification	5

Qualified Events - 2005	5

Current Event – Calculation Detail	5

Cumulative list of events that have qualified	5

Event Restoration – Cost Summary	6

Restoration Cost Detail by Qualifying Event	6

YTD Storm Restoration Cost Detail – Through December 25, 2005	6

Detail Documents	7

Restoration Cost Detail – Current Event	8

SAIDI, SAIFI, CAIDI – Summary Report	9

Detailed List of Distribution Circuits with Outages	10

Terms, Codes and Definitions Used on Detail Reports	15

Newsprint Media Coverage	17

# Event Description

### Date of event

December 25, 2005

### Event Type

This was a brief, yet widespread wind storm on Christmas Day morning.  Beginning at 6:00a, winds gusted to nearly 40mph, causing electric outages in Kitsap, Jefferson, King, Skagit, Whatcom and Island counties before tapering-off mid morning.

### Service Areas Affected

Kitsap and Jefferson counties experienced the greatest storm damage, much of which was the result of trees falling across power lines. Record rainfall in Kitsap and Jefferson counties likely contributed to the number of trees that came down. A significant though lesser number of outages was experienced across the remaining parts of PSE’s electric service area.

### Number of Customers Affected

54,270 customers lost power during the event.

### Summary of System Impacts

| Total Number of Outages | 388 |
| --- | --- |
| Distribution Circuits Totally Out | 15 |
| Distribution Circuits Partially Out | 373 |

| Transmission Circuits Affected | 6 |
| --- | --- |
| Substations Totally Off-line | 2 |

### Mobilization Summary

#### Operating bases

| Base | Date Opened | Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
| S. King | 12/25/2005 | 6:40a | 12/25/2005 | 3:00p |
| Thurston | 12/25/2005 | 6:40a | 12/25/2005 | 3:45p |
| Kitsap | 12/25/2005 | 6:40a | 12/26/2005 | 5:30p |
| N. King | 12/25/2005 | 7:30a | 12/25/2005 | 6:00p |
| Skagit | 12/25/2005 | 9:30a | 12/25/2005 | 11:00p |

#### Emergency Operations Center

| EOC | Date Opened | #### Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
|  | 12/25/2005 | 6:50a | 12/26/2005 | 7:00a |

# Major Event Day – Qualification

- IEEE 1366 Method

IEEE 1366 was established to present a set of terms and definitions which can be used to foster uniformity in the development of distribution service reliability indices, to identify factors which affect the indices, and to aid in consistent reporting practices among utilities.  Also, it provides guidance for new personnel in the reliability area, and tools for internal as well as external comparisons.  The Major Event Day definition was created as part of IEEE 1366 to allow for consistent calculation of reliability metrics between utilities, and enable more valid comparisons with other utility reliability metrics.

IEEE Major Event Day Calculation (2.5 BETA METHOD) - A threshold on daily SAIDI is computed once a year, following year end. - Assemble the 5 most recent years of historical values of SAIDI/day. - Discard any days in the data set that has a SAIDI/day of zero. - Find the natural logarithm of each value in the data set. - Compute the average Alpha and the standard deviation (Beta) of the natural logarithms computed in step 3. - Compute the threshold Tmed where Tmed = exp(Alpha + 2.5 * Beta) - Any day in the next year with SAIDI > Tmed is a major event day.

Puget Sound Energy’s Major Event Threshold for 2005: 4.88 Minutes

# Qualified Events - 2005

### Current Event – Calculation Detail

| Event Date | Total Customer Minutes | Average Customer Count | Daily SAIDI – Customer Minutes /Customer Count |
| --- | --- | --- | --- |
| 12/25/2005 | 18,065,147 | 1,025,244 | 17.62 |

### Cumulative list of events that have qualified

| Date(s) | T-med Score | O&M – Deferrable Accumulation |
| --- | --- | --- |
| 3/20/2005 | 28.85 | $928,453 |
| 12/2/2005 | 6.67 | $244,418 |
| 12/17/2005 | 14.28 | $878,970 |
| 12/25/2005 | 17.62 | $1,118,316 |

# Event Restoration – Cost Summary

### Restoration Cost Detail by Qualifying Event

| Date | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M – Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| 03/20/2005 | $81,999 | $0 | $76,071 | $928,453 | $1,004,524 | $1,086,523 |
| 12/02/2005 | $23,091 | $0 | $27,907 | $244,418 | $272,325 | $295,416 |
| 12/17/2005 | $73,873 | $0 | $84,577 | $878,970 | $963,547 | $1,037,420 |
| 12/25/2005 | $54,585 | $0 | $95,258 | $1,118,316 | $1,213,574 | $1,268,159 |

### YTD Storm Restoration Cost Detail – Through December 25, 2005

| Catastrophic Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| $0 | $233,548 | $0 | $283,813 | $3,170,157 | $3,453,970 | $3,687,518 |

# Detail Documents

- Restoration Cost Detail – Current Event

SAIDI, SAIFI, CAIDI – Summary Report

- Detailed List of Distribution Circuits with Outages

- Terms, Codes & Definitions Used on Detail Reports

- Newsprint Media Coverage

### Restoration Cost Detail – Current Event

|  | Puget Sound Energy |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | December 25, 2005 Storm Damage Repair Costs |  |  |  |  |  |  |  |  |
|  |  | Catastrophic Deferred Account | Capital | C&D Recoverable from Direct Billings (Costs Not Yet Billed) | O&M - Not Deferrable | O&M - Deferrable Accumulation | Total O&M | Total |  |
|  | Labor |  |  |  |  |  |  |  |  |
|  | ST |  | $0 |  |  | $4,938 | $4,938 | $4,938 |  |
|  | OT |  | $250 |  |  | $145,165 | $145,165 | $145,415 |  |
|  | Total Labor | $0 | $250 | $0 | $0 | $150,103 | $150,103 | $150,353 |  |
|  | Labor OH |  | $95 |  |  | $51,742 | $51,742 | $51,837 |  |
|  | Materials |  | $6,448 |  |  | $43,358 | $43,358 | $49,806 |  |
|  | Contractors |  | $36,731 |  |  | $850,000 | $850,000 | $886,731 |  |
|  | Other Direct Charges |  | $0 |  |  | $864 | $864 | $864 |  |
|  | Fleet |  | $145 |  |  | $11,633 | $11,633 | $11,778 |  |
|  | Other Assessments |  | $10,916 |  | $95,258 | $10,616 | $105,874 | $116,790 |  |
|  |  | $0 | $54,585 | $0 | $95,258 | $1,118,316 | $1,213,574 | $1,268,159 |  |

### SAIDI, SAIFI, CAIDI – Summary Report

|  | SAIDI SAIFI CAIDI |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | December 25-26 |  |  |  |  |  |  |  |  |
|  | Outage Cause |  | COUNT | C/MIN | C/OUT | SAIDI | SAIFI | CAIDI |  |
|  | BIRD OR ANIMAL |  | 3 | 28,962 | 184 | 0.0282 | 0.0002 | 157.4022 |  |
|  | CAR/POLE ACCIDENT |  | 1 | 118 | 1 | 0.0001 | 0 | 118 |  |
|  | CUSTOMER REQUEST |  | 1 | 110 | 1 | 0.0001 | 0 | 110 |  |
|  | DIG UP UNDERGROUND |  | 1 | 94 | 1 | 0.0001 | 0 | 94 |  |
|  | EQUIPMENT FAILURE |  | 40 | 748,385 | 1,791 | 0.73 | 0.0017 | 417.8587 |  |
|  | ELECTRICAL OVERLOAD |  | 1 | 843,281 | 1,477 | 0.8225 | 0.0014 | 570.9418 |  |
|  | PARTIAL OUTAGE |  | 2 | 251 | 2 | 0.0002 | 0 | 125.5 |  |
|  | TREE - OFF RIGHT OF WAY |  | 109 | 5,960,268 | 26,959 | 5.8135 | 0.0263 | 221.0864 |  |
|  | TREE - ON RIGHT OF WAY |  | 133 | 10,435,849 | 33,395 | 10.1789 | 0.0326 | 312.4973 |  |
|  | UNKNOWN CAUSE (UNK EQUIP INVOLVED ONLY) |  | 4 | 41,594 | 77 | 0.0406 | 0.0001 | 540.1818 |  |
|  |  | TOTALS | 295 | 18,058,912 | 63,888 | 17.6143 | 0.0623 | 282.6652 |  |
|  | Average Customer Count Used = 1,025,244 |  |  |  |  |  |  |  |  |

### Detailed List of Distribution Circuits with Outages

| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| E453373760 | 12/25/2005 | 0:32:00 | CHR-25 | ECE | TO | OCO | 1,982 | 107,028 |
| E586213589 | 12/25/2005 | 1:00:00 | DES-12 | EBJ | BA | OTF | 6 | 354 |
| E612455328 | 12/25/2005 | 5:10:00 | CHI-12 | ECD | TO | OCO | 2,642 | 1,035,806 |
| 10614842 | 12/25/2005 | 5:12:00 | AIR-23 | ECC | TF | OCO | 25 | 15,075 |
| E347912628 | 12/25/2005 | 5:12:00 | LON-22 | ECC | TO | OCO | 182 | 27,482 |
| E040276652 | 12/25/2005 | 5:21:00 | SIL-16 | ECD | TO | OCO | 147 | 49,833 |
| E148768245 | 12/25/2005 | 5:44:00 | SIL-15 | ECD | TO | OCO | 270 | 541,890 |
| E573269635 | 12/25/2005 | 5:44:00 | YEL-25 | ECC | TO | OCO | 1,256 | 280,088 |
| E160188194 | 12/25/2005 | 6:01:00 | LON-26 | ECC | TO | CDH | 1,266 | 142,380 |
| E906555703 | 12/25/2005 | 6:06:00 | SHE-25 | ECE | TO | OFU | 78 | 48,672 |
| E160028627 | 12/25/2005 | 6:08:00 | BLU-13 | ECC | TF | OSV | 2 | 510 |
| E557149294 | 12/25/2005 | 6:08:00 | MUR-16 | ECE | EO | OCO | 1,477 | 843,281 |
| E899786940 | 12/25/2005 | 6:09:00 | MIL-16 | ECE | TO | OCO | 25 | 33,900 |
| 10615040 | 12/25/2005 | 6:09:00 | TLN-0089 | ECE | TO | OCO | 5,217 | 41,736 |
| E999778054 | 12/25/2005 | 6:09:00 | MIL-22 | ECE | TO | OCO | 128 | 106,368 |
| E150026350 | 12/25/2005 | 6:11:00 | SWI-15 | ECC | TO | OCO | 89 | 17,266 |
| E481232707 | 12/25/2005 | 6:14:00 | YEL-26 | ECC | TF | OCO | 470 | 197,870 |
| E876112831 | 12/25/2005 | 6:35:00 | TLN-0065 | ECD | TF | OCO | 5,839 | 1,559,013 |
| E769173926 | 12/25/2005 | 6:38:00 | FRA-12 | ECD | TO | OCO | 50 | 79,250 |
| E383906438 | 12/25/2005 | 6:40:00 | YEL-23 | ECC | TO | OCO | 27 | 7,020 |
| E479841291 | 12/25/2005 | 6:40:00 | CHI-13 | ECD | TO | OFU | 258 | 88,236 |
| E503403436 | 12/25/2005 | 6:44:00 | STA-26 | EBJ | TO | OPO | 1,369 | 610,574 |
| E665293367 | 12/25/2005 | 6:46:00 | HAZ-12 | EBE | TF | OCO | 1,994 | 454,632 |
| E380036212 | 12/25/2005 | 6:46:00 | BON-15 | ECA | TO | OCO | 18 | 2,991 |
| E766224877 | 12/25/2005 | 6:49:00 | SEQ-13 | EBJ | TO | OFU | 81 | 12,717 |
| E970147608 | 12/25/2005 | 6:49:00 | PMA-13 | ECE | TO | OCO | 87 | 84,738 |
| E709300620 | 12/25/2005 | 6:50:00 | PMA-12 | ECE | TF | OCO | 123 | 47,478 |
| E231218554 | 12/25/2005 | 6:50:00 | EDG-13 | ECA | TO | OFU | 24 | 4,344 |
| E445810859 | 12/25/2005 | 6:50:00 | MIL-17 | ECE | TO | OCO | 48 | 66,000 |
| E505886963 | 12/25/2005 | 6:50:00 | FWY-15 | EBJ | EF | OCO | 764 | 294,140 |
| E995964116 | 12/25/2005 | 6:50:00 | BHL-12 | ECE | TO | OCO | 55 | 35,420 |
| E822829276 | 12/25/2005 | 6:50:00 | SIL-13 | ECF | TF | OCO | 51 | 17,340 |
| E822723268 | 12/25/2005 | 6:51:00 | SIL-13 | ECE | TO | OPO | 18 | 12,042 |
| E231477957 | 12/25/2005 | 6:51:00 | SIN-24 | ECD | TO | OCO | 852 | 790,656 |
| E574375561 | 12/25/2005 | 6:51:00 | COT-17 | EBD | TF | OCO | 866 | 157,612 |
| E360969414 | 12/25/2005 | 6:51:00 | BDI-12 | EBI | TO | OCO | 1,803 | 344,373 |
| E112278964 | 12/25/2005 | 6:51:00 | DIS-12 | ECF | TF | OCO | 23 | 21,827 |
| E223407720 | 12/25/2005 | 6:51:00 | SHD-18 | EBI | TO | OCO | 1,431 | 227,529 |
| E012950004 | 12/25/2005 | 6:51:00 | SIL-13 | ECE | TF | OPO | 2 | 3,588 |
| E422828017 | 12/25/2005 | 6:54:00 | BRE-36 | ECE | TF | OCO | 244 | 225,700 |
| E119185315 | 12/25/2005 | 6:54:00 | ORT-22 | ECA | TO | OCO | 13 | 4,238 |
| E012135666 | 12/25/2005 | 6:54:00 | EPO-13 | ECD | TF | OCO | 117 | 92,781 |
| E665859010 | 12/25/2005 | 6:55:00 | QUI-25 | ECF | TO | OCO | 20 | 8,760 |
| E169440950 | 12/25/2005 | 6:55:00 | BHL-13 | ECE | TF | OCO | 108 | 123,120 |
| E337304194 | 12/25/2005 | 6:55:00 | MCA-15 | ECC | TO | OCO | 21 | 7,140 |
| E036816340 | 12/25/2005 | 6:56:00 | MAN-16 | ECD | TF | OCO | 10 | 13,720 |
| E114043975 | 12/25/2005 | 6:56:00 | WIN-13 | ECE | TO | OCO | 37 | 46,028 |
| E789915034 | 12/25/2005 | 6:56:00 | CHI-15 | ECD | TO | OFU | 50 | 18,450 |
| E013568268 | 12/25/2005 | 6:58:00 | ZEN-23 | EBJ | TF | OTF | 6 | 1,080 |
| E233482801 | 12/25/2005 | 6:58:00 | WIN-12 | ECE | TO | OCO | 1,119 | 326,748 |
| E572606459 | 12/25/2005 | 6:58:00 | LGY-12 | EAD | TO | OCO | 89 | 66,483 |
| E430584200 | 12/25/2005 | 6:59:00 | PTL-13 | ECF | TO | OFU | 33 | 3,828 |
| E547104553 | 12/25/2005 | 7:02:00 | BRE-36 | ECD | EF | OPO | 874 | 401,630 |
| E209499291 | 12/25/2005 | 7:03:00 | RPT-22 | ECD | TO | OFU | 155 | 67,855 |
| E247428194 | 12/25/2005 | 7:05:00 | KLA-15 | EBF | TF | OCO | 2,427 | 237,846 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E393293527 | 12/25/2005 | 7:05:00 | KLA-17 | EBF | TF | OCO | 2,298 | 275,760 |
| E348299145 | 12/25/2005 | 7:05:00 | TLN-0116 | EBF | TF | OCO | 4,546 | 772,820 |
| E785748081 | 12/25/2005 | 7:07:00 | KCR-17 | EBJ | TF | OTF | 3 | 654 |
| E508517635 | 12/25/2005 | 7:08:00 | EPO-12 | ECD | TF | OCO | 24 | 14,208 |
| E710353636 | 12/25/2005 | 7:09:00 | LOL-23 | ECD | TO | OCO | 33 | 22,127 |
| E769474626 | 12/25/2005 | 7:11:00 | PGA-15 | ECF | TF | OCO | 4 | 1,876 |
| E508966564 | 12/25/2005 | 7:12:00 | WOO-27 | ECA | TO | OFU | 13 | 4,264 |
| E674214579 | 12/25/2005 | 7:12:00 | FAL-13 | EBF | TO | OCO | 41 | 28,556 |
| E741757646 | 12/25/2005 | 7:12:00 | FRA-13 | ECD | TO | OCO | 128 | 125,568 |
| E471427725 | 12/25/2005 | 7:13:00 | POU-16 | ECE | TO | OFU | 30 | 23,910 |
| E244469910 | 12/25/2005 | 7:14:00 | SIN-22 | ECD | TF | OCO | 182 | 259,532 |
| E807101737 | 12/25/2005 | 7:16:00 | PGA-13 | ECE | TO | OHR | 1,078 | 798,182 |
| E704153220 | 12/25/2005 | 7:18:00 | KWH-25 | EBD | TF | OCO | 1,940 | 341,418 |
| E122867230 | 12/25/2005 | 7:19:00 | FRA-15 | ECD | TF | OHR | 771 | 185,811 |
| E449439976 | 12/25/2005 | 7:19:00 | NRU-23 | EBE | TF | OCO | 284 | 71,568 |
| E148401092 | 12/25/2005 | 7:19:00 | KWH-23 | EBE | TO | OCO | 652 | 532,032 |
| E792404129 | 12/25/2005 | 7:20:00 | CHR-22 | ECE | TF | OCO | 100 | 64,000 |
| E123219245 | 12/25/2005 | 7:20:00 | FLD-12 | EAD | EF | OCO | 10 | 6,700 |
| E542827339 | 12/25/2005 | 7:25:00 | SAH-17 | EBD | TO | OCO | 10 | 5,810 |
| E280961450 | 12/25/2005 | 7:25:00 | ROS-21 | EBD | TF | OCO | 2,162 | 198,904 |
| E942535467 | 12/25/2005 | 7:28:00 | TRA-22 | ECE | TO | OCO | 1,548 | 184,212 |
| E299605295 | 12/25/2005 | 7:28:00 | DUV-12 | EBD | TF | OCO | 19 | 13,756 |
| E647788137 | 12/25/2005 | 7:28:00 | EGT-12 | EBE | TF | OCO | 28 | 12,432 |
| E086729496 | 12/25/2005 | 7:30:00 | SNQ-13 | EBF | TO | OCO | 96 | 41,496 |
| E746189943 | 12/25/2005 | 7:31:00 | BRO-15 | EAD | TO | OCO | 1,519 | 185,141 |
| E235763031 | 12/25/2005 | 7:34:00 | TOL-17 | EBD | TF | OSV | 1 | 574 |
| E992061621 | 12/25/2005 | 7:35:00 | IRO-13 | ECF | TO | OCO | 17 | 8,585 |
| E355538900 | 12/25/2005 | 7:40:00 | SIL-15 | ECE | TO | OCO | 360 | 434,000 |
| E450324964 | 12/25/2005 | 7:41:00 | HKX-12 | EAC | TO | OCO | 230 | 30,590 |
| E426291330 | 12/25/2005 | 7:42:00 | SKE-26 | ECE | TO | OHR | 1,369 | 599,622 |
| E408800137 | 12/25/2005 | 7:43:00 | HAM-13 | EAC | TO | OCO | 796 | 109,052 |
| E755815342 | 12/25/2005 | 7:43:00 | RPT-17 | ECD | TO | OFU | 608 | 247,456 |
| E538855559 | 12/25/2005 | 7:43:00 | RDO-15 | EBJ | TF | OFC | 1 | 177 |
| E836079914 | 12/25/2005 | 7:54:00 | BRO-16 | EAD | TO | OCO | 3 | 1,608 |
| E339524433 | 12/25/2005 | 7:59:00 | PHA-17 | EBE | TO | OCO | 165 | 112,200 |
| E193736990 | 12/25/2005 | 8:02:00 | SKE-23 | ECE | TO | OCO | 597 | 389,244 |
| E489916105 | 12/25/2005 | 8:09:00 | MLK-12 | EBE | TF | OCO | 52 | 10,399 |
| E595200579 | 12/25/2005 | 8:11:00 | PAN-14 | EBJ | TF | OTF | 3 | 897 |
| E817303790 | 12/25/2005 | 8:12:00 | FLD-13 | EAD | TO | OCO | 30 | 15,690 |
| E148066773 | 12/25/2005 | 8:13:00 | CPV-12 | EAD | TO | OTR | 16 | 7,232 |
| E071932100 | 12/25/2005 | 8:16:00 | SIN-25 | ECD | TF | OSV | 17 | 12,478 |
| E570136302 | 12/25/2005 | 8:20:00 | WAB-12 | EBI | EF | UPC | 1 | 490 |
| E627713537 | 12/25/2005 | 8:23:00 | LON-22 | ECC | TO | OCO | 34 | 1,020 |
| E685553629 | 12/25/2005 | 8:29:00 | SIL-16 | ECE | TO | OFU | 10 | 4,300 |
| E439353344 | 12/25/2005 | 8:29:00 | SIL-16 | ECE | TO | OCO | 8 | 12,752 |
| E049124094 | 12/25/2005 | 8:30:00 | NLM-12 | EAC | TO | OCO | 68 | 31,620 |
| E926684151 | 12/25/2005 | 8:31:00 | ORT-25 | ECA | BA | OFU | 178 | 27,768 |
| E956944914 | 12/25/2005 | 8:32:00 | VAS-13 | EBL | TF | OCO | 12 | 7,836 |
| E356027718 | 12/25/2005 | 8:33:00 | PMA-16 | ECE | TO | OCO | 252 | 354,564 |
| E497317187 | 12/25/2005 | 8:34:00 | LAT-17 | EBJ | TF | OFU | 17 | 3,077 |
| E770230972 | 12/25/2005 | 8:35:00 | LGY-15 | EAD | TO | OCO | 13 | 5,486 |
| E133384950 | 12/25/2005 | 8:40:00 | HAM-15 | EAC | TO | OCO | 20 | 11,540 |
| E972450845 | 12/25/2005 | 8:40:00 | HAM-15 | EAC | TO | OCO | 168 | 43,680 |
| E432294594 | 12/25/2005 | 8:42:00 | WAU-26 | EBJ | TF | OCO | 44 | 26,962 |
| E313425455 | 12/25/2005 | 8:46:00 | COT-13 | EBD | TF | OSV | 5 | 826 |
| E265461306 | 12/25/2005 | 8:46:00 | DUV-15 | EBD | EF | OFU | 23 | 8,947 |
| E211528172 | 12/25/2005 | 8:52:00 | LGY-16 | EAD | TO | OCO | 65 | 14,170 |
| E928307069 | 12/25/2005 | 8:55:00 | BIG-16 | EAC | EF | OPO | 1 | 695 |
| E131174682 | 12/25/2005 | 8:55:00 | PTL-16 | ECF | TO | OCO | 3 | 150 |
| E183624776 | 12/25/2005 | 8:57:00 | LYN-24 | EAA | UN | OCO | 50 | 34,200 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E586128853 | 12/25/2005 | 9:00:00 | MAN-15 | ECD | TF | OSV | 2 | 1,920 |
| E058172377 | 12/25/2005 | 9:02:00 | WLS-16 | EAC | TO | OTR | 1 | 298 |
| E014651863 | 12/25/2005 | 9:07:00 | NUG-26 | EAA | EF | OPO | 15 | 4,140 |
| E554663403 | 12/25/2005 | 9:08:00 | PGA-12 | ECE | TO | OPO | 40 | 66,900 |
| E779840481 | 12/25/2005 | 9:17:00 | BTN-36 | EAC | TO | OCO | 8 | 7,384 |
| E802266838 | 12/25/2005 | 9:18:00 | POU-15 | ECE | TF | OSV | 3 | 4,266 |
| E509132126 | 12/25/2005 | 9:20:00 | EDG-16 | ECA | EF | OTF | 4 | 560 |
| E814437451 | 12/25/2005 | 9:20:00 | LON-22 | ECC | TO | OCO | 20 | 6,060 |
| E945276895 | 12/25/2005 | 9:25:00 | QUI-26 | ECF | TO | OFU | 2 | 520 |
| E342373937 | 12/25/2005 | 9:33:00 | EDG-15 | ECA | TO | OCO | 15 | 8,910 |
| E984041040 | 12/25/2005 | 9:37:00 | SHE-26 | ECE | TO | OCR | 9 | 14,067 |
| E454434448 | 12/25/2005 | 9:40:00 | BIG-15 | EAC | TO | OTR | 2 | 402 |
| E870164175 | 12/25/2005 | 9:41:00 | LEA-16 | EBI | TF | OTR | 1 | 289 |
| 10615008 | 12/25/2005 | 9:41:00 | TLN-0009 | EEA | TF | OCO | 986 | 11,832 |
| E593744981 | 12/25/2005 | 9:45:00 | CUS-16 | EAA | TO | OPO | 569 | 65,310 |
| 10615003 | 12/25/2005 | 9:46:00 | HAM-15 | EAC | TO | OCO | 6 | 2,688 |
| E889237355 | 12/25/2005 | 9:50:00 | CLY-23 | EBE | TF | OCO | 29 | 21,692 |
| E220766358 | 12/25/2005 | 9:51:00 | PTL-13 | ECF | TF | OTF | 3 | 27 |
| E392795316 | 12/25/2005 | 9:56:00 | VWY-15 | EAA | TO | OCO | 10 | 720 |
| E330026511 | 12/25/2005 | 10:08:00 | MAN-12 | ECD | TF | OCO | 7 | 7,049 |
| E734108288 | 12/25/2005 | 10:09:00 | SMR-24 | ECA | EF | UPC | 4 | 3,600 |
| E945002841 | 12/25/2005 | 10:09:00 | SIL-16 | ECD | TO | OFU | 54 | 17,064 |
| E768873054 | 12/25/2005 | 10:14:00 | SME-12 | EBE | TF | OTR | 1 | 974 |
| E026885236 | 12/25/2005 | 10:14:00 | SHD-18 | EBJ | TF | OTF | 2 | 114 |
| E212366778 | 12/25/2005 | 10:14:00 | MCW-17 | ECE | TF | OTF | 7 | 6,797 |
| E471012965 | 12/25/2005 | 10:16:00 | SOO-23 | EBJ | TF | OTF | 3 | 312 |
| E378727941 | 12/25/2005 | 10:19:00 | TOL-15 | EBD | TF | OCO | 10 | 2,790 |
| E146429697 | 12/25/2005 | 10:20:00 | WIN-15 | ECE | TO | OCO | 8 | 12,040 |
| E404377836 | 12/25/2005 | 10:20:00 | FRA-16 | ECD | TF | OSV | 2 | 1,350 |
| E232986064 | 12/25/2005 | 10:22:00 | MUR-15 | ECE | TO | OFU | 32 | 20,416 |
| E495055371 | 12/25/2005 | 10:27:00 | NLM-15 | EAC | TO | OTR | 2 | 566 |
| E044915138 | 12/25/2005 | 10:27:00 | HAN-15 | EAA | CP | OPO | 1 | 118 |
| E274580622 | 12/25/2005 | 10:35:00 | BRS-24 | EAC | TO | OCO | 31 | 13,795 |
| E414648410 | 12/25/2005 | 10:35:00 | BRS-24 | EAC | TO | OTR | 7 | 2,065 |
| E975006552 | 12/25/2005 | 10:35:00 | CHR-25 | ECE | TF | OFC | 40 | 36,040 |
| E791893969 | 12/25/2005 | 10:35:00 | NBE-16 | EBF | TF | OCO | 114 | 43,206 |
| E929661342 | 12/25/2005 | 10:37:00 | CPV-15 | EAD | TO | OTR | 3 | 1,464 |
| E351627113 | 12/25/2005 | 10:42:00 | DES-16 | EBJ | TF | OSV | 2 | 66 |
| E029381246 | 12/25/2005 | 10:48:00 | SOO-23 | EBI | TF | OTF | 8 | 1,016 |
| E031483613 | 12/25/2005 | 10:55:00 | SHD-18 | EBI | TF | OCO | 4 | 932 |
| E937601264 | 12/25/2005 | 10:57:00 | HKX-12 | EAC | TO | OTR | 1 | 123 |
| E013089485 | 12/25/2005 | 11:00:00 | QUI-25 | ECF | TF | OCO | 2 | 1,720 |
| E575563607 | 12/25/2005 | 11:25:00 | FRG-26 | ECC | BA | OTF | 3 | 735 |
| E113394926 | 12/25/2005 | 11:26:00 | FNW-16 | ECD | TO | OFU | 18 | 9,144 |
| E559050685 | 12/25/2005 | 11:40:00 | PHA-13 | EBE | EF | OTF | 6 | 1,452 |
| E893411417 | 12/25/2005 | 11:50:00 | VAS-12 | EBL | TF | OSV | 2 | 240 |
| E759619545 | 12/25/2005 | 11:52:00 | JUA-12 | EBD | EF | UTR | 4 | 1,892 |
| E501720391 | 12/25/2005 | 11:52:00 | BON-17 | ECA | BA | OTF | 3 | 459 |
| E901697475 | 12/25/2005 | 11:58:00 | CHI-13 | ECD | TO | OCO | 10 | 12,370 |
| E823539191 | 12/25/2005 | 11:59:00 | FNW-15 | ECD | TO | OFU | 6 | 2,886 |
| E756429579 | 12/25/2005 | 12:00:00 | CHI-12 | ECE | TF | OCO | 1 | 945 |
| E363619393 | 12/25/2005 | 12:03:00 | KWH-25 | EBD | TF | OCO | 143 | 11,583 |
| E659752739 | 12/25/2005 | 12:18:00 | YEL-25 | ECC | TO | OCO | 5 | 460 |
| E675540129 | 12/25/2005 | 12:23:00 | PMA-15 | ECE | TF | OFU | 2 | 1,054 |
| E549359446 | 12/25/2005 | 12:24:00 | FNW-17 | ECD | TO | OTF | 7 | 4,347 |
| E534669518 | 12/25/2005 | 12:30:00 | LGY-16 | EAD | TO | OTR | 50 | 7,000 |
| E654815659 | 12/25/2005 | 12:30:00 | SIL-13 | ECF | TF | OCO | 51 | 13,515 |
| E623509823 | 12/25/2005 | 12:31:00 | CHI-13 | ECD | TO | OFU | 15 | 2,235 |
| E030299226 | 12/25/2005 | 12:34:00 | FWY-11 | EBJ | TF | OCO | 173 | 38,406 |
| E481109794 | 12/25/2005 | 12:34:00 | CHI-12 | ECD | TO | OFU | 31 | 5,177 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E868997773 | 12/25/2005 | 12:42:00 | VWY-15 | EAA | EF | UOT | 9 | 5,607 |
| E532148390 | 12/25/2005 | 12:51:00 | PLG-13 | ECC | TF | OTF | 2 | 138 |
| E722513484 | 12/25/2005 | 13:00:00 | BLU-13 | ECC | TF | OSV | 1 | 30 |
| E994920850 | 12/25/2005 | 13:11:00 | IRO-17 | ECF | EF | USV | 1 | 281 |
| E335490847 | 12/25/2005 | 13:16:00 | PMA-12 | ECE | TF | OCO | 90 | 86,760 |
| E512760995 | 12/25/2005 | 13:22:00 | PMA-12 | ECE | TF | OCO | 36 | 31,608 |
| E541997362 | 12/25/2005 | 13:32:00 | BIG-12 | EAC | TO | OCO | 45 | 4,822 |
| E483654947 | 12/25/2005 | 13:36:00 | MED-36 | EBE | EF | OTF | 6 | 774 |
| E390018024 | 12/25/2005 | 13:37:00 | ING-15 | EBD | TF | OCO | 6 | 3,192 |
| E844292452 | 12/25/2005 | 13:52:00 | LGY-16 | EAD | TO | OTR | 5 | 311 |
| E279805609 | 12/25/2005 | 14:18:00 | WIN-12 | ECE | UN | OTF | 7 | 714 |
| E720532875 | 12/25/2005 | 14:24:00 | RPT-22 | ECD | TO | OFU | 50 | 2,550 |
| E766106396 | 12/25/2005 | 14:28:00 | RPT-22 | ECD | TF | OCO | 18 | 954 |
| E832003012 | 12/25/2005 | 14:38:00 | SHE-25 | ECE | TO | OTF | 12 | 5,988 |
| E380558857 | 12/25/2005 | 14:41:00 | VIK-25 | EAA | EF | OSV | 1 | 83 |
| E773661175 | 12/25/2005 | 14:56:00 | WLS-16 | EAC | TO | OTR | 1 | 49 |
| E885757941 | 12/25/2005 | 15:20:00 | MUR-15 | ECE | TF | OFU | 14 | 1,638 |
| E532175171 | 12/25/2005 | 15:22:00 | HAZ-13 | EBE | TF | OCO | 1 | 80 |
| E825320628 | 12/25/2005 | 15:28:00 | QUI-25 | ECF | TO | OCO | 2 | 1,188 |
| E778547475 | 12/25/2005 | 15:29:00 | EGT-12 | EBE | TF | OCO | 1 | 84 |
| E510542310 | 12/25/2005 | 15:32:00 | MUR-16 | ECE | TF | OTR | 5 | 90 |
| E903315555 | 12/25/2005 | 15:47:00 | SUM-15 | EAC | TO | OTR | 1 | 113 |
| E077608611 | 12/25/2005 | 16:00:00 | IRO-13 | ECF | TF | OCO | 10 | 3,020 |
| E685054721 | 12/25/2005 | 16:09:00 | RPT-16 | ECD | TF | OSV | 1 | 231 |
| E559128289 | 12/25/2005 | 16:21:00 | FLD-15 | EAD | EF | OCO | 3 | 387 |
| E604985763 | 12/25/2005 | 16:29:00 | JUA-14 | EBD | TO | OCO | 26 | 3,978 |
| E914115976 | 12/25/2005 | 16:31:00 | NLM-13 | EAC | TO | OCN | 1 | 29 |
| E548717499 | 12/25/2005 | 16:36:00 | SIL-16 | ECD | TO | OFU | 24 | 6,336 |
| E089030467 | 12/25/2005 | 16:57:00 | RPT-22 | ECD | TO | OCO | 6 | 858 |
| E167141383 | 12/25/2005 | 17:00:00 | EPO-12 | ECD | TO | OFU | 25 | 15,000 |
| E597046782 | 12/25/2005 | 17:02:00 | HAM-13 | EAC | TO | OCO | 31 | 4,185 |
| E473771751 | 12/25/2005 | 17:06:00 | BRO-16 | EAD | EF | OCO | 2 | 186 |
| E078602511 | 12/25/2005 | 17:22:00 | EGT-12 | EBE | TF | OCO | 5 | 2,675 |
| E082725795 | 12/25/2005 | 17:26:00 | NLM-15 | EAC | TO | OTR | 2 | 398 |
| E003667681 | 12/25/2005 | 17:39:00 | LON-22 | ECC | EF | OTF | 5 | 598 |
| E238725769 | 12/25/2005 | 17:41:00 | PET-15 | EAC | TF | OCO | 1 | 72 |
| E297333731 | 12/25/2005 | 17:54:00 | SKE-23 | ECE | TF | OCO | 17 | 7,667 |
| E881258733 | 12/25/2005 | 18:00:00 | PMA-16 | ECE | TO | OFU | 237 | 21,330 |
| E332297550 | 12/25/2005 | 18:00:00 | CHR-22 | ECE | TF | OCO | 50 | 26,000 |
| E438845728 | 12/25/2005 | 18:04:00 | IRO-17 | ECF | EF | USV | 1 | 944 |
| E817516722 | 12/25/2005 | 18:07:00 | BHL-12 | ECE | TF | OCO | 34 | 21,862 |
| E468307133 | 12/25/2005 | 18:25:00 | SHD-18 | EBI | EF | USV | 1 | 66 |
| E766346875 | 12/25/2005 | 18:50:00 | SIL-15 | ECE | TO | OFU | 80 | 800 |
| E644573153 | 12/25/2005 | 18:53:00 | SKE-26 | ECE | TO | OCO | 5 | 3,760 |
| E477313844 | 12/25/2005 | 18:54:00 | EPO-12 | ECD | TO | OCO | 1 | 1,036 |
| E547482983 | 12/25/2005 | 19:00:00 | HAM-15 | EAC | TO | OUP | 3 | 432 |
| E732354237 | 12/25/2005 | 19:05:00 | WOO-27 | ECA | EF | OTF | 4 | 494 |
| E862650827 | 12/25/2005 | 19:19:00 | RPT-22 | ECD | TO | UTC | 2,352 | 326,697 |
| E010474188 | 12/25/2005 | 19:21:00 | LGY-16 | EAD | TO | OTR | 1 | 34 |
| E524295382 | 12/25/2005 | 19:23:00 | BIG-12 | EAC | TO | OCO | 157 | 49,298 |
| E992776936 | 12/25/2005 | 19:39:00 | SIL-15 | ECE | TF | OCO | 71 | 35,216 |
| E701607143 | 12/25/2005 | 19:45:00 | ROL-15 | EBJ | PO | OSV | 1 | 116 |
| E625475213 | 12/25/2005 | 20:37:00 | POU-16 | ECE | EF | OTR | 5 | 5,165 |
| E028704162 | 12/25/2005 | 21:03:00 | CHR-22 | ECE | TF | OCO | 18 | 5,886 |
| E099155460 | 12/25/2005 | 21:10:00 | NNO-12 | EBJ | TF | OTF | 7 | 522 |
| E346013482 | 12/25/2005 | 21:15:00 | YEL-26 | ECC | TF | OTF | 1 | 80 |
| E187209732 | 12/25/2005 | 21:18:00 | BCH-15 | EAA | TF | OTR | 2 | 120 |
| E356532256 | 12/25/2005 | 21:19:00 | VAS-12 | EBL | TO | OCO | 6 | 1,656 |
| E390933082 | 12/25/2005 | 21:25:00 | EPO-13 | ECD | TF | OCO | 81 | 57,915 |
| E560729215 | 12/25/2005 | 21:35:00 | LYN-24 | EAA | TF | OTR | 5 | 402 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E427024477 | 12/25/2005 | 21:49:00 | IRO-13 | ECF | TF | OCO | 1 | 1 |
| E043680737 | 12/25/2005 | 21:52:00 | HAM-13 | EAC | EF | OTR | 1 | 58 |
| E052479798 | 12/25/2005 | 22:17:00 | MIL-22 | ECE | TO | OCO | 14 | 3,542 |
| E470663139 | 12/25/2005 | 22:19:00 | PLG-13 | ECC | TO | OCO | 10 | 1,199 |
| E450982205 | 12/25/2005 | 22:26:00 | PGA-13 | ECE | TF | OCO | 2 | 1,228 |
| E351668234 | 12/25/2005 | 22:35:00 | BON-17 | ECA | EF | OTF | 1 | 107 |
| E814694443 | 12/25/2005 | 23:17:00 | PMA-13 | ECE | TF | OCO | 5 | 3,915 |

### Terms, Codes and Definitions Used on Detail Reports

| #### Notification | [Notification Number] A number assigned by SAP, identifying the outage record |  |
| --- | --- | --- |
| Date | The date of the outage |  |
| Time | The time of the outage |  |
| Circuit | [Reference Circuit] The circuit identifier for the affected circuit |  |
| F/LOC | [Functional Location] The grid number where the outage occurred. If the grid number is not available, the Reference Circuit identifier occupies this field |  |
| EQT NBR | [Equipment Number] A number used to tie the equipment involved in the outage to the related information in SAP. This number does not represent the physical number of the equipment |  |
| Area | [Maintenance Planner Group] A code representing the energy, region and service center |  |
|  | EAA – Bellingham | EBJ – South King |
|  | EAB – Lynden | EBK – Southwest King |
|  | EAC – Skagit | EBL – Vashon |
|  | EAD – Whidbey | ECA – Puyallup |
|  | EBD – Redmond | ECC – Olympia |
|  | EBE – Factoria | ECD – Port Orchard |
|  | EBF – Snoqualmie | ECE – Poulsbo |
|  | EBI – Enumclaw | ECF – Port Townsend |

| Cause | Cause of Outage |  |
| --- | --- | --- |
|  | AO – Accident Other | EF – Equipment Failure |
|  | BA – Bird or Animal | EO – Electrical Overload |
|  | CP – Car Pole | TF – Tree Off Right-of-Way |
|  | CR – Customer Request | TO – Tree On Right-of-Way |
|  | DU – Dig-up Underground | UN – Unknown |
|  | SO – Scheduled Outage |  |

| Equipment | Affected by, or involved in the outage |  |
| --- | --- | --- |
|  | OCN – Connector | OSW – Overhead Switch |
|  | OCO – Overhead Conductor | OTF – Overhead Transformer Fuse |
|  | OCR – Crossarm | OTR – Overhead Transformer |
|  | OFC – Overhead Cut-out | OUP – OH to UG Primary |
|  | OFS – Overhead Fire Signal | OUS – OH to UG Secondary Service |
|  | OFU – Fuse Link/OH Line Fuse | SBF – High-side Bank Fuse |
|  | OGS – Span Guy | SCB – Power Circuit Breaker |
|  | OHR – Overhead Recloser | UOT – Underground Outdoor Term |
|  | OIN – Insulator | UPC – Underground Primary Cable |
|  | OJU- Jump Wire | UPT – Padmount Transformer |
|  | OPO – Pole | USV – Underground Service |
|  | OSV – Overhead Service | UTC – Underground Terminal Fuse |
|  | ORE – Regulator | UTR – Submersible Transformer |

#### Codes, Definitions – Continued

| CUST OUT | [Customer Out] The number of customers without power for any given outage record |
| --- | --- |
| CUST MIN | [Customer Minutes] The total number of minutes customers were without power for any given record |

| CODE | [Storm Code] An event descriptor |
| --- | --- |
|  | NON – Non Storm / Normal Conditions |
|  | WTH – Weather Related (eg: wind storm, showers, etc) |
|  | MAJ – Major event |

### Newsprint Media Coverage

High winds cut electricity to thousands

By Seattle Times staff and news services

High winds downed trees and power lines Sunday, cutting electricity to thousands of homes across the region.

There were no immediate reports of serious damage or injuries. Wind gusts reached up to 50 miles an hour.

At the peak of the outages Sunday morning, about 20,000 Puget Sound Energy customers in King, Pierce, Thurston, Kitsap, Lewis, Whatcom, Island and Skagit counties had lost power, said Lynn Carlson, a spokeswoman for the utility.

In Seattle, about 250 customers in Magnolia, Beacon Hill and Skyway were without power most of the day. Seattle City Light spokesman Larry Vogel said downed branches and other wind-related problems caused the outages, and that all power was restored by 6 p.m.

Higher-than-normal temperatures and rainfall also broke some records for the second day in a row.

The National Weather Service recorded a high temperature of 55 degrees at the Sand Point observation station in Seattle, breaking the previous Christmas Day record of 52 degrees set in 2002.

Rainfall at Sand Point was 0.87 inch through midevening, breaking the record of 0.79 inch set in 1998. The station has recorded weather since the 1980s.

Sunday's heat and rainfall weren't quite enough to topple records set at the region's main recording station in SeaTac.

The National Weather Service had flood warnings and watches out for several rivers around Mount Rainier on Sunday, but meteorologist Allen Kam said the major precipitation appeared to be over Sunday night and river levels were slowly receding.

Power had been restored to all but about 5,000 homes across the region by 8 p.m. PSE expected to restore power to most of the remaining customers, primarily in Kitsap County, by the end of the day, Carlson said. She warned that some isolated customers might not get power restored until this morning.

In Oregon, Portland General Electric said 30,000 of its customers lost power at the peak of the windstorm.

PGE spokeswoman Ariana White said power was restored to all but 4,000 of those customers by 3:30 p.m., and most of the remainder — most of them southeast of Portland and in eastern Multnomah County — should be back on line by the end of the day.

Back in Washington state, the Snohomish County Public Utility District said about 4,500 of its customers lost power. Outages were reported on Camano Island, in Arlington and Marysville, and at other scattered locations.

The National Weather Service said Saturday's high of 62 degrees at SeaTac broke the previous record of 55 degrees set in 1950. Three days after the official start of winter, the temperature climbed to 63 degrees in Tacoma — tying a record set 22 years ago.