2006

Qualifying Storm Events

November 13, 2006

# Table of Contents

Table of Contents	2

Event Description	3

Date of event	3

Event Type	3

Service Areas Affected	3

Number of Customers Affected	3

Summary of System Impacts	3

Mobilization Summary	3

Major Event Day – Qualification	5

Qualified Events - 2006	5

Current Event – Calculation Detail	5

Cumulative list of events that have qualified	5

Event Restoration – Cost Summary	6

Restoration Cost Detail by Qualifying Event	6

YTD Storm Restoration Cost Detail – Through November 13, 2006	6

Detail Documents	7

Restoration Cost Detail – Current Event	8

IEEE-1366 - Detailed List of Distribution Circuits with Outages	9

Terms, Codes and Definitions Used on Detail Reports	14

Newsprint Media Coverage	16

# Event Description

### Date of event

November 13, 2006

### Event Type

Wind storm.

### Service Areas Affected

Winds gusting to 50 MPH resulted in outages throughout the southern portion of Puget Sound Energy’s service territory. The electric system in Thurston County, Pierce County and the southern portion of King County experienced storm damage resulting from falling trees and large tree limbs.

### Number of Customers Affected

Winds resulted in approximately 45,000 customers losing electric service over the course of this event.

### Summary of System Impacts

| Total Number of Outages | 276 |
| --- | --- |
| Distribution Circuits Totally Out | 7 |
| Distribution Circuits Partially Out | 269 |

| Transmission Circuits Affected | 6 |
| --- | --- |
| Substations Totally Off-line | 2 |

### Mobilization Summary

#### Operating bases

| Base | Date Opened | Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
| Pierce | 11/13/06 | 01:15 | 11/13/06 | 22:30 |
| Thrurston | 11/13/06 | 01:15 | 11/14/06 | 05:00 |
| S-King | 11/13/06 | 04:30 | 11/13/06 | 18:30 |

#### Emergency Operations Center

| EOC | Date Opened | #### Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
|  | 11/13/2006 | 06:30 | 11/13/06 | 19:30 |

# Major Event Day – Qualification

- IEEE 1366 Method

IEEE 1366 was established to present a set of terms and definitions which can be used to foster uniformity in the development of distribution service reliability indices, to identify factors which affect the indices, and to aid in consistent reporting practices among utilities.  Also, it provides guidance for new personnel in the reliability area, and tools for internal as well as external comparisons.  The Major Event Day definition was created as part of IEEE 1366 to allow for consistent calculation of reliability metrics between utilities, and enable more valid comparisons with other utility reliability metrics.

IEEE Major Event Day Calculation (2.5 BETA METHOD) - A threshold on daily SAIDI is computed once a year, following year end. - Assemble the 5 most recent years of historical values of SAIDI/day. - Discard any days in the data set that has a SAIDI/day of zero. - Find the natural logarithm of each value in the data set. - Compute the average Alpha and the standard deviation (Beta) of the natural logarithms computed in step 3. - Compute the threshold Tmed where Tmed = exp(Alpha + 2.5 * Beta) - Any day in the next year with SAIDI > Tmed is a major event day.

Puget Sound Energy’s Major Event Threshold for 2006: 4.97 Minutes

# Qualified Events - 2006

### Current Event – Calculation Detail

| Event Date | Total Customer Minutes | Average Customer Count | Daily SAIDI – Customer Minutes /Customer Count |
| --- | --- | --- | --- |
| 11/13/2006 | 13,806,051 | 1,042,369 | 13.24 |

### Cumulative list of events that have qualified

| Date(s) | T-med Score | O&M – Deferrable Accumulation |
| --- | --- | --- |
| 1/1/2006 | 5.35 | $242,708 |
| 1/31/2006 | 11.19 | $653,176 |
| 2/4/2006 | 161.65 | $6,104,116 |
| 2/10/2006 | 8.34 | $0 |
| 2/17/2006 | 40.13 | $0 |
| 3/8/2006 | 6.16 | $0 |
| 11/13/2006 | 13.24 | $0 |

# Event Restoration – Cost Summary

### Restoration Cost Detail by Qualifying Event

| Date | Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M – Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/1/2006 | $0 | $0 | $0 | $23,995 | $242,708 | $266,703 | $266,703 |
| 1/31/2006 | $0 | $70,613 | $0 | $35,780 | $653,176 | $688,956 | $759,569 |
| 2/4/2006 | $2,853,981 | $311,579 | $0 | $395,638 | $6,104,116 | $6,499,754 | $9,665,314 |
| 2/10/2006 | $468,301 | $110,144 | $0 | $17,139 | $0 | $17,139 | $595,584 |
| 2/17/2006 | $3,309,247 | $141,574 | $0 | $127,653 | $0 | $127,653 | $3,578,474 |
| 3/8/2006 | $444,758 | $3,929 | $0 | $34,731 | $0 | $34,731 | $483,418 |
| 11/13/2006 | $1,490,582 | $26,308 | $0 | $87,272 | $0 | $87,272 | $1,604,162 |

### YTD Storm Restoration Cost Detail – Through November 13, 2006

| Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| $8,566,869 | $664,147 | $0 | $722,208 | $7,000,000 | $7,722,208 | $16,953,224 |

# Detail Documents

- Restoration Cost Detail – Current Event

- Detailed List of Distribution Circuits with Outages

- Terms, Codes & Definitions Used on Detail Reports

- Newsprint Media Coverage

### Restoration Cost Detail – Current Event

|  | Puget Sound Energy |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | November 13, 2006 Storm Damage Repair Costs |  |  |  |  |  |  |  |  |
|  |  | Qualifying Events Deferred Account | Capital | C&D Recoverable from Direct Billings (Costs Not Yet Billed) | O&M - Not Deferrable | O&M - Deferrable Accumulation | Total O&M | Total |  |
|  | Labor |  |  |  |  |  |  |  |  |
|  | ST |  |  |  |  | $9,054 | $9,054 | $9,054 |  |
|  | OT |  | $0 |  |  | $78,378 | $78,378 | $78,378 |  |
|  | Total Labor | $0 | $0 | $0 | $0 | $87,433 | $87,433 | $87,433 |  |
|  | Labor OH |  |  |  |  | $39,040 | $39,040 | $39,040 |  |
|  | Materials |  | $5,706 |  |  | $183,133 | $183,133 | $188,840 |  |
|  | Contractors |  | $17,953 |  |  | $1,157,863 | $1,157,863 | $1,175,816 |  |
|  | Other Direct Charges |  |  |  |  | $3,014 | $3,014 | $3,014 |  |
|  | Fleet |  |  |  |  | $20,100 | $20,100 | $20,100 |  |
|  | Other Assessments |  | $2,649 |  | $87,272 | $0 | $87,272 | $89,920 |  |
|  | Deferred Expenses | $1,490,582 |  |  |  | ($1,490,582) | ($1,490,582) | $0 |  |
|  |  | $1,490,582 | $26,308 | $0 | $87,272 | $0 | $87,272 | $1,604,162 |  |

### IEEE-1366 - Detailed List of Distribution Circuits with Outages

| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| E735259758 | 11/13/2006 | 0:07:00 | RHO-15 | ECA | TO | OCO | 24 | 22,296 |
| E332839722 | 11/13/2006 | 0:09:00 | CHA-15 | ECC | TO | OCO | 180 | 103,680 |
| E894210803 | 11/13/2006 | 0:13:00 | ORT-23 | ECA | TO | OCO | 133 | 109,326 |
| E112943286 | 11/13/2006 | 0:13:00 | ORT-23 | ECA | TO | DNO | 69 | 16,974 |
| E063968338 | 11/13/2006 | 0:13:00 | ROC-16 | ECC | TO | OCO | 410 | 301,760 |
| E961023728 | 11/13/2006 | 0:17:00 | BON-16 | ECA | TO | OCO | 2,312 | 307,496 |
| E752655461 | 11/13/2006 | 0:21:00 | YEL-25 | ECC | TO | OTF | 12 | 12,000 |
| E974730751 | 11/13/2006 | 0:23:00 | MCA-15 | ECC | TO | OCO | 19 | 14,801 |
| 10656413 | 11/13/2006 | 0:24:00 | ORT-23 | ECA | EF | UPC | 20 | 22,200 |
| E020450044 | 11/13/2006 | 0:30:00 | WAB-13 | EBI | TF | OCO | 46 | 25,760 |
| E599755659 | 11/13/2006 | 0:31:00 | KAP-13 | ECA | TO | OCO | 7 | 7,616 |
| E650739977 | 11/13/2006 | 0:34:00 | OSC-23 | EBI | TO | OFU | 10 | 1,500 |
| E551610147 | 11/13/2006 | 0:40:00 | ROC-17 | ECC | TO | OCO | 92 | 89,700 |
| E009408162 | 11/13/2006 | 0:41:00 | OSC-22 | EBI | TF | OCO | 28 | 10,752 |
| E715017284 | 11/13/2006 | 0:42:00 | BON-17 | ECA | TO | OFC | 14 | 2,170 |
| E450619090 | 11/13/2006 | 0:45:00 | DGR-13 | ECA | TO | OSW | 15 | 3,585 |
| E479008228 | 11/13/2006 | 0:46:00 | CUM-15 | EBI | TF | OPI | 5 | 2,370 |
| E943434230 | 11/13/2006 | 0:50:00 | BDI-16 | EBI | TO | OFU | 54 | 17,280 |
| E367134718 | 11/13/2006 | 0:52:00 | LON-26 | ECC | TO | OCO | 1,315 | 120,980 |
| E766436824 | 11/13/2006 | 0:53:00 | BLU-17 | ECC | TO | OCO | 308 | 216,216 |
| E140441847 | 11/13/2006 | 0:54:00 | BLU-16 | ECC | TO | DNO | 579 | 81,639 |
| E712721600 | 11/13/2006 | 0:56:00 | LON-23 | ECC | TO | DNO | 1,476 | 363,624 |
| E988909374 | 11/13/2006 | 0:59:00 | YEL-26 | ECC | TO | OCO | 90 | 62,640 |
| E824604884 | 11/13/2006 | 0:59:00 | BDI-13 | EBI | TO | OFU | 538 | 131,810 |
| E435272979 | 11/13/2006 | 1:00:00 | EDG-15 | ECA | EF | OFC | 1,008 | 60,480 |
| E247049427 | 11/13/2006 | 1:03:00 | CED-13 | ECA | TF | OCO | 10 | 3,920 |
| E354462789 | 11/13/2006 | 1:04:00 | WOO-26 | ECA | TF | OSV | 1 | 716 |
| E243480586 | 11/13/2006 | 1:05:00 | HOB-16 | EBI | TF | OCO | 17 | 15,980 |
| E972993550 | 11/13/2006 | 1:08:00 | WOO-27 | ECA | TO | OCO | 81 | 57,186 |
| E959973515 | 11/13/2006 | 1:09:00 | SHD-15 | EBI | TF | OCO | 96 | 7,104 |
| E650686563 | 11/13/2006 | 1:15:00 | SPA-16 | ECA | EF | OFC | 928 | 279,328 |
| E563067421 | 11/13/2006 | 1:15:00 | ELD-23 | ECC | TO | OPO | 892 | 987,309 |
| E679298333 | 11/13/2006 | 1:22:00 | BDI-16 | EBJ | TF | OTF | 1 | 288 |
| E560339848 | 11/13/2006 | 1:30:00 | ROC-25 | ECC | TO | OCO | 487 | 76,459 |
| E286723644 | 11/13/2006 | 1:30:00 | GRI-13 | ECC | TF | OCO | 1,387 | 538,156 |
| E659543923 | 11/13/2006 | 1:33:00 | AIR-26 | ECC | TO | OCO | 301 | 122,507 |
| E773317791 | 11/13/2006 | 1:34:00 | TLN-0131 | ECC | TO | OCO | 3,335 | 1,955,212 |
| E121835287 | 11/13/2006 | 1:36:00 | MOT-14 | ECC | TO | OCO | 923 | 409,812 |
| E301374791 | 11/13/2006 | 1:47:00 | BAR-13 | ECC | TF | OCO | 1,017 | 603,081 |
| E675989591 | 11/13/2006 | 1:50:00 | ELD-26 | ECC | TO | OCO | 144 | 76,608 |
| E049832684 | 11/13/2006 | 1:51:00 | GRI-16 | ECC | TO | OCO | 1,642 | 467,970 |
| E865272829 | 11/13/2006 | 1:51:00 | ELD-27 | ECC | TO | OCO | 50 | 29,450 |
| E240742050 | 11/13/2006 | 1:51:00 | GRI-15 | ECC | TF | OCO | 806 | 199,888 |
| E675710676 | 11/13/2006 | 2:01:00 | ROC-26 | ECC | TF | OPO | 20 | 30,480 |
| E530369809 | 11/13/2006 | 2:05:00 | AIR-22 | ECC | TF | OPO | 1,014 | 299,130 |
| E445452196 | 11/13/2006 | 2:06:00 | BUC-15 | ECA | TO | OFC | 210 | 49,400 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E582630070 | 11/13/2006 | 2:06:00 | FRG-25 | ECC | TO | OCO | 200 | 132,000 |
| E393273124 | 11/13/2006 | 2:08:00 | SUN-12 | ECA | TO | OCO | 556 | 51,705 |
| E717043319 | 11/13/2006 | 2:08:00 | SUN-14 | ECA | EF | OFC | 416 | 75,296 |
| E121400937 | 11/13/2006 | 2:11:00 | RAI-12 | ECC | TO | OCO | 30 | 32,670 |
| E709869176 | 11/13/2006 | 2:12:00 | SWI-17 | ECC | TF | OCO | 83 | 58,349 |
| E492230276 | 11/13/2006 | 2:12:00 | GAR-13 | ECA | TO | OCO | 155 | 113,925 |
| E220552285 | 11/13/2006 | 2:12:00 | DGR-16 | ECA | TO | OFC | 2 | 1,742 |
| E123284523 | 11/13/2006 | 2:14:00 | WOL-25 | ECC | TO | OCO | 10 | 7,210 |
| E981367412 | 11/13/2006 | 2:14:00 | ELD-25 | ECC | TO | OCO | 2,044 | 991,644 |
| E229857079 | 11/13/2006 | 2:15:00 | HAS-15 | ECF | TO | OCO | 200 | 42,200 |
| E675159032 | 11/13/2006 | 2:16:00 | NHL-17 | EBD | TO | OCO | 8 | 1,320 |
| E637320784 | 11/13/2006 | 2:20:00 | IRO-17 | ECF | TO | OAR | 574 | 106,190 |
| E638864826 | 11/13/2006 | 2:20:00 | DEC-13 | ECC | TO | OCO | 40 | 32,360 |
| E689128473 | 11/13/2006 | 2:20:00 | MOT-15 | ECC | TO | OCO | 170 | 69,700 |
| E015778227 | 11/13/2006 | 2:22:00 | KAP-16 | ECA | TO | OCO | 35 | 25,830 |
| E212935724 | 11/13/2006 | 2:22:00 | GBK-13 | EAD | TF | OFU | 15 | 1,791 |
| E415954863 | 11/13/2006 | 2:24:00 | PAT-17 | ECC | TO | OPO | 10 | 7,560 |
| E594590686 | 11/13/2006 | 2:28:00 | MST-27 | EBI | TF | OCO | 17 | 9,724 |
| E904076457 | 11/13/2006 | 2:30:00 | PLG-15 | ECC | TO | OCO | 982 | 284,780 |
| E835456826 | 11/13/2006 | 2:41:00 | FRG-26 | ECC | TO | OCO | 36 | 19,044 |
| E833165171 | 11/13/2006 | 2:45:00 | BON-16 | ECA | TO | OCO | 10 | 329 |
| E100539368 | 11/13/2006 | 2:51:00 | HEM-16 | ECA | TO | OFC | 200 | 91,800 |
| E014930625 | 11/13/2006 | 2:54:00 | OBY-16 | ECC | TO | OCO | 3 | 1,962 |
| E010809560 | 11/13/2006 | 2:54:00 | PLG-13 | ECC | TF | OCO | 146 | 122,056 |
| E484239548 | 11/13/2006 | 2:55:00 | PAT-15 | ECC | TO | OCO | 66 | 54,120 |
| E042045790 | 11/13/2006 | 3:03:00 | LON-26 | ECC | TO | OCO | 166 | 119,188 |
| E037260681 | 11/13/2006 | 3:04:00 | LUH-14 | ECC | TO | OCO | 1,814 | 449,872 |
| E799040147 | 11/13/2006 | 3:08:00 | OSC-25 | EBI | TO | OTF | 4 | 259 |
| E275581019 | 11/13/2006 | 3:08:00 | CHR-22 | ECE | TO | OFU | 50 | 7,122 |
| E094311779 | 11/13/2006 | 3:12:00 | HAW-11 | ECC | TO | OCO | 14 | 4,466 |
| E363293606 | 11/13/2006 | 3:17:00 | BLU-16 | ECC | TO | OCO | 60 | 56,700 |
| E549907914 | 11/13/2006 | 3:24:00 | BON-17 | ECA | TF | OSV | 1 | 696 |
| E790794614 | 11/13/2006 | 3:27:00 | ETN-13 | EBH | TF | OCO | 6 | 977 |
| E283640246 | 11/13/2006 | 3:31:00 | BUC-26 | ECA | TF | OPO | 40 | 19,920 |
| E354658341 | 11/13/2006 | 3:33:00 | DGR-15 | ECA | TO | OCO | 6 | 4,356 |
| E943637211 | 11/13/2006 | 3:33:00 | BON-16 | ECA | TO | OCO | 54 | 21,210 |
| E064060997 | 11/13/2006 | 3:36:00 | LAC-17 | ECC | TF | OTF | 1 | 744 |
| E152819495 | 11/13/2006 | 3:36:00 | BON-16 | ECA | TO | OCO | 2 | 960 |
| E091475722 | 11/13/2006 | 3:40:00 | MKI-17 | ECC | TO | OSV | 3 | 3,930 |
| E814046199 | 11/13/2006 | 3:52:00 | SOO-25 | EBI | TF | OCO | 159 | 64,713 |
| E897210113 | 11/13/2006 | 3:56:00 | HOB-15 | EBI | TF | OCO | 7 | 3,388 |
| E759032079 | 11/13/2006 | 4:01:00 | BON-16 | ECA | TF | OCO | 21 | 6,069 |
| E660971590 | 11/13/2006 | 4:05:00 | LON-22 | ECC | TO | OTF | 50 | 56,750 |
| E308778681 | 11/13/2006 | 4:07:00 | LEA-13 | EBI | TF | OCO | 345 | 18,987 |
| E531592408 | 11/13/2006 | 4:14:00 | ENU-17 | EBI | TO | OTF | 1 | 111 |
| E096392418 | 11/13/2006 | 4:22:00 | ROC-25 | ECC | TO | OCO | 20 | 17,360 |
| E244667100 | 11/13/2006 | 4:23:00 | OSC-23 | EBI | TF | OCO | 17 | 7,242 |
| E296258598 | 11/13/2006 | 4:31:00 | CAS-16 | EBH | TO | OPO | 757 | 404,560 |
| E611445942 | 11/13/2006 | 4:42:00 | MVW-13 | EBJ | TF | OFU | 16 | 4,128 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E162478008 | 11/13/2006 | 4:45:00 | LON-23 | ECC | TO | OCO | 103 | 53,045 |
| E813130374 | 11/13/2006 | 4:59:00 | SHD-18 | EBI | TF | OCO | 31 | 14,911 |
| E163307953 | 11/13/2006 | 5:01:00 | SUM-15 | EAC | TF | OCO | 1 | 348 |
| E895005700 | 11/13/2006 | 5:04:00 | CLE-11 | EBH | TO | OCO | 802 | 240,600 |
| E031800873 | 11/13/2006 | 5:11:00 | EDG-15 | ECA | TF | OCO | 57 | 16,587 |
| E419543260 | 11/13/2006 | 5:16:00 | LWS-15 | EBJ | TF | OCO | 1 | 489 |
| E657858533 | 11/13/2006 | 5:18:00 | BAR-17 | ECC | TO | OCO | 1 | 947 |
| E658132339 | 11/13/2006 | 5:18:00 | STW-12 | ECA | TF | OSV | 1 | 132 |
| E996202080 | 11/13/2006 | 5:22:00 | WLK-13 | ECA | TO | OCO | 39 | 43,602 |
| E975223251 | 11/13/2006 | 5:24:00 | MCA-13 | ECC | TO | OCO | 47 | 19,742 |
| E926967723 | 11/13/2006 | 5:35:00 | KAP-16 | ECA | TO | OCO | 62 | 41,664 |
| E116268790 | 11/13/2006 | 5:36:00 | BDI-13 | EBI | TF | OFU | 9 | 801 |
| E932054333 | 11/13/2006 | 5:40:00 | TSB-HY | EBF | TO | OCO | 794 | 333,480 |
| E691423055 | 11/13/2006 | 5:48:00 | LAC-15 | ECC | TO | OCO | 12 | 7,344 |
| E011819771 | 11/13/2006 | 6:13:00 | LMD-16 | EBJ | TO | OTF | 1 | 92 |
| E258105491 | 11/13/2006 | 6:17:00 | RED-23 | EBD | EF | UPC | 45 | 20,925 |
| E551975665 | 11/13/2006 | 6:18:00 | VAS-23 | EBL | TF | OCO | 1 | 414 |
| E846869695 | 11/13/2006 | 6:18:00 | WOO-27 | ECA | TF | OCO | 12 | 5,484 |
| E603581818 | 11/13/2006 | 6:30:00 | CED-17 | ECA | TO | OFU | 1 | 314 |
| E243679303 | 11/13/2006 | 6:32:00 | IRO-16 | ECF | TF | OFU | 5 | 205 |
| E680474013 | 11/13/2006 | 6:39:00 | NOR-26 | EBD | EF | OTR | 2 | 432 |
| E352586995 | 11/13/2006 | 6:40:00 | GRI-16 | ECC | TO | OCO | 83 | 62,250 |
| E103046850 | 11/13/2006 | 6:41:00 | WLS-16 | EAC | TO | OFU | 56 | 6,585 |
| E067829957 | 11/13/2006 | 6:42:00 | STW-13 | ECA | TF | OSV | 3 | 2,115 |
| E966362971 | 11/13/2006 | 6:42:00 | KCR-17 | EBJ | TF | OFU | 2 | 146 |
| E939113166 | 11/13/2006 | 6:57:00 | FRU-26 | ECA | TO | OTF | 3 | 741 |
| E014858381 | 11/13/2006 | 7:03:00 | 39429 | ECC | TO | OSV | 9 | 5,373 |
| E026266295 | 11/13/2006 | 7:06:00 | LWS-15 | EBI | TF | OCO | 1 | 379 |
| E198263896 | 11/13/2006 | 7:08:00 | ENU-17 | EBI | TO | OTF | 8 | 1,216 |
| E548547249 | 11/13/2006 | 7:11:00 | LTA-18 | ECA | TO | OFC | 12 | 1,380 |
| E074170142 | 11/13/2006 | 7:12:00 | OSC-25 | EBI | TO | OFU | 2 | 416 |
| E008232059 | 11/13/2006 | 7:14:00 | LUH-14 | ECC | TO | OCO | 60 | 34,560 |
| E082340689 | 11/13/2006 | 7:23:00 | ALG-12 | EAC | CR | OSV | 2 | 354 |
| E386323176 | 11/13/2006 | 7:24:00 | SKY-23 | EBD | EF | OCO | 10 | 7,667 |
| E248028588 | 11/13/2006 | 7:44:00 | SNQ-17 | EBF | TO | OSV | 1 | 76 |
| E986246873 | 11/13/2006 | 8:05:00 | LAC-13 | ECC | TO | OCO | 2 | 578 |
| E573101933 | 11/13/2006 | 8:16:00 | LAC-16 | ECC | TF | OCO | 4 | 896 |
| E714788370 | 11/13/2006 | 8:19:00 | UHL-23 | EBD | TO | OCO | 1 | 131 |
| E991792792 | 11/13/2006 | 8:20:00 | VAS-12 | EBL | EF | OTR | 4 | 1,776 |
| E767247540 | 11/13/2006 | 8:28:00 | AIR-26 | ECC | TF | OCO | 134 | 153,028 |
| E881281188 | 11/13/2006 | 8:38:00 | BUC-16 | ECA | TO | OCO | 24 | 11,304 |
| E740588594 | 11/13/2006 | 8:38:00 | BUC-16 | ECA | PO | OSV | 1 | 387 |
| E110431260 | 11/13/2006 | 8:40:00 | SHD-17 | EBI | TF | OSV | 1 | 270 |
| E043368564 | 11/13/2006 | 8:43:00 | FWY-15 | EBJ | TO | OFC | 6 | 1,092 |
| E399192352 | 11/13/2006 | 8:47:00 | LLT-16 | EBD | TO | OCO | 1 | 297 |
| E112253889 | 11/13/2006 | 8:50:00 | KCR-17 | EBJ | TF | OTF | 1 | 95 |
| E896296336 | 11/13/2006 | 8:52:00 | GRI-15 | ECC | TO | OCO | 3 | 2,274 |
| E979910843 | 11/13/2006 | 8:59:00 | LYO-15 | EBJ | TF | OCO | 14 | 994 |
| E208212632 | 11/13/2006 | 9:01:00 | ORT-22 | ECA | TO | OFC | 2 | 1,256 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E503532381 | 11/13/2006 | 9:04:00 | ROC-15 | ECC | TO | OSV | 3 | 2,778 |
| E616265905 | 11/13/2006 | 9:07:00 | BON-16 | ECA | TO | OSV | 1 | 344 |
| E405349571 | 11/13/2006 | 9:10:00 | MAN-12 | ECD | TF | OSV | 1 | 145 |
| E771431147 | 11/13/2006 | 9:14:00 | MCK-12 | EAA | PO | OTF | 1 | 84 |
| E700486265 | 11/13/2006 | 9:16:00 | MOT-14 | ECC | TO | OCO | 15 | 16,410 |
| E087822557 | 11/13/2006 | 9:17:00 | WLS-13 | EAC | PO | OSV | 2 | 196 |
| E304957584 | 11/13/2006 | 9:22:00 | VIS-22 | EAA | DU | UPC | 60 | 23,280 |
| E033697041 | 11/13/2006 | 9:22:00 | BUC-16 | ECA | TO | OTF | 2 | 616 |
| E257902842 | 11/13/2006 | 9:22:00 | MOT-15 | ECC | TO | OCO | 141 | 13,818 |
| E322677112 | 11/13/2006 | 9:38:00 | MHT-15 | EBJ | TF | OSV | 4 | 328 |
| E841411376 | 11/13/2006 | 9:49:00 | ETN-13 | EBH | DU | UPC | 1 | 769 |
| E767962870 | 11/13/2006 | 9:55:00 | BUC-16 | ECA | TO | OFC | 4 | 1,460 |
| E467863354 | 11/13/2006 | 10:05:00 | AIR-22 | ECC | TF | OSW | 76 | 41,572 |
| E954064365 | 11/13/2006 | 10:07:00 | LTA-18 | ECA | AO | OCO | 1 | 218 |
| E679376298 | 11/13/2006 | 10:16:00 | EDG-15 | ECA | TO | OTF | 4 | 476 |
| E467500294 | 11/13/2006 | 10:20:00 | VAS-13 | EBL | TF | OSV | 1 | 75 |
| E395802515 | 11/13/2006 | 10:27:00 | CWD-22 | EBD | PO | USV | 1 | 153 |
| E226255553 | 11/13/2006 | 10:44:00 | BUC-16 | ECA | TO | OTF | 2 | 622 |
| E996394642 | 11/13/2006 | 10:53:00 | WAB-13 | EBI | TF | OFU | 5 | 635 |
| E357424019 | 11/13/2006 | 10:59:00 | BRI-15 | EAA | PO | USV | 1 | 129 |
| E324112880 | 11/13/2006 | 11:12:00 | MER-16 | EBE | EF | PMF | 4 | 752 |
| E687497645 | 11/13/2006 | 11:42:00 | BAR-13 | ECC | TO | OCO | 232 | 88,160 |
| E658781673 | 11/13/2006 | 11:44:00 | PIN-26 | EBD | EF | OSV | 1 | 182 |
| E455587530 | 11/13/2006 | 11:52:00 | MOT-15 | ECC | TF | OHR | 169 | 55,094 |
| E760975137 | 11/13/2006 | 11:59:00 | OSC-22 | EBI | TF | OCO | 48 | 11,568 |
| E138679201 | 11/13/2006 | 12:03:00 | KAP-13 | ECA | CP | OPO | 3 | 1,995 |
| E382304005 | 11/13/2006 | 12:07:00 | BLA-13 | EAA | DU | UPC | 2 | 552 |
| E916690733 | 11/13/2006 | 12:11:00 | BRS-13 | EAC | UN | OFC | 4 | 480 |
| E658961293 | 11/13/2006 | 12:14:00 | PEA-15 | EBJ | TO | OCR | 867 | 155,243 |
| E846868298 | 11/13/2006 | 12:18:00 | PRI-21 | ECC | TF | OPO | 95 | 103,740 |
| E652817113 | 11/13/2006 | 12:23:00 | CHA-15 | ECC | TO | OSV | 4 | 1,708 |
| E950874325 | 11/13/2006 | 12:37:00 | ROC-16 | ECC | TO | OTF | 80 | 49,840 |
| E884128906 | 11/13/2006 | 12:42:00 | BLU-17 | ECC | TO | OCO | 24 | 4,512 |
| E578146255 | 11/13/2006 | 13:27:00 | BLU-13 | ECC | TO | OPO | 13 | 5,057 |
| E459495422 | 11/13/2006 | 13:38:00 | HAN-13 | EAA | EF | OTF | 1 | 70 |
| E857911350 | 11/13/2006 | 13:38:00 | SHD-18 | EBI | TO | UTC | 1 | 38 |
| E857749470 | 11/13/2006 | 13:42:00 | LON-23 | ECC | TO | OCO | 19 | 7,182 |
| E888153689 | 11/13/2006 | 14:17:00 | ORT-23 | ECA | TO | OCO | 35 | 17,675 |
| E234496400 | 11/13/2006 | 14:18:00 | ORT-23 | ECA | TO | OPO | 50 | 35,048 |
| E249638159 | 11/13/2006 | 14:19:00 | BON-16 | ECA | TO | OFC | 4 | 628 |
| E571148275 | 11/13/2006 | 14:24:00 | LAC-16 | ECC | TF | OTF | 2 | 192 |
| E859065769 | 11/13/2006 | 14:36:00 | WLK-15 | ECA | TO | OCO | 5 | 1,150 |
| E192544660 | 11/13/2006 | 14:40:00 | GAR-15 | ECA | TO | OFC | 1 | 10 |
| E112189185 | 11/13/2006 | 15:02:00 | LEA-15 | EBI | TO | OTF | 2 | 156 |
| 10657350 | 11/13/2006 | 15:15:00 | SKY-23 | EBE | EF | OPO | 2 | 854 |
| E249948332 | 11/13/2006 | 15:21:00 | LON-26 | ECC | TF | OTF | 8 | 3,400 |
| E457402927 | 11/13/2006 | 15:22:00 | LTA-18 | ECA | TO | OCO | 8 | 1,192 |
| E895500632 | 11/13/2006 | 15:30:00 | GAR-15 | ECA | TO | OSV | 1 | 14 |
| 10656508 | 11/13/2006 | 15:43:00 | FAC-13 | EBE | EF | USV | 1 | 470 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E599459032 | 11/13/2006 | 15:44:00 | GAR-15 | ECA | PO | OSV | 1 | 141 |
| E700294445 | 11/13/2006 | 15:50:00 | HAZ-13 | EBE | EF | UTR | 20 | 13,507 |
| E218089723 | 11/13/2006 | 15:57:00 | MAP-16 | EBE | DU | UPC | 25 | 10,450 |
| E108655826 | 11/13/2006 | 15:58:00 | ZEN-23 | EBJ | TF | OFU | 94 | 7,238 |
| E544138777 | 11/13/2006 | 16:18:00 | KAP-16 | ECA | TO | OCO | 10 | 1,600 |
| E211377229 | 11/13/2006 | 16:18:00 | WOB-23 | EAA | EF | UPC | 15 | 2,576 |
| E714880584 | 11/13/2006 | 16:23:00 | SHD-17 | EBI | TF | OSV | 1 | 290 |
| E609902635 | 11/13/2006 | 16:35:00 | BON-17 | ECA | TF | OSV | 1 | 80 |
| E821826858 | 11/13/2006 | 16:41:00 | RDO-15 | EBJ | TO | OTF | 5 | 270 |
| E778595214 | 11/13/2006 | 16:44:00 | SHD-18 | EBI | EF | OCO | 58 | 17,211 |
| E158065098 | 11/13/2006 | 16:51:00 | BLU-17 | ECC | TO | OCO | 3 | 1,107 |
| E556834153 | 11/13/2006 | 17:16:00 | OSC-23 | EBI | TO | OTF | 1 | 153 |
| E428676668 | 11/13/2006 | 17:29:00 | LMD-16 | EBJ | EF | USV | 1 | 177 |
| E510654193 | 11/13/2006 | 17:39:00 | STA-13 | EBK | EF | USV | 1 | 82 |
| E300865383 | 11/13/2006 | 17:47:00 | NOR-26 | EBD | EF | OTF | 12 | 2,148 |
| E854418270 | 11/13/2006 | 17:55:00 | MOT-15 | ECC | TF | OTF | 14 | 1,288 |
| E789863784 | 11/13/2006 | 18:26:00 | ELD-25 | ECC | TO | OCO | 3 | 1,407 |
| E883644137 | 11/13/2006 | 18:28:00 | STW-13 | ECA | TF | OSV | 1 | 190 |
| E943421923 | 11/13/2006 | 18:31:00 | GRI-13 | ECC | TF | OCO | 4 | 1,672 |
| E579446297 | 11/13/2006 | 18:38:00 | GRV-15 | ECA | TO | DNO | 17 | 2,924 |
| E262158677 | 11/13/2006 | 19:08:00 | DGR-13 | ECA | TO | OCO | 1 | 147 |
| E457090598 | 11/13/2006 | 19:17:00 | AIR-22 | ECC | TO | DNO | 34 | 1,156 |
| 10656509 | 11/13/2006 | 19:35:00 | ROS-13 | EBE | EF | USV | 1 | 145 |
| E904376356 | 11/13/2006 | 19:56:00 | PMA-16 | ECE | TO | OFU | 53 | 1,537 |
| E333631393 | 11/13/2006 | 20:22:00 | GRI-16 | ECC | TF | OCO | 5 | 1,515 |
| E062672683 | 11/13/2006 | 20:42:00 | BIG-12 | EAC | EF | OTF | 2 | 159 |
| E871298410 | 11/13/2006 | 20:44:00 | RAI-12 | ECC | TF | OCO | 3 | 717 |
| E368831970 | 11/13/2006 | 20:44:00 | BLU-13 | ECC | TF | OTR | 5 | 1,655 |
| E347499765 | 11/13/2006 | 20:59:00 | PHA-16 | EBE | EF | UFJ | 96 | 45,312 |
| E047259260 | 11/13/2006 | 21:17:00 | PIN-26 | EBF | EF | UFJ | 5 | 1,312 |
| E747546114 | 11/13/2006 | 21:37:00 | NUG-26 | EAA | EF | OIN | 84 | 8,172 |
| E096334014 | 11/13/2006 | 21:54:00 | SHD-18 | EBI | EO | OTF | 2 | 303 |
| E470022779 | 11/13/2006 | 22:48:00 | WOL-23 | ECC | EF | USV | 1 | 852 |
| E225677110 | 11/13/2006 | 23:14:00 | ROC-16 | ECC | TF | OTF | 5 | 640 |

### Terms, Codes and Definitions Used on Detail Reports

| #### Notification | [Notification Number] A number assigned by SAP, identifying the outage record |
| --- | --- |
| Date | The date of the outage |
| Time | The time of the outage |
| Circuit | [Reference Circuit] The circuit identifier for the affected circuit |
| F/LOC | [Functional Location] The grid number where the outage occurred. If the grid number is not available, the Reference Circuit identifier occupies this field |
| EQT NBR | [Equipment Number] A number used to tie the equipment involved in the outage to the related information in SAP. This number does not represent the physical number of the equipment |

| Area | [Maintenance Planner Group] A code representing the energy, region and service center |  |
| --- | --- | --- |
|  | EAA – Bellingham | EBJ – South King |
|  | EAB – Lynden | EBK – Southwest King |
|  | EAC – Skagit | EBL – Vashon |
|  | EAD – Whidbey | ECA – Puyallup |
|  | EBD – Redmond | ECC – Olympia |
|  | EBE – Factoria | ECD – Port Orchard |
|  | EBF – Snoqualmie | ECE – Poulsbo |
|  | EBI – Enumclaw | ECF – Port Townsend |

| Cause | Cause of Outage |  |
| --- | --- | --- |
|  | AO – Accident Other | EF – Equipment Failure |
|  | BA – Bird or Animal | EO – Electrical Overload |
|  | CP – Car Pole | FI – Faulty Installation |
|  | CR – Customer Request | TF – Tree Off Right-of-Way |
|  | DU – Dig-up Underground | TO – Tree On Right-of-Way |
|  | SO – Scheduled Outage | UN – Unknown |

| Equipment | Affected by, or involved in the outage |  |
| --- | --- | --- |
|  | OCN – Connector | OSW – Overhead Switch |
|  | OCO – Overhead Conductor | OTF – Overhead Transformer Fuse |
|  | OCR – Crossarm | OTR – Overhead Transformer |
|  | OFC – Overhead Cut-out | OUP – OH to UG Primary |
|  | OFS – Overhead Fire Signal | OUS – OH to UG Secondary Service |
|  | OFU – Fuse Link/OH Line Fuse | SBF – High-side Bank Fuse |
|  | OGS – Span Guy | SCB – Power Circuit Breaker |
|  | OHR – Overhead Recloser | UOT – Underground Outdoor Term |
|  | OIN – Insulator | UPC – Underground Primary Cable |
|  | OJU- Jump Wire | UPT – Padmount Transformer |
|  | OPI – Overhead Pin Insulator | USV – Underground Service |
|  | OPO – Pole | UTC – Underground Terminal Fuse |
|  | OSV – Overhead Service | UTR – Submersible Transformer |
|  | ORE – Regulator |  |

#### Codes, Definitions – Continued

| CUST OUT | [Customer Out] The number of customers without power for any given outage record |
| --- | --- |
| CUST MIN | [Customer Minutes] The total number of minutes customers were without power for any given record |

| CODE | [Storm Code] An event descriptor |
| --- | --- |
|  | NON – Non Storm / Normal Conditions |
|  | WTH – Weather Related (eg: wind storm, showers, etc) |
|  | MAJ – Major event |

### Newsprint Media Coverage

November 14, 2006

High winds snap limbs, topple trees, cut power

Jeremy Pawloski, The Olympian

Trees and branches downed by wind gusts Sunday night and Monday morning caused up to 200 power outages in Thurston County, including one that led to canceling classes at The Evergreen State College for the first time since 2004.

The Thurston County area was the hardest hit by outages Monday among Puget Sound Energy's coverage area, said Puget Sound Energy spokeswoman Dorothy Bracken.

The 200 or so outages in the Thurston County area were tough to deal with and labor intensive because of the number of small outages, she added.

"The power was out for about 13 hours," said Evergreen spokesman Anthony Sermonti during an on-campus interview Monday afternoon about 2:30. "It just came back on. There was significant damage to the power lines around campus."

Another outage darkened an estimated 1,000 homes in the Littlerock Road area, when a falling tree struck a power line parallel to the road at 1:42 a.m. Monday, Bracken said. The area was between 103rd and 110th avenues, said Thurston County Sheriff's Sgt. Alvin Griffin. Littlerock Road was closed for part of the day Monday.

Power would not be restored to the last 50 or so customers in the Littlerock Road area until this morning, Bracken said Monday night. The outage in the Littlerock Road area was taking a long time to fix because a tree severed three separate rows of lines, which is uncommon and difficult to repair, Bracken said.

New outages caused by falling trees continued during the day Monday, with a power line reportedly down late Monday afternoon at 101st Avenue and Delphi Road Southwest, Griffin said.

"It's very long tedious work, going from one small outage to the next small outage," Bracken said. "Ever since the power outages occurred, they've been working to get the power restored."

Wind gusts at Olympia Airport were measured at 33 miles per hour near midnight Sunday, Dennis D'Amico, a spokesman for the National Weather Service in Seattle, said. However a gust of 63 miles per hour was reported Sunday night by a weather spotter who lives near Lake Lawrence, he said.

What's next

Western Washington is supposed to get a brief break from rains today, but by Wednesday a "decent-sized storm" bringing more wind and rains will move through the area quickly, D'Amico said. Wednesday's rains will bring rains to higher elevations in the mountains, and the potential for minor flooding, D'Amico said. No flood warnings or flood watches had been issued as of Monday night, but D'Amico said officials would be watching the river levels closely.

High winds snap limbs, topple trees, cut power - continued

"It's a decent-sized storm, but it's going to be a quick mover," D'Amico said of the storm expected to hit on Wednesday.

A full day of classes at Evergreen had not been canceled since heavy snows hit Olympia in 2004, Sermonti said. Classes at Evergreen will resume with their normal schedules today, he added.

After power was restored to Evergreen, one off-campus apartment complex near the college, Cooper's Glen Apartments on Overhulse Road, remained without power Monday afternoon. A resident of the apartments, Zach Schutz, said that so far, he was not too bothered by the inconvenience, but wished he could turn on his heat.

"It's just kind of cold right now," Schutz said. "We just want to get it back soon so our milk doesn't go bad."

Another prolonged outage in Thurston County caused by falling trees and tree limbs was reported in the area of Bald Hills Road and Smith Prairie Road in Yelm, Bracken said. Power was restored there Monday night, Bracken said.

The Department of Transportation reported having to move downed power lines that were blocking state Route 507 in both directions near the border of Thurston and Lewis counties in Bucoda on Monday morning. The lines were removed and the road was reopened shortly after 11 a.m. Monday, according to a DOT news release.

Power outages weren't the only problems caused by the high winds Sunday and Monday.

A couple who lives in Seashore Villa in Olympia reported that a strong gust of wind early Monday morning blew the metal roof off of their back deck.

"I never heard such a noise in my life," said Jeannette Ward, who said it sounded like "a freight train coming through."

Law enforcement reported the usual increase in fender benders and minor crashes as heavier rains hit during rush hour Monday.

DOT also reported that U.S. Highway 101 north of Shelton, closed since Nov. 6 by a mudslide caused by heavy rains, will not reopen until Wednesday at the earliest. The slopes surrounding the slide were too unstable during the weekend to complete the work clearing the debris, according to DOT. The work is scheduled to be completed today and the road to reopen on Wednesday, but Monday night, a DOT spokesman said those dates are not fixed in stone.

Safety tips

Puget Sound Energy offers the following safety tips for how to deal with power outages.

Before a storm

• Assemble an emergency kit. It should include a battery-powered radio, a flashlight, extra batteries, a first-aid kit, a fire extinguisher and bottled water and non-perishable food.

• Make sure your blanket supply is adequate for extended outages. In an emergency, blankets and cardboard can be hung over windows and doorways to minimize heat loss.

High winds snap limbs, topple trees, cut power – continued

During an outage

• Report outages or downed power lines by calling Puget Sound Energy at 1-888-225-5773. The automated outage reporting system allows for direct input of outage information and helps speed restoration.

• Keep refrigerators and freezers shut, opening them only when absolutely necessary.

• Open faucets slightly so they drip to prevent pipes from freezing.

• Disconnect house circuits from Puget Sound Energy power lines if you are using a portable generator during an outage. Pull or switch to "off" all main fuses or circuit breakers to protect power line crews working to restore service.