2006

Qualifying Storm Events

December 11, 2006

# Table of Contents

Table of Contents	2

Event Description	3

Date of event	3

Event Type	3

Service Areas Affected	3

Number of Customers Affected	3

Summary of System Impacts	3

Mobilization Summary	3

Major Event Day – Qualification	5

Qualified Events - 2006	5

Current Event – Calculation Detail	5

Cumulative list of events that have qualified	5

Event Restoration – Cost Summary	6

Restoration Cost Detail by Qualifying Event	6

YTD Storm Restoration Cost Detail – Through December 11, 2006	6

Detail Documents	7

Restoration Cost Detail – Current Event	8

IEEE-1366 - Detailed List of Distribution Circuits with Outages	9

Terms, Codes and Definitions Used on Detail Reports	13

Newsprint Media Coverage	15

# Event Description

### Date of event

December 11, 2006

### Event Type

Wind storm.

### Service Areas Affected

With winds gusting to more than 60 MPH, this short, high intensity wind storm impacted primarily the western and northern portions of Puget Sound Energy’s electric service area. The event began with high winds in Kitsap, Whatcom and Skagit Counties and was followed just hours later by a second smaller burst of highs wind in north King County.

Falling trees and large limbs caused limited storm damage to the electric system in Kitsap, Jefferson, King, Island, Skagit and Whatcom Counties.

### Number of Customers Affected

Approximately 34,980 electric service customers were without power.

### Summary of System Impacts

| Total Number of Outages | 394 |
| --- | --- |
| Distribution Circuits Totally Out | 11 |
| Distribution Circuits Partially Out | 383 |

| Transmission Circuits Affected | 1 |
| --- | --- |
| Substations Totally Off-line | 1 |

### Mobilization Summary

#### Operating bases

| Base | Date Opened | Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
| Kitsap | 12/11/2006 | 13:00 | 12/11/2006 | 16:00 |
| Whatcom | 12/11/2006 | 14:00 | 12/12/2006 | 15:00 |
| Skagit | 12/11/2006 | 15:15 | 12/12/2006 | 08:00 |
| N King | 12/12/2006 | 00:30 | 12/12/2006 | 09:15 |

#### Emergency Operations Center

| EOC | Date Opened | #### Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
|  | 12/11/2006 | 17:00 | 12/12/2006 | 13:30 |

# Major Event Day – Qualification

- IEEE 1366 Method

IEEE 1366 was established to present a set of terms and definitions which can be used to foster uniformity in the development of distribution service reliability indices, to identify factors which affect the indices, and to aid in consistent reporting practices among utilities.  Also, it provides guidance for new personnel in the reliability area, and tools for internal as well as external comparisons.  The Major Event Day definition was created as part of IEEE 1366 to allow for consistent calculation of reliability metrics between utilities, and enable more valid comparisons with other utility reliability metrics.

IEEE Major Event Day Calculation (2.5 BETA METHOD) - A threshold on daily SAIDI is computed once a year, following year end. - Assemble the 5 most recent years of historical values of SAIDI/day. - Discard any days in the data set that has a SAIDI/day of zero. - Find the natural logarithm of each value in the data set. - Compute the average Alpha and the standard deviation (Beta) of the natural logarithms computed in step 3. - Compute the threshold Tmed where Tmed = exp(Alpha + 2.5 * Beta) - Any day in the next year with SAIDI > Tmed is a major event day.

Puget Sound Energy’s Major Event Threshold for 2006: 4.97 Minutes

# Qualified Events - 2006

### Current Event – Calculation Detail

| Event Date | Total Customer Minutes | Average Customer Count | Daily SAIDI – Customer Minutes /Customer Count |
| --- | --- | --- | --- |
| 12/11/2006 | 13,542,896 | 1,044,330 | 12.97 |

### Cumulative list of events that have qualified

| Date(s) | T-med Score | O&M – Deferrable Accumulation |
| --- | --- | --- |
| 1/1/2006 | 5.35 | $242,708 |
| 1/31/2006 | 11.19 | $653,176 |
| 2/4/2006 | 161.65 | $6,104,116 |
| 2/10/2006 | 8.34 | $0 |
| 2/17/2006 | 40.13 | $0 |
| 3/8/2006 | 6.16 | $0 |
| 11/13/2006 | 13.24 | $0 |
| 11/15/2006 | 107.64 | $0 |
| 11/26/2006 | 27.58 | $0 |
| 12/11/2006 | 12.97 | $0 |

# Event Restoration – Cost Summary

### Restoration Cost Detail by Qualifying Event

| Date | Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M – Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/1/2006 | $0 | $0 | $0 | $23,995 | $242,708 | $266,703 | $266,703 |
| 1/31/2006 | $0 | $70,613 | $0 | $35,780 | $653,176 | $688,956 | $759,569 |
| 2/4/2006 | $2,853,981 | $311,579 | $0 | $395,638 | $6,104,116 | $6,499,754 | $9,665,314 |
| 2/10/2006 | $468,301 | $110,144 | $0 | $17,139 | $0 | $17,139 | $595,584 |
| 2/17/2006 | $3,309,247 | $141,574 | $0 | $127,653 | $0 | $127,653 | $3,578,474 |
| 3/8/2006 | $444,758 | $3,929 | $0 | $34,731 | $0 | $34,731 | $483,418 |
| 11/13/2006 | $1,490,582 | $26,308 | $0 | $87,272 | $0 | $87,272 | $1,604,162 |
| 11/15/2006 | 7,866,039 | $15,072 | $20,536 | $422,960 | $0 | $422,960 | $8,324,607 |
| 11/26/2006 | $5,149,885 | $197,468 | $0 | $273,586 | $0 | $273,586 | $5,620,939 |
| 12/11/2006 | $1,491,309 | $11,697 | $0 | $10,288 | $0 | $10,288 | $1,513,294 |

### YTD Storm Restoration Cost Detail – Through December 11, 2006

| Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| $23,588,072 | $888,384 | $20,536 | $1,425,777 | $7,000,000 | $8,425,777 | $32,922,769 |

# Detail Documents

- Restoration Cost Detail – Current Event

- Detailed List of Distribution Circuits with Outages

- Terms, Codes & Definitions Used on Detail Reports

- Newsprint Media Coverage

### Restoration Cost Detail – Current Event

|  | Puget Sound Energy |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | December 11 Storm Damage Repair Costs |  |  |  |  |  |  |  |  |
|  |  | Qualifying Events Deferred Account | Capital | C&D Recoverable from Direct Billings (Costs Not Yet Billed) | O&M - Not Deferrable | O&M - Deferrable Accumulation | Total O&M | Total |  |
|  | Labor |  |  |  |  |  |  |  |  |
|  | ST |  |  |  |  | $14,248 | $14,248 | $14,248 |  |
|  | OT |  |  |  |  | $166,067 | $166,067 | $166,067 |  |
|  | Total Labor | $0 | $0 | $0 | $0 | $180,316 | $180,316 | $180,316 |  |
|  | Labor OH |  |  |  |  | $78,724 | $78,724 | $78,724 |  |
|  | Materials |  | $11,220 |  |  | $52,334 | $52,334 | $63,554 |  |
|  | Contractors |  | $478 |  |  | $1,164,124 | $1,164,124 | $1,164,602 |  |
|  | Other Direct Charges |  |  |  |  | $6,261 | $6,261 | $6,261 |  |
|  | Fleet |  |  |  |  | $9,550 | $9,550 | $9,550 |  |
|  | Other Assessments |  |  |  | $10,288 |  | $10,288 | $10,288 |  |
|  | Deferred Expenses | $1,491,309 |  |  |  | ($1,491,309) | ($1,491,309) | $0 |  |
|  |  | $1,491,309 | $11,698 | $0 | $10,288 | ($0) | $10,288 | $1,513,295 |  |

### IEEE-1366 - Detailed List of Distribution Circuits with Outages

| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 10659967 | 12/11/2006 | 0:29:00 | CPV-13 | EAD | TF | OCR | 546 | 63,651 |
| E622874540 | 12/11/2006 | 1:48:00 | PET-13 | EAC | TO | OCO | 635 | 199,765 |
| E358685788 | 12/11/2006 | 2:34:00 | SLA-17 | EAA | TF | OCO | 25 | 14,000 |
| E084012477 | 12/11/2006 | 3:20:00 | BCH-12 | EAA | TF | OCO | 558 | 182,466 |
| E223612933 | 12/11/2006 | 3:42:00 | ROS-17 | EBD | EF | OTF | 8 | 1,144 |
| E442859287 | 12/11/2006 | 4:31:00 | KAP-13 | ECA | TF | OCO | 50 | 3,776 |
| E903101096 | 12/11/2006 | 4:52:00 | BLU-13 | ECC | TO | OCO | 80 | 21,880 |
| E129200469 | 12/11/2006 | 4:56:00 | MTV-16 | EAC | TF | OFC | 8 | 917 |
| E421428324 | 12/11/2006 | 5:05:00 | PMA-12 | ECE | TO | OCO | 20 | 459 |
| E433792108 | 12/11/2006 | 5:51:00 | GRI-13 | ECC | TF | OCO | 53 | 15,953 |
| E854866758 | 12/11/2006 | 6:46:00 | CRE-12 | EAD | TF | OCO | 1 | 207 |
| E192362800 | 12/11/2006 | 7:20:00 | BIG-15 | EAC | EF | UPC | 3 | 1,161 |
| E679717622 | 12/11/2006 | 7:23:00 | NBE-15 | EBF | EF | OTF | 1 | 35 |
| E183676287 | 12/11/2006 | 8:01:00 | PTL-16 | ECF | TF | OSV | 1 | 106 |
| 10659974 | 12/11/2006 | 8:15:00 | EDG-15 | ECA | EF | OCO | 1 | 160 |
| E526201856 | 12/11/2006 | 8:30:00 | COT-15 | EBD | SO | OPO | 2 | 664 |
| E322231209 | 12/11/2006 | 8:43:00 | SCH-13 | EAA | EF | OTF | 1 | 47 |
| E269376165 | 12/11/2006 | 8:48:00 | WOB-25 | EAA | TF | OTF | 1 | 57 |
| E319432044 | 12/11/2006 | 9:43:00 | PLA-21 | EBD | EF | UEL | 47 | 13,019 |
| E924899162 | 12/11/2006 | 9:44:00 | HWD-22 | EBD | SO | UPC | 79 | 27,176 |
| E447032787 | 12/11/2006 | 10:01:00 | SHE-16 | ECE | PO | OTF | 1 | 88 |
| E141551775 | 12/11/2006 | 10:09:00 | BIG-12 | EAC | PO | USV | 1 | 131 |
| E729291807 | 12/11/2006 | 10:34:00 | ROE-13 | EAA | TF | OCO | 40 | 11,240 |
| E755664647 | 12/11/2006 | 11:25:00 | WOB-26 | EAA | EF | OAR | 24 | 4,440 |
| E082436697 | 12/11/2006 | 11:32:00 | PGA-13 | ECE | TO | OCO | 44 | 13,024 |
| E151708345 | 12/11/2006 | 11:56:00 | ROC-15 | ECC | EF | OTF | 1 | 56 |
| E479127773 | 12/11/2006 | 11:56:00 | IRO-13 | ECF | AO | OTR | 1 | 1,303 |
| E160253107 | 12/11/2006 | 11:59:00 | HIG-15 | EBE | DU | UHH | 8 | 1,728 |
| 10660204 | 12/11/2006 | 12:04:00 | HAN-13 | EAB | TF | OCO | 1,551 | 134,317 |
| E948079257 | 12/11/2006 | 12:11:00 | ROC-26 | ECC | EF | OTF | 3 | 120 |
| E164649250 | 12/11/2006 | 12:26:00 | SIL-16 | ECD | TO | CDH | 47 | 49,068 |
| E859721515 | 12/11/2006 | 12:31:00 | SIL-15 | ECD | TO | OHR | 450 | 29,700 |
| 10660088 | 12/11/2006 | 12:33:00 | MKI-14 | ECC | TF | OSV | 1 | 22 |
| E132881955 | 12/11/2006 | 12:36:00 | SIL-13 | ECF | TO | OHR | 89 | 19,491 |
| E119172530 | 12/11/2006 | 12:39:00 | RPT-15 | ECD | EF | OFC | 5 | 525 |
| E646993945 | 12/11/2006 | 12:42:00 | FRA-15 | ECD | TO | OCO | 13 | 4,095 |
| E002043163 | 12/11/2006 | 12:44:00 | PTR-16 | EAA | TF | OCO | 143 | 60,203 |
| E993179388 | 12/11/2006 | 12:45:00 | TRA-26 | ECE | TO | OFC | 47 | 62,275 |
| E114729798 | 12/11/2006 | 12:49:00 | MIL-16 | ECE | TO | OCO | 63 | 89,775 |
| E465048852 | 12/11/2006 | 12:49:00 | LOL-23 | ECD | EF | OFC | 25 | 2,300 |
| E637325371 | 12/11/2006 | 12:54:00 | IRO-15 | ECF | TO | OFC | 27 | 24,462 |
| E001523502 | 12/11/2006 | 12:55:00 | CAR-16 | EAA | EF | OTF | 59 | 26,845 |
| E272379835 | 12/11/2006 | 12:58:00 | LAB-27 | EAA | TF | OTF | 27 | 1,809 |
| E391597404 | 12/11/2006 | 13:01:00 | WIN-13 | ECE | TO | OCO | 636 | 325,164 |
| E402072933 | 12/11/2006 | 13:09:00 | CRE-15 | EAD | EF | OCO | 51 | 17,340 |
| E755187490 | 12/11/2006 | 13:13:00 | VWY-12 | EAA | TF | OTF | 32 | 3,744 |
| E761996084 | 12/11/2006 | 13:22:00 | HAN-16 | EAA | TF | OTF | 1 | 530 |
| E373142782 | 12/11/2006 | 13:22:00 | CHR-22 | ECE | EF | OFC | 537 | 321,126 |
| E642675826 | 12/11/2006 | 13:25:00 | SKE-22 | ECE | TO | OCR | 1,690 | 349,884 |
| E368379679 | 12/11/2006 | 13:29:00 | PMA-13 | ECE | TF | CDH | 12 | 15,108 |
| 10660248 | 12/11/2006 | 13:33:00 | PAT-15 | ECC | TO | OCO | 10 | 1,620 |
| E599613584 | 12/11/2006 | 13:36:00 | CHA-15 | ECC | EF | OTF | 2 | 78 |
| E537446746 | 12/11/2006 | 13:37:00 | CUS-13 | EAA | TO | OCO | 25 | 18,950 |
| E517096621 | 12/11/2006 | 13:38:00 | SKE-26 | ECE | TO | OCO | 427 | 182,103 |
| E529361015 | 12/11/2006 | 13:38:00 | PGA-12 | ECE | TO | OCR | 643 | 409,738 |
| E358225276 | 12/11/2006 | 13:41:00 | LGY-15 | EAD | EF | OHR | 117 | 53,118 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E096202874 | 12/11/2006 | 13:42:00 | CUS-16 | EAA | TF | OTF | 38 | 2,508 |
| E218939274 | 12/11/2006 | 13:43:00 | SIL-13 | ECE | TO | CDH | 387 | 185,984 |
| E086744231 | 12/11/2006 | 13:50:00 | FLD-15 | EAD | TO | OCO | 389 | 132,308 |
| E610169130 | 12/11/2006 | 13:50:00 | PTL-13 | ECF | TO | OFC | 4 | 760 |
| E964515806 | 12/11/2006 | 13:51:00 | FNW-17 | ECD | TO | OCO | 11 | 4,323 |
| E542361274 | 12/11/2006 | 13:52:00 | ALG-12 | EAC | TF | OCO | 588 | 119,364 |
| E135015384 | 12/11/2006 | 13:52:00 | CRE-12 | EAD | TF | OCO | 49 | 31,507 |
| E791649548 | 12/11/2006 | 13:53:00 | WIN-16 | ECE | TO | OSV | 1 | 946 |
| E292929269 | 12/11/2006 | 13:57:00 | TLN-0029 | EAA | TF | OCO | 983 | 381,404 |
| E575345644 | 12/11/2006 | 13:57:00 | KEN-01 | EAA | TF | OCO | 2,195 | 934,290 |
| E596488383 | 12/11/2006 | 13:58:00 | WLS-15 | EAC | TO | OTF | 2 | 274 |
| E512658507 | 12/11/2006 | 13:59:00 | GBK-13 | EAD | TO | OCO | 226 | 160,212 |
| E447405715 | 12/11/2006 | 14:01:00 | PMA-15 | ECE | TO | OCR | 33 | 34,617 |
| E440179668 | 12/11/2006 | 14:02:00 | ALG-15 | EAC | TF | OTF | 7 | 826 |
| E689988698 | 12/11/2006 | 14:04:00 | VIK-23 | EAA | TF | OCO | 22 | 17,512 |
| E779646642 | 12/11/2006 | 14:06:00 | HAP-15 | EAA | TF | OCO | 1,290 | 356,040 |
| E033766101 | 12/11/2006 | 14:08:00 | CHR-25 | ECE | TO | OPO | 113 | 39,211 |
| E147881303 | 12/11/2006 | 14:09:00 | BON-17 | ECA | TF | OCO | 63 | 3,775 |
| E099105608 | 12/11/2006 | 14:09:00 | HKX-16 | EAC | TO | OTF | 5 | 455 |
| E906686711 | 12/11/2006 | 14:11:00 | CAR-12 | EAA | TF | OSV | 2 | 1,538 |
| E110333772 | 12/11/2006 | 14:11:00 | GBK-15 | EAD | TF | OCO | 81 | 73,224 |
| E245533233 | 12/11/2006 | 14:12:00 | VAS-23 | EBL | TO | OCO | 98 | 52,038 |
| E414347123 | 12/11/2006 | 14:14:00 | LON-23 | ECC | TF | OCO | 7 | 735 |
| E836198758 | 12/11/2006 | 14:17:00 | ALG-15 | EAA | TF | OTF | 3 | 444 |
| E175797178 | 12/11/2006 | 14:18:00 | PTL-13 | ECF | TO | CDH | 17 | 17,935 |
| E599520772 | 12/11/2006 | 14:20:00 | TLN-0059 | EAD | TF | OCO | 3,195 | 1,394,734 |
| E786430920 | 12/11/2006 | 14:21:00 | CHI-12 | ECD | EF | OCO | 149 | 30,098 |
| E373070927 | 12/11/2006 | 14:21:00 | CRE-16 | EAD | TF | OTF | 6 | 258 |
| E893542422 | 12/11/2006 | 14:21:00 | LYN-17 | EAA | TF | OCO | 55 | 70,388 |
| E589786554 | 12/11/2006 | 14:28:00 | MIL-22 | ECE | TO | CDH | 180 | 170,460 |
| E855425661 | 12/11/2006 | 14:31:00 | LAB-27 | EAA | TF | OCO | 57 | 34,143 |
| E826044823 | 12/11/2006 | 14:32:00 | HWD-26 | EBD | TF | OCO | 37 | 2,738 |
| E884206631 | 12/11/2006 | 14:32:00 | GRI-16 | ECC | TF | OCO | 15 | 825 |
| E266814941 | 12/11/2006 | 14:33:00 | BAK-26 | EAA | TF | OTF | 644 | 94,669 |
| E232678032 | 12/11/2006 | 14:33:00 | BLS-23 | EAA | TF | OCO | 179 | 30,788 |
| E288325047 | 12/11/2006 | 14:33:00 | VIS-26 | EAA | TF | OCO | 40 | 22,120 |
| E282875571 | 12/11/2006 | 14:34:00 | SLA-17 | EAA | TF | OCO | 5 | 3,930 |
| E477971853 | 12/11/2006 | 14:34:00 | LYN-24 | EAA | TF | OCO | 14 | 13,524 |
| E176184251 | 12/11/2006 | 14:35:00 | BRW-13 | EAC | TF | OCO | 18 | 5,580 |
| E460095606 | 12/11/2006 | 14:36:00 | LYN-23 | EAA | TF | OCO | 2 | 1,602 |
| E792984117 | 12/11/2006 | 14:36:00 | BLS-25 | EAA | TF | OCO | 40 | 3,960 |
| E822622971 | 12/11/2006 | 14:37:00 | BIG-15 | EAC | TF | OTF | 2 | 696 |
| E372085381 | 12/11/2006 | 14:38:00 | IRO-17 | ECF | TO | OSW | 11 | 4,972 |
| E231858358 | 12/11/2006 | 14:38:00 | ROE-17 | EAA | TF | OCO | 22 | 10,384 |
| E656570949 | 12/11/2006 | 14:38:00 | SCH-15 | EAA | TF | OCO | 38 | 40,546 |
| E501642926 | 12/11/2006 | 14:38:00 | NUG-26 | EAA | TF | OCO | 25 | 28,625 |
| E626946356 | 12/11/2006 | 14:39:00 | BLS-22 | EAA | TO | OCO | 61 | 5,856 |
| E638324590 | 12/11/2006 | 14:40:00 | SUM-15 | EAC | TF | OCO | 182 | 132,230 |
| E821755113 | 12/11/2006 | 14:42:00 | NLM-16 | EAC | TO | OSV | 4 | 1,692 |
| E438824929 | 12/11/2006 | 14:42:00 | SWA-12 | EAD | TF | OCO | 10 | 1,980 |
| E766133563 | 12/11/2006 | 14:44:00 | CUS-15 | EAA | PO | OCO | 4 | 3,944 |
| E352295706 | 12/11/2006 | 14:44:00 | PTL-13 | ECD | TO | OFC | 1 | 840 |
| E701992070 | 12/11/2006 | 14:47:00 | LAB-26 | EAA | TF | OPO | 900 | 180,650 |
| E810158998 | 12/11/2006 | 14:48:00 | TLN-0060 | EAA | TO | OCO | 2,552 | 1,709,723 |
| E080397530 | 12/11/2006 | 14:49:00 | CUS-16 | EAA | TF | OCO | 5 | 980 |
| E175444235 | 12/11/2006 | 14:49:00 | BLA-13 | EAA | TF | OCO | 77 | 73,689 |
| E253785305 | 12/11/2006 | 14:49:00 | POU-15 | ECE | TO | OCO | 33 | 23,595 |
| E664663596 | 12/11/2006 | 14:49:00 | LLS-15 | EAA | TF | OCO | 1,151 | 778,076 |
| E187104445 | 12/11/2006 | 14:51:00 | LON-22 | ECC | TO | OCO | 1,440 | 220,320 |
| E213172350 | 12/11/2006 | 14:52:00 | WIN-15 | ECE | TO | OFC | 26 | 9,584 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E921653568 | 12/11/2006 | 14:52:00 | SCH-13 | EAA | TF | OCO | 40 | 36,920 |
| E178479155 | 12/11/2006 | 14:54:00 | HAM-13 | EAC | TO | OCO | 66 | 10,296 |
| E993437239 | 12/11/2006 | 14:54:00 | HAM-13 | EAC | TO | OCO | 208 | 63,232 |
| E873154138 | 12/11/2006 | 14:54:00 | HAW-12 | ECC | TF | OCO | 2,240 | 201,600 |
| E692054995 | 12/11/2006 | 14:55:00 | FAB-15 | EAD | TF | OSV | 1 | 35 |
| E981234550 | 12/11/2006 | 14:56:00 | WLS-16 | EAC | TF | OPO | 10 | 3,840 |
| E137960047 | 12/11/2006 | 14:57:00 | LOL-23 | ECD | TO | OSV | 13 | 1,404 |
| E961040166 | 12/11/2006 | 14:57:00 | BAK-25 | EAA | TF | OTF | 3 | 159 |
| E172296652 | 12/11/2006 | 15:06:00 | BIG-12 | EAC | TF | OCO | 22 | 11,902 |
| E376691710 | 12/11/2006 | 15:10:00 | HKX-12 | EAC | TO | OCO | 131 | 55,134 |
| E000669082 | 12/11/2006 | 15:11:00 | NLM-13 | EAC | TF | OCO | 416 | 133,621 |
| E554549860 | 12/11/2006 | 15:12:00 | LYN-26 | EAA | TF | OCO | 39 | 19,422 |
| E941119482 | 12/11/2006 | 15:12:00 | FRA-13 | ECD | TO | OCO | 9 | 5,166 |
| E719969136 | 12/11/2006 | 15:12:00 | FWY-11 | EBJ | TF | CDH | 95 | 7,410 |
| E177745402 | 12/11/2006 | 15:12:00 | SLA-16 | EAA | TO | OTF | 3 | 4,134 |
| E532783755 | 12/11/2006 | 15:13:00 | PMA-12 | ECE | TO | OTR | 46 | 43,010 |
| E348857179 | 12/11/2006 | 15:14:00 | CRE-16 | EAD | UN | OCO | 67 | 57,553 |
| E963136551 | 12/11/2006 | 15:14:00 | GRV-16 | ECA | TO | OCO | 14 | 8,414 |
| E651360424 | 12/11/2006 | 15:16:00 | PET-13 | EAC | TF | OCO | 127 | 17,653 |
| E901859447 | 12/11/2006 | 15:17:00 | LGY-12 | EAD | TF | OCO | 9 | 6,057 |
| E815336336 | 12/11/2006 | 15:17:00 | MWD-16 | EBE | TF | OCO | 6 | 326 |
| E880370135 | 12/11/2006 | 15:18:00 | MAN-16 | ECD | TO | CDH | 13 | 3,393 |
| E245483782 | 12/11/2006 | 15:22:00 | LUH-14 | ECC | DU | USV | 1 | 136 |
| E035017390 | 12/11/2006 | 15:23:00 | BRI-15 | EAA | EF | OFU | 6 | 2,742 |
| E380010341 | 12/11/2006 | 15:24:00 | WAU-25 | EBJ | UN | OTF | 1 | 50 |
| E354055825 | 12/11/2006 | 15:25:00 | BRI-14 | EAA | TF | OTF | 6 | 2,310 |
| E831527521 | 12/11/2006 | 15:26:00 | FLD-13 | EAD | TO | OCO | 152 | 109,288 |
| E651308859 | 12/11/2006 | 15:30:00 | UHL-23 | EBD | TF | OCO | 1,179 | 136,764 |
| E736161888 | 12/11/2006 | 15:32:00 | PGA-15 | ECF | TO | CDH | 43 | 47,472 |
| E043002433 | 12/11/2006 | 15:33:00 | PLY-13 | EAA | TF | OTF | 6 | 1,392 |
| E888526366 | 12/11/2006 | 15:34:00 | ROE-13 | EAA | TF | OJU | 56 | 41,776 |
| E174082494 | 12/11/2006 | 15:39:00 | LAT-14 | EBJ | TF | OCO | 1 | 158 |
| E872567346 | 12/11/2006 | 15:45:00 | BRO-16 | EAD | TF | OTF | 1 | 465 |
| E456901389 | 12/11/2006 | 15:46:00 | TRA-22 | ECE | TO | OPO | 425 | 413,950 |
| E489255565 | 12/11/2006 | 15:48:00 | LYN-13 | EAA | TF | OCO | 17 | 7,854 |
| E018545301 | 12/11/2006 | 15:50:00 | ANA-15 | EAC | TF | OTF | 5 | 1,525 |
| E351718124 | 12/11/2006 | 15:50:00 | SST-17 | EAA | TO | OCO | 48 | 32,160 |
| E394860388 | 12/11/2006 | 15:51:00 | CLV-16 | EAD | TF | OCO | 36 | 16,812 |
| E966877227 | 12/11/2006 | 15:53:00 | SIL-16 | ECE | TO | OCO | 14 | 12,866 |
| E251617396 | 12/11/2006 | 15:53:00 | BEL-25 | EBJ | TF | OTF | 12 | 670 |
| E884187940 | 12/11/2006 | 15:56:00 | BAK-25 | EAA | TF | OTF | 4 | 3,016 |
| E736180630 | 12/11/2006 | 15:56:00 | LAB-23 | EAA | TF | OTR | 3 | 2,307 |
| E407114567 | 12/11/2006 | 16:00:00 | SIL-15 | ECD | TO | CDH | 108 | 113,712 |
| E106051739 | 12/11/2006 | 16:02:00 | BRO-15 | EAD | TF | OCO | 10 | 4,680 |
| E106195949 | 12/11/2006 | 16:06:00 | OPC-39 | EAA | TF | OTF | 4 | 1,236 |
| E288060296 | 12/11/2006 | 16:13:00 | SHE-26 | ECE | TO | OCO | 585 | 167,895 |
| E249680799 | 12/11/2006 | 16:15:00 | SIL-13 | ECF | TO | OCO | 30 | 19,810 |
| E623409968 | 12/11/2006 | 16:16:00 | ALG-15 | EAC | TF | OTF | 3 | 225 |
| E185463625 | 12/11/2006 | 16:17:00 | NUG-25 | EAA | TF | OCO | 1 | 1,143 |
| E063233268 | 12/11/2006 | 16:17:00 | BHL-13 | ECE | TO | OCO | 198 | 65,538 |
| E842053600 | 12/11/2006 | 16:19:00 | SIL-15 | ECD | TO | OCO | 195 | 14,430 |
| E671060150 | 12/11/2006 | 16:19:00 | FLD-12 | EAD | TF | OCO | 788 | 266,344 |
| E428861188 | 12/11/2006 | 16:21:00 | WOB-23 | EAA | TF | OCO | 56 | 33,096 |
| E902485822 | 12/11/2006 | 16:27:00 | BLS-23 | EAA | TF | OTF | 5 | 340 |
| E739749906 | 12/11/2006 | 16:30:00 | PGA-13 | ECE | TF | CDH | 49 | 15,190 |
| E306997371 | 12/11/2006 | 16:30:00 | PMA-16 | ECE | TO | OCO | 8 | 5,504 |
| E916646083 | 12/11/2006 | 16:31:00 | BTN-36 | EAC | TF | OTF | 3 | 537 |
| E108198907 | 12/11/2006 | 16:35:00 | MVW-17 | EBJ | TO | OCO | 1,419 | 140,150 |
| E261295350 | 12/11/2006 | 16:39:00 | MTV-17 | EAC | TO | UOT | 1 | 254 |
| E221650155 | 12/11/2006 | 16:47:00 | CED-13 | ECA | AO | OSV | 830 | 56,394 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E262170361 | 12/11/2006 | 16:50:00 | KIT-22 | EBH | EF | OTF | 3 | 315 |
| E189174262 | 12/11/2006 | 16:53:00 | HAN-12 | EAA | TF | OTF | 2 | 794 |
| E719039832 | 12/11/2006 | 16:53:00 | BLS-25 | EAA | TF | OFU | 40 | 1,840 |
| E678226687 | 12/11/2006 | 16:55:00 | CAM-25 | EBJ | EF | OCN | 1 | 65 |
| E058912337 | 12/11/2006 | 16:59:00 | FWY-15 | EBJ | TF | OJU | 9 | 1,371 |
| E267568528 | 12/11/2006 | 17:00:00 | PTL-13 | ECF | TO | OFC | 239 | 44,932 |
| E735940013 | 12/11/2006 | 17:02:00 | ELL-13 | EBI | TF | OCO | 32 | 4,334 |
| E737257437 | 12/11/2006 | 17:02:00 | EPO-15 | ECD | TO | OSV | 1 | 258 |
| E993716481 | 12/11/2006 | 17:04:00 | BRS-13 | EAC | TF | OCO | 20 | 7,120 |
| E548715228 | 12/11/2006 | 17:16:00 | FAL-15 | EBF | TF | OCO | 276 | 149,592 |
| E137564811 | 12/11/2006 | 17:20:00 | PTL-13 | ECF | TO | UTR | 7 | 5,320 |
| E819119118 | 12/11/2006 | 17:33:00 | PET-16 | EAC | TF | OCO | 3 | 276 |
| E837856980 | 12/11/2006 | 17:34:00 | NLM-15 | EAC | TF | OCO | 1 | 256 |
| E568171667 | 12/11/2006 | 17:48:00 | SIL-15 | ECD | TO | CDH | 33 | 14,421 |
| E923549910 | 12/11/2006 | 17:48:00 | CHI-12 | ECD | TO | OFC | 33 | 16,038 |
| E807569770 | 12/11/2006 | 17:57:00 | ALG-15 | EAC | TF | OCO | 6 | 2,310 |
| E837353330 | 12/11/2006 | 17:59:00 | AVO-13 | EBD | EF | USV | 1 | 271 |
| E710541162 | 12/11/2006 | 18:08:00 | DUV-12 | EBD | TF | OCO | 15 | 3,792 |
| E928185219 | 12/11/2006 | 18:10:00 | BDI-12 | EBI | TO | OFU | 31 | 2,111 |
| E942634017 | 12/11/2006 | 18:11:00 | WAY-15 | EBD | TF | OSV | 3 | 481 |
| E713786948 | 12/11/2006 | 18:23:00 | SIL-13 | ECF | TF | OCO | 20 | 8,195 |
| E402361257 | 12/11/2006 | 19:03:00 | CRE-15 | EAD | UN | OCO | 10 | 5,670 |
| E093456646 | 12/11/2006 | 19:07:00 | HYA-13 | EBF | EF | UPT | 5 | 3,265 |
| E044631618 | 12/11/2006 | 19:29:00 | ALG-15 | EAA | TF | OPO | 4 | 3,344 |
| E019595319 | 12/11/2006 | 19:40:00 | PIP-23 | EBI | EF | USV | 1 | 72 |
| E553346382 | 12/11/2006 | 19:40:00 | HAZ-12 | EBE | EF | USV | 1 | 190 |
| E308764777 | 12/11/2006 | 19:53:00 | BRW-13 | EAC | TF | OTF | 2 | 134 |
| E785267901 | 12/11/2006 | 19:55:00 | PLY-13 | EAA | TF | OSV | 5 | 925 |
| E243116677 | 12/11/2006 | 19:56:00 | HAP-15 | EAA | TF | OCO | 95 | 15,580 |
| E778321456 | 12/11/2006 | 19:58:00 | HAM-13 | EAC | TF | OCO | 4 | 1,488 |
| E549439750 | 12/11/2006 | 20:06:00 | CHR-25 | ECE | EF | OCO | 100 | 44,700 |
| E539454186 | 12/11/2006 | 20:06:00 | PTR-14 | EAA | TF | OTF | 4 | 4,056 |
| E346004910 | 12/11/2006 | 20:23:00 | BRS-24 | EAC | TF | OTF | 7 | 1,736 |
| E548936010 | 12/11/2006 | 20:27:00 | FLD-15 | EAD | UN | OSW | 4 | 1,272 |
| E051320869 | 12/11/2006 | 21:17:00 | CAR-16 | EAA | TF | OCO | 22 | 7,876 |
| E362090169 | 12/11/2006 | 21:19:00 | MOT-14 | ECC | EF | OTF | 1 | 58 |
| E827469623 | 12/11/2006 | 21:33:00 | MCW-17 | ECE | TO | OTF | 5 | 435 |
| E798124631 | 12/11/2006 | 21:34:00 | RPT-17 | ECD | TO | OTF | 19 | 2,489 |
| E864869874 | 12/11/2006 | 22:01:00 | CPV-15 | EAD | TF | OFC | 143 | 95,953 |
| E026311859 | 12/11/2006 | 22:36:00 | BLU-16 | ECC | EF | UPC | 1 | 533 |
| E811370939 | 12/11/2006 | 23:13:00 | BRI-17 | EAA | UN | OTF | 4 | 728 |
| E848453560 | 12/11/2006 | 23:18:00 | ORT-22 | ECA | TO | OCO | 1 | 196 |
| E017828551 | 12/11/2006 | 23:25:00 | CHR-22 | ECE | TO | OFU | 2 | 10 |
| E470128332 | 12/11/2006 | 23:32:00 | FNW-17 | ECD | TO | OCO | 2 | 334 |
| E605560707 | 12/11/2006 | 23:35:00 | LOL-23 | ECD | TO | OCO | 6 | 1,302 |
| E875585258 | 12/11/2006 | 23:38:00 | SPA-16 | ECA | EF | OFC | 2 | 427 |
| E886503795 | 12/11/2006 | 23:40:00 | MWD-16 | EBE | TO | OFU | 5 | 384 |
| E040981049 | 12/11/2006 | 23:45:00 | VAS-12 | EBL | TO | OTR | 21 | 1,953 |
| E519143453 | 12/11/2006 | 23:51:00 | FNW-16 | ECD | TO | OTR | 1 | 262 |
| E655469320 | 12/11/2006 | 23:52:00 | MHT-15 | EBJ | TO | CDH | 1,052 | 165,543 |
| E875604808 | 12/11/2006 | 23:55:00 | WLK-15 | ECA | TO | OCO | 8 | 4,688 |
| E063899827 | 12/11/2006 | 23:56:00 | TRA-23 | ECE | TO | OCO | 18 | 4,932 |
| E445816437 | 12/11/2006 | 23:57:00 | LON-22 | ECC | TO | OCO | 2 | 1,394 |
| E804961231 | 12/11/2006 | 23:59:00 | OVE-13 | EBE | TF | OCO | 301 | 33,411 |

### Terms, Codes and Definitions Used on Detail Reports

| #### Notification | [Notification Number] A number assigned by SAP, identifying the outage record |
| --- | --- |
| Date | The date of the outage |
| Time | The time of the outage |
| Circuit | [Reference Circuit] The circuit identifier for the affected circuit |
| F/LOC | [Functional Location] The grid number where the outage occurred. If the grid number is not available, the Reference Circuit identifier occupies this field |
| EQT NBR | [Equipment Number] A number used to tie the equipment involved in the outage to the related information in SAP. This number does not represent the physical number of the equipment |

| Area | [Maintenance Planner Group] A code representing the energy, region and service center |  |
| --- | --- | --- |
|  | EAA – Bellingham | EBJ – South King |
|  | EAB – Lynden | EBK – Southwest King |
|  | EAC – Skagit | EBL – Vashon |
|  | EAD – Whidbey | ECA – Puyallup |
|  | EBD – Redmond | ECC – Olympia |
|  | EBE – Factoria | ECD – Port Orchard |
|  | EBF – Snoqualmie | ECE – Poulsbo |
|  | EBI – Enumclaw | ECF – Port Townsend |

| Cause | Cause of Outage |  |
| --- | --- | --- |
|  | AO – Accident Other | EF – Equipment Failure |
|  | BA – Bird or Animal | EO – Electrical Overload |
|  | CP – Car Pole | FI – Faulty Installation |
|  | CR – Customer Request | TF – Tree Off Right-of-Way |
|  | DU – Dig-up Underground | TO – Tree On Right-of-Way |
|  | SO – Scheduled Outage | UN – Unknown |

| Equipment | Affected by, or involved in the outage |  |
| --- | --- | --- |
|  | OCN – Connector | OSW – Overhead Switch |
|  | OCO – Overhead Conductor | OTF – Overhead Transformer Fuse |
|  | OCR – Crossarm | OTR – Overhead Transformer |
|  | OFC – Overhead Cut-out | OUP – OH to UG Primary |
|  | OFS – Overhead Fire Signal | OUS – OH to UG Secondary Service |
|  | OFU – Fuse Link/OH Line Fuse | SBF – High-side Bank Fuse |
|  | OGS – Span Guy | SCB – Power Circuit Breaker |
|  | OHR – Overhead Recloser | UOT – Underground Outdoor Term |
|  | OIN – Insulator | UPC – Underground Primary Cable |
|  | OJU- Jump Wire | UPT – Padmount Transformer |
|  | OPI – Overhead Pin Insulator | USV – Underground Service |
|  | OPO – Pole | UTC – Underground Terminal Fuse |
|  | OSV – Overhead Service | UTR – Submersible Transformer |
|  | ORE – Regulator |  |

#### Codes, Definitions – Continued

| CUST OUT | [Customer Out] The number of customers without power for any given outage record |
| --- | --- |
| CUST MIN | [Customer Minutes] The total number of minutes customers were without power for any given record |

| CODE | [Storm Code] An event descriptor |
| --- | --- |
|  | NON – Non Storm / Normal Conditions |
|  | WTH – Weather Related (eg: wind storm, showers, etc) |
|  | MAJ – Major event |

### Newsprint Media Coverage

Monday, December 11, 2006

Wind Temporarily Closes Hood Canal Bridge

The Hood Canal floating bridge was closed for about four hours yesterday due to winds that gusted to nearly 60 miles per hour. Elsewhere in Western Washington, wind-felled trees caused sporadic power outages and two kayakers were rescued from heavy swells on Bellingham Bay. Heavy snow fell in the Cascade mountains.

The Hood Canal bridge, linking the Kitsap and Olympic peninsulas, was closed from 2:50 p-m to 7 p.m. Officials kept it closed while some downed power lines were removed from state Highway 104. The bridge is closed when winds are sustained at 40 miles per hour for 15 minutes or more. Sporadic road closures and power outages also were reported in many areas of Western Washington. Two more storms are lined up to blow in from the Pacific this week: one late tonight and into tomorrow, and one late Thursday into Friday morning.

Wednesday, Dec 13, 2006

High winds wreak havoc in North End

By Herald Staff

A wave of high winds, which peaked at 70 mph, washed through the North End Monday afternoon leaving power outages and traffic snarls in its wake.

The Hood Canal Bridge was closed at 2 p.m. due to high gusts and didn’t reopen until 7 p.m., said Washington State Department of Transportation spokeswoman Kelly Stowe.

“Part of the reason we kept it closed was because of downed power lines on (State Highway) 104, and we didn’t want to have traffic backed up,” Stowe said.

The threshold for bridge closures is winds of at least 40 mph sustained for 15 minutes or more, she said.

“People need to make sure their cars are adequately filled with gas and they have blankets, water and food,” Stowe said. “If they need to reach someone on the other side of the bridge, they need to have a back-up plan.”

About 12,500 residents and businesses lost power in North Kitsap during the storm, and Puget Sound Energy was still working to restore power Tuesday morning, PSE officials said. Power was lost between 1-5 p.m. in most areas, but electricity was expected to be restored by Tuesday evening at the latest. Neighborhoods in Hansville lost power when a tree downed powerlines at the hairpin turn on Hood Canal Drive.

Electricity wasn’t restored there until about 2 a.m. Tuesday.

The North Kitsap School District had planned for a possible delayed start time Tuesday after the storm knocked out power to schools throughout the district Monday.

Though some schools were powerless Monday, there were no cancellations other than the Kingston Junior High School/Gordon Elementary Winter Concert that night, but all schools ran on a normal schedule Tuesday, said NKSD community relations director Chris Case.

Fire stations in the area were busy, but there were no severe accidents during the storm, said North Kitsap Fire & Rescue public information officer Michele Laboda.

“They were kept busy,” she said. “But there was nothing critical that came up.”

Several roadways were closed, including Port Gamble Road and Orca Drive, Laboda said. The storm also disrupted the NKF&R Santa schedule. Monday night’s visits will be rescheduled for Dec. 19, with Santa at the Suquamish Village parking lot from 5:30-6 p.m. and at the Miller Bay Estates clubhouse from 6:15-6:45 p.m.