2007

Qualifying Storm Events

January 2, 2007

# Table of Contents

Table of Contents	2

Event Description	3

Date of event	3

Event Type	3

Service Areas Affected	3

Number of Customers Affected	3

Summary of System Impacts	3

Mobilization Summary	3

Major Event Day – Qualification	3

Qualified Events - 2007	3

Current Event – Calculation Detail	3

Cumulative list of events that have qualified	3

Event Restoration – Cost Summary	3

Restoration Cost Detail by Qualifying Event	3

YTD Storm Restoration Cost Detail – Through January 2, 2007	3

Detail Documents	3

Restoration Cost Detail – Current Event	3

IEEE-1366 - Detailed List of Distribution Circuits with Outages	3

Terms, Codes and Definitions Used on Detail Reports	3

Newsprint Media Coverage	3

# Event Description

### Date of event

January 2, 2007

### Event Type

Wind storm.

### Service Areas Affected

With heavy rain and wind gusts up to 50 MPH, this moderate wind event impacted primarily the northern portion of PSE’s electric service area. King and Kitsap Counties were also affected, however with a smaller number of outages.

### Number of Customers Affected

This wind event resulted in the loss of electric service for approximately 24,050 customers.

### Summary of System Impacts

| Total Number of Outages | 296 |
| --- | --- |
| Distribution Circuits Totally Out | 17 |
| Distribution Circuits Partially Out | 285 |

| Transmission Circuits Affected | 5 |
| --- | --- |
| Substations Totally Off-line | 0 |

### Mobilization Summary

#### Operating bases

| Base | Date Opened | Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
| Kitsap | 1/2/2007 | 0830 | 1/3/2007 | 0130 |
| Skagit | 1/2/2007 | 0845 | 1/3/2007 | 1300 |
| N King | 1/2/2007 | 0945 | 1/2/2007 | 1930 |
| S King | 1/2/2007 | 1015 | 1/2/2007 | 1930 |

#### Emergency Operations Center

| EOC | Date Opened | #### Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
|  | 1/2/2007 | 0945 | 1/3/2007 | 0000 |

# Major Event Day – Qualification

- IEEE 1366 Method

IEEE 1366 was established to present a set of terms and definitions which can be used to foster uniformity in the development of distribution service reliability indices, to identify factors which affect the indices, and to aid in consistent reporting practices among utilities.  Also, it provides guidance for new personnel in the reliability area, and tools for internal as well as external comparisons.  The Major Event Day definition was created as part of IEEE 1366 to allow for consistent calculation of reliability metrics between utilities, and enable more valid comparisons with other utility reliability metrics.

IEEE Major Event Day Calculation (2.5 BETA METHOD) - A threshold on daily SAIDI is computed once a year, following year end. - Assemble the 5 most recent years of historical values of SAIDI/day. - Discard any days in the data set that has a SAIDI/day of zero. - Find the natural logarithm of each value in the data set. - Compute the average Alpha and the standard deviation (Beta) of the natural logarithms computed in step 3. - Compute the threshold Tmed where Tmed = exp(Alpha + 2.5 * Beta) - Any day in the next year with SAIDI > Tmed is a major event day.

Puget Sound Energy’s Major Event Threshold for 2007: 6.87 Minutes

# Qualified Events - 2007

### Current Event – Calculation Detail

| Event Date | Total Customer Minutes | Average Customer Count | Daily SAIDI – Customer Minutes /Customer Count |
| --- | --- | --- | --- |
| 1/2/2007 | 8,789,446 | 1,045,485 | 8.41 |

### Cumulative list of events that have qualified

| Date(s) | T-med Score | O&M – Deferrable Accumulation |
| --- | --- | --- |
| 1/2/2007 | 8.41 | $1,339,165 |

# Event Restoration – Cost Summary

### Restoration Cost Detail by Qualifying Event

| Date | Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M – Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/2/2007 | $0 | $0 | $0 | $38,044 | $1,339,165 | $1,377,209 | $1,377,209 |

### YTD Storm Restoration Cost Detail – Through January 2, 2007

| Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| $0 | $0 | $0 | $38,044 | $1,339,165 | $1,377,209 | $1,377,209 |

# Detail Documents

- Restoration Cost Detail – Current Event

- Detailed List of Distribution Circuits with Outages

- Terms, Codes & Definitions Used on Detail Reports

- Newsprint Media Coverage

### Restoration Cost Detail – Current Event

|  | Puget Sound Energy |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | January 2, 2007 Storm Damage Repair Costs |  |  |  |  |  |  |  |  |
|  |  | Qualifying Events Deferred Account | Capital | C&D Recoverable from Direct Billings (Costs Not Yet Billed) | O&M - Not Deferrable | O&M - Deferrable Accumulation | Total O&M | Total |  |
|  | Labor |  |  |  |  |  |  |  |  |
|  | ST |  |  |  |  | $25,231 | $25,231 | $25,231 |  |
|  | OT |  |  |  |  | $93,607 | $93,607 | $93,607 |  |
|  | Total Labor | $0 | $0 | $0 | $0 | $118,839 | $118,839 | $118,839 |  |
|  | Labor OH |  |  |  |  | $53,026 | $53,026 | $53,026 |  |
|  | Materials |  |  |  |  | $22,647 | $22,647 | $22,647 |  |
|  | Contractors |  | $23,890 |  |  | $1,096,035 | $1,096,035 | $1,119,925 |  |
|  | Other Direct Charges |  | $29,589 |  |  | $19,248 | $19,248 | $48,838 |  |
|  | Fleet |  |  |  |  | $25,587 | $25,587 | $25,587 |  |
|  | Other Assessments |  | $3,071 |  | $38,044 | $3,782 | $41,826 | $44,897 |  |
|  | Deferred Expenses | $1,339,165 |  |  |  | ($1,339,165) | ($1,339,165) | $0 |  |
|  |  | $1,339,165 | $56,550 | $0 | $38,044 | $0 | $38,044 | $1,433,760 |  |

### IEEE-1366 - Detailed List of Distribution Circuits with Outages

| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| E601197090 | 1/2/2007 | 0:47:00 | LGY-15 | EAD | TO | OCO | 363 | 30,855 |
| E406118415 | 1/2/2007 | 0:50:00 | FLD-12 | EAD | EF | OSW | 132 | 25,231 |
| E907790477 | 1/2/2007 | 1:00:00 | CHA-15 | ECC | TF | OCO | 10 | 977 |
| 10662428 | 1/2/2007 | 1:20:00 | PTL-13 | ECF | TO | OCO | 5 | 1,550 |
| E716168671 | 1/2/2007 | 1:51:00 | VAS-13 | EBL | TF | OCO | 51 | 35,394 |
| E621976636 | 1/2/2007 | 2:54:00 | BRO-16 | EAD | TO | OCO | 40 | 10,360 |
| E832155125 | 1/2/2007 | 3:23:00 | HOL-15 | ECA | EF | OTF | 5 | 362 |
| E156188437 | 1/2/2007 | 4:04:00 | CED-17 | ECA | EF | OPI | 10 | 3,000 |
| E136291987 | 1/2/2007 | 4:52:00 | MIR-15 | EBF | EF | UEL | 9 | 5,067 |
| E918136646 | 1/2/2007 | 5:29:00 | SLA-17 | EAA | EF | OTF | 2 | 252 |
| E127393183 | 1/2/2007 | 6:02:00 | VAS-12 | EBL | TO | OCO | 939 | 174,233 |
| E471855447 | 1/2/2007 | 6:30:00 | LGY-15 | EAD | TO | OCO | 46 | 66,608 |
| E996477268 | 1/2/2007 | 6:34:00 | RPT-15 | ECD | TO | OCO | 1 | 560 |
| E107792734 | 1/2/2007 | 6:41:00 | HKX-16 | EAC | EF | OCO | 73 | 69,277 |
| E255120048 | 1/2/2007 | 6:42:00 | PLU-13 | ECC | EF | OTF | 3 | 159 |
| E111442551 | 1/2/2007 | 6:50:00 | FRA-15 | ECD | TO | OCO | 6 | 1,668 |
| E030193759 | 1/2/2007 | 6:58:00 | LOL-21 | ECD | TO | OCO | 15 | 4,035 |
| E987308059 | 1/2/2007 | 7:02:00 | BRO-15 | EAD | EF | OCO | 66 | 19,668 |
| E678225576 | 1/2/2007 | 7:06:00 | CRE-15 | EAD | EF | CDH | 9 | 5,616 |
| E148689266 | 1/2/2007 | 7:07:00 | GBK-13 | EAD | EF | OCO | 111 | 115,773 |
| E466025375 | 1/2/2007 | 7:22:00 | FAL-15 | EBF | TO | OCO | 273 | 112,476 |
| E284642167 | 1/2/2007 | 7:28:00 | LEA-17 | EBI | UN | OCO | 1,610 | 96,600 |
| E810604894 | 1/2/2007 | 7:33:00 | RED-13 | EBD | TF | OCO | 88 | 6,776 |
| E391963271 | 1/2/2007 | 7:36:00 | KWH-25 | EBD | TF | OCO | 81 | 5,589 |
| E611705528 | 1/2/2007 | 7:38:00 | BIG-12 | EAC | TO | OCO | 222 | 251,874 |
| E185342433 | 1/2/2007 | 7:45:00 | FLD-13 | EAD | TF | OCO | 112 | 149,072 |
| E476238108 | 1/2/2007 | 7:46:00 | CHR-22 | ECE | TO | OCO | 300 | 157,200 |
| E871627991 | 1/2/2007 | 7:47:00 | SIL-13 | ECF | TO | OCO | 106 | 66,578 |
| E763820110 | 1/2/2007 | 7:48:00 | FRA-16 | ECD | TO | OCO | 300 | 132,900 |
| E656641404 | 1/2/2007 | 7:49:00 | FLD-15 | EAD | EF | OCO | 52 | 58,032 |
| E101459165 | 1/2/2007 | 7:55:00 | IRO-13 | ECF | TO | UTC | 4 | 252 |
| 10717724 | 1/2/2007 | 7:55:00 | SWA-12 | EAD | EF | OFC | 86 | 38,012 |
| E507724216 | 1/2/2007 | 8:00:00 | SIL-15 | ECD | TO | OCO | 121 | 83,369 |
| E581021564 | 1/2/2007 | 8:00:00 | GRV-16 | ECA | SO | UTC | 1 | 300 |
| E948501867 | 1/2/2007 | 8:01:00 | CHR-25 | ECE | TO | OHR | 485 | 67,900 |
| E261480149 | 1/2/2007 | 8:03:00 | RDO-16 | EBJ | TF | OCO | 51 | 3,723 |
| E433067220 | 1/2/2007 | 8:06:00 | SIL-16 | ECD | TO | OFU | 668 | 76,152 |
| E878647473 | 1/2/2007 | 8:07:00 | KAP-16 | ECA | TO | OCO | 23 | 6,532 |
| E938937101 | 1/2/2007 | 8:09:00 | BCH-16 | EAA | EF | OIN | 5 | 2,680 |
| E033921064 | 1/2/2007 | 8:11:00 | HAM-13 | EAC | EF | OCO | 122 | 141,848 |
| E185019860 | 1/2/2007 | 8:11:00 | NLM-15 | EAC | EF | OPO | 54 | 63,396 |
| E301645340 | 1/2/2007 | 8:11:00 | HAP-13 | EAA | TO | OCO | 28 | 2,912 |
| E510421040 | 1/2/2007 | 8:14:00 | BIG-15 | EAC | TO | OCO | 160 | 184,340 |
| E686305560 | 1/2/2007 | 8:14:00 | PMA-15 | ECE | TO | OCO | 22 | 5,236 |
| E423452871 | 1/2/2007 | 8:18:00 | PTL-13 | ECF | TO | OFU | 1 | 107 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E579410094 | 1/2/2007 | 8:18:00 | KCR-16 | EBJ | TF | OCR | 1,348 | 297,376 |
| E467284560 | 1/2/2007 | 8:19:00 | GBK-15 | EAD | TO | OPO | 31 | 12,896 |
| E924305944 | 1/2/2007 | 8:21:00 | LOL-23 | ECD | TO | OPO | 562 | 257,958 |
| E472932343 | 1/2/2007 | 8:23:00 | BRO-16 | EAD | TO | OCO | 1,006 | 467,790 |
| E035828580 | 1/2/2007 | 8:24:00 | PET-12 | EAC | EF | OTF | 8 | 3,768 |
| E890173681 | 1/2/2007 | 8:25:00 | NLM-13 | EAC | EF | OPO | 2,138 | 625,932 |
| E145458181 | 1/2/2007 | 8:26:00 | EPO-13 | ECD | TO | OTF | 4 | 496 |
| E037686884 | 1/2/2007 | 8:26:00 | DUV-13 | EBD | TF | OCO | 2 | 352 |
| E845161379 | 1/2/2007 | 8:27:00 | KCR-17 | EBJ | TO | OTR | 133 | 141,113 |
| E742746753 | 1/2/2007 | 8:28:00 | POU-16 | ECE | TO | OFU | 6 | 618 |
| E664744516 | 1/2/2007 | 8:33:00 | NLM-12 | EAC | TO | OCO | 666 | 189,525 |
| E096837172 | 1/2/2007 | 8:34:00 | BRI-17 | EAA | TO | OCO | 499 | 136,227 |
| E629298486 | 1/2/2007 | 8:37:00 | WOB-25 | EAA | TF | OPO | 1,374 | 277,044 |
| 10718931 | 1/2/2007 | 8:42:00 | TLN-0059 | EAD | TF | OCO | 3,202 | 453,675 |
| E941405505 | 1/2/2007 | 8:42:00 | FRA-13 | ECD | TO | OFU | 1,289 | 153,391 |
| E875880063 | 1/2/2007 | 8:45:00 | HAZ-13 | EBE | TO | OCO | 208 | 61,360 |
| E477331495 | 1/2/2007 | 8:50:00 | HAM-15 | EAC | TF | OCR | 799 | 930,835 |
| E231269980 | 1/2/2007 | 8:51:00 | BLA-13 | EAA | EF | OFC | 41 | 4,264 |
| E359338201 | 1/2/2007 | 8:52:00 | FRA-12 | ECD | TO | OTF | 11 | 1,078 |
| E732851305 | 1/2/2007 | 8:53:00 | SCH-15 | EAA | EF | CDH | 46 | 12,650 |
| E436039605 | 1/2/2007 | 8:54:00 | SCH-13 | EAA | UN | OCO | 1,275 | 123,675 |
| E434264871 | 1/2/2007 | 8:56:00 | WLS-16 | EAC | EF | OPO | 35 | 46,340 |
| E034544539 | 1/2/2007 | 8:57:00 | HAN-15 | EAA | TO | CDH | 4 | 1,584 |
| E258647164 | 1/2/2007 | 8:57:00 | BRE-33 | ECD | EF | OTF | 1 | 212 |
| E929429006 | 1/2/2007 | 8:58:00 | POU-15 | ECE | TO | OFU | 50 | 6,250 |
| E013161713 | 1/2/2007 | 8:59:00 | RIT-17 | EAC | TO | OPO | 1 | 1,141 |
| E676108056 | 1/2/2007 | 9:00:00 | NUG-25 | EAA | EF | OTF | 10 | 1,700 |
| E244764072 | 1/2/2007 | 9:02:00 | CHI-12 | ECD | TO | OFU | 10 | 2,220 |
| E694326279 | 1/2/2007 | 9:02:00 | IRO-17 | ECF | TO | OJU | 24 | 7,968 |
| E806014112 | 1/2/2007 | 9:03:00 | IRO-13 | ECF | TO | OPO | 3 | 4,178 |
| E764192124 | 1/2/2007 | 9:05:00 | RIT-16 | EAC | EF | CDH | 9 | 3,465 |
| E813141443 | 1/2/2007 | 9:08:00 | IRO-13 | ECF | TO | OPO | 1 | 3,304 |
| E505221007 | 1/2/2007 | 9:09:00 | QUI-25 | ECF | TO | OFU | 27 | 11,124 |
| E371178452 | 1/2/2007 | 9:10:00 | CRE-12 | EAD | EF | OCO | 9 | 2,880 |
| E994867477 | 1/2/2007 | 9:14:00 | EGT-28 | EBE | EF | OCO | 8 | 1,520 |
| E799778966 | 1/2/2007 | 9:18:00 | DUV-15 | EBD | TO | OCO | 9 | 2,808 |
| E049062933 | 1/2/2007 | 9:19:00 | PET-16 | EAC | EF | CDH | 10 | 6,410 |
| E243664047 | 1/2/2007 | 9:22:00 | UHL-25 | EBD | TO | OCO | 120 | 56,400 |
| E955696406 | 1/2/2007 | 9:25:00 | VAS-22 | EBL | TO | OCO | 5 | 2,265 |
| E856876274 | 1/2/2007 | 9:25:00 | BTR-23 | EBE | EF | UFJ | 298 | 59,252 |
| E155323088 | 1/2/2007 | 9:26:00 | LAB-23 | EAA | EF | OSW | 2 | 248 |
| E330601090 | 1/2/2007 | 9:27:00 | ING-13 | EBD | TO | OCO | 1,791 | 267,573 |
| E168975916 | 1/2/2007 | 9:27:00 | MWD-16 | EBE | TO | OCO | 77 | 8,701 |
| E140681772 | 1/2/2007 | 9:28:00 | ROL-15 | EBJ | TF | OCO | 2,046 | 243,474 |
| E674666670 | 1/2/2007 | 9:28:00 | OSC-23 | EBI | TO | OCO | 9 | 2,853 |
| E724895648 | 1/2/2007 | 9:29:00 | BEL-17 | EBJ | TF | OCO | 6 | 1,566 |
| E483923722 | 1/2/2007 | 9:31:00 | WIS-12 | EBF | TO | OCO | 11 | 3,289 |
| E691643781 | 1/2/2007 | 9:32:00 | DUV-12 | EBD | TO | OCO | 19 | 8,740 |
| E469309385 | 1/2/2007 | 9:32:00 | PLA-23 | EBD | EF | OCN | 6 | 1,188 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E320140799 | 1/2/2007 | 9:40:00 | FWY-11 | EBJ | TF | OFU | 29 | 8,990 |
| E152683872 | 1/2/2007 | 9:41:00 | WAY-15 | EBD | TF | OTF | 4 | 616 |
| E137317080 | 1/2/2007 | 9:44:00 | MTV-15 | EAC | TO | OTF | 1 | 376 |
| E515338026 | 1/2/2007 | 9:48:00 | EDG-12 | EBJ | TF | OCO | 63 | 12,096 |
| E241865531 | 1/2/2007 | 9:49:00 | EPO-12 | ECD | TO | OCO | 1,381 | 154,672 |
| E867074866 | 1/2/2007 | 9:49:00 | FRU-25 | ECA | TF | OCO | 9 | 2,905 |
| E881535314 | 1/2/2007 | 9:50:00 | DGR-15 | ECA | TF | OCO | 277 | 19,390 |
| E305801200 | 1/2/2007 | 9:53:00 | PLG-13 | ECC | TF | OJU | 211 | 58,447 |
| E587622462 | 1/2/2007 | 9:53:00 | PAN-14 | EBJ | TO | OCO | 2,254 | 211,876 |
| E329839485 | 1/2/2007 | 9:53:00 | PMA-12 | ECE | TF | OCO | 32 | 12,560 |
| E391173511 | 1/2/2007 | 10:00:00 | PHA-13 | EBE | TF | OFU | 16 | 5,637 |
| E896363815 | 1/2/2007 | 10:00:00 | FAL-13 | EBF | TO | OCO | 24 | 6,816 |
| E666796761 | 1/2/2007 | 10:02:00 | LON-26 | ECC | TO | OPO | 1,285 | 125,055 |
| E477401280 | 1/2/2007 | 10:03:00 | BIG-16 | EAC | TF | OSV | 2 | 1,164 |
| E350560631 | 1/2/2007 | 10:05:00 | THU-16 | ECC | EF | OCN | 1 | 55 |
| E633990141 | 1/2/2007 | 10:09:00 | SIL-15 | ECE | TO | OCO | 2 | 1,090 |
| E484944588 | 1/2/2007 | 10:10:00 | PAN-12 | EBJ | TF | OCO | 682 | 75,020 |
| E112170020 | 1/2/2007 | 10:15:00 | MAP-15 | EBF | TO | OCO | 217 | 46,221 |
| E241142831 | 1/2/2007 | 10:16:00 | BRW-13 | EAC | TO | OSV | 50 | 8,000 |
| E350096018 | 1/2/2007 | 10:17:00 | RDO-15 | EBJ | TF | OCO | 1 | 530 |
| E564773342 | 1/2/2007 | 10:23:00 | STW-13 | ECA | TF | OCO | 55 | 17,810 |
| E642065543 | 1/2/2007 | 10:25:00 | NOB-24 | EBE | EF | OPO | 1 | 356 |
| E899445787 | 1/2/2007 | 10:25:00 | BUC-16 | ECA | TO | OCO | 5 | 2,067 |
| E890523988 | 1/2/2007 | 10:27:00 | GWR-16 | EBI | TF | OSV | 31 | 11,718 |
| E157065646 | 1/2/2007 | 10:30:00 | LYN-17 | EAA | EF | OCO | 12 | 1,512 |
| E902140418 | 1/2/2007 | 10:33:00 | WIN-12 | ECE | TF | OCO | 2 | 798 |
| E108757696 | 1/2/2007 | 10:33:00 | ROC-16 | ECC | EF | OTR | 4 | 948 |
| E800288672 | 1/2/2007 | 10:44:00 | BLA-13 | EAA | EF | OFC | 21 | 3,885 |
| E147387329 | 1/2/2007 | 10:47:00 | BLU-13 | ECC | EF | OTF | 1 | 66 |
| E383435727 | 1/2/2007 | 10:51:00 | RJN-13 | EBJ | TF | OSV | 4 | 756 |
| E753550125 | 1/2/2007 | 10:52:00 | JUA-13 | EBD | PO | OSV | 6 | 438 |
| E474445679 | 1/2/2007 | 11:01:00 | PTL-13 | ECF | TO | OFC | 2 | 947 |
| E598156902 | 1/2/2007 | 11:05:00 | BUC-26 | ECA | TF | OCO | 2 | 200 |
| E168832631 | 1/2/2007 | 11:05:00 | FRA-13 | ECD | TO | OCO | 26 | 5,486 |
| E703842825 | 1/2/2007 | 11:10:00 | HKX-12 | EAC | TO | OSV | 9 | 1,512 |
| E644307267 | 1/2/2007 | 11:14:00 | EGT-27 | EBE | TF | OSV | 15 | 4,035 |
| E814331793 | 1/2/2007 | 11:23:00 | HKX-13 | EAC | EF | OPO | 1 | 1,237 |
| E925639696 | 1/2/2007 | 11:25:00 | LMD-12 | EBJ | TF | OSV | 8 | 240 |
| E339752269 | 1/2/2007 | 11:40:00 | FRA-15 | ECD | TO | OTF | 1 | 50 |
| E930189501 | 1/2/2007 | 11:49:00 | CRE-16 | EAD | EF | CDH | 5 | 2,980 |
| E198415096 | 1/2/2007 | 11:51:00 | CAS-16 | EBH | EF | OTR | 1 | 159 |
| E614395503 | 1/2/2007 | 11:59:00 | NOR-23 | EBD | TO | OCO | 64 | 37,632 |
| E440737389 | 1/2/2007 | 12:10:00 | MUR-16 | ECE | TF | OSV | 1 | 246 |
| E383237599 | 1/2/2007 | 12:14:00 | STA-16 | EBJ | EF | OTR | 2 | 812 |
| E258725897 | 1/2/2007 | 12:16:00 | VIT-16 | EBD | EF | OCO | 1 | 216 |
| E475363522 | 1/2/2007 | 12:23:00 | FWD-15 | EBJ | TF | OFU | 91 | 8,827 |
| 10717735 | 1/2/2007 | 12:29:00 | VAS-22 | EBL | TO | OCO | 5 | 695 |
| E414768183 | 1/2/2007 | 12:33:00 | LWS-13 | EBI | TF | OTR | 5 | 3,440 |
| E644748902 | 1/2/2007 | 12:38:00 | EPO-12 | ECD | TO | OCO | 14 | 1,414 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E726518880 | 1/2/2007 | 12:39:00 | MWD-16 | EBE | TO | OCO | 1 | 51 |
| E939215095 | 1/2/2007 | 12:45:00 | FWD-16 | EBJ | TF | OFU | 9 | 675 |
| E049302053 | 1/2/2007 | 12:45:00 | CWD-25 | EBD | TF | OSV | 29 | 6,235 |
| E459921148 | 1/2/2007 | 12:48:00 | BLU-13 | ECC | EO | OFU | 98 | 12,642 |
| E983666877 | 1/2/2007 | 12:54:00 | HYA-13 | EBF | EF | USV | 1 | 296 |
| E002907567 | 1/2/2007 | 13:06:00 | SME-15 | EBE | EF | USV | 5 | 1,225 |
| E295300339 | 1/2/2007 | 13:17:00 | PMA-13 | ECE | TO | OFU | 55 | 8,470 |
| E492241987 | 1/2/2007 | 13:17:00 | PMA-15 | ECE | TO | OCO | 1,193 | 220,043 |
| E510679193 | 1/2/2007 | 13:23:00 | DES-12 | EBJ | TF | OJU | 75 | 10,275 |
| 10713809 | 1/2/2007 | 13:29:00 | IRO-13 | ECF | EF | OTR | 3 | 1,833 |
| E592594855 | 1/2/2007 | 13:31:00 | MTV-16 | EAC | EF | OPO | 25 | 14,825 |
| E321115766 | 1/2/2007 | 13:39:00 | SCH-15 | EAA | TO | OCO | 55 | 4,730 |
| E670800985 | 1/2/2007 | 13:51:00 | MKI-17 | ECC | TF | OCO | 1 | 229 |
| E576973971 | 1/2/2007 | 13:59:00 | FNW-16 | ECD | TO | ACE | 1 | 68 |
| E036740674 | 1/2/2007 | 14:01:00 | FRU-22 | ECA | TF | OCO | 3 | 177 |
| E646277395 | 1/2/2007 | 14:06:00 | VAS-13 | EBL | TO | OJU | 26 | 7,228 |
| E175785001 | 1/2/2007 | 14:11:00 | CPV-15 | EAD | EF | CDH | 26 | 25,454 |
| E108164442 | 1/2/2007 | 14:16:00 | VAS-12 | EBL | TF | CDH | 12 | 4,668 |
| E617578535 | 1/2/2007 | 14:18:00 | BRS-24 | EAC | TO | OCR | 433 | 250,652 |
| E085009208 | 1/2/2007 | 14:24:00 | ROS-21 | EBD | TF | OSV | 4 | 624 |
| E598147016 | 1/2/2007 | 14:26:00 | BLA-13 | EAA | TO | OSW | 30 | 5,070 |
| E144364509 | 1/2/2007 | 14:30:00 | EGT-12 | EBE | EF | OFU | 1 | 150 |
| E128787892 | 1/2/2007 | 14:37:00 | WIS-13 | EBF | EF | OCR | 10 | 2,630 |
| E362742406 | 1/2/2007 | 14:55:00 | NBE-15 | EBF | TO | OCO | 14 | 3,164 |
| E013444916 | 1/2/2007 | 15:03:00 | PAT-15 | ECC | TF | OSV | 1 | 112 |
| E617909777 | 1/2/2007 | 15:09:00 | BRW-15 | EAC | TO | OFC | 3 | 846 |
| E658032420 | 1/2/2007 | 15:10:00 | SCH-13 | EAA | EF | OCR | 4 | 1,032 |
| E964419050 | 1/2/2007 | 15:27:00 | STW-15 | ECA | EF | OSV | 1 | 117 |
| E366665606 | 1/2/2007 | 15:30:00 | HOB-16 | EBI | TF | OTF | 1 | 160 |
| E931142531 | 1/2/2007 | 15:34:00 | PGA-13 | ECE | TO | OTF | 2 | 328 |
| E927418302 | 1/2/2007 | 15:38:00 | SWA-12 | EAD | TO | OTR | 15 | 8,430 |
| E096524474 | 1/2/2007 | 15:47:00 | OVE-12 | EBE | EF | OCN | 1 | 120 |
| E715940878 | 1/2/2007 | 15:55:00 | CUS-13 | EAA | TO | OFC | 70 | 6,300 |
| E937436893 | 1/2/2007 | 16:00:00 | NLM-12 | EAC | EF | OFC | 22 | 3,872 |
| E480991205 | 1/2/2007 | 16:13:00 | CHR-22 | ECE | TO | OCO | 111 | 32,634 |
| 10662442 | 1/2/2007 | 16:16:00 | BON-16 | ECA | TF | OSV | 1 | 101 |
| E139083199 | 1/2/2007 | 16:45:00 | NBO-25 | EBD | EF | OFC | 1 | 125 |
| E096399631 | 1/2/2007 | 16:46:00 | WOB-23 | EAA | TO | OTF | 2 | 222 |
| E765571425 | 1/2/2007 | 16:51:00 | MAN-12 | ECD | EF | UPC | 107 | 31,458 |
| E293782614 | 1/2/2007 | 17:10:00 | KCR-16 | EBJ | TF | OPO | 50 | 2,250 |
| E222956963 | 1/2/2007 | 17:19:00 | LMD-16 | EBJ | EF | UTR | 58 | 4,801 |
| E884795238 | 1/2/2007 | 17:23:00 | BUC-16 | ECA | TO | OCO | 1 | 267 |
| E281521789 | 1/2/2007 | 17:23:00 | THO-04 | EBH | EF | OIN | 15 | 2,415 |
| E763158203 | 1/2/2007 | 17:30:00 | FRA-13 | ECD | TO | OCO | 12 | 4,452 |
| E518599395 | 1/2/2007 | 17:54:00 | RIT-16 | EAC | EF | CDH | 32 | 12,192 |
| E761405277 | 1/2/2007 | 17:56:00 | GBK-15 | EAD | EF | OTR | 4 | 976 |
| E073157652 | 1/2/2007 | 17:59:00 | OSC-23 | EBI | TF | OCO | 4 | 960 |
| E062884531 | 1/2/2007 | 18:06:00 | DGR-13 | ECA | TO | OCO | 15 | 585 |
| E635887142 | 1/2/2007 | 18:36:00 | TAN-15 | ECC | EF | USV | 1 | 1,205 |
| Notification | Date | Time | Circuit | Area | Cause | Equipment | Cust Outs | Cust Mins |
| E067066484 | 1/2/2007 | 19:01:00 | HAP-16 | EAA | TF | CDH | 50 | 11,050 |
| E576611045 | 1/2/2007 | 19:35:00 | MIL-17 | ECE | TO | OTF | 3 | 315 |
| E668764010 | 1/2/2007 | 20:45:00 | VAS-13 | EBL | TO | OCO | 1 | 285 |
| E833626885 | 1/2/2007 | 22:21:00 | FRG-16 | ECC | EO | OSV | 1 | 104 |
| E633500257 | 1/2/2007 | 22:37:00 | MUR-16 | ECE | EF | UTC | 19 | 5,684 |
| E961428071 | 1/2/2007 | 22:43:00 | NBE-16 | EBF | TO | OCO | 3,468 | 17,340 |
| E530232971 | 1/2/2007 | 22:56:00 | PHA-15 | EBE | EF | OPO | 1 | 119 |

### Terms, Codes and Definitions Used on Detail Reports

| #### Notification | [Notification Number] A number assigned by SAP, identifying the outage record |
| --- | --- |
| Date | The date of the outage |
| Time | The time of the outage |
| Circuit | [Reference Circuit] The circuit identifier for the affected circuit |
| F/LOC | [Functional Location] The grid number where the outage occurred. If the grid number is not available, the Reference Circuit identifier occupies this field |
| EQT NBR | [Equipment Number] A number used to tie the equipment involved in the outage to the related information in SAP. This number does not represent the physical number of the equipment |

| Area | [Maintenance Planner Group] A code representing the energy, region and service center |  |
| --- | --- | --- |
|  | EAA – Bellingham | EBJ – South King |
|  | EAB – Lynden | EBK – Southwest King |
|  | EAC – Skagit | EBL – Vashon |
|  | EAD – Whidbey | ECA – Puyallup |
|  | EBD – Redmond | ECC – Olympia |
|  | EBE – Factoria | ECD – Port Orchard |
|  | EBF – Snoqualmie | ECE – Poulsbo |
|  | EBI – Enumclaw | ECF – Port Townsend |

| Cause | Cause of Outage |  |
| --- | --- | --- |
|  | AO – Accident Other | EF – Equipment Failure |
|  | BA – Bird or Animal | EO – Electrical Overload |
|  | CP – Car Pole | FI – Faulty Installation |
|  | CR – Customer Request | TF – Tree Off Right-of-Way |
|  | DU – Dig-up Underground | TO – Tree On Right-of-Way |
|  | SO – Scheduled Outage | UN – Unknown |

| Equipment | Affected by, or involved in the outage |  |
| --- | --- | --- |
|  | OCN – Connector | OSW – Overhead Switch |
|  | OCO – Overhead Conductor | OTF – Overhead Transformer Fuse |
|  | OCR – Crossarm | OTR – Overhead Transformer |
|  | OFC – Overhead Cut-out | OUP – OH to UG Primary |
|  | OFS – Overhead Fire Signal | OUS – OH to UG Secondary Service |
|  | OFU – Fuse Link/OH Line Fuse | SBF – High-side Bank Fuse |
|  | OGS – Span Guy | SCB – Power Circuit Breaker |
|  | OHR – Overhead Recloser | UOT – Underground Outdoor Term |
|  | OIN – Insulator | UPC – Underground Primary Cable |
|  | OJU- Jump Wire | UPT – Padmount Transformer |
|  | OPI – Overhead Pin Insulator | USV – Underground Service |
|  | OPO – Pole | UTC – Underground Terminal Fuse |
|  | OSV – Overhead Service | UTR – Submersible Transformer |
|  | ORE – Regulator |  |

#### Codes, Definitions – Continued

| CUST OUT | [Customer Out] The number of customers without power for any given outage record |
| --- | --- |
| CUST MIN | [Customer Minutes] The total number of minutes customers were without power for any given record |

| CODE | [Storm Code] An event descriptor |
| --- | --- |
|  | NON – Non Storm / Normal Conditions |
|  | WTH – Weather Related (eg: wind storm, showers, etc) |
|  | MAJ – Major event |

### Newsprint Media Coverage

Tuesday, January 2, 2007

Power restored to most after new storm

P-I STAFF

Seattle City Light has restored electricity to nearly all of the 600 homes that had lost power Tuesday because of the most recent storm, the utility said.

Crews were expected to turn the power back on for the remaining 80 customers in Delridge by about 6 p.m., City Light spokespeople said.

Power for nearly all of the 400 customers in West Seattle was back by about 1 p.m. About 200 Shoreline customers also regained power Tuesday around 9:30 a.m.

Utility officials stressed that additional power failures might occur before the storm ceases.

"City Light reminds customers that the soil is soaked, and some trees were weakened from the last storm, so even a mild storm could cause more damage and more outages," said City Light spokesman Peter Clarke in a statement.

A storm system is expected to bring gusts of up to 40 mph and more intense rain to the Seattle area Tuesday afternoon, the National Weather Service said.

While the agency has issued a wind advisory until 4 p.m. Tuesday, the system is not expected to be anything like what swept over the region in November and December.

Puget Sound Energy reported about 150 homes without power around 1:30 p.m. on Tuesday. The power failures were scattered around five Puget Sound counties the utility serves, and PSE officials weren't anticipating many more.

"(The storm) is a baby compared to the last one," spokesman Dave Reid said.

There were a small number of homes without power in King County, but they weren't concentrated in any one area, Reid said.

Tuesday's specific wind advisory is in effect for the Seattle, Bremerton, Tacoma and Strait of Juan de Fuca areas. Some of these areas could see winds as high as 50 to 60 mph.

The agency said it is possible that branches could snap, trees could fall and more power outages could occur.

Winter conditions Tuesday also caused snow to slide onto U.S. Highway 2 around 7:30 a.m., state transportation officials said.

The slide was blocking all lanes in both directions. Crews reopened the highway at 10 a.m.

Seattle-area residents can expect a quarter to a half inch of rain Tuesday, said Carl Cerniglia, a Weather Service meteorologist in Seattle.

From Monday morning until Tuesday morning, he added, three-quarters to 1 inch of rain had fallen in the region.

Sustained winds for Tuesday in the Seattle area are estimated to be between 15 to 25 mph, he added.

For areas outside of Seattle, though, the agency said a flood watch remains in effect for King, Snohomish, Mason, Clallam, Jefferson, Skagit and Grays Harbor counties.

Forecasters are keeping an eye on heavy rainfall in the Olympics, as well.

"Rivers draining off the Cascades from King County northward also have a threat of significant rises," according to the Weather Service Web site.

A flood warning has been issued for the Skokomish River, which is expected to go over its flood level Tuesday, on the Olympic Peninsula.

From Monday morning to Tuesday morning, the storm system had dropped 2 to 4 inches of precipitation in the Cascades, particularly in the area north of Snoqualmie Pass.

The precipitation includes rain, snow, freezing rain and sleet.

Cerniglia said forecasters expect rain to fall in the Cascades for the rest of Tuesday.

January 03. 2007

If it's wet and windy, it must be wintertime: Rough weather causes power outages, traffic snarls

By Bruce Rommel
Journal Reporter

Heavy rains Tuesday were blamed for scattered power outages around the Eastside and south King County, a spate of accidents on local freeways and flooding of streets that slowed peak afternoon traffic in some communities.

Minor flooding also was expected along the Tolt River near Carnation sometime Tuesday night, but the National Weather Service and King County officials weren't anticipating any serious problems.

The Weather Service is calling for more rain showers through Saturday, continuing a wet weather trend. At Sea-Tac Airport, 2.09 inches of rain fell during the 24-hour period that ended at 4 p.m. Tuesday.

"This is your typical winter storm: We get some rain and we get some wind," said Johnny Burg, a Weather Service meteorologist.

The storm system that swept through the area Tuesday brought high winds that caused about 80 scattered power outages around the nine counties served by Puget Sound Energy. About 30 of those were in King County, said Dorothy Bracken, a PSE spokeswoman.

"Most of these were tree limbs breaking off and falling onto the power lines, and it was just a matter of our crews getting there to brush them off the lines," Bracken said.

She said PSE crews hoped to have service restored to all customers by 8 p.m. Tuesday.

Heavy rainfall contributed to a number of accidents along the county's freeways. While troopers normally respond to 10 or 15 calls a day, by 5:30 p.m. Tuesday, they'd responded to 42.

"It's a lot more than normal," trooper Jeff Merrill said, though he noted none of the accidents were serious or blocking. "There were a lot of debris calls, standing water, and one- to four-car accidents spread throughout the county."

During heavy rain, it's incumbent upon drivers to slow down, be observant and increase following distance, Merrill said. In the event one does start to hydroplane, Merrill advised staying off the brakes, letting the car slow down and trying to steer in a straight line.

"When you regain control, drive accordingly," he said. "It might behoove you to switch lanes. The big thing is you just gotta slow down. That's usually all that's necessary to ensure you have a safe commute."

In Bellevue, a tree blown onto power lines forced the closure of Southeast 64th Street in the 11300 block for about an hour. It was reopened about 2:30 p.m.

In Auburn, a portion of Auburn Way South near the State Route 18 interchange and several busy arterials around downtown Kent were closed because of minor flooding.

The persistent rains prompted a Weather Service advisory for chances of minor flooding in King, Snohomish, Mason and Skagit counties.

In King County, minor flooding was anticipated only along the Tolt River. Water was expected to rise over Tolt River Road near Carnation, the Weather Service advisory said.

Linda Thielke, spokeswoman for the county's Department of Transpiration, said road services crews planned to be watching overnight for any problems along the roadways where recent storms have caused flooding.

Burg said the rains and heavy winds are typical January weather patterns.

"Every winter we get a good soaking from these rains and the winds," he said.

According to Weather Service records, January normally is the third-wettest month of the year. November and December, respectively, are the wettest and second-wettest months.