PACIFICORP ENERGY	Proposal Date:  12/20/2011

Plant:  Jim Bridger	APR#:  90000565

TITLE: 	Jim Bridger Unit 2 Turbine Upgrade High Pressure/Intermediate Pressure/Low Pressure

OBJECTIVE: 	Replace the high pressure, intermediate pressure and low pressure turbines to increase the turbine/generator output by 17.0 megawatts guaranteed, 18.0 megawatts expected (11.4 megawatts guaranteed, 12.0 megawatts expected, PacifiCorp’s share) from technological improvements and 8.0 megawatts (5.3 megawatts PacifiCorp’s share) from reduced degradation over the life of the turbine. Increased output with no increase in fuel input or operating cost will improve the heat rate and decrease unit cost for electricity produced. Project costs are increased due to the addition of a blocking filter for sub-synchronous resonance resolution and turbine vendor charges as a result of the suspension and resumption of turbine fabrication.

Decisions Required:	Request approval to replace the high pressure, intermediate pressure and low pressure turbines for Jim Bridger Unit 2.

Executive Summary:	Recent advances in steam turbine design technologies have increased the efficiency of new steam turbines. These new design technologies are transferable to steam turbine retrofits and will improve turbine efficiency, which increases generator output without increasing boiler heat input or emissions. The turbine manufacturer is guaranteeing a generator output increase of 17.0 megawatts (11.4 megawatts PacifiCorp’s share) due to steam turbine design technology improvements. The expected increase due to technology improvements is 18.0 megawatts (12.0 megawatts PacifiCorp’s share). The total output expected after the upgrade is 586.8 megawatts gross, which is 18 megawatts more than the current design output of the General Electric Advanced Design Steam Path upgrade installed in 1997. There will also be an average of 8.0 megawatts (5.3 megawatts PacifiCorp’s share) additional generation capacity realized due to reduced degradation over the life of the turbine. The total megawatt increase expected for the project will be 26.0 megawatts (17.3 megawatts PacifiCorp’s share). However, the financial evaluation for this project change request only uses the 18 megawatt increase attributable to technology as the stated capacity increase.

The turbine replacement would take place during the scheduled spring 2013 overhaul.

A competitive process was used to award a contract to replace the high pressure, intermediate pressure and low pressure turbines for Jim Bridger Unit 1. An evaluation process selected one vendor to have the best proposal, based on price, megawatt increase, ability to deliver on schedule, previous turbine upgrade experience and safety performance. Separate contracts for each of the Jim Bridger Unit 2, Unit 3 and Unit 4 turbine upgrades were negotiated based on the Jim Bridger Unit 1 contract terms and conditions, with price adjustments for delivery and installation in consecutive years following Jim Bridger Unit 1 installation.

The fabrication of the low pressure turbines for Jim Bridger Unit 1 was suspended by PacifiCorp in September, 2009, due to identified SSR conflicts between the new low pressure turbine rotors and the transmission system. The high pressure and intermediate pressure turbines were installed on Jim Bridger Unit 1 in 2010. The fabrication of the high pressure, intermediate pressure and low pressure turbines on all three remaining Jim Bridger units was suspended in February, 2010, until a resolution for the sub-synchronous resonance problem could be identified. In December, 2010, the fabrication and installation of the high pressure, intermediate pressure and low pressure turbines for Jim Bridger Unit 2 and Unit 4 were terminated, as well as the low pressure turbine for Unit 3. The contract provisions for the low pressure turbine for Jim Bridger Unit 1 and the high pressure and intermediate pressure turbine for Jim Bridger Unit 3 were not terminated but remained suspended pending further evaluation of sub-synchronous resonance mitigation options. The fabrication progress for these two turbine sections was significant before they were previously suspended.

In an effort to determine potential options for mitigation of the sub-synchronous resonance problem, General Electric was contracted to conduct a series of studies to determine what could be done to resolve the issue, at what risk, and for what cost. General Electric found that mitigation would eventually be necessary for either the new turbines or the existing turbines if the Gateway West 500 kilovolt transmission project was installed, at an estimated cost of $20.0m. An interim solution was required to provide for the installation of a single high pressure, intermediate pressure and low pressure turbine upgrade in a single unit which consists of installing a blocking filter specific to Jim Bridger Unit 2 at an estimated cost of $5.0m.

Subsequent to a determination that sub-synchronous resonance concerns could be mitigated, negotiations were held with the turbine vendor to determine the possibility and cost of completing the partially fabricated high pressure and intermediate pressure turbine originally intended for Jim Bridger Unit 3 and low pressure turbine originally intended for Jim Bridger Unit 1 and installing them in Jim Bridger Unit 2 in 2013. The vendor has since confirmed that they can complete the fabrication of these turbine components for installation in Jim Bridger Unit 2 in 2013, and have provided a cost proposal for doing so. This project change request is for the additional funding to complete the project as described, including the installation of the blocking filter, the re-negotiated turbine contract cost changes, and the applicable out of scope suspension and resumption charges.

Key Issues:	The key issues for discussion include:

•	The expected generation capacity increase of 18.0 megawatts (12.0 megawatts PacifiCorp’s share) due to technology improvements matches the proposed 2012 ten year plan.

•	The original cost for the upgrade project, as approved in 2008, was $33,014,207 total, $31,259,364 without allowance for funds used during construction, and $20,840,618 PacifiCorp’s share without allowance for funds used during construction.

•	The proposed cost for the upgrade project is $44,138,113 total, $40,816,058 without allowance for funds used during construction, and $27,210,704 PacifiCorp’s share without allowance for funds used during construction.

•	The increase in project cost is $11,123,906 total, $9,556,692 without allowance for funds used during construction, $6,371,128 PacifiCorp’s share without allowance for funds used during construction. The increases are due to installation of a blocking filter for sub-synchronous resonance mitigation, increased turbine contract costs, cost incurred due to suspension/resumption and out of scope work, e.g. storage during suspension, and increased allowance for funds used during construction due to the cancellation of two turbine projects and transferring these costs to Jim Bridger Unit 2.

- Utilizing the partially fabricated turbine materials from Jim Bridger Unit 1 and Unit 3 avoids the need to cancel fabrication and the costs incurred to date on these projects to be expensed. The total amount to be transferred from the Jim Bridger Unit 1 and Unit 3 projects to the Jim Bridger Unit 2 project is $14,307,170 without allowance for funds used during construction, PacifiCorp share is $9,538,114 without allowance for funds used during construction.

•	The requested amount exceeds the 2012 proposed ten year plan budgeted amount for 2012 by $434,261; $289,507 PacifiCorp’s share. The requested amount exceeds the 2013 budget amount by $1,676,266; $1,117,511 PacifiCorp’s share. The negotiations with the turbine vendor for the contract adjustments were taking place about the same time as the 2012 budgets were set. The final details of the costs of the Jim Bridger Unit 2 turbine project, taking into account the transfers from the Jim Bridger Unit 1 and Jim Bridger Unit 3 projects, together with the timing of the payments to the turbine vendor, were not yet determined, and consequently the requested budget amounts were not sufficient.

•	The installed price for the technological improvement at the expected capacity increase of 18.0 megawatts is $2,452 per kilowatt-hour (including allowance for funds used during construction).

•	The estimated net unit heat rate improvement is 417 British thermal units per kilowatt-hour based on comparison of design heat balance information for the existing and retrofit turbines.

•	The turbine vendor is Mechanical Dynamics and Analysis, LTD. Originally Mechanical Dynamics and Analysis, LTD had contracts to install turbine upgrades on all four of the Jim Bridger units. The turbine upgrade projects on Jim Bridger Unit 3 and Unit 4 have been cancelled, and the turbine installation on Jim Bridger Unit 1 has been limited to the high pressure and intermediate pressure turbines only; the low pressure turbine project for Jim Bridger Unit 1 has been cancelled. The low pressure turbine materials originally intended for Jim Bridger Unit 1 and the high pressure and intermediate pressure turbine materials originally intended for Jim Bridger Unit 3 partially fabricated before the projects were suspended will be used for the Jim Bridger Unit 2 project and installed in 2013.

PVRR(d) ($000’s):	There is a $43,427 ($28,952 PacifiCorp’s share) benefit according to the Utah stipulated book life which ends in 2037 to customers for completing the project compared to not completing the project and incurring additional market purchases and future maintenance costs. The benefit according to the Oregon Public Utilities Commission book life which ends in 2025 is $8,133 ($5,422 PacifiCorp’s share).

OMAG Budget Status:	Operations and maintenance costs were not budgeted for this project.

CAPEX Budget Status:	The budget for the turbine upgrade is $11,105,007 in 2012 and $11,867,142 in 2013 total without allowance for funds used during construction. The requested amount is $11,539,268 in 2012 and $13,543,408 in 2013 total without allowance for funds used during construction. PacifiCorp’s share budget and requested funds are shown in the table below.

PacifiCorp share values are based on 1/3:2/3 split with joint owner; actual split may be slightly different

Final Approver:	Greg Abel, PacifiCorp Chairman and CEO

Sponsor:		Mike Dunn, President, PacifiCorp Energy

Author:		Tom Faucheux, Project Manager, Generation Engineering

1.	Introduction

Advancements in turbine technology have resulted in increased megawatt output without increasing main steam flow. Efficiency improvements come without increasing fuel input, maintenance costs or emissions. Turbine vendors have installed and tested these upgrades in many electric utility plants and have proven the performance improvements and provide guarantees.

Mechanical Dynamics and Analysis, LTD, a wholly owned subsidiary of Hitachi, Ltd., was awarded a contract for the Jim Bridger Units 1 through 4 turbine upgrades in 2008. These contract awards were made after a competitive bidding process for Jim Bridger Unit 1, followed by a negotiated price for Jim Bridger Unit 2, Unit 3 and Unit 4. Selection was based on an evaluation of megawatt increase, price, and ability to deliver on schedule, previous experience and safety performance. Benefits of the multi-unit package, along with the low price, are enhanced warranty coverage and discounts on replacement parts.

Once the Jim Bridger Unit 1 basic turbine design was completed by the turbine vendor, they provided detailed information regarding the turbine mechanical resonance. This value was used in an interconnection study of the transmission system. The study revealed the mechanical resonance of the low pressure turbine would put the turbine rotor shaft in danger of damage and possible failure due to the sub-synchronous resonance conflict between the transmission system electrical resonance and the mechanical resonance of low pressure turbine rotors. Discussions with the turbine vendor to determine if the low pressure rotor could be modified to eliminate the risk concluded that major changes would be necessary at significantly increased expense.

It was for this reason the fabrication of the low pressure turbines for Jim Bridger Unit 1 was suspended by PacifiCorp in September, 2009. The high pressure and intermediate pressure turbines were installed on Unit 1 in 2010. The fabrication of the high pressure, intermediate pressure and low pressure turbines on all three remaining Jim Bridger units was suspended in February, 2010 until a resolution for the sub-synchronous resonance problem could be found. In December 2010, contracts for the fabrication of the high pressure, intermediate pressure and low pressure turbines for Jim Bridger Unit 2 and Jim Bridger Unit 4 were terminated, as well as the low pressure turbine for Jim Bridger Unit 3. Only the low pressure turbine for Jim Bridger Unit 1 and the high pressure and intermediate pressure turbine for Jim Bridger Unit 3 remained suspended, as significant progress in fabrication had been made before work was suspended.

General Electric was contracted to conduct a series of studies to determine what could be done to resolve the sub-synchronous resonance issue, at what risk, and for what cost. General Electric found that mitigation would be necessary for either the new turbines or the existing turbines if the Gateway West 500 kilovolt transmission project was installed, at an estimated cost of $20.0m. An interim solution was identified to provide for the installation of a single high pressure, intermediate pressure and low pressure turbine upgrade in a single unit which consists of installing a specially designed blocking filter specific to Jim Bridger Unit 2 at an estimated cost of $5.0m.

Negotiations were held with the turbine vendor to determine the possibility and cost of installing the partially fabricated high pressure, intermediate pressure and low pressure turbines in Jim Bridger Unit 2 in 2013. The vendor confirmed that they can complete the fabrication for installation in 2013, and provided a cost proposal in October 2011.

2.	Description and Strategic Fit

The proposed turbine upgrade project is to replace the high pressure, intermediate pressure and low pressure turbines in Jim Bridger Unit 2 during the scheduled overhaul in 2013. The total megawatt gain is derived from two separate components of performance increase: 1) inherent design modifications of the turbine steam path due to technological improvements and 2) the decrease in overall expected degradation, both rate and quantity, over the life of the turbine. The technological improvements are guaranteed at 17 megawatts, compared to the General Electric Advanced Design Steam Path upgrade design currently installed. The expected value for the technological improvements is 18 megawatts, 12 megawatts PacifiCorp’s share. The expected increase due to recovery of degradation is eight megawatts, 5.3 megawatts PacifiCorp’s share. The financial analysis of the project is based on the 18 megawatt technology gain only, and does not include capacity improvements due to  degradation recovery.

The requested total project capital expense is $44,138,113 total, $40,816,058 without AFUDC ($27,210,704 PacifiCorp’s share without AFUDC). The project change request amount increased compared to the original appropriation request by $11,123,906; $9,556,692 without allowance for funds used during construction, $6,371,128 PacifiCorp’s share without allowance for funds used during construction. The cause for the increase is due to four main areas (100%):

- Installation of a blocking filter; $5,000,000

- Turbine contract settlement resulting from the suspension and resumption, and material price increase; $3,299,372

- Turbine contract settlement for out of scope work, e.g. storage, additional engineering, transportation to and from storage, etc.; $1,118,428

- Allowance for funds used during construction related to Jim Bridger Unit 3 high pressure, intermediate pressure turbine and Jim Bridger Unit 1 low pressure turbine investments were transferred to Unit 2; $1,340,228

The sub-synchronous resonance problem that was revealed during the transmission study affects only the low pressure turbine rotors (each Jim Bridger unit has two low pressure turbine rotors). The studies conducted by General Electric have determined that the sub-synchronous resonance concerns for the turbine can be mitigated by installing a blocking filter connected to the step up transformer neutral of the associated unit. The blocking filter will protect the turbine and generator shafts from fatigue damage which the shafts would experience if no mitigation steps were taken.

Completion of the Jim Bridger Unit 2 turbine installation using the partially fabricated components from Jim Bridger Unit 1 and Jim Bridger Unit 3 avoids terminating a significant amount of fabrication and other costs incurred to date. The costs for these turbine contracts combined is $12,720,603 total, $8,480,402 PacifiCorp’s share. The total project cost to be transferred from the other two projects to the Jim Bridger Unit 2 project, which includes the turbine vendor contract is $14,307,170 without allowance for funds used during construction, PacifiCorp share is $9,538,114 without allowance for funds used during construction.

3.	Benefits

Customer Service

The customer benefit is through improved efficiency for generation of electricity which provides increased generation without an increase in fuel consumption, avoiding or delaying construction of new generation capacity, and avoiding purchase of electricity from less efficient, more costly sources.

Financial

The expected performance capacity increase is 26 megawatts (17.3 megawatts PacifiCorp’s share). The estimated net unit heat rate improvement will be 417 British thermal units per kilowatt-hour for the guaranteed increase. Expenditures began in 2008 and will be completed in 2013. Performance improvements begin in June 2013, and the expected life is 25 years, or the remaining book depreciation life of the plant. The present value of revenue requirement difference is a benefit of $43.4m ($29.0m PacifiCorp’s share) to customers based on non-Oregon asset lives, or $8.1m ($5.4m PacifiCorp’s share) based on Oregon asset lives, for completing the project compared to not completing the project and incurring additional market purchases and future maintenance costs.

Risk Mitigation

Contract terms with the turbine supplier will require liquidated damages for failure to deliver on time and failure to provide the guaranteed performance increase. The expected capacity increase and heat rate improvement is justified by the experience of similar new technology turbine upgrades. The turbine vendor’s guaranteed megawatt increase is considered conservative. The contract price for engineering, fabrication, delivery, installation and overheads are firm prices, with no allowance for escalation due to market or other economic changes.

4.	Alternatives Considered

The preferred option is to modify the high pressure, intermediate pressure and low pressure turbines together. This provides the largest increase in generator output. This option provides a total installed cost of $2,452 per kilowatt for the expected capacity increase of 18 megawatts. This is based on the total project cost, including the allowance for funds used during construction divided by the total expected megawatt increase due to technology.

Present Value of Revenue Requirement (PVRR) Analysis ($000’s):

For the Utah stipulated book life through 2037

PVRR of Project Presented	 $  -50,986

PVRR of Not Completing the Project 	 $  -94,413  (Market Purchase of Power)

PVRR(d) Benefit	 $   43,427

For the Oregon Public Utilities Commission book life through 2025

PVRR of Project Presented	 $  -49,472

PVRR of Not Completing the Project 	 $  -57,605  (Market Purchase of Power)

PVRR(d) Benefit	 $   8,133

5.	Risk Factors Evaluated

Performance Risk

Performance guarantees by the turbine vendor are considered to be conservative. Actual performance increases are expected to exceed the guaranteed amount. Turbine degradation after the project will continue, but is expected at a slower rate and reduced overall quantity than previous degradation. Liquidated damages for failure to meet performance guarantees will be included in the contract.

The blocking filter also carries a performance risk, as this is technology that only one vendor has used throughout the world. General Electric successfully installed this type blocking filter in only two other locations. Awarding the contract for the blocking filter to General Electric helps to minimize the risk.

Delivery Risk

Delivery of the materials must be on time for installation in spring of 2013. Major fabrication will occur in Japan; special insurance requirements for shipment are included in the contract terms. Liquidated damages for late delivery will be included in the contract.

The blocking filter must be online when the turbine comes on line or transmission series capacitors cannot be used. The schedule for design, fabrication and installation of the blocking filter is not considered to be critical at this time, but any delay can create a critical timing problem. A turnkey contract is proposed to avoid any time delay between contractors, and to ensure that the sole contractor, which would be General Electric, owns the schedule and any resulting delays. Expediting the contract with General Electric and including liquidated damages are also intended to reduce risk to PacifiCorp.

Installation Risk

The planned duration of the overhaul is 44 days. The vendor plans to work two shifts per day, seven days a week. The current estimated time required for the turbine installation is 41 days, turning gear to turning gear. Contract negotiations will confirm the installation requirements, with installation schedule compression possible at additional cost. Labor availability at the time of installation may also impact installation. Failure to complete installation of the turbine by the end of the scheduled overhaul will result in an unplanned outage and lost generation. Liquidated damages will be included for failure to meet installation deadlines, but allowances for some grace period and graduated damages are included in the Jim Bridger Unit 2 turbine upgrade contract.

The blocking filter can be mostly installed prior to the outage, only final connections to the transformer neutral and the control system will be necessary during the outage and before start up.

Equipment Risk

A review by an outside consulting firm has been conducted to determine if additional equipment upgrades will be required to optimize the unit performance with the upgraded turbine. Funds for upgrading other equipment, such as adding cooling capacity for the main step-up transformer and generator, are included.

The equipment for the blocking filter is typical that to what would be used in normal transmission and distribution/substation facilities, and risks would be similar to that same type of equipment.

Vendor Performance Risk

The turbine vendor, selected through an evaluation process from the responses to a request for proposals, is Mechanical Dynamics and Analysis, LTD. A firm price contract has been awarded based on the general services agreement. A review by the risk management group has determined that financial security precautions, such as a letter of credit or parental guarantee, is required and has been provided by the vendor.

The blocking filter vendor, General Electric, has a long history of working with PacifiCorp. The contract with General Electric will have standard protections for performance.

Material Market Price Risk

Material price escalation during the period of suspension has been negotiated with the turbine vendor; no additional price changes are anticipated.

Project Cost Risk

The project cost estimate is based on a re-negotiated firm price contract with the turbine vendor. Performance and schedule (delivery and installation) are guaranteed and covered under liquidated damages. Other project costs for consultants, in house labor, five percent contingency, associated equipment updates such as exciter and hydrogen cooler upgrades are included in the total project price.

6.	Retirement and Removal Information

The high pressure, intermediate pressure and low pressure turbines will be removed and replaced. General Electric Corporation manufactured the existing turbines (manufacturer’s serial number. 170X547). This unit is a tandem compound, reheat, 3,600 revolutions per minute steam turbine with a combined high and intermediate pressure section with two double-flow low pressure sections.

7.	Financial Analysis

- An expected 18.0 megawatt turbine capacity increase due to technology improvements is assumed with benefits beginning in June of 2013. Expected degradation recovery megawatts are not included in the financial analysis.

- 25 year life of performance increase (remaining book depreciation life of plant).

- Avoided operations and maintenance costs of $1.2m (0.80m PacifiCorp’s share) are included for 2017.

- Project economics: The economics below show the difference between completing the project and not completing the project and incurring additional market purchases and future maintenance costs.

- Project economics for Utah stipulated book life through 2037:

- Project economics for Oregon Public Utilities Commission depreciation life through 2025:

8. 	Regulatory Recovery Strategy

The asset will be included in construction work-in-progress (CWIP) until the project is used and useful. Allowance for funds used during construction (AFUDC) will be applied while the asset remains in CWIP. Recovery through retail rates will begin once the asset is included in the applicable regulatory filing as made in each state. Filings include general rate cases or other cost recovery mechanisms that may allow for recovery of all or part of the project costs. Assets (and any impacts on the company’s ongoing revenue requirement) will be included in regulatory filings if the project is or will be used and useful during the test year used in the respective filing.

Rate recovery is subject to approval by the public service commission in each state served by the company and such approval will be sought on a state-by-state basis. Each commission will evaluate the prudence of the company’s investment and ultimately determine any allowed recovery. The company anticipates this project will be approved as a prudent investment and recovery of its ongoing revenue requirement will be allowed, including a return on the amount included in rate base.

9. Project Contingency

A contingency of five percent is included in the total project cost. The contingency will cover any difficulties related to unknown problems that could be experienced during the replacement of the turbine, or associated equipment that must be upgraded to achieve the full output of the upgrade.

10. Procurement Strategy

A request for proposals for the Jim Bridger Unit 1 turbine upgrade was sent to six turbine vendors. Two responses were received: Mechanical Dynamics and Analysis, LTD and General Electric. Mechanical Dynamics and Analysis, LTD was selected as providing the best proposal based on the megawatt increase, quoted price, ability to deliver the quoted megawatts on schedule, turbine upgrade experience and safety performance. A contract with Mechanical Dynamics and Analysis, LTD for Jim Bridger Unit 1 turbine upgrade has been signed. PacifiCorp Energy negotiated a contract with Mechanical Dynamics and Analysis, LTD for the remaining three units at the Jim Bridger Plant. The rationale is based on taking advantage of a multi-unit packaged price, improved warranty and parts discounts offered by Mechanical Dynamics and Analysis, LTD, and the operational advantage of standardization of turbine design and operating system across the entire plant. Standardization also simplifies training and improves safety, by removing lack of unit familiarization as a potential factor in accidents.

PacifiCorp suspended work on the Jim Bridger turbines in 2010, except the Unit 1 high pressure and intermediate pressure turbine which was installed in 2010. After studies determined that the low pressure turbine could be installed safely if a blocking filter is also installed on the unit at the same time. Negotiations with the turbine vendor were held to revise the contract and adjust the price. This has been done and the revised contract price is included in the project cost and financial evaluation.

Materials initially intended for the Unit 1 low pressure turbine and the Unit 3 high pressure and intermediate pressure projects will be used in the Unit 2 installation. The contract documents for the Unit 1 and Unit 3 projects will be revised and the payments made on these materials will be transferred to Unit 2.

11.	Project Management

Project Team consists of:

Rod Roberts, Managing Director, Generation Support

Bob Arambel, Managing Director, Jim Bridger Plant

Jim Sedey, Manager Engineering/Environmental, Jim Bridger Plant

Lon Udy, Manager Engineering/Environmental, Generation Engineering

Tim Bingley, Engineer, Lead/Senior, Generation Engineering

Bob Klein, Engineer, Lead/Senior, Jim Bridger Plant

Jeff Palmer, Procurement Sourcing Manager

Tom Faucheux, Project Manager, Generation Engineering

12.	Project Milestones

Technical Specifications Completed: 	September 22, 2008

Sole Source Justification submitted		November 17, 2008

APR Approved:				December 18, 2008

Contract recommendation approval: 		December 18, 2008

Contract Executed: 				December 19, 2008

Re-negotiated contract:			December 22, 2011

Materials on site:				February 14, 2013

(Overhaul starts March 23, 2013–44 days)

Overhaul completion 				May 6, 2013

13.	Recommendation

Approval is recommended to purchase and install the high pressure, intermediate pressure and low pressure turbine upgrades on Jim Bridger Unit 2 for the spring 2013 overhaul.