2010

Qualifying Storm Events

May 03, 2010

# Table of Contents

Table of Contents	2

Event Description	3

Date of event	3

Event Type	3

Service Areas Affected	3

Number of Customers Affected	3

Summary of System Impacts	3

Mobilization Summary	3

Major Event Day – Qualification	5

Qualified Events - 2010	5

Current Event – Calculation Detail	5

Cumulative list of events that have qualified	5

Event Restoration – Cost Summary	6

Restoration Cost Detail by Qualifying Event	6

YTD Storm Restoration Cost Detail – Through May 3, 2010	6

Detail Documents	7

Restoration Cost Detail – Current Event	8

IEEE-1366 - Detailed List of Distribution Circuits with Outages	9

Terms, Codes and Definitions Used on Detail Reports	14

Media Coverage	16

# Event Description

### Date of event

May 03, 2010

### Event Type

Wind storm.

### Service Areas Affected

This weather event affected Skagit, Island and south King Counties.

### Number of Customers Affected

Approximately 69,950 customers were without power over the course of this outage event.

### Summary of System Impacts

| Total Number of Outages | 369 |
| --- | --- |
| Distribution Circuits Totally Out | 21 |
| Distribution Circuits Partially Out | 348 |

| Transmission Circuits Affected | 1 |
| --- | --- |
| Substations Totally Off-line | 1 |

### Mobilization Summary

#### Operating Bases

| Base | Date Opened | Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
| Skagit | 05/03/2010 | 12:01 | 05/04/2010 | 07:30 |
| Island | 05/03/2010 | 12:01 | 05/04/2010 | 07:30 |
| South King | 05/03/2010 | 14:30 | 05/04/2010 | 08:00 |

#### Emergency Operations Center

| EOC | Date Opened | #### Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
|  | -- | -- | -- | -- |

# Major Event Day – Qualification

- IEEE 1366 Method

IEEE 1366 was established to present a set of terms and definitions which can be used to foster uniformity in the development of distribution service reliability indices, to identify factors which affect the indices, and to aid in consistent reporting practices among utilities.  Also, it provides guidance for new personnel in the reliability area, and tools for internal as well as external comparisons.  The Major Event Day definition was created as part of IEEE 1366 to allow for consistent calculation of reliability metrics between utilities, and enable more valid comparisons with other utility reliability metrics.

IEEE Major Event Day Calculation (2.5 BETA METHOD) - A threshold on daily SAIDI is computed once a year, following year end. - Assemble the 5 most recent years of historical values of SAIDI/day. - Discard any days in the data set that has a SAIDI/day of zero. - Find the natural logarithm of each value in the data set. - Compute the average Alpha and the standard deviation (Beta) of the natural logarithms computed in step 3. - Compute the threshold Tmed where Tmed = exp (Alpha + 2.5 * Beta) - Any day in the next year with SAIDI > Tmed is a major event day.

Puget Sound Energy’s Major Event Threshold for 2010: 7.21 Minutes

# Qualified Events - 2010

### Current Event – Calculation Detail

| Event Date | Total Customer Minutes | Average Customer Count | Daily SAIDI – Customer Minutes /Customer Count |
| --- | --- | --- | --- |
| 05/03/2010 | 14,666,233 | 1,081,955 | 13.55 |

### Cumulative list of events that have qualified

| Date(s) | T-med Score | O&M – Deferrable Accumulation |
| --- | --- | --- |
| 01/17/2010 | 29.25 | $862,417 |
| 03/16/2010 | 10.61 | $481,430 |
| 05/03/2010 | 13.55 | $721,305 |

# Event Restoration – Cost Summary

### Restoration Cost Detail by Qualifying Event

| Date | Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M – Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01/17/2010 | $0 | $50,785 | $0 | $79,959 | $862,417 | $942,376 | $993,161 |
| 03/16/2010 | $0 | $110,581 | $0 | $43,339 | $481,430 | $524,769 | $635,349 |
| 05/03/2010 | $0 | $154,017 | $0 | $44,568 | $721,305 | $765,872 | $919,889 |

### YTD Storm Restoration Cost Detail – Through May 3, 2010

| Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| $0 | $315,383 | $0 | $167,866 | $2,065,152 | $2,233,017 | $2,548,399 |

# Detail Documents

- Restoration Cost Detail – Current Event

- Detailed List of Distribution Circuits with Outages

- Terms, Codes & Definitions Used on Detail Reports

- Newsprint Media Coverage

### Restoration Cost Detail – Current Event

|  |  |  | Puget Sound Energy |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | May 3, 2010 Storm Damage Repair Costs |  |  |  |  |  |  |
|  |  | Qualifying Events Deferred Account | Capital | C&D Recoverable from Direct Billings (Costs Not Yet Billed) | O&M - Not Deferrable | O&M - Deferrable Accumulation | Total O&M | Total |  |
|  | Labor |  |  |  |  |  |  |  |  |
|  | ST |  | $ 571 |  |  | $ 5,678 | $ 5,678 | $ 6,249 |  |
|  | OT |  | $ 79 |  |  | $ 59,658 | $ 59,658 | $ 59,736 |  |
|  | Total Labor | $0 | $ 650 | $0 | $0 | $ 65,335 | $ 65,335 | $ 65,986 |  |
|  | Labor OH |  | $ 412 |  |  | $ 22,345 | $ 22,345 | $ 22,757 |  |
|  | Materials |  | $ 24,614 |  |  | $ 26,156 | $ 26,156 | $ 50,771 |  |
|  | Contractors |  | $ 103,545 |  |  | $ 580,060 | $ 580,060 | $ 683,605 |  |
|  | Other Direct Charges |  |  |  |  | $ 5,746 | $ 5,746 | $ 5,746 |  |
|  | Fleet |  | $ 74 |  |  | $ 14,492 | $ 14,492 | $ 14,566 |  |
|  | Other Assessments |  | $ 24,721 |  | $ 44,568 | $ 7,170 | $ 51,737 | $ 76,458 |  |
|  | Deferred Expenses |  |  |  |  | $0 | $0 | $ - |  |
|  |  | $0 | $154,017 | $0 | $44,568 | $ 721,305 | $765,872 | $919,889 |  |

### IEEE-1366 - Detailed List of Distribution Circuits with Outages

| NUMBER | DATE | TIME | CKT | MPG | Cause | EQT | CUST.OUT | CUST.MIN |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 10943036 | 5/3/2010 | 12:25:00 AM | CUS-16 | EAA | TV | OFU | 38 | 2,963 |
| 10943304 | 5/3/2010 | 1:55:59 AM | HKX-16 | EAC | CP | OPO | 77 | 29,082 |
| 10942722 | 5/3/2010 | 2:46:00 AM | PLA-23 | EBD | TV | OCO | 10 | 1,030 |
| E594420186 | 5/3/2010 | 3:26:00 AM | GRA-17 | EBE | TV | OCO | 1,874 | 409,600 |
| E923679781 | 5/3/2010 | 3:30:00 AM | FRA-16 | ECD | TV | OCO | 395 | 84,530 |
| E833050661 | 5/3/2010 | 3:45:00 AM | PCR-14 | EBE | TF | OCO | 514 | 206,032 |
| E184603424 | 5/3/2010 | 3:50:00 AM | CHI-12 | ECD | TF | OCO | 2,837 | 241,712 |
| E379538213 | 5/3/2010 | 4:01:00 AM | MWD-16 | EBE | TV | OCO | 50 | 4,316 |
| E847410913 | 5/3/2010 | 4:02:00 AM | MVW-17 | EBJ | TV | OFU | 39 | 9,867 |
| E353485584 | 5/3/2010 | 4:03:00 AM | SIL-15 | ECD | TV | OCR | 303 | 96,657 |
| E210907403 | 5/3/2010 | 4:03:00 AM | VAS-23 | EBL | TV | OCO | 87 | 57,594 |
| E597844321 | 5/3/2010 | 4:07:00 AM | HWD-25 | EBD | TV | OFU | 2 | 334 |
| E527412042 | 5/3/2010 | 4:14:00 AM | RJN-27 | EBJ | TV | OCO | 6 | 714 |
| E263783188 | 5/3/2010 | 4:15:00 AM | VAS-12 | EBL | TV | OCO | 19 | 9,386 |
| E013919405 | 5/3/2010 | 4:19:00 AM | NBE-13 | EBF | EF | OJU | 44 | 12,848 |
| E055418584 | 5/3/2010 | 4:21:00 AM | ALG-15 | EAA | TV | OCO | 11 | 3,212 |
| E052555582 | 5/3/2010 | 4:23:00 AM | NUG-26 | EAA | TV | OFU | 16 | 3,072 |
| E376303447 | 5/3/2010 | 4:26:00 AM | MAP-16 | EBF | TV | OCO | 8 | 3,208 |
| E423342671 | 5/3/2010 | 4:44:00 AM | ZEN-25 | EBJ | TV | OFC | 188 | 43,804 |
| E628048695 | 5/3/2010 | 5:06:00 AM | MAP-17 | EBE | TV | OPO | 4 | 3,096 |
| E395717620 | 5/3/2010 | 5:15:00 AM | BLU-16 | ECC | TV | OCO | 40 | 10,440 |
| E181679112 | 5/3/2010 | 5:29:00 AM | LAT-16 | EBJ | TV | OFC | 24 | 11,064 |
| E824910404 | 5/3/2010 | 5:29:00 AM | VAS-13 | EBL | TV | OCO | 62 | 29,884 |
| E572623147 | 5/3/2010 | 5:33:00 AM | MVW-15 | EBJ | TV | OIN | 170 | 88,570 |
| E712294389 | 5/3/2010 | 5:48:00 AM | BRW-15 | EAC | TV | OCO | 12 | 14,028 |
| E176006275 | 5/3/2010 | 5:50:00 AM | CED-15 | ECA | TV | OFU | 22 | 3,080 |
| E195788711 | 5/3/2010 | 5:52:00 AM | HOB-16 | EBI | TV | OCO | 41 | 31,324 |
| E964106403 | 5/3/2010 | 5:52:00 AM | HAS-13 | ECF | TV | OFU | 21 | 2,898 |
| E780532014 | 5/3/2010 | 5:57:00 AM | RDO-16 | EBJ | TV | OFU | 47 | 10,011 |
| E507217115 | 5/3/2010 | 5:58:00 AM | MWD-16 | EBE | TV | OCO | 29 | 4,843 |
| E621660439 | 5/3/2010 | 6:02:00 AM | LAT-14 | EBJ | TV | OFC | 1 | 346 |
| E960321217 | 5/3/2010 | 6:02:00 AM | SUM-21 | EAC | TV | OFU | 11 | 1,573 |
| E393635353 | 5/3/2010 | 6:11:00 AM | NBE-16 | EBF | TV | OCO | 1,861 | 247,720 |
| E678758251 | 5/3/2010 | 6:11:00 AM | MAN-13 | ECD | TV | OCO | 12 | 2,100 |
| E934033161 | 5/3/2010 | 6:18:00 AM | LGY-12 | EAD | TV | OCO | 7 | 10,451 |
| 10943343 | 5/3/2010 | 6:27:00 AM | PIP-23 | EBI | TV | OCO | 973 | 50,926 |
| E460103805 | 5/3/2010 | 6:34:00 AM | CRE-15 | EAD | TV | OPI | 4 | 824 |
| E028669886 | 5/3/2010 | 6:37:00 AM | BLA-12 | EAA | TV | OCO | 1 | 382 |
| E397843157 | 5/3/2010 | 6:46:00 AM | HKX-16 | EAC | PO | OPO | 77 | 6,699 |
| E891998046 | 5/3/2010 | 6:55:00 AM | GAR-12 | ECA | TV | OCO | 343 | 7,889 |
| E393617268 | 5/3/2010 | 7:04:00 AM | FRG-22 | ECC | EF | OTF | 2 | 62 |
| E165337769 | 5/3/2010 | 7:15:00 AM | FAC-13 | EBE | TV | OCO | 25 | 15,825 |
| E373848068 | 5/3/2010 | 7:16:00 AM | HAS-15 | ECF | TV | OCO | 526 | 97,310 |
| E496146001 | 5/3/2010 | 7:22:00 AM | FRA-13 | ECD | TV | OSV | 1 | 76 |
| E922659377 | 5/3/2010 | 7:30:00 AM | CRE-16 | EAD | TV | OTR | 2 | 760 |
| E256391263 | 5/3/2010 | 7:38:00 AM | LLT-16 | EBD | EF | UJU | 1 | 196 |
| E614772029 | 5/3/2010 | 7:40:00 AM | OSC-25 | EBI | TV | OCO | 2 | 926 |
| E001317844 | 5/3/2010 | 7:44:00 AM | CLV-16 | EAD | TV | OCO | 32 | 12,512 |
| E762462605 | 5/3/2010 | 7:45:00 AM | BRS-24 | EAC | TV | OHR | 121 | 22,385 |
| E015745553 | 5/3/2010 | 7:59:00 AM | NUG-26 | EAA | TV | OCO | 40 | 10,680 |
| 10942690 | 5/3/2010 | 8:00:00 AM | HAS-15 | ECF | TV | OCO | 115 | 15,525 |
| E874758381 | 5/3/2010 | 8:22:00 AM | SIL-13 | ECE | BA | OFU | 3 | 345 |
| E314033184 | 5/3/2010 | 8:28:00 AM | LWS-15 | EBJ | TV | OFU | 19 | 2,166 |
| E808426654 | 5/3/2010 | 8:29:00 AM | BCH-12 | EAA | TV | OFU | 2 | 230 |
| E860724801 | 5/3/2010 | 8:32:00 AM | BRS-13 | EAC | TV | OTF | 2 | 376 |
| E129310326 | 5/3/2010 | 8:36:00 AM | FRU-25 | ECA | TV | OCO | 1,443 | 197,997 |
| E501541379 | 5/3/2010 | 8:40:00 AM | CPV-15 | EAD | TV | OCO | 42 | 15,555 |
| E784079208 | 5/3/2010 | 8:43:00 AM | NOR-26 | EBD | SO | UPT | 3 | 951 |
| E043930990 | 5/3/2010 | 8:50:00 AM | LEA-15 | EBI | TF | OPO | 2,070 | 385,110 |
| E428332544 | 5/3/2010 | 8:50:00 AM | CLE-11 | EBH | EF | USV | 1 | 235 |
| E956351094 | 5/3/2010 | 9:02:00 AM | LMD-16 | EBJ | TV | OFU | 1 | 79 |
| E304946138 | 5/3/2010 | 9:04:00 AM | ELD-23 | ECC | TV | OCO | 23 | 4,393 |
| E482807996 | 5/3/2010 | 9:08:00 AM | DUV-15 | EBD | TV | OSV | 1 | 292 |
| E170058175 | 5/3/2010 | 9:08:00 AM | SKY-23 | EBD | SO | UPC | 1 | 172 |
| E774841637 | 5/3/2010 | 9:10:00 AM | SIL-16 | ECD | TV | OCO | 1 | 310 |
| E183373713 | 5/3/2010 | 9:34:00 AM | BRW-13 | EAC | TV | OCO | 111 | 77,589 |
| E704807618 | 5/3/2010 | 9:36:00 AM | ALG-12 | EAC | EF | OFU | 8 | 800 |
| E329987126 | 5/3/2010 | 9:39:00 AM | SWE-13 | EBJ | TV | OFU | 16 | 1,344 |
| E921582424 | 5/3/2010 | 9:45:00 AM | NBE-13 | EBF | TV | OSV | 1 | 7 |
| E188174724 | 5/3/2010 | 9:55:00 AM | PET-16 | EAC | TV | OCO | 2 | 2,530 |
| E696391158 | 5/3/2010 | 9:56:00 AM | HAM-15 | EAC | TV | OCR | 249 | 109,560 |
| E450455010 | 5/3/2010 | 10:06:00 AM | RIV-16 | EAC | TV | OCO | 10 | 12,080 |
| E220793922 | 5/3/2010 | 10:10:00 AM | MVW-13 | EBJ | TV | OFU | 6 | 360 |
| E189685915 | 5/3/2010 | 10:10:00 AM | PET-13 | EAC | TV | OAR | 110 | 105,380 |
| E927086301 | 5/3/2010 | 10:11:00 AM | NLM-12 | EAC | TV | OCO | 41 | 15,129 |
| E013578022 | 5/3/2010 | 10:12:00 AM | RDO-16 | EBJ | TV | OCO | 46 | 7,008 |
| E250127615 | 5/3/2010 | 10:19:00 AM | SEQ-16 | EBJ | TV | OSV | 1 | 56 |
| E047754097 | 5/3/2010 | 10:23:00 AM | EDG-15 | ECA | TV | OCO | 4 | 176 |
| E546149732 | 5/3/2010 | 10:25:00 AM | LTA-17 | ECA | TV | OCO | 28 | 2,100 |
| E324681693 | 5/3/2010 | 10:27:00 AM | MKI-16 | ECC | TV | OCO | 2 | 392 |
| E716878230 | 5/3/2010 | 10:38:00 AM | PAN-16 | EBJ | TV | OFC | 5 | 1,475 |
| E727804682 | 5/3/2010 | 10:47:00 AM | BIG-12 | EAC | TV | OCO | 6 | 3,618 |
| E124391429 | 5/3/2010 | 10:49:00 AM | FCR-12 | EBI | TF | OCO | 1,385 | 51,245 |
| E623709885 | 5/3/2010 | 10:50:00 AM | WLS-16 | EAC | TV | OCO | 17 | 6,800 |
| E833393837 | 5/3/2010 | 10:51:00 AM | CPV-13 | EAD | TF | OFU | 566 | 16,414 |
| E864365730 | 5/3/2010 | 10:54:00 AM | HAS-15 | ECF | EF | OFU | 20 | 1,660 |
| E511246049 | 5/3/2010 | 10:58:00 AM | NBE-15 | EBF | EF | OSV | 1 | 81 |
| E638112391 | 5/3/2010 | 11:01:00 AM | DGR-15 | ECA | TV | OCO | 9 | 504 |
| 10942476 | 5/3/2010 | 11:07:40 AM | IRO-17 | ECF | TV | OCO | 12 | 3,784 |
| E479453449 | 5/3/2010 | 11:11:00 AM | SWE-13 | EBJ | TV | OTF | 4 | 640 |
| E059438567 | 5/3/2010 | 11:27:00 AM | SHA-15 | ECA | TV | OCO | 2,569 | 105,329 |
| E112138089 | 5/3/2010 | 11:27:00 AM | PRI-13 | ECC | TV | OCO | 4 | 324 |
| E495141076 | 5/3/2010 | 11:29:00 AM | MVW-13 | EBJ | TV | OFU | 90 | 5,490 |
| E243440437 | 5/3/2010 | 11:29:00 AM | IRO-17 | ECF | TV | OCO | 628 | 114,296 |
| E304791025 | 5/3/2010 | 11:29:00 AM | SOO-25 | EBI | TV | OCO | 982 | 84,386 |
| E738604665 | 5/3/2010 | 11:30:00 AM | SWA-12 | EAD | TV | OCO | 4 | 3,764 |
| E748140391 | 5/3/2010 | 11:30:00 AM | BLU-16 | ECC | TV | OCO | 33 | 2,574 |
| E243871183 | 5/3/2010 | 11:37:00 AM | PET-15 | EAC | TV | OCO | 34 | 33,422 |
| E321234193 | 5/3/2010 | 11:37:00 AM | GAR-12 | ECA | EF | OTF | 1 | 60 |
| E893484809 | 5/3/2010 | 11:39:00 AM | KCR-17 | EBJ | TV | OFC | 32 | 9,568 |
| E865357960 | 5/3/2010 | 11:41:00 AM | PLG-13 | ECC | TV | OCO | 34 | 2,380 |
| E532592524 | 5/3/2010 | 11:42:00 AM | FRG-24 | ECC | TV | OTF | 2 | 142 |
| E135980331 | 5/3/2010 | 11:43:00 AM | CRE-12 | EAD | TV | OFU | 1,300 | 68,900 |
| E051575404 | 5/3/2010 | 11:46:00 AM | CED-13 | ECA | TV | OCO | 18 | 3,218 |
| E688540417 | 5/3/2010 | 11:50:00 AM | PIP-23 | EBI | TF | OCO | 54 | 41,472 |
| E723201217 | 5/3/2010 | 11:50:00 AM | BDI-15 | EBI | TV | OFU | 5 | 275 |
| E104839630 | 5/3/2010 | 11:50:00 AM | HLC-26 | EAD | TF | OFU | 67 | 17,966 |
| E749041614 | 5/3/2010 | 11:52:00 AM | LMD-15 | EBJ | TF | OCR | 2,282 | 280,686 |
| E086967507 | 5/3/2010 | 11:59:00 AM | BDI-12 | EBI | TF | OCR | 194 | 89,046 |
| E280122259 | 5/3/2010 | 12:00:00 PM | MAP-15 | EBF | EF | OFU | 38 | 3,800 |
| E830777118 | 5/3/2010 | 12:03:00 PM | GRV-15 | ECA | TV | OJU | 34 | 5,202 |
| E447183795 | 5/3/2010 | 12:06:00 PM | HKX-12 | EAC | TF | OCO | 1,599 | 308,607 |
| E961176001 | 5/3/2010 | 12:07:00 PM | HKX-16 | EAC | TV | OCO | 37 | 33,226 |
| E921555982 | 5/3/2010 | 12:07:00 PM | EDG-12 | ECA | TV | OFU | 51 | 7,701 |
| E997695058 | 5/3/2010 | 12:08:00 PM | HKX-16 | EAC | TV | OCO | 50 | 49,450 |
| E090156128 | 5/3/2010 | 12:11:00 PM | WOO-23 | ECA | TV | OPO | 931 | 116,277 |
| E783595858 | 5/3/2010 | 12:12:00 PM | CAM-26 | EBJ | TV | OFC | 3 | 1,281 |
| E855786396 | 5/3/2010 | 12:13:00 PM | FLD-12 | EAD | TV | OCO | 123 | 78,795 |
| E535679776 | 5/3/2010 | 12:15:00 PM | BUC-26 | ECA | TV | OCO | 1 | 454 |
| E498671469 | 5/3/2010 | 12:18:00 PM | GAR-15 | ECA | EF | OCO | 74 | 5,328 |
| E209087000 | 5/3/2010 | 12:21:00 PM | SWA-15 | EAD | TV | OTF | 2 | 928 |
| E212326818 | 5/3/2010 | 12:21:00 PM | BIG-15 | EAC | TV | OCO | 36 | 25,956 |
| E345567119 | 5/3/2010 | 12:23:00 PM | SIL-15 | ECD | TV | OFU | 11 | 2,244 |
| E602646589 | 5/3/2010 | 12:34:00 PM | FAL-13 | EBF | TV | OCO | 12 | 984 |
| E362232571 | 5/3/2010 | 12:36:00 PM | GRI-16 | ECC | TV | OCO | 11 | 2,497 |
| E943797087 | 5/3/2010 | 12:44:00 PM | SHD-18 | EBI | TV | OFU | 33 | 2,211 |
| E680241417 | 5/3/2010 | 12:47:00 PM | NLM-13 | EAC | TV | OFU | 19 | 5,662 |
| E273055893 | 5/3/2010 | 12:48:00 PM | RIT-18 | EAC | TV | OTF | 31 | 7,657 |
| E553988860 | 5/3/2010 | 12:49:00 PM | CRE-15 | EAD | TV | OCO | 144 | 20,304 |
| 10942793 | 5/3/2010 | 12:58:00 PM | BON-13 | ECA | EF | USV | 1 | 720 |
| E410633556 | 5/3/2010 | 1:03:00 PM | BLU-13 | ECC | EF | OFU | 71 | 4,473 |
| E864403753 | 5/3/2010 | 1:03:00 PM | BIG-15 | EAC | TV | OFC | 615 | 304,425 |
| E220592186 | 5/3/2010 | 1:05:00 PM | NLM-16 | EAC | TV | OFU | 19 | 5,738 |
| E912075829 | 5/3/2010 | 1:06:00 PM | CAR-15 | EAA | EF | OSV | 5 | 720 |
| E067569573 | 5/3/2010 | 1:07:00 PM | ELD-25 | ECC | TV | OCO | 10 | 1,510 |
| E081269599 | 5/3/2010 | 1:09:00 PM | LGY-15 | EAD | EF | OFU | 388 | 45,784 |
| E687503906 | 5/3/2010 | 1:12:00 PM | SUM-22 | EAC | TV | OCO | 2 | 1,196 |
| E372004109 | 5/3/2010 | 1:14:00 PM | RAI-14 | ECC | TV | OCO | 1 | 66 |
| E189898284 | 5/3/2010 | 1:14:00 PM | FRA-15 | ECD | TV | OCO | 16 | 3,760 |
| E330083858 | 5/3/2010 | 1:16:00 PM | OSC-23 | EBI | TV | OCO | 37 | 12,358 |
| E169565254 | 5/3/2010 | 1:26:00 PM | HEM-13 | ECA | TV | OCO | 2,605 | 657,278 |
| E763163281 | 5/3/2010 | 1:29:00 PM | HEM-15 | ECA | TV | OCO | 41 | 13,540 |
| E079197711 | 5/3/2010 | 1:31:00 PM | HKX-16 | EAC | TV | XFR | 120 | 75,120 |
| E989838303 | 5/3/2010 | 1:33:00 PM | WOO-27 | ECA | TV | OCO | 23 | 7,452 |
| E684964136 | 5/3/2010 | 1:40:00 PM | OSC-22 | EBI | TV | OHR | 124 | 8,556 |
| 10942712 | 5/3/2010 | 1:40:00 PM | IRO-17 | ECF | TV | OCO | 1,151 | 39,134 |
| E812189659 | 5/3/2010 | 1:44:00 PM | SHD-18 | EBJ | TV | OFC | 988 | 472,264 |
| E627439384 | 5/3/2010 | 1:46:00 PM | HAM-15 | EAC | TV | OCO | 13 | 3,705 |
| E546231144 | 5/3/2010 | 1:47:00 PM | CLE-11 | EBH | TV | OFU | 2 | 186 |
| E406714521 | 5/3/2010 | 1:47:00 PM | OSC-22 | EBJ | TV | OFU | 1 | 68 |
| E583111846 | 5/3/2010 | 1:48:00 PM | GRI-15 | ECC | TV | OCO | 3 | 156 |
| E576234155 | 5/3/2010 | 1:50:00 PM | ELL-16 | EBI | TV | OCO | 483 | 112,780 |
| E411813561 | 5/3/2010 | 1:51:00 PM | PEA-15 | EBJ | TV | OFU | 47 | 7,050 |
| E964584025 | 5/3/2010 | 1:51:00 PM | LEA-17 | EBI | TF | OCO | 2,092 | 939,308 |
| E122167314 | 5/3/2010 | 1:52:00 PM | RDO-16 | EBJ | TV | OFC | 147 | 61,152 |
| E346697175 | 5/3/2010 | 1:53:00 PM | MTH-16 | EBI | TV | OFU | 662 | 67,524 |
| E442018282 | 5/3/2010 | 1:54:00 PM | CHA-16 | ECC | TV | OCO | 1 | 396 |
| E983120386 | 5/3/2010 | 2:00:00 PM | BLU-16 | ECC | TV | OCO | 33 | 1,980 |
| E703513056 | 5/3/2010 | 2:01:00 PM | KCR-16 | EBJ | TV | OFU | 89 | 56,871 |
| E791295919 | 5/3/2010 | 2:02:00 PM | SPA-16 | ECA | TV | OCO | 988 | 156,104 |
| E641487071 | 5/3/2010 | 2:03:00 PM | SEQ-13 | EBI | TV | OFU | 3 | 312 |
| E644263858 | 5/3/2010 | 2:07:00 PM | SOO-25 | EBI | TV | OCR | 10 | 10,180 |
| E232768953 | 5/3/2010 | 2:07:00 PM | SHA-15 | ECA | TV | OCO | 2,569 | 136,157 |
| E968939947 | 5/3/2010 | 2:17:00 PM | EDG-13 | ECA | TV | OCO | 20 | 14,156 |
| E449851740 | 5/3/2010 | 2:21:00 PM | ROC-26 | ECC | TV | OCO | 70 | 4,410 |
| 10942713 | 5/3/2010 | 2:22:00 PM | SIL-15 | ECE | TV | OFU | 25 | 2,450 |
| E512039137 | 5/3/2010 | 2:22:00 PM | IRO-17 | ECF | TV | OCO | 4 | 1,116 |
| E685841434 | 5/3/2010 | 2:25:00 PM | AIR-23 | ECC | TV | OCO | 43 | 10,105 |
| E266546427 | 5/3/2010 | 2:26:00 PM | LEA-16 | EBI | TF | OSW | 1,971 | 815,994 |
| E965309788 | 5/3/2010 | 2:26:00 PM | CHM-11 | ECF | TF | OCO | 1,364 | 122,760 |
| E409145057 | 5/3/2010 | 2:28:00 PM | GRV-12 | ECA | TV | OSV | 1 | 378 |
| E922681045 | 5/3/2010 | 2:31:00 PM | GBK-15 | EAD | TF | OFU | 1,280 | 87,040 |
| E701794966 | 5/3/2010 | 2:36:00 PM | WCA-16 | EBJ | TV | OFC | 3 | 2,712 |
| E693842514 | 5/3/2010 | 2:36:00 PM | VAS-13 | EBL | TV | OFU | 45 | 4,770 |
| E252844835 | 5/3/2010 | 2:36:00 PM | FLD-13 | EAD | TV | OFU | 22 | 19,492 |
| E789103937 | 5/3/2010 | 2:39:00 PM | KAP-15 | ECA | TV | OCO | 31 | 6,758 |
| E981321536 | 5/3/2010 | 2:40:00 PM | GAR-15 | ECA | EF | OJU | 85 | 46,240 |
| E730225933 | 5/3/2010 | 2:40:00 PM | DGR-13 | ECA | TV | OCO | 573 | 220,590 |
| E550812331 | 5/3/2010 | 2:42:00 PM | ELD-23 | ECC | TV | OSV | 1 | 243 |
| E583124118 | 5/3/2010 | 2:44:00 PM | ELD-26 | ECC | TV | OCO | 1,324 | 87,384 |
| E228593463 | 5/3/2010 | 2:46:00 PM | PGA-13 | ECE | EF | OTF | 5 | 1,365 |
| E155833452 | 5/3/2010 | 2:53:00 PM | LAT-17 | EBJ | TV | OSV | 3 | 411 |
| E415440284 | 5/3/2010 | 2:53:00 PM | BIG-16 | EAC | TV | OCO | 3 | 1,011 |
| E626286712 | 5/3/2010 | 2:56:00 PM | FLD-15 | EAD | TV | OFU | 18 | 12,726 |
| E568014057 | 5/3/2010 | 2:56:00 PM | VAS-12 | EBL | TV | OCO | 8 | 5,072 |
| E358980540 | 5/3/2010 | 2:57:00 PM | LEA-13 | EBI | TV | OCO | 20 | 17,660 |
| E155166324 | 5/3/2010 | 2:58:00 PM | SKY-23 | EBD | EF | OTF | 1 | 82 |
| E323880361 | 5/3/2010 | 2:59:00 PM | SEQ-22 | EBJ | TV | OFC | 13 | 9,633 |
| E555096520 | 5/3/2010 | 3:00:00 PM | LTA-17 | ECA | TV | OFU | 32 | 18,560 |
| E233532264 | 5/3/2010 | 3:01:00 PM | LAT-13 | EBJ | TV | OFU | 16 | 11,504 |
| E459072743 | 5/3/2010 | 3:07:00 PM | CRE-01 | EAD | BA | SWD | 3,489 | 1,762,637 |
| E664886196 | 5/3/2010 | 3:08:00 PM | SHD-18 | EBI | TV | OFU | 186 | 9,672 |
| E695699083 | 5/3/2010 | 3:10:00 PM | LTA-17 | ECA | TV | UPC | 12 | 11,436 |
| E126094869 | 5/3/2010 | 3:14:00 PM | EDG-16 | ECA | TO | OCO | 35 | 3,010 |
| E616443752 | 5/3/2010 | 3:22:00 PM | GBK-13 | EAD | TV | OCO | 484 | 279,752 |
| E222382928 | 5/3/2010 | 3:23:00 PM | DIS-13 | ECF | TV | OCO | 2 | 1,172 |
| E168189523 | 5/3/2010 | 3:23:00 PM | LMD-15 | EBJ | TF | OFU | 37 | 6,290 |
| E865972371 | 5/3/2010 | 3:27:00 PM | LWS-13 | EBI | TV | OCR | 25 | 19,075 |
| E723461944 | 5/3/2010 | 3:31:00 PM | CAM-25 | EBJ | TV | OFC | 49 | 20,237 |
| E831650949 | 5/3/2010 | 3:35:00 PM | BDI-15 | EBI | TV | OFU | 12 | 5,340 |
| E709960268 | 5/3/2010 | 3:36:00 PM | NUG-26 | EAA | UN | OTF | 1 | 99 |
| E544439330 | 5/3/2010 | 3:36:00 PM | FRG-22 | ECC | TV | OCO | 310 | 54,250 |
| E839496309 | 5/3/2010 | 3:36:00 PM | WOL-25 | ECC | TV | OJU | 94 | 87,702 |
| E842196313 | 5/3/2010 | 3:38:00 PM | WLK-15 | ECA | TV | OCO | 1 | 201 |
| E108910794 | 5/3/2010 | 3:38:00 PM | LGY-15 | EAD | TV | OFU | 35 | 8,340 |
| 10942716 | 5/3/2010 | 3:41:00 PM | FRA-15 | ECD | TV | OCO | 10 | 490 |
| E724852173 | 5/3/2010 | 3:49:00 PM | LMD-16 | EBJ | TV | OPO | 88 | 56,848 |
| E576905743 | 5/3/2010 | 3:50:00 PM | KNT-37 | EBJ | TV | OFC | 12 | 6,180 |
| E865295933 | 5/3/2010 | 3:52:00 PM | ROC-16 | ECC | TV | OCO | 5 | 1,500 |
| E278291995 | 5/3/2010 | 3:55:00 PM | BON-13 | ECA | TV | OCO | 1,214 | 468,180 |
| E568710440 | 5/3/2010 | 3:58:00 PM | FRA-12 | ECD | TV | OTR | 1,049 | 118,537 |
| E147578931 | 5/3/2010 | 3:58:00 PM | GBK-15 | EAD | TV | OCO | 492 | 303,072 |
| E784841571 | 5/3/2010 | 3:59:00 PM | HOB-15 | EBI | TV | OFU | 6 | 3,606 |
| E249455216 | 5/3/2010 | 4:05:00 PM | CHM-11 | ECF | TF | OCO | 1 | 386 |
| E843045252 | 5/3/2010 | 4:06:00 PM | BTN-36 | EAC | TV | OPO | 25 | 13,000 |
| E043624648 | 5/3/2010 | 4:12:00 PM | FCR-12 | EBI | TV | OFU | 1,385 | 77,560 |
| E403492562 | 5/3/2010 | 4:17:00 PM | BRO-16 | EAD | TV | OCO | 49 | 17,199 |
| E159883603 | 5/3/2010 | 4:19:00 PM | DGR-15 | ECA | TV | OCO | 15 | 1,275 |
| E507974309 | 5/3/2010 | 4:20:00 PM | LON-25 | ECC | EF | OFU | 5 | 370 |
| E937154675 | 5/3/2010 | 4:24:00 PM | VAS-13 | EBL | TV | OCO | 123 | 6,273 |
| E871357638 | 5/3/2010 | 4:27:00 PM | LYO-15 | EBJ | TV | OCO | 6 | 1,338 |
| 10950013 | 5/3/2010 | 4:31:00 PM | ZEN-25 | EBJ | TV | OCO | 395 | 68,335 |
| E038262187 | 5/3/2010 | 4:35:00 PM | FCR-12 | EBJ | TV | OFU | 79 | 5,530 |
| E746914967 | 5/3/2010 | 4:36:00 PM | ELD-25 | ECC | TV | OCO | 2,019 | 398,068 |
| E589346092 | 5/3/2010 | 4:41:00 PM | OSC-22 | EBI | TV | OCO | 24 | 6,936 |
| E693824346 | 5/3/2010 | 4:44:00 PM | GRI-13 | ECC | EF | OTF | 2 | 340 |
| E835475799 | 5/3/2010 | 4:45:00 PM | LEA-16 | EBJ | TF | OFC | 9 | 8,037 |
| E184747360 | 5/3/2010 | 4:47:00 PM | SNQ-15 | EBF | TV | OCO | 1 | 68 |
| E108816186 | 5/3/2010 | 4:51:00 PM | CLV-16 | EAD | TV | OCO | 27 | 10,908 |
| E773555681 | 5/3/2010 | 4:59:00 PM | CUS-13 | EAA | TV | OCO | 23 | 14,174 |
| E659590935 | 5/3/2010 | 5:01:00 PM | HKX-16 | EAC | TV | OPO | 1 | 859 |
| E761284188 | 5/3/2010 | 5:01:00 PM | WAB-13 | EBJ | TV | OFU | 1 | 509 |
| E811831783 | 5/3/2010 | 5:02:00 PM | ZEN-23 | EBJ | TF | OCO | 1,304 | 134,312 |
| E480822379 | 5/3/2010 | 5:06:00 PM | HAR-15 | EBJ | TV | UTC | 3 | 1,257 |
| E260951350 | 5/3/2010 | 5:06:00 PM | EDG-16 | ECA | TV | OFU | 87 | 56,898 |
| E788430338 | 5/3/2010 | 5:07:00 PM | WAB-13 | EBI | TV | OFU | 31 | 15,593 |
| E920285307 | 5/3/2010 | 5:12:00 PM | ORC-13 | EBJ | TV | OFU | 24 | 12,192 |
| E100549499 | 5/3/2010 | 5:13:00 PM | SHD-17 | EBI | TV | OPI | 10 | 6,870 |
| 10942770 | 5/3/2010 | 5:13:00 PM | LON-26 | ECC | TV | OCO | 3 | 237 |
| E506785600 | 5/3/2010 | 5:16:00 PM | ROC-17 | ECC | TV | OCO | 6 | 708 |
| 10950144 | 5/3/2010 | 5:17:00 PM | GAR-15 | ECA | EF | OJU | 171 | 66,177 |
| E028187953 | 5/3/2010 | 5:20:00 PM | HLC-24 | EAD | TV | OFU | 1,271 | 241,490 |
| E821406660 | 5/3/2010 | 5:21:00 PM | EDG-16 | ECA | TV | OSV | 1 | 414 |
| E684315313 | 5/3/2010 | 5:22:00 PM | SMR-24 | ECA | TV | OPO | 339 | 358,219 |
| E122322981 | 5/3/2010 | 5:23:00 PM | LWS-13 | EBJ | TO | OTF | 6 | 2,652 |
| E134756638 | 5/3/2010 | 5:25:00 PM | HAM-15 | EAC | TV | OCO | 21 | 11,487 |
| E693155601 | 5/3/2010 | 5:25:00 PM | CPV-15 | EAD | TV | OCO | 12 | 3,624 |
| E647858235 | 5/3/2010 | 5:36:00 PM | BTN-35 | EAC | TV | OCO | 22 | 19,228 |
| E656564320 | 5/3/2010 | 5:37:00 PM | ELL-13 | EBI | TV | OFU | 32 | 2,976 |
| E661814082 | 5/3/2010 | 5:37:00 PM | LMD-13 | EBJ | TV | OJU | 1 | 373 |
| E443317416 | 5/3/2010 | 5:40:00 PM | FNW-17 | ECD | TV | OCO | 2 | 330 |
| E663382638 | 5/3/2010 | 5:49:00 PM | CRE-15 | EAD | TV | OCO | 95 | 15,580 |
| E127835141 | 5/3/2010 | 6:02:00 PM | FNW-16 | ECD | TV | OCO | 1,419 | 61,017 |
| 10942684 | 5/3/2010 | 6:06:26 PM | DGR-15 | ECA | TV | OCO | 4 | 2,710 |
| E333466668 | 5/3/2010 | 6:08:00 PM | MVW-13 | EBJ | TV | OFC | 12 | 4,944 |
| E536371648 | 5/3/2010 | 6:09:00 PM | STA-16 | EBJ | TV | OFC | 2 | 1,708 |
| 10942744 | 5/3/2010 | 6:11:00 PM | HAS-12 | ECF | TV | OCO | 1 | 35 |
| E407187364 | 5/3/2010 | 6:16:00 PM | BON-15 | ECA | TV | OCO | 13 | 1,755 |
| E682495272 | 5/3/2010 | 6:19:00 PM | NLM-12 | EAC | TV | OHR | 55 | 15,455 |
| E364357303 | 5/3/2010 | 6:21:00 PM | MCA-15 | ECC | TV | OCO | 6 | 528 |
| E556903382 | 5/3/2010 | 6:28:00 PM | SHA-15 | ECA | TV | OCO | 2,569 | 390,488 |
| 10942686 | 5/3/2010 | 6:28:51 PM | DIS-13 | ECF | TV | OCO | 31 | 12,436 |
| E330918140 | 5/3/2010 | 6:31:00 PM | LAT-14 | EBJ | TV | OFC | 11 | 7,744 |
| 10942649 | 5/3/2010 | 6:36:00 PM | KIT-22 | EBH | TV | OTF | 1 | 164 |
| E234818926 | 5/3/2010 | 6:40:00 PM | FCR-12 | EBI | TF | OCO | 15 | 8,850 |
| E122521036 | 5/3/2010 | 6:58:00 PM | OSC-23 | EBI | TV | OCO | 34 | 16,048 |
| E222966166 | 5/3/2010 | 7:04:00 PM | BTN-36 | EAC | EF | OPO | 1 | 692 |
| E611580966 | 5/3/2010 | 7:08:00 PM | CTR-25 | EBI | TV | OFU | 2 | 324 |
| 10942645 | 5/3/2010 | 7:11:00 PM | HWD-25 | EBD | BA | OTF | 1 | 96 |
| E666997648 | 5/3/2010 | 7:15:00 PM | BIG-12 | EAC | TV | OPO | 1 | 674 |
| E306460729 | 5/3/2010 | 7:21:00 PM | NUG-26 | EAA | EF | OTF | 5 | 592 |
| E736764372 | 5/3/2010 | 7:21:00 PM | BDI-12 | EBI | TF | OFU | 40 | 18,360 |
| E692764670 | 5/3/2010 | 7:28:00 PM | BCH-13 | EAA | TV | OCN | 1 | 95 |
| E978523575 | 5/3/2010 | 7:33:00 PM | VAS-23 | EBL | TV | OCO | 11 | 6,754 |
| E098148257 | 5/3/2010 | 7:42:00 PM | ELD-23 | ECC | TV | OSV | 1 | 563 |
| 10942757 | 5/3/2010 | 8:04:56 PM | ELD-23 | ECC | TV | OCO | 2 | 328 |
| E266233522 | 5/3/2010 | 8:19:00 PM | ZEN-25 | EBJ | TV | OFU | 31 | 2,511 |
| E771835689 | 5/3/2010 | 9:02:00 PM | FNW-17 | ECD | TV | OTF | 1 | 88 |
| E999033062 | 5/3/2010 | 9:12:00 PM | KEN-12 | EAA | EF | OTF | 1 | 80 |
| 10942746 | 5/3/2010 | 9:17:00 PM | FRA-15 | ECD | TV | OCO | 1 | 24 |
| E113476242 | 5/3/2010 | 9:17:00 PM | MST-23 | EBI | TF | OFU | 1 | 175 |
| E010081324 | 5/3/2010 | 9:25:00 PM | SOO-26 | EBJ | TV | OFC | 5 | 1,600 |
| E181833112 | 5/3/2010 | 9:38:00 PM | LGY-15 | EAD | EF | UPC | 3 | 1,836 |
| E050791069 | 5/3/2010 | 9:49:00 PM | FNW-16 | ECD | EF | OAR | 5 | 655 |
| E147533352 | 5/3/2010 | 9:58:00 PM | HEM-15 | ECA | TV | OCO | 15 | 795 |
| 10942794 | 5/3/2010 | 10:02:00 PM | STW-13 | ECA | TV | OCO | 3 | 915 |
| E722580632 | 5/3/2010 | 10:17:00 PM | ROC-16 | ECC | EF | OTF | 3 | 169 |
| E881958783 | 5/3/2010 | 10:41:00 PM | BRO-15 | EAD | TV | OCO | 144 | 27,434 |
| E205275148 | 5/3/2010 | 10:43:00 PM | CPV-15 | EAD | TV | OCO | 5 | 3,120 |
| E608503881 | 5/3/2010 | 10:58:00 PM | HOB-16 | EBI | TV | OFC | 22 | 3,564 |
| E663030270 | 5/3/2010 | 11:10:00 PM | LEA-17 | EBI | TV | OPO | 8 | 4,160 |
| 10950148 | 5/3/2010 | 11:21:00 PM | GAR-15 | ECA | EF | OJU | 872 | 19,184 |
| E226744903 | 5/3/2010 | 11:24:00 PM | GRI-16 | ECC | TV | OCO | 1 | 339 |

### Terms, Codes and Definitions Used on Detail Reports

| #### Notification | [Notification Number] A number assigned by SAP, identifying the outage record |
| --- | --- |
| Date | The date of the outage |
| Time | The time of the outage |
| Circuit | [Reference Circuit] The circuit identifier for the affected circuit |

| Area | [Maintenance Planner Group] A code representing the energy, region and service center |  |
| --- | --- | --- |
|  | EAA – Bellingham | EBJ – South King |
|  | EAB – Lynden | EBK – Southwest King |
|  | EAC – Skagit | EBL – Vashon |
|  | EAD – Whidbey | ECA – Puyallup |
|  | EBD – Redmond | ECC – Olympia |
|  | EBE – Factoria | ECD – Port Orchard |
|  | EBF – Snoqualmie | ECE – Poulsbo |
|  | EBI – Enumclaw | ECF – Port Townsend |

| Cause | Cause of Outage |  |
| --- | --- | --- |
|  | AO – Accident Other | EF – Equipment Failure |
|  | BA – Bird or Animal | EO – Electrical Overload |
|  | CP – Car Pole | FI – Faulty Installation |
|  | CR – Customer Request | TF – Tree Off Right-of-Way |
|  | DU – Dig-up Underground | TO – Tree On Right-of-Way |
|  | TV – Trees/Vegetation | SO – Scheduled Outage |
|  | UN – Unknown |  |

| Equipment | Affected by, or involved in the outage |  |
| --- | --- | --- |
|  | OCN – Connector | OSW – Overhead Switch |
|  | OCO – Overhead Conductor | OTF – Overhead Transformer Fuse |
|  | OCR – Crossarm | OTR – Overhead Transformer |
|  | OFC – Overhead Cut-out | OUP – OH to UG Primary |
|  | OFS – Overhead Fire Signal | OUS – OH to UG Secondary Service |
|  | OFU – Fuse Link/OH Line Fuse | SBF – High-side Bank Fuse |
|  | OGS – Span Guy | SCB – Power Circuit Breaker |
|  | OHR – Overhead Recloser | UOT – Underground Outdoor Term |
|  | OIN – Insulator | UPC – Underground Primary Cable |
|  | OJU- Jump Wire | UPT – Padmount Transformer |
|  | OPI – Overhead Pin Insulator | USV – Underground Service |
|  | OPO – Pole | UTC – Underground Terminal Fuse |
|  | OSV – Overhead Service | UTR – Submersible Transformer |
|  | ORE – Regulator |  |

#### Codes, Definitions – Continued

| CUST OUT | [Customer Out] The number of customers without power for any given outage record |
| --- | --- |
| CUST MIN | [Customer Minutes] The total number of minutes customers were without power for any given record |

### Media Coverage

Monday, May 03, 2010

Storm brings high winds, outages to Western Wash.

By KING5.com and TERESA YUAN / KING 5 News

Watch story here.

SEATTLE -- A spring storm is sweeping across Western Washington Monday with heavy rain and high winds that are causing scattered power outages.

Forecasters expect 20-to-30 mph winds through the day with gusts to 50 mph. Early Monday, 48 mph wind gusts were reported in Seattle, 47 mph gusts in Everett and 40 mph in Tacoma.

Power outages were reported early Monday morning. Seattle City Light reports nearly 3,500 customers are without power in the Rainier Beach neighborhood. And Puget Sound Energy has about 2,800 customers in the dark, mostly in Seabeck on the Kitsap Peninsula.

Firefighters in Renton are still on scene of an active fire and power line that was taken down by a fallen tree. Firefighters are waiting for Puget Sound Energy crews to come and turn off the power before they can douse the flames with water.

Crews believe weather was to blame for the fire; most likely strong winds snapped the tree which is now laying and blocking the middle of the road. Nearby residents have been warned to stay away from this road as firefighters deal with the "live wire" in the street.

Crews are also dealing with pockets of power outages across Renton. A section of downtown Renton is in complete darkness around the transit center. Several blocks were without power around Logan and Second Avenue South, and many buildings were dark and street lights and stoplights were out. Puget Sound Energy says it's dealing with an underground cable problem in that outage. A number of residential areas in Renton were also without electricity.

"Winds have peaked and they are diminishing right now," said KING 5 Meteorologist Rich Marriott. "Up in the North Sound, showers and windy this morning. Look for showers, sunbreaks and breezy this afternoon, though it will stay windy in the Strait of Juan de Fuca and across Whidbey Island in the afternoon."

Marriott says the South Sound can expect the same for Monday. Forecasters expect the blustery weather to ease Tuesday but for unsettled conditions to continue this week.

School closures

St. Anthony School in Renton is scheduled to close Monday because the building does not have power. School officials say if the power is back on by 8 a.m., they will do a late start. But for now, no classes are scheduled Monday at St. Anthony School in Renton.

Monday, May 03, 2010

SEATTLE -- Another spring storm is sweeping across Western Washington, causing scattered power outages and bringing more snow to the mountains. 
 	Overnight several hundred Puget Sound Energy customers lost power in Mercer Island and Renton, and at least one school was closed because they had no electricity.
 	Seattle City Light crews were restoring scattered outages in the Rainier Beach area. 

Winds of 20 to 30 mph are expected through the day on Monday, with gusts to around 40-50 mph likely in some areas. 
 	The spot expected to have the greatest wind speeds is along Admiralty Inlet which would include the western shores of Whidbey Island. A High Wind Warning is in effect here through 9 p.m. Monday for a few westerly gusts of 45-55 mph, maybe a gust to 60 mph.
 	For the rest of Western Washington, a lesser Wind Advisory remains in effect through 7 p.m. for occasional gusts to 40-45 mph, with maybe a few isolated gusts to 50 mph in exposed areas along shorelines and ridgetops. (The High Wind Warning around Everett and Mount Vernon was downgraded a wind advisory too.)
 	Winds die down all areas Monday afternoon into Monday evening.
Mountain Snow:
 	This storm will also bring a late season dose of snow to the mountains. A Winter Storm Warning is in effect through 6 a.m. Tuesday. Snow level will be around 5,000 feet Sunday night, but will drop to 2,500 feet Monday morning.
 	We could see 6-12 inches of snow by Monday night, with greatest amounts above 3,500 feet. Gusty winds to 35-45 mph are possible during the day Monday up there making blowing snow a concern as well.
 	Just be sure to check the mountain pass reports before you head up there. (You can call 511 for road information for free. I just used it last week on a trip through the mountains. Works great!)
 	Snow levels will remain low into Tuesday with snow showers continuing in the mountains.
Active Tuesday, too
 	The main rain and wind will be done with Monday evening, but with a very cold air mass in place on Tuesday, it's a recipe for heavy showers roaming around with potential for thunderstorms with hail and/or ice pellets. A Convergence Zone is also a good bet for Tuesday morning in the usual Everett to Northgate area, bringing a higher chance of thunderstorms there.
 	The zone could also slide south into Seattle during the day or afternoon, so keep an eye to the skies Tuesday as well.
 	By Wednesday, we start getting back to some semblance of normal with calmer weather the rest of the week -- which would be nice to have a Mother's Day without so much Mother Nature.

Monday, May 3, 2010 - Page updated at 01:01 PM

- Get ready for wind around Sound, blowing snow in passes

By Susan Gilmore

Seattle Times staff reporter

The National Weather Service has issued a wind advisory for the Seattle-Tacoma-Everett area, where winds could get up to 30 mph with gusts to 50 mph through 7 p.m. Monday.

And a winter storm warning has been issued for the Olympic and Cascade Mountains until 6 a.m. Tuesday. Forecasters said the snow level has dropped to 2,000 feet, and there could be 6 to 12 inches of snow on the mountain passes. Along with strong winds, that could cause hazardous driving conditions through the passes, said forecaster Johnny Burg.

The weather has caused the state Department of Transportation to close the North Cascades Highway, and high winds have caused several power outages around Puget Sound.

Susan Gilmore: 206-464-2054 or sgilmore@seattletimes.com

Copyright © The Seattle Times Company

Washington windstorm knocks down limbs, blows dust

Monday, May 3, 2010  The Associated Press

A spring storm with 40 mph winds blew down tree limbs in Western Washington then kicked up dust storms in Eastern Washington while adding another dash of snow in the mountains.

Power outages were reported early Monday at Seabeck in Kitsap County and in the Rainier Beach neighborhood of Seattle. An outage canceled classes at Green River Community College in Auburn.

Blowing dust closed Highway 281 between Quincy and George. Grant County Emergency Managment advised people not to travel.

The Yakima County sheriff's office also reported roads closed by dust. KNDU reported Prosser declared an emergency because of wind damage.

The National Weather Service has a winter storm warning in effect until 6 a.m. Tuesday in the Cascades. The Transportation Department has closed the North Cascades Pass due to avalanche danger.

Copyright © The Seattle Times Company

- Spring storm brings snow, 60 mph gusts, blowing dust

A powerful spring storm packing winds that gusted to more than 60 mph blew down trees in Western Washington then kicked up dust

Tuesday, May 4, 2010   The Associated Press

A powerful spring storm packing winds that gusted to more than 60 mph blew down trees in Western Washington then kicked up dust storms in Eastern Washington while dropping fresh snow in the mountains.

Washington State Ferries canceled Monday's 8:30 p.m. sailing from Port Townsend and the 9:15 p.m. sailing from Keystone because of high winds and rough seas.

The North Cascades Highway was closed because of blowing snow and snow slides. Check pass conditions at: www.wsdot.wa.gov (click on Mountain Passes at top right).

At the height of Monday's storm, more than 40,000 utility customers lost power across Washington and into Northern Idaho.

In Central Washington, blowing dust prompted the temporary closure of two state highways. The dust storms were blamed for a number of traffic accidents.

Monday, May 3, 2010

East Jefferson bears brunt of high winds on Olympic Peninsula
By Rob Ollikainen and Charlie Bermant

An unusually strong May cold front swept through the North Olympic Peninsula on Monday, blowing down branches, kicking up debris and knocking out power to nearly 1,500 customers.
 	Jefferson County took the brunt of the blow with 1,350 Puget Sound Energy customers losing power. Most of the outages were in the Port Ludlow and Port Hadlock areas. 
 	By 8:45 p.m., all but seven were back on the grid, said Dorothy Bracken, PSE spokeswoman.
 	Crews were working in three locations to replace wire, felled by fallen trees and limbs, that funneled electrical power to those seven customers, she said.
 	All of the outages were wind-related, PSE spokeswoman MacKenzie McDowell confirmed.
 	About 120 Clallam County Public Utility District customers experienced wind-caused outages, the largest of which affected 62 in the Priest Road area west of Sequim.
 	Another outage affected 39 PUD customers along Towne Road north of Sequim.
 	Power had been restored to all PUD customers by 5 p.m., PUD spokesman Jeff Beaman said.

55 mph gusts
 	The highest gust on the Peninsula was recorded at Point Wilson near Port Townsend: 55 mph.
 	Quilcene was relatively calm, with the highest recorded wind speed being 16 mph in the early morning hours, according to National Weather Service observations.
 	Sequim's strongest gust was 43 mph at about 11:30 a.m.
 	The wind hit 33 mph at William R. Fairchild International Airport in Port Angeles on Monday afternoon. Sustained winds of more than 20 mph were felt in the morning. 
 	On the West End of Clallam County, wind gusts hit highs of 37 mph at LaPush and Neah Bay and 36 mph at the Quillayute Airport near Forks.
 	"We have a pretty strong low pressure system that went through," said Johnny Burg, a meteorologist with the National Weather Service in Seattle. 
 	"There was a good difference between the pressure gradients."
 	The winds shifted from the south to the west as the cold front passed over the region and headed into southern British Columbia, Burg said.
 	He said the storm was fairly uncommon for this time of year.
 	Walter Hill, 65, of Port Townsend, was traveling north on Jacob Miller road at about 9:30 a.m. when he saw the tree on the opposite side of the street start to fall, the Jefferson County Sheriff's Office said. 
 	He was unable to stop, and the tree fell onto his 1986 Nissan pickup, crushing the front of the truck and the windshield. Hill was not injured, the sheriff's office said.
 Power off at jail
 	At about 2:50 p.m., electrical power went off at the Jefferson County Sheriff's Office and jail, and the generators kicked in immediately. 
 	The power was out for about 45 minutes, but the office was able to work with the backup systems. 	
 	"If the power goes out during the day we get enough light through the windows, said Deputy Joe Nole, "so it's not that big a deal to have to rely on the generators."
 	Ross Tyler, Clallam County Engineer, said most of the damage occurred on the east side of Clallam County.
 	"We had a couple trees down in the east end but nothing of any significance, except one was hung up in a power line," Tyler said.
 	The tree that fell into the line was actually in East Jefferson County on a short section of Chicken Coop Road that Clallam County maintains near Gardiner.
 	Olympic National Park reported a 2,000-foot snow level with an additional 4 to 10 inches of snow possible overnight. There was 91 inches of snow at Hurricane Ridge on Monday.
 	The National Weather Service lifted a high wind advisory for the region on Monday. Winds were forecast to subside to 10 to 15 mph today, Burg said.

Tuesday, May 04, 2010

Spring storm blows through

High winds, hail cause power outages, accidents

By TAHLIA GANSER

There is a saying for spring weather in Washington. If you don’t like it, wait 10 minutes. But Monday in Skagit County there might have been a better adage: If you don’t like it, drive 10 miles. In the afternoon, the sun shined   in Burlington. Just north in the Alger area, a heavy hail storm was contributing to a multiple-vehicle accident. Farther south in Conway, branches were snapping and tearing down power lines. Farther east, snow dumped in the Cascade Mountains.

“We’ve got our crews out racing around to lots of different spots,” said state Department of Transportation spokesman Dustin Terpening.

Trees and tree limbs were the biggest culprits, blocking roads such as Highway 534 near Bulson Road in Mount Vernon. Fallen trees and power poles blocked both lanes of the road.

Slippery roads from the sudden hail storm in the Alger area led to six accidents involving eight cars within minutes just before 1 p.m. today, according to the State Patrol.

Six cars slid off Interstate 5 into   the median. Two of those cars hit each other. The driver of a semitruck pulled over to help the people in the median, and he was struck by a passenger car.

A woman driving the passenger car that struck the truck suffered possible leg and hip injuries and was taken to the Skagit Valley Hospital.        No one else was injured in those accidents, which closed the southbound lanes of the highway for more than 30 minutes.

Snapping trees and branches tugged on power lines, leaving thousands of residents without power around the county.

‍Puget ‍Sound ‍Energy did not have the total number of people who lost power throughout the day.

However, a spokeswoman said 1,900 customers lost power in Anacortes in the morning. At noon, 1,000 customers throughout the county   did not have power. By 4:30 p.m., nearly 700 customers were still without power, most of them in small neighborhood pockets in the Concrete and Sedro-Woolley areas.

Wind gusts ripped through the county at as much as 50 mph Monday, according to National Weather Service meteorologist Doug McDonnal.

“The winds are unusually strong for early May,” McDonnal said.

But a reprieve should come today.

“That will start easing off this evening,” he said.

Whidbey Island was hit with the strongest gusts in the area, with sustained winds at 40 mph and gusts more than 50 mph.

The Cascade Mountains were expected to have a foot of snow by early this morning. The snow has closed the North Cascades highway due to avalanche danger, according to the DOT.

It is unknown when the highway will reopen.

Skagit County’s mild winter might have been a tease for those expecting an early summer this year, McDonnal said.

He added, “May and June tend to be frustrating months for people who are waiting for summer to arrive.”

Monday, May 3, 2010

Rare May storm knocks out power to thousands

By Scott Sistek

SEATTLE -- According to the calendar, we are almost closer to summer than winter now.

To anyone who walked outside today or spent the afternoon in the dark, that might seem like a cruel joke.

A very late winter-like storm rolled through Western Washington Monday, bringing gusty winds, heavy mountain snows, and knocking out power to over 24,000 people.

Whidbey Island was getting the brunt of the storm's winds, with frequent gusts over 50 mph through Monday morning and afternoon, topping out with a peak gust of 56 mph.

Here are some other peak gusts from the storm so far:

- Oak Harbor: 56 mph

- Alki Beach (W. Seattle): 51 mph

- Arlington: 48 mph

- Everett: 47 mph

- Shelton: 47 mph

- Tacoma: 45 mph

- Port Angeles: 41 mph

- Gig Harbor: 41 mph

- Olympia: 40 mph

- Bellingham: 39 mph

- Seattle (Sea-Tac): 39 mph

- Hoquiam: 39 mph

The strong winds knocked over trees and limbs in several areas across the Puget Sound region, causing scattered power outages. We've seen trees down in Renton, Federal Way, Arlington and Auburn.

In Mount Vernon, a tree fell across SR-534 near Bulson Road, and as our news crew was filming the downed tree, another one came down just a few feet away. In Arlington, a massive tree wiped out a second-story deck of a home and punched a hole in the roof.

"Well, I was just glad it wasn't raining because there is a hole in the roof and I didn't want to have to eat dinner in the rain," said Curtis McKay, who is renting the home.

In Federal Way, a tree toppled across SR-18 near 42nd Ave. S.during the early Monday commute, blocking most of the lanes and snarling traffic.

Puget Sound Energy reported 16,000 without power at one point Monday afternoon, with most in the Puyallup area. Mercer Island and Renton had outages earlier in the morning.

Snohomish County PUD said 8,000 were in the dark, mainly in Marysville and Arlington areas.

Seattle City Light had scattered outages, mainly in the early Monday morning hours in the Rainier Beach area.

A High Wind Warning remains in effect for the Whidbey Island area until 9 p.m. but other wind advisories have been dropped as the winds have peaked and will slowly subside through Monday evening and night.

Mountain Snow:

This storm also brought a late season dose of snow to the mountains. Stevens Pass reported 12 inches of snow since Sunday evening, and another 6-10 inches more were possible Monday night. Snoqualmie Pass has been spared snow so far, but they were on the hook for some snow Monday night as a Puget Sound Convergence Zone formed.

A Winter Storm Warning is in effect for the Cascades through 6 a.m. Tuesday.

Focus Changes From Wind To Lightning

As the winds calm down, we turn our attention to an active Puget Sound Convergence Zone that has formed in its usual spot between Seattle and Everett. This zone is likely to touch off heavy rain showers with possible lightning and hail and/or ice pellets through Monday night. It's also possible this zone will sink south through the night, spreading heavy rain and possible hail into the Downtown Seattle/Bellevue area, and even down as far as Tukwila and Renton toward dawn.

Outside this zone, we'll see scattered showers roaming around through the night that could also contain some lightning and/or hail.

Active Tuesday, too

The main rain and wind will be done with Monday evening, but with a very cold air mass in place on Tuesday, it's a recipe for heavy showers roaming around with potential for thunderstorms with hail and/or ice pellets. A Convergence Zone is also a good bet to reform Tuesday morning in the usual Everett to Northgate area, bringing a higher chance of rain and thunderstorms there.

The zone could also slide south into Seattle during the day or afternoon again, so keep an eye to the skies Tuesday as well.

By Wednesday, we start getting back to some semblance of normal with calmer weather the rest of the week -- which would be nice to have a Mother's Day without so much Mother Nature.

Monday, May 3, 2010

UPDATED: Loss of power shuts college in Auburn

Posted By Mike Archbold

1:50 p.m. Update: Puget Sound Energy has notified the City of Auburn that the damage to the power feeder pole on Lea Hill is more extensive than first thought.
The estimated restoration of power is now expected to be 8 p.m.

PSE has been able to restore power to around 750 customers using another circuit, according to city officials. There are still 758 customers, including Green River Community College, without power.

The high winds hitting South King County have taken out power to the Green River Community College campus in Auburn and students are being sent home, Auburn officials said.

College officials hope to reopen at 3 p.m. The east entrance to the campus is closed.

The power outage in the Lea Hill area of Auburn where the campus is located was due to wires coming down at Southeast 320th  near the college. The outage closed Southeast 320th which probably won't re-open hours.

Alternate routes are strongly advised.

Monday, May 3, 2010

Power outage cancels classes at Green River Community College

AUBURN, Wash. -- Strong winds pushed trees into power lines and caused an outage at Auburn’s Green River Community College.

The power went out shortly before 9 a.m. Monday and classes were expected to resume by 3 p.m., but officials later canceled classes for the day.

The main entrance to the campus was closed as crews worked to clean up the tree and downed power lines. With one exit blocked, traffic was slow on the remaining exit from campus, prompting some students to walk.

“Traffic was all the way backed up so we couldn't get out, decided to go get some food,” said Lorena Velazquez.

Grounds keepers also decided to pull a second tree down safely before it was blown down by the wind.

The downed trees also cut power to about 17,000 customers, Puget Sound Energy said.

GRCC web site: http://www.greenriver.edu/.

Monday, May 3, 2010

Power outages in Renton, possible thunderstorms tonight

By CELESTE GRACEY

Heavy winds knocked down trees and power lines causing two major power outages in Renton today.

Power was cut in the Renton Highlands around 5 a.m. after a tree took down power lines and ignited a fire, affecting about 520 customers, said Puget Sound Energy Spokeperson Abigail Elliott.

A wind advisory is in effect until 7 p.m., which could be followed by thunderstorms tonight, according to the National Weather Service.

South and southwest winds are expected to sustain speeds of 20 to 30 mph with gusts up to 50 throughout the Seattle area.

The skies have remained blue with little rain, though that's expected to change Tuesday.

A second power outage on Raymond Avenue Southwest was also reported this morning and fixed at about 10 a.m., Elliott said.

PSE doesn't know yet how many customers that power outage affected.

There were also reports of outages in Downtown Renton including at St. Anthony's school and Merrill Gardens.

"We did have small scattered outages through our service area," she said. "Our crews are ready and their responding as needed."

An wind advisory is called when winds are strong enough that they can snap tree branches, topple small trees and cause local power outages.

Monday there is a 70 percent chance of showers all day with a high of 53 and a low of 40, according to NWS.

The rain and thunder is expected to continue Tuesday morning with a high of 53 and a chance of thunderstorms Tuesday night.

Monday, May 3, 2010

- Wind knocks down trees on Whidbey

By ROY JACOBSON

Brisk winds overnight knocked down some trees and caused small, scattered power outages across Whidbey Island, but no injuries were reported, officials said Monday morning.

Wind gusts to 47 miles per hours were reported at Naval Air Station Whidbey Island in Oak Harbor shortly after 8 a.m. Monday, and gusts in the low 40-mph range were reported at Langley throughout Sunday night and Monday morning, said Chris Burke of the National Weather Service in Seattle.

Wind gusts from out of the west were expected to continue throughout the day Monday, diminishing by 9 p.m., Burke said.

Trees were blown down on four roadways between 10:30 p.m. Sunday and 6 a.m. Monday in South Whidbey, Island County Fire District 3 Deputy Chief Mike Cotton said.

Traffic was blocked for a short time at Quade Road near Maxwelton and Ewing roads Sunday night, and at Campbell Road near Highway 525, at Wahl Road and at Lone Lake Road early Monday morning, Cotton said.

Also around 6 a.m. Monday, smoking branches were reported on power lines near Campbell Road and Highway 525, he said.

Puget Sound Energy reported small outages affecting fewer than 10 customers each at various Whidbey locations, said Abigail Elliott, a PSE spokeswoman.

"Just a few customers here and there," she said. She said crews were repairing outages as they were reported.

Meanwhile, on Sunday morning a 20-foot pleasure boat was found overturned and washed up on the beach at Admiralty Inlet north of South Whidbey State Park.

Neighbors called the Coast Guard, who determined that the boat had been unoccupied, and the owners were contacted.

Mike Wiatt of Greenbank, a resident of the area, said three men in a small aluminum boat arrived early Sunday afternoon to retrieve the beached craft. Failing to right the overturned boat, they began towing it semi-submerged toward Lagoon Point as darkness fell, Wiatt said.

"It was pitch dark and the seas were really rocking, so who knows where they ended up last night," Wiatt said in an e-mail to the Record.

Burke of the National Weather Service said gale warnings were in effect in all coastal waters, and that the winds were creating a convergence zone near the King-Snohomish County line, which could result in thunderstorms later in the day Monday.

Monday, May 3, 2010

Spring storm blows through Northwest, causing outages

SEATTLE -- A spring storm swept across Western Washington Monday bringing heavy rain, thundershowers, ice pellet showers and high winds that were causing scattered power outages and some damage.

At the height of Monday's storm, more than 40,000 utility customers lost power across Washington and into north Idaho.

Peak wind gusts Monday morning hit 48 mph in Seattle, 55 mph in Oak Harbor, 47 mph in Everett and 40 mph in Tacoma and Puyallup.

High winds caused several problems. In Renton, winds toppled trees and knocked out power to sections of the city. Trees fell onto homes in Woodinville and Auburn. Firefighters in Renton also fought an early morning fire thought to have been caused by strong winds.

The National Weather Service has a winter storm warning in effect until 6 a.m. Tuesday in the Cascades. Up to a foot of snow could fall by Tuesday morning. The Transportation Department has closed the North Cascades Pass due to avalanche danger.

High winds and rough seas Monday afternoon led to the cancellation of two sailings on the Keystone-Port Townsend route. The 3:45 p.m. sailing from Port Townsend and the 4:30 p.m. sailing from Keystone have been cancelled, according to Washington State Ferries.

Seattle City Light reported nearly 3,500 customers were without power in the Rainier Beach neighborhood, and Puget Sound Energy had about 2,800 customers without electricity, mostly in Seabeck on the Kitsap Peninsula. About 8,000 customers were without electricity in Snohomish County, and Skagit, Thurston, Jefferson and Island counties also experienced scattered outages.

On Camano Island, strong westerly winds decimated trees and knocked down power poles. By midday Monday, Stanwood Camano Fire Department crews had responded to 25 separate wind-related calls.

"Every time we respond to a report of a tree down, we get another call somewhere else," says Assistant Chief Levon Yengoyan, Stanwood Camano Fire Department. "The road closures are causing us to take alternate routes to medical calls."

Strong winds decreased Monday evening and the high wind warning has been canceled. However, a wind advistory is still in effect until 11 p.m. Monday. Winds of 30 to 40 mph with gusts to 50 mph will continue through the evening, then decrease to 20 to 30 mph by midnight.

"This is all going to start to quiet down overnight tonight. Tomorrow promises to be a little bit more quiet," said Guy.

Meanwhile, the spring storm is causing a dust warning for Eastern Washington, which visibility is reduced between Quincy and George in Grant County. Some part of Yakima County also are affected. The dust warning is in effect until 11 p.m. Monday.

KING 5's Teresa Yuan and Jake Whittenberg, and KGW Staff contributed to this report.

Tuesday, May 4, 2010

Unusual storm blasts Whidbey

By Sue Ellen White

For the Examiner

This is Severe Weather Awareness Week in the Pacific Northwest, according to the National Weather Service.

Right out of central casting, a strong windstorm showed up overnight Sunday and blasted the regional all day Monday, resulting in an Oak Harbor substation shutdown affecting 3,600 customers in the Crescent Harbor area.

The Keystone-Port Townsend ferry was cancelled, and the vessel remained tied up at the dock all day.

The unusual May storm was predicted by the weather service, which issued a winter storm warning and a high wind warning for Admiralty Inlet. It reported on its website Monday morning winds gusting to 56 miles per hour at a location north of Oak Harbor.

Equipment at the substation was damaged by the storm at about 4:30 p.m. Monday afternoon, resulting in the outage, said Dorothy Bracken of Puget Sound Energy. She said that power was expected to be restored by late Monday evening.

In addition to the Oak Harbor outage, scattered blackouts were reported at 22 locations affecting about 1,000 customers on Whidbey, according to Bracken.

“Whenever you’ve got trees and wind and power lines, there’s going to be instances,” said Dom Amor, PSE local government and community relations manager.

Only about 15 Coupeville residents reported power outages, and numerous outages on South Whidbey.

“In almost all those locations there is a tree that has taken wires out. Crews are moving from one location to another, restringing wire,” Bracken said.

Four crews were working Whidbey, and Bracken said power was to be restored by early Tuesday.

Customers experiencing outages at any time can get information on their specific service location when they call in to report the problem, Bracken said.

Call 1-888-225-5773, wait until the recorded report ends, then follow the prompts for outages and customer information. The line is staffed 24 hours a day, she added.