BEFORE THE 
WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION

| WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION, Complainant, v. CASCADE NATURAL GAS CORPORATION, Respondent. | DOCKET NO. PG-110443 ANSWER |
| --- | --- |

## INTRODUCTION

Cascade Natural Gas Corporation's ("Cascade" or "the Company") address for purposes of this proceeding is:

Katherine Barnard 
Manager--Gas Supply & Regulatory Affairs
Tina Beach

Manager- Standards and Compliance
Cascade Natural Gas 
8113 W Grandridge Blvd

Kennewick, WA 99336-7166
Phone:  509 734-4593
	 509 734-4576
Email:  kathie.barnard@cngc.com
	tina.beach@cngc.com

Cascade's representatives for purposes of this proceeding are:

Sheree Strom Carson
Donna L. Barnett
Perkins Coie LLP
10885 N.E. Fourth Street, Suite 700
Bellevue, WA 98004-5579
Phone: 425-635-1400
Fax:	425-635-2400
SCarson@perkinscoie.com
DBarnett@perkinscoie.com

Cascade recognizes the Commission's important responsibilities in auditing and enforcing pipeline safety with respect to the companies it regulates.  Cascade is committed to operational excellence, and the Company strives for full compliance with federal and state regulations. Cascade recognized many of the issues addressed in this Complaint prior to its filing, and Cascade has heightened its efforts and has taken appropriate action to correct such issues.  The Company believes it operates and maintains a safe and reliable system.  Nevertheless, Cascade is constantly looking for ways to improve and enhance pipeline safety.  In that regard, the Company welcomes the Commission Staff's audits of its facilities as a means of identifying systems and processes related to pipeline safety that are both working effectively, and that may be improved with the goal of providing safe and reliable gas service.

With these fundamental principles in mind, Cascade answers the Complaint of the Washington Utilities and Transportation Commission (the "Commission") dated March 21, 2011 (the "Complaint") as stated below.

## ANSWER

Because paragraph 1 contains no legal or factual allegations, Cascade neither admits nor denies this paragraph.

# I.	PARTIES

Answering paragraph 2, Cascade admits that the Commission is an agency of the State of Washington, authorized by Title 80 RCW to regulate in the public interest the rates, services, facilities and practices of all persons engaging within the State of Washington in the business of supplying any utility service or commodity to the public for compensation, and related activities, including gas companies, and by RCW 81.88 to regulate persons or entities constructing, owning, or operating gas pipelines for transporting gas.

Answering paragraph 3, Cascade admits that it is a corporation that, among other things, owns and operates a system for transporting natural gas within the State of Washington.

# II.	JURISDICTION

Answering paragraph 4, Cascade admits that the Commission generally has jurisdiction over this matter pursuant to the provisions of RCW 80.28 and RCW 81.88.  Cascade admits that the conduct alleged in this complaint occurred within the State of Washington.  With respect to specific provisions cited in the Complaint, paragraph 4 contains legal conclusions to which no answer is required.

8.	Answering paragraph 5, Cascade admits that the Commission generally has jurisdiction over this matter pursuant to the provisions of RCW 80.01, RCW 80.04, RCW 80.28, RCW 81.88, and WAC 480-93.  With respect to specific provisions cited in the Complaint, paragraph 4 contains legal conclusions to which no answer is required.

# III.	BACKGROUND

9.	Answering paragraph 6, Cascade admits that the Commission has adopted, through WAC 480-93-999(1), Part 192 of the Title 49 of the Code of Federal Regulations (C.F.R.) and has promulgated gas pipeline rules codified in WAC 480-93 and WAC 480-90. The first sentence of paragraph 6 states a legal opinion or conclusion for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 6, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

10,	Answering paragraph 7, Cascade admits that WAC 480-93-180(1) states in part that a gas utility such as Cascade must "have and follow" a "gas pipeline plan and procedure manual" and "that manual must include plans and procedures for meeting all applicable requirements of 4 CFR §§ 191, 192 and Chapter 480-93 WAC."

11.	Answering paragraph 8, Cascade admits that it possessed a plan and procedures manual at all times relevant to the Complaint.  Cascade neither admits nor denies the second sentence of paragraph 8, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

12.	Answering paragraph 9, Cascade neither admits nor denies paragraph 9 because it describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 9, Cascade denies the same.

13.	Cascade neither admits nor denies paragraph 10, which describes aspects of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.

14.	Cascade neither admits nor denies paragraph 11, which describes aspects of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.

# IV.	NATURE OF THE COMPLAINT

15.	Answering paragraph 12, Cascade neither admits nor denies the first sentence of paragraph 12, which describes aspects of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.  Cascade admits that Staff conducted investigations of Cascade's gas facilities, records and practices in the five districts listed in paragraph 12.  The remainder of paragraph 12 states legal opinions and conclusions for which an answer is not necessary.

16.	Answering paragraph 13, Cascade denies the allegations in the first sentence of paragraph 13.  Cascade admits that the Commission has statutory authority to issue monetary penalties for gas safety rule violations and that the Commission may set standards for service.  The remainder of paragraph 13 states legal opinions and conclusions for which an answer is inappropriate and is therefore denied.

# V.	ALLEGATIONS

## A.	Claims and Causes of Action

### 1.	First Cause of Action (Overpressure)

17.	Answering paragraph 14, Cascade admits that Cascade had one overpressure event on December 2, 2009.  Cascade immediately responded to the event and remedied the condition.

18.	Answering paragraph 15, the first sentence of paragraph 15 states a legal opinion or conclusion for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 15, which does not contain any factual or legal allegations that require an answer.

19.	Answering paragraph 16, Cascade admits that it notified the Commission of the incident at approximately 2:00 P.M. on December 3, 2009.  Cascade also admits that the pipeline was possibly operated at 120 pounds per square inch gauge ("psig").  The gauge was installed and the relief stopped almost, if not immediately, after the regulator was shut down.  This indicates that pressure was close to, if not less than, the relief set pressure.  The regulator station has been removed, and the system has been looped back to the main city regulator, and pressure is being monitored.

20.	Answering paragraph 17, the first sentence of paragraph 17 states a legal opinion or conclusion for which an answer is inappropriate and is therefore denied.  The last sentence of paragraph 17 does not contain any factual or legal allegations that require an answer.  Further answering paragraph 17, Cascade has a long history of compliance with WAC 480-93-200(1)(f) prior to the December 2, 2009 event, and Cascade complied with the rule after the event.  Cascade's failure to notify Commission Staff within two hours of an overpressure event on December 2, 2009, was an anomaly.  In fact, Cascade has notified Staff of overpressure events as small as one pound over the maximum allowable operating pressure (MAOP), which was less than the amount that requires Staff notification.  When it became apparent on December 3, 2009, that Staff had not been notified, Cascade immediately notified Staff, correcting the reporting error.  Further, Cascade took steps to educate personnel regarding timely reporting, and has implemented long-term corrections to enhance its compliance with reporting requirements such as WAC 480-93-200(1)(f).  For example, Cascade has recently developed new Emergency Notification Guidelines and Emergency Contact Guidelines, which specifically address the types of event described in this cause of action.

21.	Answering paragraph 18, Cascade admits that it repaired the regulator by approximately 11:25 A.M. on December 2, 2009.  Cascade denies the remainder of the allegations in paragraph 18.  The second sentence of paragraph 18 states opinions and conclusions of Staff for which an answer is inappropriate and is therefore denied.

22.	Answering paragraph 19, the first sentence of paragraph 19 states a legal opinion and conclusion for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 19, which does not contain any factual or legal allegations that require an answer.

23.	Answering paragraph 20, Cascade admits the allegations in paragraph 20.  Further answering paragraph 20, Cascade is in the process of correcting its company procedure #3370 to appropriately address Investigation of Failures.

24.	Answering paragraph 21, the first sentence of paragraph 21 states a legal opinion or conclusion for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 21, which does not contain any factual or legal allegations that require an answer.

25.	Cascade neither admits nor denies 22, which does not contain any factual or legal allegations that require an answer.

### 2.	Second Cause of Action (Corrosion Control - Monitoring)

### Whatcom District [9.1]

26.	Answering paragraph 23, Cascade admits that it failed to inspect Section I009 for atmospheric corrosion within 39 months of its last inspection.  Further answering paragraph 23, Section I009 was inadvertently omitted from work schedules upon a transition from walking collection for meter data to vehicle mobile collection.  Upon discovery of the error during Staff's inspection on September 23, 2009, Cascade immediately began surveying the omitted meters, completing the survey before December 25, 2009.  In addition, Cascade is in the process of implementing a new maintenance management system, which will enhance timely meter inspections.

27.	Answering paragraph 24, the first sentence of paragraph 24 states a legal opinion or conclusion for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 24, which does not contain any factual or legal allegations that require an answer.

### Kitsap District [17.2]

28.	Answering paragraph 25, Cascade admits the allegations of the first sentence of paragraph 25.  The second sentence of paragraph 25 describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.  Further answering paragraph 25, Cascade is in the process of implementing a new maintenance management system, which will enhance timely corrosion monitoring.

29.	Answering paragraph 26, the first sentence of paragraph 26 states a legal opinion or conclusion for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 26, which does not contain any factual or legal allegations that require an answer.

Tri-Cities District [25]

30.	Answering paragraph 27, Cascade denies the allegations of the first sentence of paragraph 29.  Cascade performed atmospheric corrosion monitoring in compliance with all code requirements.  Records of performance were available at the time of Staff's field inspection, but Staff either did not review the records that were provided, or in some cases, Staff did not ask for such records.  The second sentence of paragraph 27 describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.

31.	Answering paragraph 28, the first and third sentences of paragraph 28 state legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 28, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 28, Cascade denies the same.

32.	Cascade neither admits nor denies paragraph 29, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 29, Cascade denies the same.

### 3.	Third Cause of Action (Corrosion Control – Records)

#### Whatcom District [9.3]

33.	Answering paragraph 30, Cascade admits the allegation of the first sentence of paragraph 30.  The second sentence of paragraph 30 describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.  Further answering paragraph 30, Cascade took immediate action to correct any record-keeping errors.  Cascade has corrected each of the instances described in Attachment A to the Complaint by providing Staff with corrosion control records.

34.	Answering paragraph 31, the first sentence of paragraph 31 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 31, which does not contain any factual or legal allegations that require an answer.

#### Aberdeen District [4]

35.	Answering paragraph 32, Cascade denies the allegations in the first sentence of paragraph 32.  The second sentence of paragraph 32 describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.  Further answering paragraph 32, Cascade did record the conditions of exposed pipes at both the locations of the alleged violations, and it was recorded at the time of Staff's inspection on September 18, 2009.  While the conditions were not listed on Cascade's Substructure Damage/Leak Report form, the conditions were recorded on work orders attached to the respective incident records.  These records were provided to Staff on November 30, 2009, in Docket No. PG-080108.

36.	Answering paragraph 33, the first sentence of paragraph 33 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 33, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 33, Cascade denies the same.

#### Tri-Cities District [26]

37.	Answering paragraph 34, Cascade denies the first part of the first sentence of paragraph 34 that it failed to maintain atmospheric corrosion control records, but admits the second part of the first sentence of paragraph 34, that it failed to make such records available to Staff upon request in the field.  The second sentence of paragraph 34 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  The third sentence of paragraph 34 describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.  Further answering paragraph 34, Cascade does maintain atmospheric corrosion control records, and did so at the time of Staff's inspection.  However, Cascade acknowledges that its former record storage system made it difficult to quickly identify and provide the records to Staff upon their request in the field.  Cascade has improved its records storage system by standardizing the records storage system across districts.  Records are color-coded, and are consistently uniform across districts to more easily identify applicable records.

38.	Answering paragraph 35, the first sentence of paragraph 35 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 35, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 35, Cascade denies the same.

39.	Cascade neither admits nor denies paragraph 36, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 36, Cascade denies the same.

### 4.	Fourth Cause of Action (Gas Leak Surveys)

#### Whatcom District [4.2, 4.2]

40.	Answering paragraph 37, Cascade admits the allegation in the first sentence of paragraph 37.  Cascade denies the allegation in the second sentence of paragraph 37.  Further answering paragraph 37, with the help of Staff, Cascade has identified several instances where Cascade's mapping system is insufficient or inaccurate.  Cascade has made several corrections and improvements to its mapping system, and continues to implement additional improvements.  Cascade's mapping system involves manually highlighting physical maps following inspections.  It appears there were isolated instances where the maps were not appropriately updated, and it appears employees should have spent more time documenting surveys on the maps.  Cascade has identified, and is in the process of correcting, these anomalies.  Cascade believes that all the surveys were in fact performed, but the maps were insufficiently updated to reflect the surveys.  Cascade recognizes its obligation related to survey documentation and has implemented short term corrections through personnel training.  Cascade is also in the process of implementing long-term corrections by converting its mapping system to an electronic geographic information system ("GIS"), which will incorporate system-wide mapping system improvements.

41.	Answering paragraph 38, the first sentence of paragraph 38 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 38, which does not contain any factual or legal allegations that require an answer.

42.	Answering paragraph 39, Cascade admits the allegations stated in the first and second sentence of paragraph 39.  Cascade denies the allegations stated in the third sentence of paragraph 39.  Cascade has performed self-audits and has identified instances where certain services were not located accurately on maps.  Cascade believes these are isolated instances, and the vast majority of Cascade's maps are accurate with respect to locations of services.  Cascade has corrected its mapping error with respect to the locations referenced in paragraph 39.  Cascade believes that the surveys were in fact performed, but in these two instances, the maps did not reflect the surveys.

43.	Answering paragraph 40, the first sentence of paragraph 40 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 40, which does not contain any factual or legal allegations that require an answer.

Kitsap District [10]

44.	Answering paragraph 41, Cascade admits the allegations stated in paragraph 41.  Cascade corrected this mapping error.

45.	Answering paragraph 42, the first sentence of paragraph 42 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 42, which does not contain any factual or legal allegations that require an answer.

#### Aberdeen District [14, 15.2]

46.	Answering paragraph 43, Cascade denies the allegations stated in the first sentence of paragraph 43.  The second sentence of paragraph 43 describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegations that require an answer.  Further answering paragraph 43, Cascade's records regarding the locations of the alleged violations referenced in paragraph 43 are sufficient to meet the requirements of WAC 480-93-188(4)(e) and WAC 480-93-018(1).  Staff's findings regarding incident # 6740 do not specify which, if any, information is insufficient.  On November 30, 2009, Cascade provided Staff with records for both locations of the alleged violations.

47.	Answering paragraph 44, the first two sentences of paragraph 44 state legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the third sentence of paragraph 44, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 44, Cascade denies the same.

48.	Answering paragraph 45, Cascade denies the allegations stated in paragraph 45 with regard to the specific instances identified in Finding 15.2(a).  With regard to Finding 15.2(b), Cascade admits that its leak survey report identified the instrument identification name rather than the instrument identification number.  Cascade admits that, with regard to Finding 15.2(c), Cascade recorded follow-up leak surveys on work orders rather than on Cascade's typical leak report.  Cascade provided Staff with records of these leak surveys on November 30, 2009.

49.	Answering paragraph 46, the first sentence of paragraph 46 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 46, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 46, Cascade denies the same.

Tri-Cities District [11.13, 14, 15.2, 15.3, 18, 19]

50.	Answering paragraph 47, Cascade admits the allegations stated in paragraph 47.

51.	Answering paragraph 48, the first sentence of paragraph 48 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 48, which does not contain any factual or legal allegations that require an answer.

52.	Answering paragraph 49, Cascade admits that it conducted a self audit on May 29, 2008, at Road 84 (Section 1 business district) using leak survey maps 2-C and 3-C.  Cascade denies the remaining allegations stated in paragraph 49 and the implication that the allegations constitute a violation of WAC 480-93-188(6).

53.	Answering paragraph 50, the first sentence of paragraph 50 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 50, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 50, Cascade denies the same.

54.	Answering paragraph 51, Cascade admits that it did not provide calibration records for FI and CGI equipment used to survey leaks at three locations identified in Attachment A to the Complaint.  Staff requested, and was provided, leak records for the locations referenced in paragraph 51; however, calibration information is not required to be listed on the leak records.  Cascade maintains adequate calibration records that comply with all aspects of WAC 480-93-188(2).

55.	Answering paragraph 52, the first sentence of paragraph 52 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 52, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 52, Cascade denies the same.

56.	Answering paragraph 53, Cascade admits that it did not provide calibration records for FI and CGI equipment used to survey leaks at high occupancy buildings.  Cascade performed, and continues to perform, calibrations in accordance with WAC 480-93-188(2).  Cascade maintains adequate calibration records in full compliance with all aspects of WAC 480-93-188(2).

57.	Answering paragraph 54, the first sentence of paragraph 54 states legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 54, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 54, Cascade denies the same.

58.	Answering paragraph 55, Cascade admits the allegation in the first sentence of paragraph 55.  Cascade denies the allegations in the second sentence of paragraph 55.  WAC 480-93-188 requires Cascade to, among other things, maintain leak survey records that contain a description of the system and area surveyed (including maps and leak survey logs).  Cascade does, and did at the time of Staff's audit, maintain such leak survey records.  As stated in paragraph 39, above, Cascade has corrected several instances of inaccurate maps and is currently implementing further improvements to its mapping system.  However, WAC 480-93-188(5)(a) merely requires that Cascade's leak surveys provide a description of the system and area surveyed, which Cascade's leak surveys do.

59.	Answering paragraph 56, the first and second sentences of paragraph 56 state legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the third sentence of paragraph 56, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required, Cascade denies the same.

60.	Answering paragraph 57, Cascade admits the first two sentences of paragraph 57.  Cascade denies the allegations stated the third and fourth sentences in paragraph 57 and the implication that the allegations constitute a violation of WAC 480-93-188(6).  Cascade performed self audits in accordance with WAC 480-93-188(6) and made all audit records available to Staff.  Cascade neither admits nor denies the last sentence of paragraph 57, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

61.	Answering paragraph 58, the first sentence of paragraph 58 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 58, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 58, Cascade denies the same.

62.	Cascade neither admits nor denies paragraph 59, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 59, Cascade denies the same.

### 5.	Fifth Cause of Action (Gas Leak Evaluations)

#### Kitsap District [7.3, 8]

63.	Answering paragraph 60, Cascade admits the allegations in paragraph 60.  The allegations referenced in the Complaint that refer to Kitsap District are a result of Staff's audit performed during November 2009 in Docket No. PG-090003.  However, Staff did not provide Cascade with the results of the audit for almost one year, until September 2010.  By letter dated September 8, 2010, Staff stated that it was closing the docket and, "We have decided not to conduct additional enforcement action at this time due to the extreme time lag in issuing this findings letter."  Cascade has implemented improvements to its gas leak evaluations procedures, which either have corrected, or will correct, the majority of alleged violations in this cause of action.  Cascade has developed a new company procedure that specifically addresses the types of issues in this cause of action.  For example, Cascade's procedures address assigning leak grades for compliance with WAC 480-93-186(1); Cascade has established new procedures for follow-up leak inspections, and Cascade has developed new procedures for properly documenting the perimeter of a leak area.  These improvements are efforts to correct the errors described in this cause of action, and to improve overall gas safety and recordkeeping compliance.

64.	Answering paragraph 61, the first sentence of paragraph 61 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 61, which does not contain any factual or legal allegations that require an answer.

65.	Answering paragraph 62, Cascade admits the allegations in the first sentence of paragraph 62.  Cascade neither admits nor denies the second sentence of paragraph 62, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

66.	Answering paragraph 63, the first sentence of paragraph 63 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 63, which does not contain any factual or legal allegations that require an answer.

67.	Answering paragraph 64, Cascade admits the allegations in the first sentence of paragraph 64.  Cascade neither admits nor denies the second sentence of paragraph 64, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

68.	Answering paragraph 65, the first sentence of paragraph 65 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 65, which does not contain any factual or legal allegations that require an answer.

69.	Answering paragraph 66, Cascade admits the allegations in the first sentence of paragraph 66.  Cascade neither admits nor denies the second sentence of paragraph 66, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

70.	Answering paragraph 67, the first sentence of paragraph 67 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 67, which does not contain any factual or legal allegations that require an answer.

#### Tri-Cities District [12.1]

71.	Answering paragraph 68, Cascade admits the allegations in the first sentence of paragraph 68.  Cascade neither admits nor denies the second sentence of paragraph 68, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

72.	Answering paragraph 69, the first sentence of paragraph 69 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the second sentence of paragraph 69, which does not contain any factual or legal allegations that require an answer.

73.	Cascade neither admits nor denies paragraph 70, which does not contain any factual or legal allegations that require an answer.

### 6.	Sixth Cause of Action (Gas Leak Records)

#### Whatcom District [3]

74.	Answering paragraph 71, Cascade denies the allegation in the first sentence of paragraph 71.  Cascade neither admits nor denies the second sentence of paragraph 71, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.  Staff states in Attachment A to its Complaint that Cascade's gas leak records are inadequate in that they identify the magnitude of CGI reads as a percentage rather than as a percentage and with a unit label.  Staff claims that it is unclear whether the percentage read identifies LEL or gas to air.  However, Cascade staff is trained to use the "Search" mode using "%LEL" to detect leaks and then to report using the "% Gas in Air" setting.  Cascade understands Staff's concern that it is difficult for Staff to determine which magnitude is indicated unless Cascade specifies the scale that is used.  Accordingly, Cascade has committed to training employees to indicate which scale they are recording.

75.	Answering paragraph 72, the first two sentences of paragraph 72 state legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the remainder of paragraph 72, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 72, Cascade denies the same.

#### Kitsap District [9]

76.	Answering paragraph 73, Cascade admits the allegations of the first sentence of paragraph 73.  Cascade neither admits nor denies the second sentence of paragraph 73, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.  Cascade has corrected the specific instances and deficiencies alleged in paragraph 73.

77.	Answering paragraph 74, the first sentence of paragraph 74 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the remainder of paragraph 74, which does not contain any factual or legal allegations that require an answer.

#### Tri-Cities District [11.14, 13]

78.	Answering paragraph 75, Cascade admits the allegation in the first sentence of paragraph 75.  Cascade neither admits nor denies the second sentence of paragraph 75, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.  Cascade denies the implication that the allegations in paragraph 75 constitute a separate and additional violation of WAC 480-93-187(13), beyond those alleged in the fifth cause of action.

79.	Answering paragraph 76, the first sentence of paragraph 76 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the remainder of paragraph 76, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 76, Cascade denies the same.

80.	Answering paragraph 77, Cascade admits the allegation in the first sentence of paragraph 77.  Cascade neither admits nor denies the second sentence of paragraph 77, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

81.	Answering paragraph 78, the first sentence of paragraph 78 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the remainder of paragraph 78, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 78, Cascade denies the same.

82.	Cascade neither admits nor denies paragraph 79, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 79, Cascade denies the same.

### 7.	Seventh Cause of Action (Plans and Procedures)

#### Aberdeen District [8]

83.	Answering paragraph 80, Cascade denies the allegations stated in paragraph 80.  Regarding customer notification, Cascade notifies customers within 90 days of their responsibility for those service lines not maintained by the operator.  Such notification is performed for all accounts via a customer letter mailed to each service address.  Cascade provided Staff with an example of such letter.  Notification is further monitored by personnel who log the number of letters sent each day.  Cascade provided Staff with a copy of its 2009 log.  Such notification is in full compliance with 49 C.F.R. § 192.16.

84.	Further answering paragraph 80, with respect to updating the Manual, Cascade has recently performed a company-wide audit of the contents of all procedures manuals.  All manuals were updated, if needed, and all procedure manuals are currently up to date.

85.	Further answering paragraph 80, with respect to documentation of underground leaks, Cascade is in the process of implementing changes to its document management system, mapping systems, and company procedures to enhance and improve documentation of underground leaks.

86.	Further answering paragraph 80, with respect to identifying the person performing substructure damage/leak reports, Cascade has committed to re-training personnel to completely fill out all reports.

87.	Further answering paragraph 80, with respect to painting and coating a regulator station, Cascade has corrected the alleged violation referenced in paragraph 80, and Cascade's procedures currently call for appropriate painting.

88.	Further answering paragraph 80, with respect to addressing atmospheric corrosion, Cascade has corrected the alleged violation referenced in paragraph 80, and Cascade's procedures currently require appropriate corrosion and pitting remediation.

89.	Further answering paragraph 80, with respect to pipeline marker procedures, pipeline marker maps are not specifically required by code.  Further, while Cascade's company procedure may be improved to clarify that personnel reviewed pipeline markers during their survey, Cascade does not believe it has violated any rule or procedure regarding pipeline markers.  Nonetheless, Cascade has updated its company procedure and is in the process of updating its maps with pipeline marker location information in an effort to further clarify its pipeline marker locations.

90.	Further answering paragraph 80, with respect to regulator vent installations, Cascade is in the process of correcting regulator vent orientations such that they comply with Cascade's company procedures.

91.	Further answering paragraph 80, with respect to meter set installation, the alleged violation referenced in paragraph 80 was an apparent anomaly, and Cascade has corrected the error.

92.	Further answering paragraph 80, with respect to pipeline markers noted on patrol logs, while the violations alleged in paragraph 80 refer to Cascade's pipeline patrols, the referenced examples list leak survey records.  While Cascade believes there is no violation of rule or procedure, Cascade intends to document the location of pipeline markers on leak survey maps so that pipeline marker surveys may be performed in conjunction with leak surveys.

93.	Further answering paragraph 80, with respect to public awareness procedures, Cascade will update company procedure 835 to reflect Cascade's improved Public Awareness Program.

94.	Answering paragraph 81, paragraph 81 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  To the extent an answer is required to paragraph 81, Cascade denies the same.

95.	Cascade neither admits nor denies paragraph 82, which does not contain any factual or legal allegations that require an answer.

#### Tri-Cities District [2.3, 2.4, 11.1, 11.2, 11.4, 11.7, 11.15, 11.19, 11.20, 11.22, 11.23]

96.	Answering paragraph 83, Cascade denies the allegation stated in the first sentence of paragraph 83.  Sniff test instrument calibration records show that all instruments used by employees during the specified period were calibrated as required by WAC 480-93-015(4).  Staff reviewed such calibration records during their inspection.  Cascade neither admits nor denies the second sentence of paragraph 83, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

97.	Answering paragraph 84, the first two sentences of paragraph 84 state legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 84, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 84, Cascade denies the same.

98.	Answering paragraph 85, Cascade admits that certain incongruities existed from the 2007 Leak Survey for Section 5.  Cascade investigated the anomalies and made corrections, which were described in a letter response to Staff on October 2, 2009.

99.	Answering paragraph 86, the first two sentences of paragraph 86 state legal opinions or conclusions for which an answer is inappropriate and are therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 86, which does not contain any factual or legal allegations that require an answer.

100.	Answering paragraph 87, Cascade admits the allegations stated in the first sentence of paragraph 87.  Cascade denies the allegations stated in the second sentence of paragraph 87.  Cascade's CP 760.09 includes requirements for visual inspection of welds.  This update was completed prior to September 1, 2007.  The procedure was updated again on May 2, 2008.

101.	Answering paragraph 88, the first sentence of paragraph 88 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 88, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 88, Cascade denies the same.

102.	Answering paragraph 89, Cascade denies the allegations in the first sentence of paragraph 89.  Cascade neither admits nor denies the second sentence of paragraph 89, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.  Cascade sent Staff copies of its manual in a timely fashion.  Cascade sent additional copies of these procedures on August 11, 2009.

103.	Answering paragraph 90, the first sentence of paragraph 90 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 90, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 90, Cascade denies the same.

104.	Answering paragraph 91, Cascade denies the allegations stated in paragraph 91.  Cascade updated Procedure No. 760 prior to September 1, 2007.  The procedure was updated again on May 2, 2008.

105.	Answering paragraph 92, the first sentence of paragraph 92 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 92, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 92, Cascade denies the same.

106.	Answering paragraph 93, Cascade admits the allegations stated in the first two sentences on paragraph 93.  Cascade neither admits nor denies the second sentence of paragraph 93, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

107.	Further answering paragraph 93, item (b), as referenced in Attachment A to the Complaint, was not completed until April 13, 2009.  It was not required to be posted until October 13, 2009.  It is currently identified as completed.  In general, the remainder of the records (asbuilts) of the facilities referenced in paragraph 93 were available within six (6) months, as required by WAC 480-93-018(5).  However, they may not have been posted to the operating maps within that time.  As described above, Cascade is in the process of converting its maps to an electronic/GIS format, which will greatly improve Cascade's mapping accuracy.

108.	Answering paragraph 94, the first sentence of paragraph 94 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 94, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 94 Cascade denies the same.

109.	Answering paragraph 95, Cascade admits the allegations stated in the first and second sentences of paragraph 95.  Cascade provided a detailed response to Staff regarding these allegations on October 2, 2009, which Cascade refers hereto.  Cascade neither admits nor denies the second sentence of paragraph 95, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

110.	Answering paragraph 96, the first sentence of paragraph 96 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 96, which does not contain any factual or legal allegations that require an answer.

111.	Answering paragraph 97, Cascade admits the allegations stated in the first four sentences of paragraph 97.  Cascade has committed to personnel training to properly record accurate check dates for FI units.  Cascade neither admits nor denies the fifth sentence of paragraph 97, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.

112.	Answering paragraph 98, the first sentence of paragraph 98 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 98, which does not contain any factual or legal allegations that require an answer.

113.	Answering paragraph 99, Cascade admits the allegations stated in paragraph 99.  Cascade has corrected the error.

114.	Answering paragraph 100, the first and second sentences of paragraph 100 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 100, which does not contain any factual or legal allegations that require an answer.

115.	Answering paragraph 101, Cascade admits the allegations stated in paragraph 101.  Cascade has corrected these errors.  Further, Cascade is in the process of implementing corrections and improvements to its company procedures and mapping systems in order to enhance overall recordkeeping compliance.

116.	Answering paragraph 102, the first sentence of paragraph 102 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 102, which does not contain any factual or legal allegations that require an answer.

117.	Answering paragraph 103, Cascade admits the allegation stated in the first sentence of paragraph 103.  Cascade denies the allegation stated in the second sentence of paragraph 103.  Employees did not record the action taken for these items; however, Cascade revisited each location, identified any problem, and took corrective action.  Cascade informed Staff of these actions on October 2, 2009.

118.	Answering paragraph 104, the first sentence of paragraph 104 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 104, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 104, Cascade denies the same.

119.	Cascade neither admits nor denies paragraph 105, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 105, Cascade denies the same.

### 8.	Eighth Cause of Action (Public Awareness)

120.	Answering paragraph 106, Cascade denies the allegations stated in paragraph 106.  Cascade currently maintains information regarding Cascade's public awareness program for the Kitsap District, and it had such information at the time of Staff's inspection.  As stated in paragraph 63, above, the allegations referenced in the Complaint that refer to Kitsap District are a result of Staff's audit performed during November 2009 in Docket No. PG-090003.  However, Staff did not provide Cascade with the results of the audit until almost one year after the audit, in September 2010.  By letter dated September 8, 2010, Staff stated that it was closing the docket and, "We have decided not to conduct additional enforcement action at this time due to the extreme time lag in issuing this findings letter."  Accordingly, while Cascade was able and willing to provide such information, Cascade was instructed that such information was no longer required for the audit.

121.	Answering paragraph 107, the first sentence of paragraph 107 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 107, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 107, Cascade denies the same.

#### Wenatchee/Moses Lake District [4]

122.	Answering paragraph 108, Cascade admits the allegations stated in the first sentence of paragraph 108.  Cascade denies the allegations stated in the second sentence of paragraph 108.  Cascade completed the evaluation of the effectiveness of its public awareness program prior to June 20, 2010.  At the time of Staff's inspection on July 6-8, 2010, Cascade advised Staff that Cascade's surveys of effectiveness had been completed.  Additionally, Cascade provided Staff with documentation of Cascade's evaluations of its public awareness program, including electronic links to completed public surveys for excavators, public officials and emergency responders.  Further, Cascade offered to send Staff a hard copy of such documentation, but Staff declined the offer.

123.	Answering paragraph 109, the first sentence of paragraph 109 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade admits the second sentence of paragraph 109.  Cascade denies the allegation stated in the third sentence of paragraph 109.  Cascade neither admits nor denies the last sentence of paragraph 109, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 109, Cascade denies the same.

124.	Cascade neither admits nor denies paragraph 110, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 110, Cascade denies the same.

### 9.	Ninth Cause of Action (Records)

#### Kitsap District [2.2, 2.3, 2.4]

125.	Answering paragraph 111, Cascade admits the allegations stated in paragraph 111.  Cascade has implemented numerous changes such as a standardized filing system, an on-line data entry and tracking system, and additional staff for quality control monitoring.  These changes have improved, and will continue to improve, recordkeeping procedures system-wide.

126.	Answering paragraph 112, the first sentence of paragraph 112 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 112, which does not contain any factual or legal allegations that require an answer.

127.	Answering paragraph 113, Cascade admits the allegations stated in paragraph 113. Cascade has implemented changes, which have, and will continue to improve recordkeeping procedures system-wide.  As stated earlier in this Answer, Cascade is currently in the process of implementing a transition from paper maps to an electronic/GIS mapping system.  Such transition is a significant and time-consuming process, but will provide vast improvements to Cascade's recordkeeping and mapping capabilities and regulatory compliance.

128.	Answering paragraph 114, the first sentence of paragraph 114 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 114, which does not contain any factual or legal allegations that require an answer.

#### Aberdeen District [2]

129.	Answering paragraph 115, Cascade denies the allegations stated in the first sentence of paragraph 115.  Cascade neither admits nor denies the second sentence of paragraph 115, which describes an aspect of the structural format of the Complaint and does not contain any factual or legal allegation that requires an answer.  Records of construction activities are maintained in the local operations office.  Such records are available to operating personnel within six (6) months of the construction activity, pursuant to WAC 480-93-018.  While Cascade believes that the allegations in paragraph 115 and Attachment A appear to expand the obligations required by regulation, Cascade will provide updated maps to field personnel.

130.	Answering paragraph 116, the first sentence of paragraph 116 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 116, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 116, Cascade denies the same.

#### Tri-Cities District [2.1, 3.1, 3.2, 29.1]

131.	Answering paragraph 117, Cascade admits the allegations stated in paragraph 117.  As stated above, Cascade is in the process of transitioning from physical maps to an electronic/GIS mapping system.  This transition, while a lengthy process, will improve Cascade's mapping systems and recordkeeping procedures.

132.	Answering paragraph 118, the first sentence of paragraph 118 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 118, which does not contain any factual or legal allegations that require an answer.

133.	Answering paragraph 119, Cascade denies the allegations stated in paragraph 119.  Survey records showing pipeline marker placement were used by employees before June 5, 2007.  These records were difficult to find during the inspection, and Cascade was unable to provide them to Staff in the field.  However, these records have been located, and are available for Staff review.  As stated above, Cascade is in the process of transitioning from physical maps to an electronic/GIS mapping system.  This transition, while a lengthy process, will improve Cascade's mapping systems and recordkeeping procedures.

134.	Answering paragraph 120, the first sentence of paragraph 120 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 120, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 120, Cascade denies the same.

135.	Cascade neither admits nor denies paragraph 121, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 121, Cascade denies the same.

### 10.	Tenth Cause of Action (Recordkeeping)

#### Aberdeen District [25]

136.	Answering paragraph 122, Cascade denies the allegations stated in paragraph 122.  While Cascade was unable to provide Staff the documents upon request in the field, Cascade nonetheless maintains records that include such identifying information.  Such qualification records are available upon request.

137.	Answering paragraph 123, the first sentence of paragraph 123 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  Cascade neither admits nor denies the last sentence of paragraph 123, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 123, Cascade denies the same.

138.	Cascade neither admits nor denies paragraph 124, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 138, Cascade denies the same.

### 11.	Eleventh Cause of Action (Periodic Review for Effectiveness)

#### Tri-Cities District [30]

139.	Answering paragraph 125, Cascade denies the allegations stated in paragraph 125 and the implication that the allegations constitute a violation of 49 C.F.R. § 192.605(b)(8).  Rather than requiring the review of work done by gas safety personnel, 49 C.F.R. § 192.605(b)(8) requires that gas utilities maintain a procedures manual that must include, if applicable, procedures for reviewing the work done by its gas safety personnel.  The regulation requires operators to perform evaluations of written procedures for their effective and adequate performance, and modify the procedure when deficiencies are found.

140.	Answering paragraph 126, paragraph 126 states legal opinions or conclusions for which an answer is inappropriate and is therefore denied.  To the extent an answer is required to paragraph 126, Cascade denies the same.

141.	Cascade neither admits nor denies paragraph 127, which does not contain any factual or legal allegations that require an answer.  To the extent an answer is required to paragraph 58, Cascade denies the same.

142.	Paragraphs 128-130 of the Complaint state legal opinions or conclusions or describe procedural matters for the conduct of the hearing into this matter that do not require an answer.  Thus, Cascade neither admits nor denies paragraphs 128-130 of the Complaint.  Generally, Cascade denies that the Commission should impose penalties on Cascade.  If the Commission determines that penalties should be imposed, the amount of the penalty should reflect Cascade's cooperation and assistance with Staff's inspections and good faith response in correcting issues and attempting to achieve compliance after being made aware of potential compliance issues more than a year ago.  Further, Cascade has initiated numerous self-audits, and has initiated both short-term and long-term system-wide improvements.

## DEFENSES AND AFFIRMATIVE DEFENSES

143.	Cascade is responsible for the construction and maintenance of an extensive natural gas pipeline system and has numerous programs and procedures in place to seek to ensure that its system is safe.  Cascade believes its system is safe.  After learning of the alleged violations from Commission Staff, Cascade acted in good faith and immediately cooperated with Commission Staff's investigations and conducted its own investigations and inspections.  As a result, Cascade has put in place, and continues to put in place, additional measures to promote compliance

144.	Some of the violations alleged are barred by the statute of limitations.

145.	Certain alleged violations are inappropriately classified as a "continuing violation."

146.	The doctrines of waiver, estoppel and/or laches preclude the imposition of penalties for certain of the alleged violations.

DATED:  April 11, 2011.

PERKINS COIE LLP



By

Sheree Strom Carson, WSBA # 25349
Donna Barnett, WSBA # 36794
Attorneys for Respondent Cascade Natural Gas Corporation

STATE OF WASHINGTON	)
	) ss.
COUNTY OF KING	)

Timothy M. Clark, being first duly sworn, deposes and says that he is the Vice President of Operations for Cascade Natural Gas Corporation; that he has read the foregoing Answer of Cascade Natural Gas Corporation and knows the contents thereof; that the facts set forth therein are true based on his own knowledge, except as to matters which are therein stated on information or belief, and as to those matters, he believes them to be true.

Timothy M. Clark

SUBSCRIBED and SWORN to before me this ____ day of _________, 2011, by __________________________.

Print Name:	
Notary Public in and for the State of Idaho, residing at 	
My commission expires: