2010

Qualifying Storm Events

November 22, 2010

# Table of Contents

Table of Contents	2

Event Description	3

Date of event	3

Event Type	3

Service Areas Affected	3

Number of Customers Affected	3

Summary of System Impacts	3

Mobilization Summary	3

Major Event Day – Qualification	5

Qualified Events - 2010	5

Current Event – Calculation Detail	5

Cumulative list of events that have qualified	5

Event Restoration – Cost Summary	6

Restoration Cost Detail by Qualifying Event	6

YTD Storm Restoration Cost Detail – Through November 22, 2010	6

Detail Documents	7

Restoration Cost Detail – Current Event	8

IEEE-1366 - Detailed List of Distribution Circuits with Outages	9

Terms, Codes and Definitions Used on Detail Reports	14

Media Coverage	15

# Event Description

### Date of event

November 22, 2010

### Event Type

Wind and snow storm.

### Service Areas Affected

This weather event significantly impacted Kitsap County, Jefferson County and Vashon Island. Also affected were Whatcom, Skagit, King (south), Pierce and Thurston Counties.

### Number of Customers Affected

Approximately 137,900 customers were without power over the course of this outage event.

### Summary of System Impacts

| Total Number of Outages | 830 |
| --- | --- |
| Distribution Circuits Totally Out | 38 |
| Distribution Circuits Partially Out | 792 |

| Transmission Circuits Affected | 20 |
| --- | --- |
| Substations Totally Off-line | 10 |

### Mobilization Summary

#### Operating Bases

| Base | Date Opened | Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
| Whatcom | 11/22/2010 | 17:45 | 11/23/2010 | 21:30 |
| Skagit | 11/22/2010 | 17:45 | 11/23/2010 | 21:30 |
| South King | 11/22/2010 | 20:45 | 11/23/2010 | 18:00 |
| Pierce | 11/23/2010 | 00:30 | 11/23/2010 | 20:00 |
| Thurston | 11/22/2010 | 00:30 | 11/23/2010 | 20:00 |
| Kitsap | 11/22/2010 | 17:30 | 11/27/2010 | 07:30 |
| Jefferson | 11/22/2010 | 17:30 | 11/27/2010 | 07:30 |
| Vashon | 11/22/2010 | 17:30 | 11/27/2010 | 07:30 |

#### Emergency Operations Center

| EOC | Date Opened | #### Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
|  | 11/22/2010 | 20:00 | 11/24/2010 | 21:00 |

# Major Event Day – Qualification

- IEEE 1366 Method

IEEE 1366 was established to present a set of terms and definitions which can be used to foster uniformity in the development of distribution service reliability indices, to identify factors which affect the indices, and to aid in consistent reporting practices among utilities.  Also, it provides guidance for new personnel in the reliability area, and tools for internal as well as external comparisons.  The Major Event Day definition was created as part of IEEE 1366 to allow for consistent calculation of reliability metrics between utilities, and enable more valid comparisons with other utility reliability metrics.

IEEE Major Event Day Calculation (2.5 BETA METHOD) - A threshold on daily SAIDI is computed once a year, following year end. - Assemble the 5 most recent years of historical values of SAIDI/day. - Discard any days in the data set that has a SAIDI/day of zero. - Find the natural logarithm of each value in the data set. - Compute the average Alpha and the standard deviation (Beta) of the natural logarithms computed in step 3. - Compute the threshold Tmed where Tmed = exp (Alpha + 2.5 * Beta) - Any day in the next year with SAIDI > Tmed is a major event day.

Puget Sound Energy’s Major Event Threshold for 2010: 7.21 Minutes

# Qualified Events - 2010

### Current Event – Calculation Detail

| Event Date | Total Customer Minutes | Average Customer Count | Daily SAIDI – Customer Minutes /Customer Count |
| --- | --- | --- | --- |
| 11/22/2010 | 134,662,542 | 1,084,774 | 124.14 |

### Cumulative list of events that have qualified

| Date(s) | T-med Score | O&M – Deferrable Accumulation |
| --- | --- | --- |
| 01/17/2010 | 29.25 | $862,417 |
| 03/16/2010 | 10.61 | $481,430 |
| 05/03/2010 | 13.55 | $721,305 |
| 11/15/2010 | 101.18 | $5,016,951 (r) |
| 11/22/2010 | 124.14 | $917,897 |

(r) – Revised

# Event Restoration – Cost Summary

### Restoration Cost Detail by Qualifying Event

| Date | Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M – Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01/17/2010 | $0 | $50,785 | $0 | $79,959 | $862,417 | $942,376 | $993,161 |
| 03/16/2010 | $0 | $110,581 | $0 | $43,339 | $481,430 | $524,769 | $635,349 |
| 05/03/2010 | $0 | $154,017 | $0 | $44,568 | $721,305 | $765,872 | $919,889 |
| 11/15/2010 | $0 | $578,471(r) | $0 | $261,686 (r) | $5,016,951(r) | $5,278,638 (r) | $5,857,108(r) |
| 11/22/2010 | $7,837,044 | $932,518 | $0 | $342,190 | $917,897 | $1,260,087 | $10,029,649 |

(r) – Revised

### YTD Storm Restoration Cost Detail – Through November 22, 2010

| Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| $7,837,044 | $1,826,371 | $0 | $771,741 | $8,000,000 | $8,771,741 | $18,435,156 |

# Detail Documents

- Restoration Cost Detail – Current Event

- Detailed List of Distribution Circuits with Outages

- Terms, Codes & Definitions Used on Detail Reports

- Newsprint Media Coverage

### Restoration Cost Detail – Current Event

|  |  |  | Puget Sound Energy |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | November 22, 2010 Storm Damage Repair Costs |  |  |  |  |  |  |
|  |  | Qualifying Events Deferred Account | Capital | C&D Recoverable from Direct Billings (Costs Not Yet Billed) | O&M - Not Deferrable | O&M - Deferrable Accumulation | Total O&M | Total |  |
|  | Labor |  |  |  |  |  |  |  |  |
|  | ST |  | $ 1,828 |  | $ 129,324 | $ 26,683 | $ 156,008 | $ 157,835 |  |
|  | OT |  | $ 531 |  |  | $ 664,541 | $ 664,541 | $ 665,071 |  |
|  | Total Labor | $ - | $ 2,358 | $ - | $ 129,324 | $ 691,224 | $ 820,548 | $ 822,907 |  |
|  | Labor OH |  | $ 1,599 |  | $ 106,868 | $ 298,962 | $ 405,829 | $ 407,428 |  |
|  | Materials |  | $ 225,209 |  | $ 43,222 | $ 389,977 | $ 433,199 | $ 658,409 |  |
|  | Contractors |  | $ 551,550 |  | $ 12,683 | $ 7,212,627 | $ 7,225,311 | $ 7,776,861 |  |
|  | Other Direct Charges |  |  |  |  | $ 113,901 | $ 113,901 | $ 113,901 |  |
|  | Fleet |  | $ 371 |  |  | $ 48,260 | $ 48,260 | $ 48,631 |  |
|  | Other Assessments |  | $ 151,430 |  | $ 50,093 | $ (11) | $ 50,082 | $ 201,512 |  |
|  | Deferred Expenses | $ 7,837,044 |  |  |  | $ (7,837,044) | $ (7,837,044) | $ - |  |
|  |  | $ 7,837,044 | $ 932,518 | $ - | $ 342,190 | $ 917,897 | $ 1,260,087 | $ 10,029,649 |  |

### IEEE-1366 - Detailed List of Distribution Circuits with Outages

| NUMBER | DATE | TIME | CKT | MPG | CAZ | EQT | CUST OUT | CUST MIN |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 10984165 | 11/22/2010 | 12:35:00 AM | MAN-16 | ECD | TV | OCO | 25 | 6275 |
| 10984923 | 11/22/2010 | 1:00:00 AM | SKE-23 | ECE | TV | OFU | 20 | 880 |
| E254015293 | 11/22/2010 | 1:04:00 AM | HYA-15 | EBF | SO | OSW | 71 | 17111 |
| E871709380 | 11/22/2010 | 1:04:00 AM | HYA-13 | EBF | SO | OSW | 780 | 187980 |
| 10983646 | 11/22/2010 | 1:25:00 AM | SPI-16 | EBE | EF | USV | 1 | 108 |
| 10984166 | 11/22/2010 | 2:00:00 AM | WIN-13 | ECE | EF | OFU | 3 | 417 |
| E015588321 | 11/22/2010 | 6:24:33 AM | MIR-17 | EBF | EF | UOT | 2 | 1043 |
| 10983643 | 11/22/2010 | 6:28:00 AM | NBE-16 | EBE | AO | OPO | 1 | 373 |
| E365180803 | 11/22/2010 | 7:14:31 AM | HAS-12 | ECF | EF | UPC | 16 | 13992 |
| E028842563 | 11/22/2010 | 7:33:23 AM | SMR-23 | ECA | EF | OFU | 32 | 1716 |
| E566946887 | 11/22/2010 | 8:01:15 AM | AIR-26 | ECC | EF | OCO | 32 | 10072 |
| E877732274 | 11/22/2010 | 8:30:00 AM | CWD-23 | EBD | SO | OTR | 13 | 1612 |
| E280976428 | 11/22/2010 | 8:31:49 AM | KCR-17 | EBJ | EF | OSV | 1 | 163 |
| E003090673 | 11/22/2010 | 8:59:27 AM | IRO-13 | ECF | CP | OAR | 21 | 3918 |
| E748138820 | 11/22/2010 | 9:00:00 AM | SMR-26 | ECA | SO | UFJ | 2 | 540 |
| E333657679 | 11/22/2010 | 9:18:10 AM | TIL-23 | ECA | CP | OCO | 25 | 2211 |
| E774806859 | 11/22/2010 | 9:50:09 AM | DUV-15 | EBD | TV | OSV | 1 | 150 |
| E747701898 | 11/22/2010 | 9:55:56 AM | RAI-14 | ECC | TV | OCO | 16 | 5934 |
| E525912613 | 11/22/2010 | 10:00:10 AM | BLU-17 | ECC | TV | OCO | 48 | 14094 |
| E412057134 | 11/22/2010 | 10:00:36 AM | VIC-16 | EBJ | EF | USV | 1 | 89 |
| E719813473 | 11/22/2010 | 10:16:10 AM | KIN-23 | ECE | EF | USV | 1 | 262 |
| E389860622 | 11/22/2010 | 10:54:19 AM | GRI-16 | ECC | EF | OFC | 207 | 83562 |
| E483276970 | 11/22/2010 | 11:00:00 AM | NUG-26 | EAA | SO | UPC | 4 | 740 |
| E431081977 | 11/22/2010 | 11:10:09 AM | SIL-13 | ECF | TV | OSV | 2 | 734 |
| E301541322 | 11/22/2010 | 11:12:00 AM | SIL-13 | ECD | TV | OCO | 29 | 10585 |
| 10985041 | 11/22/2010 | 11:52:00 AM | YEL-23 | ECC | EF | USV | 1 | 248 |
| E681648716 | 11/22/2010 | 12:00:09 PM | ALG-12 | EAC | CP | OPO | 400 | 235110 |
| E737804234 | 11/22/2010 | 12:10:55 PM | BLU-16 | ECC | TV | OCO | 156 | 5785 |
| E314468536 | 11/22/2010 | 12:14:43 PM | HAS-15 | ECF | EF | OTF | 6 | 1322 |
| E617492997 | 11/22/2010 | 12:16:08 PM | KAP-13 | ECA | TV | OFU | 2 | 309 |
| E236048549 | 11/22/2010 | 12:29:09 PM | LOL-23 | ECD | AO | USV | 1 | 364 |
| E946691020 | 11/22/2010 | 12:52:57 PM | LTA-17 | ECA | TV | OCO | 18 | 2398 |
| E119522300 | 11/22/2010 | 1:06:48 PM | BON-15 | ECA | TV | OFU | 15 | 1835 |
| E118674919 | 11/22/2010 | 1:16:46 PM | SOM-15 | EBE | EF | UTR | 48 | 17132 |
| E627033026 | 11/22/2010 | 1:33:34 PM | WLS-12 | EAC | EF | OFU | 1 | 84 |
| E404238140 | 11/22/2010 | 2:08:51 PM | KIN-24 | ECE | TV | OSV | 1 | 133 |
| E988162307 | 11/22/2010 | 2:21:31 PM | JUA-25 | EBD | EF | UPC | 25 | 12512 |
| 10983776 | 11/22/2010 | 2:22:02 PM | LOC-23 | EBE | EF | USV | 1 | 196 |
| E187155786 | 11/22/2010 | 2:34:50 PM | SEM-15 | EAA | TV | OCO | 29 | 13838 |
| E758428939 | 11/22/2010 | 2:45:36 PM | LAB-25 | EAA | TV | OCO | 12 | 6773 |
| E387737059 | 11/22/2010 | 2:48:44 PM | BRE-21 | ECE | EF | OTF | 6 | 788 |
| E909978335 | 11/22/2010 | 2:54:48 PM | VWY-15 | EAA | TV | OCO | 3 | 1300 |
| E750094933 | 11/22/2010 | 3:03:55 PM | BAK-22 | EAA | TV | OCO | 1024 | 305580 |
| E198762002 | 11/22/2010 | 3:26:54 PM | KEN-12 | EAA | TV | OCO | 32 | 38955 |
| E557282994 | 11/22/2010 | 3:29:45 PM | WAB-13 | EBI | EF | UTF | 2 | 98 |
| E529799200 | 11/22/2010 | 3:58:32 PM | SLA-16 | EAA | TV | OCO | 150 | 99685 |
| E339284604 | 11/22/2010 | 4:02:15 PM | BRS-24 | EAC | TV | OCO | 46 | 60617 |
| E511741709 | 11/22/2010 | 4:10:40 PM | NNO-13 | EBJ | EF | OSV | 1 | 148 |
| E696669364 | 11/22/2010 | 4:11:04 PM | CHI-12 | ECD | TV | OCO | 850 | 2026343 |
| E537806563 | 11/22/2010 | 4:15:30 PM | COT-15 | EBD | TV | OCO | 33 | 11450 |
| E569662950 | 11/22/2010 | 4:16:27 PM | HAN-16 | EAA | TV | OFU | 30 | 8507 |
| E377585457 | 11/22/2010 | 4:27:49 PM | SKE-22 | ECE | TV | OPO | 1300 | 3565528 |
| E885554126 | 11/22/2010 | 4:32:01 PM | HAP-13 | EAA | TV | UNK | 76 | 37163 |
| E105022801 | 11/22/2010 | 4:37:40 PM | RPT-17 | ECD | TV | OCO | 685 | 1977823 |
| E336771235 | 11/22/2010 | 4:38:46 PM | WIN-13 | ECE | TV | OTR | 1185 | 3516087 |
| E667341557 | 11/22/2010 | 4:42:49 PM | SWD-12 | ECE | TV | OCO | 194 | 153490 |
| E156027865 | 11/22/2010 | 4:43:34 PM | QUI-26 | ECF | TV | OCO | 41 | 42453 |
| E855435801 | 11/22/2010 | 4:48:34 PM | SIL-15 | ECD | TV | OPO | 887 | 2737666 |
| E162237368 | 11/22/2010 | 4:50:00 PM | TLN-0271 | ECD | TV | OCO | 15710 | 2763562 |
| E624719325 | 11/22/2010 | 4:57:33 PM | HAN-15 | EAA | TV | OFU | 2 | 225 |
| E740822228 | 11/22/2010 | 4:57:40 PM | SIL-16 | ECD | TV | OCO | 236 | 759763 |
| E151545876 | 11/22/2010 | 4:57:51 PM | FNW-16 | ECD | TV | OPO | 1418 | 3254523 |
| E551193219 | 11/22/2010 | 5:01:45 PM | WIN-12 | ECE | TV | OAR | 786 | 3535625 |
| E127189486 | 11/22/2010 | 5:03:05 PM | LMC-25 | EBF | TV | OCO | 140 | 51228 |
| E439829584 | 11/22/2010 | 5:05:54 PM | BIG-15 | EAC | TV | OFU | 14 | 3837 |
| E555118355 | 11/22/2010 | 5:06:23 PM | PGA-12 | ECE | TV | OCO | 610 | 1557706 |
| E657254558 | 11/22/2010 | 5:07:37 PM | RPT-16 | ECD | TV | OCO | 325 | 725525 |
| E259182000 | 11/22/2010 | 5:08:41 PM | QUI-25 | ECF | TV | OCO | 55 | 15252 |
| E839885462 | 11/22/2010 | 5:10:57 PM | RPT-22 | ECD | TV | OCO | 107 | 480328 |
| E591728520 | 11/22/2010 | 5:12:57 PM | PMA-15 | ECE | TV | OFU | 390 | 205939 |
| E376361048 | 11/22/2010 | 5:14:06 PM | POU-16 | ECE | TV | OCO | 226 | 274793 |
| E484939752 | 11/22/2010 | 5:16:12 PM | SIL-15 | ECD | TV | OCO | 2 | 5700 |
| E576675231 | 11/22/2010 | 5:19:50 PM | CHI-15 | ECD | TV | OPO | 762 | 1605661 |
| E667791661 | 11/22/2010 | 5:20:00 PM | TLN-0065 | ECD | TF | OCO | 7897 | 11359970 |
| E176245437 | 11/22/2010 | 5:20:26 PM | RPT-15 | ECD | TV | OPO | 721 | 2090203 |
| E344016893 | 11/22/2010 | 5:21:00 PM | TLN-0271 | ECD | TV | OCO | 5275 | 2210225 |
| E058080980 | 11/22/2010 | 5:23:03 PM | RPT-26 | ECD | TV | OCO | 70 | 178987 |
| E000389194 | 11/22/2010 | 5:23:07 PM | PMA-16 | ECE | TV | OFU | 453 | 688960 |
| E207428761 | 11/22/2010 | 5:24:45 PM | ROE-17 | EAA | TV | OFU | 14 | 14494 |
| E187565318 | 11/22/2010 | 5:26:52 PM | LAB-23 | EAA | TV | OJU | 85 | 57556 |
| E255745548 | 11/22/2010 | 5:30:05 PM | VAS-12 | EBL | TV | OCO | 1661 | 5286825 |
| E285217128 | 11/22/2010 | 5:32:31 PM | MCW-15 | ECE | TV | OPO | 665 | 1671466 |
| E722306727 | 11/22/2010 | 5:34:04 PM | PMA-12 | ECE | TV | OCO | 1000 | 1509933 |
| E932999211 | 11/22/2010 | 5:34:12 PM | SHE-17 | ECE | TV | OCO | 342 | 664096 |
| E344266012 | 11/22/2010 | 5:34:39 PM | MVW-16 | EBJ | TV | OPO | 640 | 1222362 |
| 10984924 | 11/22/2010 | 5:35:00 PM | LOL-23 | ECD | TV | OCO | 1492 | 2458816 |
| E263842954 | 11/22/2010 | 5:35:00 PM | TLN-0075 | ECE | TV | OCO | 7819 | 12068642 |
| E471776613 | 11/22/2010 | 5:36:01 PM | TRA-22 | ECE | TV | OCO | 661 | 477231 |
| E798825240 | 11/22/2010 | 5:36:02 PM | SKE-23 | ECE | TV | OCO | 150 | 429595 |
| E889906328 | 11/22/2010 | 5:38:01 PM | MCW-15 | ECD | TV | OPO | 16 | 37792 |
| E345870660 | 11/22/2010 | 5:38:21 PM | TRA-23 | ECE | TV | OCO | 276 | 419975 |
| E946717226 | 11/22/2010 | 5:38:40 PM | MCW-17 | ECE | TV | OCO | 1115 | 974882 |
| E228195712 | 11/22/2010 | 5:39:25 PM | WIN-15 | ECE | TV | OTR | 447 | 1794966 |
| E317715675 | 11/22/2010 | 5:39:36 PM | KIN-22 | ECE | TV | OCO | 46 | 165212 |
| E432097282 | 11/22/2010 | 5:40:27 PM | NUG-25 | EAA | TV | OTF | 2 | 1819 |
| E962211010 | 11/22/2010 | 5:41:56 PM | SHE-17 | ECD | TV | OCO | 5 | 10890 |
| E024904836 | 11/22/2010 | 5:42:02 PM | WIN-16 | ECE | TV | OCO | 770 | 2231434 |
| E663439121 | 11/22/2010 | 5:42:30 PM | HAN-12 | EAA | TV | OTF | 2 | 255 |
| E222923165 | 11/22/2010 | 5:42:58 PM | BHL-15 | ECE | TV | OCO | 1223 | 638447 |
| E538418594 | 11/22/2010 | 5:43:05 PM | SHE-15 | ECE | TV | OCO | 194 | 315622 |
| E655030675 | 11/22/2010 | 5:48:26 PM | RPT-23 | ECD | TV | OCO | 365 | 1624822 |
| E780374162 | 11/22/2010 | 5:48:49 PM | CHR-22 | ECE | TV | OCO | 114 | 234747 |
| E173233281 | 11/22/2010 | 5:51:21 PM | KIN-24 | ECE | TV | OCO | 55 | 244676 |
| E831422863 | 11/22/2010 | 5:51:31 PM | HEM-16 | ECA | TV | OCO | 10 | 821 |
| E011629232 | 11/22/2010 | 5:51:54 PM | SUM-21 | EAC | TV | OFU | 5 | 1386 |
| E644389197 | 11/22/2010 | 5:53:43 PM | VAS-13 | EBL | TV | OTR | 41 | 177829 |
| E216366375 | 11/22/2010 | 5:54:52 PM | CHI-13 | ECD | TV | OTR | 827 | 1768236 |
| E021657570 | 11/22/2010 | 5:56:54 PM | GRI-16 | ECC | TV | OCO | 10 | 1136 |
| E547485456 | 11/22/2010 | 5:57:43 PM | FRU-25 | ECA | TV | OFC | 10 | 2165 |
| E043648693 | 11/22/2010 | 5:57:47 PM | HAN-13 | EAA | EF | OTF | 2 | 952 |
| E162847111 | 11/22/2010 | 6:00:20 PM | BHL-16 | ECE | TV | OCO | 41 | 20691 |
| E634920134 | 11/22/2010 | 6:01:31 PM | PMA-13 | ECE | TV | OPO | 422 | 625608 |
| E774724096 | 11/22/2010 | 6:02:41 PM | SCH-16 | EAA | TV | CDH | 2 | 1415 |
| E567909139 | 11/22/2010 | 6:03:08 PM | MIL-23 | ECE | TV | OCO | 875 | 1112883 |
| E650023985 | 11/22/2010 | 6:03:14 PM | IRO-13 | ECF | TV | OFU | 53 | 13927 |
| E670838869 | 11/22/2010 | 6:12:15 PM | RAI-11 | ECC | TV | OCO | 60 | 30045 |
| E238036950 | 11/22/2010 | 6:14:25 PM | TRA-23 | ECE | TV | OCO | 614 | 1005476 |
| E628837721 | 11/22/2010 | 6:15:25 PM | EDG-16 | ECA | TV | OPO | 6 | 9700 |
| E027370531 | 11/22/2010 | 6:18:25 PM | SHE-25 | ECE | EO | VCB | 2287 | 1494563 |
| E998039677 | 11/22/2010 | 6:18:33 PM | LYN-26 | EAA | TV | OFU | 3 | 2464 |
| E549177380 | 11/22/2010 | 6:18:36 PM | MIL-17 | ECE | TV | OCO | 1734 | 2246086 |
| E617053149 | 11/22/2010 | 6:18:45 PM | SHE-26 | ECE | TV | OCO | 81 | 134723 |
| E280084775 | 11/22/2010 | 6:22:59 PM | FRA-13 | ECD | TV | OCR | 1334 | 2127555 |
| E871519875 | 11/22/2010 | 6:25:42 PM | SOO-25 | EBI | EF | OFU | 66 | 10184 |
| E410447693 | 11/22/2010 | 6:28:30 PM | RDO-16 | EBJ | TV | OFU | 35 | 42403 |
| E813569434 | 11/22/2010 | 6:29:46 PM | DUT-16 | ECA | TV | OTF | 1 | 360 |
| E427968139 | 11/22/2010 | 6:30:00 PM | TLN-0089 | ECE | TF | OCO | 7265 | 5061050 |
| E617877001 | 11/22/2010 | 6:30:26 PM | LON-23 | ECC | TV | OCO | 2 | 1869 |
| E541665292 | 11/22/2010 | 6:30:40 PM | CUS-15 | EAA | TF | OCO | 420 | 106820 |
| E615263274 | 11/22/2010 | 6:31:21 PM | BAK-26 | EAA | TF | OCO | 241 | 21124 |
| E466049909 | 11/22/2010 | 6:34:19 PM | LAU-12 | EAA | TV | OTF | 1 | 670 |
| E736787200 | 11/22/2010 | 6:34:48 PM | YEL-27 | ECC | TV | OCO | 5 | 6096 |
| E580462866 | 11/22/2010 | 6:41:00 PM | TLN-0192 | ECE | TF | OCO | 3722 | 6814431 |
| E430761017 | 11/22/2010 | 6:41:51 PM | WIN-16 | ECF | TV | OCO | 40 | 74086 |
| E860559761 | 11/22/2010 | 6:42:11 PM | BRE-21 | ECE | TV | OCO | 55 | 59555 |
| E575980103 | 11/22/2010 | 6:43:24 PM | GRA-25 | EBJ | TV | OCO | 74 | 42076 |
| E246828258 | 11/22/2010 | 6:43:25 PM | SKE-26 | ECE | TV | OCO | 331 | 1054829 |
| E962153826 | 11/22/2010 | 6:45:06 PM | VAS-23 | EBL | TV | OCO | 182 | 694312 |
| E773315832 | 11/22/2010 | 6:47:30 PM | MOT-14 | ECC | TV | OCO | 150 | 92775 |
| E140401592 | 11/22/2010 | 6:48:51 PM | POU-15 | ECE | TV | OCO | 467 | 796305 |
| E887546685 | 11/22/2010 | 6:50:58 PM | POU-13 | ECE | TV | OCO | 215 | 591042 |
| E716600548 | 11/22/2010 | 6:54:00 PM | TLN-0094 | EBJ | TV | OPO | 6666 | 3642210 |
| E821573024 | 11/22/2010 | 6:54:00 PM | TLN-0140 | EBJ | TV | OCO | 6681 | 1332366 |
| E159179056 | 11/22/2010 | 6:55:00 PM | LOL-25 | ECD | TV | OCO | 1812 | 2594784 |
| E409042614 | 11/22/2010 | 6:56:42 PM | PRE-13 | EBE | TV | OTR | 17 | 10579 |
| E799524213 | 11/22/2010 | 6:57:25 PM | MIL-16 | ECE | TV | OCO | 157 | 188806 |
| E273319357 | 11/22/2010 | 6:59:49 PM | SCH-13 | EAA | TV | OCO | 60 | 31511 |
| E866378880 | 11/22/2010 | 7:02:00 PM | ROE-13 | EAA | TV | OFU | 6 | 5868 |
| E568445750 | 11/22/2010 | 7:08:17 PM | BHL-13 | ECE | TV | CDH | 38 | 91645 |
| E013879273 | 11/22/2010 | 7:09:00 PM | TLN-0063 | ECE | TF | OCO | 4790 | 1681290 |
| E619016011 | 11/22/2010 | 7:09:30 PM | HEM-13 | ECA | TF | OCO | 2099 | 82911 |
| E340030996 | 11/22/2010 | 7:12:17 PM | LOL-22 | ECD | TV | OCO | 1179 | 1520576 |
| E548341588 | 11/22/2010 | 7:16:05 PM | OSC-22 | EBI | TV | OFU | 31 | 5081 |
| E553150194 | 11/22/2010 | 7:19:56 PM | HOL-13 | ECA | TV | OCO | 6 | 4560 |
| E154609305 | 11/22/2010 | 7:21:00 PM | TLN-0271 | ECD | TV | OCO | 8819 | 9909970 |
| 10986171 | 11/22/2010 | 7:23:00 PM | TLN-0098 | EBL | TF | OCO | 4838 | 58056 |
| E486782180 | 11/22/2010 | 7:24:51 PM | BHL-12 | ECE | TV | OCO | 112 | 281697 |
| E684896894 | 11/22/2010 | 7:27:15 PM | ROC-26 | ECC | TV | OJU | 100 | 83175 |
| E059505985 | 11/22/2010 | 7:29:54 PM | VAS-22 | EBL | TV | OCR | 100 | 220510 |
| E161276753 | 11/22/2010 | 7:34:02 PM | RAI-13 | ECC | TV | OCO | 10 | 1860 |
| E586710169 | 11/22/2010 | 7:36:16 PM | BLU-16 | ECC | TV | OCR | 10 | 2657 |
| E216506904 | 11/22/2010 | 7:37:43 PM | CEK-16 | ECE | TV | OCO | 15 | 2284 |
| E760301398 | 11/22/2010 | 7:39:50 PM | NBO-22 | EBD | EF | OFC | 6 | 2107 |
| E083266792 | 11/22/2010 | 7:40:27 PM | GRV-16 | ECA | TV | OCO | 9 | 8681 |
| E252454423 | 11/22/2010 | 7:42:35 PM | CLE-11 | EBH | TV | OCO | 63 | 18989 |
| E510388176 | 11/22/2010 | 7:44:07 PM | KIN-21 | ECE | TV | OCO | 62 | 86235 |
| E897376440 | 11/22/2010 | 7:45:17 PM | LUH-15 | ECC | TV | OCO | 27 | 19162 |
| E197367280 | 11/22/2010 | 7:47:25 PM | KCR-16 | EBJ | TV | OCO | 81 | 92144 |
| E582014023 | 11/22/2010 | 7:48:24 PM | WCA-17 | EBJ | UN | OFU | 1278 | 417395 |
| E793033358 | 11/22/2010 | 7:51:33 PM | MCW-16 | ECE | TV | OFU | 48 | 56662 |
| E663477915 | 11/22/2010 | 7:59:43 PM | WCA-16 | EBJ | TF | UPC | 1241 | 1194721 |
| E036967515 | 11/22/2010 | 8:06:02 PM | CHI-16 | ECD | TV | OFU | 21 | 14678 |
| E203666771 | 11/22/2010 | 8:20:23 PM | BEL-17 | EBJ | TV | OSV | 3 | 1469 |
| E267703381 | 11/22/2010 | 8:25:53 PM | NUG-26 | EAA | TV | OCO | 790 | 897423 |
| E464182759 | 11/22/2010 | 8:26:58 PM | PLY-15 | EAA | TV | OSW | 51 | 33203 |
| E299908564 | 11/22/2010 | 8:28:29 PM | MIL-22 | ECE | TV | OCO | 19 | 28054 |
| E765360408 | 11/22/2010 | 8:35:37 PM | TRA-22 | ECE | TV | OCR | 13 | 17555 |
| E078267140 | 11/22/2010 | 8:38:25 PM | LAT-14 | EBJ | TV | OFU | 163 | 21122 |
| E365251574 | 11/22/2010 | 8:41:29 PM | MHT-13 | EBJ | TV | OPO | 20 | 14690 |
| E474245552 | 11/22/2010 | 9:12:54 PM | BAK-25 | EAA | TV | OCO | 5 | 3411 |
| E799305509 | 11/22/2010 | 9:13:40 PM | HAN-16 | EAA | TV | OCO | 22 | 17893 |
| E120326722 | 11/22/2010 | 9:17:03 PM | PEA-15 | EBJ | TV | OTF | 2 | 2226 |
| E410186422 | 11/22/2010 | 9:32:55 PM | PLY-13 | EAA | TV | OCO | 19 | 7621 |
| E237563711 | 11/22/2010 | 9:35:41 PM | LAU-14 | EAA | TV | OCO | 6 | 2288 |
| E767854641 | 11/22/2010 | 9:52:01 PM | BON-17 | ECA | TV | OCO | 1 | 698 |
| E764962153 | 11/22/2010 | 9:54:04 PM | GRV-15 | ECA | TV | OCO | 35 | 21308 |
| E517695080 | 11/22/2010 | 9:58:10 PM | PAT-16 | ECC | TV | OCO | 11 | 10503 |
| E225368661 | 11/22/2010 | 10:04:46 PM | TAN-13 | ECC | TF | OCO | 2141 | 242433 |
| 10986174 | 11/22/2010 | 10:07:00 PM | TLN-0075 | EBL | TV | OCO | 3472 | 6944 |
| E232553713 | 11/22/2010 | 10:11:58 PM | SME-12 | EBE | TV | OCO | 1266 | 544562 |
| E996868992 | 11/22/2010 | 10:30:14 PM | KAP-13 | ECA | TV | OCO | 10 | 10798 |
| E762025280 | 11/22/2010 | 10:34:00 PM | TLN-0153 | ECC | TF | OCO | 4391 | 1026236 |
| E794411845 | 11/22/2010 | 10:45:42 PM | MCA-15 | ECC | TF | OCO | 335 | 203110 |
| E661101140 | 11/22/2010 | 10:55:18 PM | EDG-12 | ECA | TV | OSV | 10 | 7297 |
| E832641222 | 11/22/2010 | 10:58:50 PM | LWS-16 | EBJ | TV | OCO | 44 | 28343 |
| E277168231 | 11/22/2010 | 11:05:26 PM | RAI-12 | ECC | TV | OCO | 30 | 17837 |
| E968117313 | 11/22/2010 | 11:12:38 PM | BHS-14 | EAA | TV | OCO | 3 | 2077 |
| E848033131 | 11/22/2010 | 11:27:06 PM | BON-13 | ECA | TV | OCO | 26 | 11775 |

### Terms, Codes and Definitions Used on Detail Reports

| #### Notification | [Notification Number] A number assigned by SAP, identifying the outage record |
| --- | --- |
| Date | The date of the outage |
| Time | The time of the outage |
| Circuit | [Reference Circuit] The circuit identifier for the affected circuit |

|  | Area | [Maintenance Planner Group] A code representing the energy, region and service center |  |
| --- | --- | --- | --- |
|  |  | EAA – Bellingham | EBJ – South King |
|  |  | EAB – Lynden | EBK – Southwest King |
|  |  | EAC – Skagit | EBL – Vashon |
|  |  | EAD – Whidbey | ECA – Puyallup |
|  |  | EBD – Redmond | ECC – Olympia |
|  |  | EBE – Factoria | ECD – Port Orchard |
|  |  | EBF – Snoqualmie | ECE – Poulsbo |
|  |  | EBI – Enumclaw | ECF – Port Townsend |
|  | Cause | Cause of Outage |  |
|  |  | AO – Accident Other | EF – Equipment Failure |
|  |  | BA – Bird or Animal | EO – Electrical Overload |
|  |  | CP – Car Pole | FI – Faulty Installation |
|  |  | CR – Customer Request | TF – Tree Off Right-of-Way |
|  |  | DU – Dig-up Underground | TO – Tree On Right-of-Way |
|  |  | TV – Trees/Vegetation | SO – Scheduled Outage |
|  |  | UN – Unknown |  |
| Equipment |  | Affected by, or involved in the outage |  |
|  |  | OCN – Connector | OSW – Overhead Switch |
|  |  | OCO – Overhead Conductor | OTF – Overhead Transformer Fuse |
|  |  | OCR – Crossarm | OTR – Overhead Transformer |
|  |  | OFC – Overhead Cut-out | OUP – OH to UG Primary |
|  |  | OFS – Overhead Fire Signal | OUS – OH to UG Secondary Service |
|  |  | OFU – Fuse Link/OH Line Fuse | SBF – High-side Bank Fuse |
|  |  | OGS – Span Guy | SCB – Power Circuit Breaker |
|  |  | OHR – Overhead Recloser | UOT – Underground Outdoor Term |
|  |  | OIN – Insulator | UPC – Underground Primary Cable |
|  |  | OJU- Jump Wire | UPT – Padmount Transformer |
|  |  | OPI – Overhead Pin Insulator | USV – Underground Service |
|  |  | OPO – Pole | UTC – Underground Terminal Fuse |
|  |  | OSV – Overhead Service | UTR – Submersible Transformer |
|  |  | ORE – Regulator |  |

| CUST OUT | [Customer Out] The number of customers without power for any given outage record |
| --- | --- |
| CUST MIN | [Customer Minutes] The total number of minutes customers were without power for any given record |

### Media Coverage

Monday, November 22, 2010 - Page updated at 03:25 PM

MIKE SIEGEL / THE SEATTLE TIMES

Cars stack up in both directions along Northeast 175th Street in Shoreline between Aurora Avenue North and Interstate 5.

MIKE SIEGEL / THE SEATTLE TIMES

A woman waits for a bus along North 205th Street along the King Snohomish County line early Monday morning as snow fall and sticks on the roadway during the morning commute.

MIKE SIEGEL / THE SEATTLE TIMES

Traffic is crawling on Interstate 5 Monday morning in the southbound lanes from Shoreline all the way downtown.

STEVE RINGMAN / THE SWEATTLE TIMES

A car rests in the ditch after a spin out from icy roads on SE 128th Ave. in Maple Valley.

- More snow, wind on the way Monday evening

By Jack Broom, Seattle Times staff reporter

A surge of cold, wet air could dump an additional two to six inches of snow on Western Washington Monday afternoon and evening, driving the wind chill as low as zero degrees and setting the stage for potential widespread power outages.

The Weather Service's "winter storm warning," in effect until 10 p.m. Monday, comes at the end of a day in which snowfall slickened roadways throughout Puget Sound, causing countless spinouts and accidents, including two that closed five of six lanes on the Aurora Bridge for an hour.

Gusts of up to 45 mph are expected late Monday as cold air barrels down from British Columbia's Queen Charlotte Islands. The chance of precipitation was listed as 100 percent for Monday afternoon, dropping to 80 percent Monday night.

The high winds carry the potential to down trees or power lines. Western Washington residents are advised to have emergency supplies on hand, and to avoid unsafe methods of alternate power.

Residents who lose power at home are reminded not to use generators, gas grills or barbecues indoors because of the possibility of fatal carbon-monoxide poisoning.

Monday morning's commute took up to 60 minutes from Tacoma to Seattle and 77 minutes from Tacoma to Bellevue, the state Department of Transportation reported about 7:30 a.m., and those delays continued throughout the commute, said the Washington State Patrol.

Midmorning, commuters from West Seattle were facing 45-minute drives just to get to Interstate 5 because of congestion.

"It's getting kind of bad out there, we've got snow sticking all over the place," Washington State Patrol Trooper Julie Startup in Bellevue said about 8:30 a.m.

Startup said the snowfall was affecting travel even on major freeways, including Interstate 5 southbound through the University District and on the Highway 520 bridge. "We have a lot of people sliding around, so traffic is moving very slowly," she said.

About 9 a.m., two separate crashes blocked five of the Aurora Bridge's six lanes, including all southbound lanes. The crashes were cleared by shortly after 10 a.m., but traffic remained backed up for several miles.

Snow was falling over much of the metropolitan area, including downtown Seattle, and King County Metro Transit had put its buses on a snow routes. Information on bus routes is on www.kingcounty.gov/metro/snow.

Metro said while the accumulations are not expected to be deep, its managers want to be prepared and don't want to change to snow routes during the middle of the busiest travel times. Snow continued falling during the morning commute, creating hazardous driving conditions.

Seattle Department of Transportation (SDOT) applied anti-icing material on hills and icy spots Sunday night. Crews began plowing main roadways on Monday morning.

Heavy snowfall was reported early Monday in South King County and Pierce County and multiple minor traffic accidents contributed to traffic delays.

Seattle School District reported Monday morning that it would dismiss middle schools and high schools early at 12:35 p.m. Elementary and K-8 schools were already closed for parent-teacher conferences. The conferences would continue, the district said. Other school districts in Western Washington were starting late Monday, including two-hour delays and the cancellation of programs in the Puyallup, Eatonville, Sumner and Orting districts in Pierce County, KOMO-TV reported.

Information on school closures and delays can be found at www.schoolreport.org.

Jack Broom: 206-464-2222 or jbroom@seattletimes.com

- Snow, below freezing temperatures in the Northwest

Credit: Rachel Kowalski

Olympic Peninsula

by KING 5 News

Posted on November 19, 2010 at 9:45 PM - Updated today at 3:24 PM

SEATTLE – Washington has been hit by its first significant snowfall of the season, making traffic a mess in the Puget Sound area.

The snow is expected to continue across Western Washington through this afternoon.

KING 5 Meteorologist Jeff Renner says low pressure is moving across the Olympic Peninsula, pulling even colder air into western Washington from the interior of British Columbia.

"As the cold air moves south, it will behave like a wedge, plowing moist air near the ground upward. That will give us one more burst of snow shower," said Renner.

The lightest snow will be over Whatcom and San Juan counties-probably trace amounts to an inch, trace to 3" over much of the Puget Sound area, though the foothills could see local additional accumulations of trace to 4". The heaviest snowfall will be over the north end of the Olympic pPeninsula, with another 1 to 6 inches.

As that cold Arctic air shoves southward, snow should diminish from the north; in most places, that should happen by 6 to 7 pm, said Renner. That will be accompanied by gusty northerly winds as it drops southward.

Expect northerly sustained winds of 20-35 mph with gusts exceeding 40 mph over the Sound, and 25 to 45 mph with gusts exceeding 50 mph over Whatcom, Skagit and San Juan counties.

The combination of overnight lows in the low teens to low 20s and strong winds will likely result in frigid wind chills of single digits to well below zero.

High temperatures both today and Tuesday will be below freezing across most of Western Washington, a rare event for November.

At Sea-Tac there have only been 14 days in the history of the airport weather records - which go back to 1945 - where the high has been 32 degrees or less in November.

Tuesday, November 23, 2010 - Page updated at 12:01 AM

- Salt treatment no match for temperature drop

By Mike Lindblom, Seattle Times transportation reporter

Despite treatment with brine and rock salt, Seattle's streets froze Monday afternoon, forcing the closure of the Alaskan Way Viaduct and several other major streets as the afternoon commute turned into a fiasco.

The city's fleet of 26 trucks were to stay on rounds overnight, in hopes of melting ice before drivers hit the roads again Tuesday morning.

Most roads were bare and wet Monday in the morning, so much that a salt-truck driver on the West Seattle Bridge route had to treat only a small ramp connection at Beacon Hill. There was one significant crash in the morning commute, snarling the Aurora Bridge.

Seattle's revamped snow and ice plan initially seemed to be working well.

But then the temperatures plummeted about 3 p.m. A drive from Woodland Park to South Park took 90 minutes.

As of 6 p.m., the viaduct, the Battery Street Tunnel, the Dravus Street overpass, Denny Way over Interstate 5 and the 5100 block of Latona Avenue North were closed because of ice. Gridlock marked downtown and the surrounding areas as commuters struggled to get onto highways.

A spokesman for Mayor Mike McGinn said it was too early to assess the city's response. "I think [Tuesday], we'll have a better idea of how everybody did," said Mark Matassa, speaking from a bus that was delayed more than an hour because of a gridlocked Mercer Street.

The city strategy overnight is to put rock salt in the road lanes, in hopes of breaking up any snow so that it runs off into storm drains instead of freezing, said Steve Pratt, maintenance operations director for the Seattle Department of Transportation. The salt will melt snow and ice down to 15 degrees, he said.

High winds might help dry the pavement at ground level, "but it doesn't do any good on elevated structures," he said.

If more snow falls quickly, the city could add four more vehicles, call in more drivers or run plows in tandem to clear major arterials quickly.

King County announced that it will be working "around the clock" to clear suburban and rural roads.

City truck drivers, their bosses and local politicians remember all too clearly the snowstorm of Dec. 18, 2008, which turned to packed ice that lingered several days. The city relied then on sand and compaction. Now the strategy is to blanket the streets with salt before, during and after the storm.

Pratt had predicted that late Monday afternoon would be a critical time. Some forecasts called for 1 to 3 inches to suddenly fall. If snow relented, he hoped to be able to prevent ice.

Trucks ran continuously and hit every street in the city snow-route map, said Pratt, hired five weeks ago from Snohomish County.

Just about any Seattle road was bare and wet at midday, except for recurring freezing on viaducts and bridges, where there is no soil to insulate the road from beneath. Robert Clarke, of the city road-maintenance center, said that conditions had been perfect over the weekend to prepare Monday morning, because crews had time to sprinkle brine on dry roadways, covering the entire city snow-removal network.

It seemed to work for half a day Monday. Tuesday's freeze will be another test.

Mike Lindblom: 206-515-5631 or mlindblom@seattletimes.com

Copyright © The Seattle Times Company

Tuesday, November 23, 2010 - Page updated at 02:25 PM

- More snow and cold temperatures ahead

By Seattle Times staff

Don't expect any immediate relief to the bitter cold and icy, treacherous conditions facing Western Washington.

Bitter cold and the likelihood of round of snowfall are expected for the next couple of days.

Although Tuesday and Wednesday are forecast to be least partly sunny, temperatures are expected to stay below freezing until nearly midday Thanksgiving Day, according to a "winter weather advisory" from the National Weather Service.

Tuesday's forecast high in the Seattle area is 24 degrees, dipping to 13 degrees Tuesday night and topping out just below freezing on Wednesday.

Clouds are forecast to return Wednesday evening, bringing a 60 percent chance of snow, although accumulations are expected to be a half-inch or less.

Another half-inch of snow could fall on Thanksgiving Day, according to the Weather Service, but showers are expected to turn to rain by about 10 a.m. Thursday in the Seattle area.

Warmer, wetter weather is on the way for the latter part of the holiday weekend, with high temperatures ranging into the 40s and rain expected each day.

The freeze overnight has caused a very slick commute in the Seattle area Tuesday morning. Drivers are being cautioned that if they don't absolutely have to go out, stay home.

Streets, roads and highways in the area are slick because snow from overnight froze, making compact snow and ice, and causing cars and trucks to spin out throughout the area.

Schools are closed in many areas, including Seattle Schools. The University of Washington has canceled operations and classes Tuesday at its Seattle, Tacoma and Bothell campuses.

King County Metro buses are operating on snow routes Tuesday morning and some routes have been canceled because of the slippery conditions. Metro officials are also urging people in general to stay home and off the roads if they can.

The Associated Press is reporting that tens of thousands of customers in the Puget Sound area are without power due to the storm that passed through the area Sunday and Monday.

Copyright © The Seattle Times Company

KEN LAMBERT / THE SEATTLE TIMES

An unidentified passer-by early Tuesday checks out a tangled mess of vehicles abandoned during the snowstorm that paralyzed the Seattle area. The vehicles, some with cryptic messages on their snow-caked windows, were blocking East Boston Street between Boylston and Franklin avenues east.

STEVE RINGMAN / THE SEATTLE TIMES

A homeless man in Pioneer Square carries the essentials necessary to survive bone-chilling cold while living on the streets. Seattle officials opened several shelters this week.

STEVE RINGMAN / THE SEATTLE TIMES

Car owners across the region were returning to rescue their abandoned cars Tuesday. As many as 40 cars were left overnight on Issaquah's Highlands Boulevard.

November 23, 2010 at 2:30 PM

- Storm leaves 50,000 customers without power in Kitsap County

Posted by Susan Gilmore

Some 50,000 Puget Sound Energy customers in Kitsap County were without power Tuesday after the snow and windstorm blew through and toppled trees and tree limbs which then downed power lines.

"Kitsap just got hammered, more than any other county" said PSE spokesman Roger Thompson.

Thompson said 40 crews are working to restore power and he hopes that will be done by Thanksgiving, but he said there still may some pockets in the dark on Thursday.

In addition to the PSE crews, the utility is bringing in two dozen workers outside the region, from British Columbia, Oregon Eastern Washington and Idaho.

"Given the extent of the damage we'll be into tomorrow for certain," Thompson said of the outage.

Part of the repair problem is that may of the roads in Kitsap County are impassible and tough for repair crews to reach.

"Thanksgiving is a big priority for us," Thompson said. "We want our crews home."

About 100,000 Puget Sound Energy customers were without power at the outage's peak.

Seattle City Light reported fewer than 1,500 customers without power and Snohomish PUD says they had fewer than 100 without power.

Comments (0)     E-mail article      Print view      Share

November 23, 2010 at 1:42 PM

To report a missing paper, subscribers should call 206-464-2121 or 1-800-542-0820 toll-free in Washington state. They can also e-mail customerservice@seattletimes.com.

Wednesday, Nov. 24, 2010

Thousands in Kitsap County face cold, dark Thanksgiving

By VANESSA VAN HYFTE

Watch story here.

BREMERTON, Wash. – Power crews in Kitsap County were still working Wednesday night to get electricity back to some 13,000 customers who lost power in Monday's storm – and some of them may still be in the dark for Thanksgiving. But, Puget Sound Energy said late Wednesday that it hoped to have everyone back on the grid by midnight.

Downed lines and trees scatter county roads, making it tough for power crews to get to all the trouble spots.
 	It's been a miserable couple of days for residents. The Colemans have been without power since Monday night. They have a gas heater for warmth, but it still fell to 40 degrees in their home overnight.
 	"We wear gloves and scarves and really try to bundle up. We don't have TV or a radio, so we are bundled in the living room playing games and trying to stay warm," said Anita Coleman. She says Thanksgiving has been moved to her mom's house. Most of her refrigerated food is spoiled.
 	Things are worse for neighbor Joe Palenick. His pipes are frozen solid. He lost eight trees and his camper was destroyed by a 220-foot fir tree.
 	"The wind was screaming like banshees," said Palenick. "I was sort of in emotional shock yesterday. Palenick says he feels completely out of touch with no power for two days. He can't charge his cell phone.
 	PSE crews are working as fast as they can. Some 500 workers from all over the Northwest are trying to mend snapped lines. Brad Frazier, from Idaho, started working at 5 a.m. Tuesday and has gotten little sleep since then.
 	"I think they geared pretty good to get as many people as they can in there to get it back up before Thanksgiving," said Frazier. He says he's not counting on making it back home in time to be with his family.
 	For those still without power, there is a warming shelter at the Kitsap County Fairgrounds.

Wednesday, Nov. 24, 2010

On Thanksgiving Eve, thousands in cold dark in Kitsap County, Vashon Island

Watch story here.

PORT ORCHARD, Wash. -- On the eve of Thanksgiving Day, thousands of families remain in the cold dark in Kitsap County, giving new meaning to the phrase "cold turkey."
 	The outage has rendered hundreds of ovens useless, leaving residents in the dark and with no way to cook their frozen birds.
 	Line crews traveled from Oregon on Wednesday to help Puget Sound Energy crews scrambling to get lights back on throughout Kitsap County. 
 	The power has been out since Monday's snowstorm, which arrived with powerful gusts that knocked trees into power lines and left 50,000 customers in the dark.
 	"We've had prevailing winds before that come from one direction, but this was swirling and the trees out here were all going different directions," said Port Orchard resident Landon Brazier. 
 	A huge fir tree in Brazier's yard gave way and took out a power pole on its way down. But it could have been worse.
 	"You can see how close it is to the house," he said. 
 	The homeowner invested in a generator a few weeks ago, and had limited electricity. But he's worried about hosting the holiday meal.
 	Brazier's generator won't power the oven, which means all he has is a cold turkey. But he says the turkey day celebration will go on without or without the electricity. He has one backup plan. 
 	"It might be Subway," he said, adding he'd serve turkey subs from the sandwich shop in the cold bird's stead. 
 	Meantime, Brazier, his wife and their grandson are staying bundled up while they wait for the crews to get the power flowing.
 	As of late Wednesday afternoon, some 15,000 PSE customers were still without power. Approximately 13,000 of them were in Kitsap County, and 1,200 on Vashon Island. 
 	Everybody was counting on the line crews to give one more reason to be thankful this Thanksgiving.
 	"We're hoping these guys out here are successful today," said Brazier. 
 	The lights did come on briefly on Wednesday afternoon, but quickly died again. 
Waiting for light, heat on Vashon Island
 	Laverne Dormberger is 90 years old.
 	And for the last three days she's survived, alone, inside her small Vashon Island home with no electricity in frigid temperatures. 
 	A couple logs in the wood stove is all that's keeping her warm, and it's the only place where she can heat-up water and cook food.
 	"I put a couple of these on and an old afghan," she said. 
 	While Vashon's emergency management team decides the best plan to get power to hundreds of homes back up and running, King County Executive Dow Constantine visited the island on Wednesday, ready to declare an emergency if needed.
 	"When the entire island is cutoff in weather like this, that is a very significant concern," Constantine said. 
 	The problem is there aren't enough crews on the island to repair all the problems. Many of the island's crews are already running on no sleep. 
 	Meantime, the hum of generators can be heard all over the island, powering everything from homes to cell towers. 
 	Up until Wednesday morning, Dormberger's home was hooked up to her son-in-law's generator. Then the generator ran out of gas, and they've been scrounging for fuel ever since.
 	"We've stripped the cars, the lawn mower, the weed eater," she said. 
 	She hopes her power comes on soon.
 	"It's part of living, I guess," she said. 
 	Crews were hoping to have power restored some time Wednesday night, but in the worst-case scenario, the residents were expected to be in the dark until Thanksgiving Day. 
 	The power company said it hopes to have all its customers restored no later than midnight. It urged any residents still without power after midnight to give the utility a call.

Wednesday, Nov. 24, 2010

Thanksgiving Storm Tradition

By Phyllis Fletcher

The Thanksgiving storm seems like a tradition in Seattle. KUOW's Phyllis Fletcher has this timeline.

Listen to story here.

Andy Wappler grew up in Seattle. He's a meteorologist, and a spokesperson for Puget Sound Energy. He puts it this way.

Wappler: "It's always kind of a classic on Thanksgiving that you might be without power."

In 1983, a wind storm hit Seattle.

On Thanksgiving.

Wappler: "And I actually saw shop windows along First Avenue blowing out just because of the wind. It was that strong a storm."

The wind cut power lines as turkeys were roasting. Thousands of people threw them away half cooked.

In 1985, it was snow.

Wappler: "Couldn't drive even from the UW to downtown. Had to walk. My dad, as I remember, had a terrible flu."

His dad, Harry Wappler. Long–time meteorologist for KIRO–TV.

Wappler: "So I think we literally had something like TV dinners for Thanksgiving. But it was still kind of an adventure anyway."

In 1998, another wind storm hit the Seattle area three days before Thanksgiving. Two hundred thousand homes lost power.

This year, Puget Sound Energy says 100,000 customers lost power in Kitsap County.

A spokesperson for the National Weather Service says storms cross the Puget Sound region about once every seven days in winter.

So it might seem like a pattern to people who remember storms and power outages at Thanksgiving. But four storms in 27 years is about average.

I'm Phyllis Fletcher, KUOW News.

Wednesday, Nov. 24, 2010

Fallen Trees Shred Kitsap's Sunnyslope Neighborhood

By Chris Legeros

KITSAP COUNTY, Wash. -- Puget Sound Energy was making progress Wednesday, trying to restore power to customers in Kitsap County. Many have been without since Monday night and it looks like some will still be in the dark for Thanksgiving.

To understand why it's taking so long for utility crews to restore power in parts of Kitsap, you've got to tour the Sunnyslope area. Trees didn't just tear through power lines; they hit houses, car ports and one even landed on a limousine.

"Falling, cracking -- we were afraid to go outside," said Niki Wasmer, who lost power to her home on Monday. "We snuggled all together with our pit bulls on the bed, with all the blankets, and it was still freezing. I mean, I've never been so cold in my life."

On Wednesday, Wasmer's water pipes broke. Fortunately, a neighbor let her borrow a camper to sleep in, so she'll have a warm place to stay.

Others aren't so lucky.

So many trees fell in Bill Terryll's front yard that he couldn't get out of his driveway until a crew collecting firewood offered to help him out on Wednesday.

Terryll has been without heat and has had to bundle up with a down coat, insulated coveralls and a sweatshirt.

"I don't do anything for heat; I dress warm," Terryll said. "They're working their rear ends off (to restore power) -- hey, that's all we can do."

Even with crews working to restore power, some will be left celebrating a subdued Thanksgiving.

"What Thanksgiving?" Wasmer said. "I'm just thankful that we're alive and that we're warm tonight."

Thursday, Nov. 25, 2010

BREMERTON, Wash. – Puget Sound Energy crews continued to work on Thanksgiving to get power restored to Kitsap County.

Monday's storm brought dozens of trees and power lines down across the county, causing more than 50,000 households to lose power. View PSE's Flickr photo album of the aftermath of the storm here.

Credit: Puget Sound Energy

Puget Sound Energy crews work in difficult conditions to restore power to Vashon Island.

Thursday morning, Dorothy Bracken with Puget Sound Energy reported most of those homes have power once again, but there may still be pockets of customers without power around Kitsap County. There was no estimate of how many homes remain without power.

Bracken said three dozen or more crews continue to work to get the power restored today.

Bracken said PSE encourages customers to call if their power remains out, 1-888-225-5773.

As of Wednesday night, there were still about 13,000 homes without power around Kitsap County.

Puget Sound Energy said late Wednesday that it hoped to have everyone back on the grid by midnight.

Some 500 workers from all over the Northwest are trying to mend snapped lines. Brad Frazier, from Idaho, started working at 5 a.m. Tuesday and has gotten little sleep since then.

"I think they geared pretty good to get as many people as they can in there to get it back up before Thanksgiving," said Frazier. He says he's not counting on making it back home in time to be with his family.

For those still without power, there is a warming shelter at the Kitsap County Fairgrounds.

Thursday, Nov. 25, 2010

A Few Pockets of Kitsap Still Without Power

Puget Sound Energy is asking those still without power to call and make sure repair crews know about you.

Most of the 50,000 Kitsap customers left in the dark by Monday’s storm had power to cook Thanksgiving dinner and watch football on Thursday. There were about 13,000 without power Wednesday evening, and PSE had hoped to get them all energized by midnight. They didn’t make it, said spokeswoman Dorothy Bracken.

Dozens of crews are still in the county repairing scattered, isolated outages. Bracken didn’t have an exact number Thursday evening of how many remained, and hesitated to predict when the work would be completed.

Crews are focusing on the Fernwood area of South Kitsap, south Port Orchard, Manchester and Port Madison, she said.

“Our crews are going up one street and down another to make sure they’re getting the last group of customers,” Bracken said. “We’ve also put out a plea to our customers who are still without power to call.”

The number is (888) 225-5773.

Thursday, Nov. 25, 2010

TURKEY DAY WILL BE DIFFERENT FOR SOME PUGET SOUND FAMILIES
Some residents still without power from the snow storm

(REGIONAL) -- As many Sky Valley families sit down to enjoy Thanksgiving dinner today with the luxury of lights that turn on with a switch, ovens that work and electric baseboard and full home heating systems that bring warmth at the touch of a finger, some families will be enjoying the day quite differently.
 	Some will be eating out, some will be using their outdoor barbecue grills to make dinner and many of them will be using a fireplace or wood stove to heat their homes as there were some Puget Sound families still without electrical power Wednesday night as a result of the snow storm Monday.
 	Initially some 50,000 people were without power primarily in Kitsap County, Vashon Island and a few other areas as high winds crashed trees and heavy branches into power lines knocking out juice to many neighborhoods.
 	By late Wednesday afternoon roughly 15,000 Puget Sound Energy customers were still without power, some 13,000 of them in Kitsap County and 1,200 on Vashon Island. 
 	Electrical line crews have been working on the problem ever since the lights went out.
 	ICE POSSIBLE EARLY THURSDAY: DRIVERS SHOULD BE PREPARED AND CHECK THEIR ROUTE
 	With road temperatures still well below freezing, a new weather forecast that calls for a mix of rain and snow Thursday could mean roadway ice from Chehalis all the way up to Bellingham. 
 	“When any moisture hits while the road temperatures are still hovering around 20 degrees, it will likely turn to ice,” said Chris Christopher, maintenance director for the Washington State Department of Transportation (WSDOT). 
 	“That could mean hazardous driving conditions. Our crews will be out very early Thursday and we are all watching the forecast overnight. It’s very important for all drivers to check conditions all along their route before they leave.” 
 	Christopher said forecasts for Thursday show about a 50/50 chance of that precipitation and possible ice forming on most Puget Sound routes from mid morning through mid afternoon. The roads will be much better as the temperatures increase later Thursday. 
 	Drivers should prepare for winter weather by packing cold-weather supplies and tire chains, and check travel and roadway conditions on WSDOT’s website before hitting the highways.

Friday, Nov. 26, 2010

Underground Power Lines Are Final Challenge for PSE

By Josh Farley

BAINBRIDGE ISLAND —

Dozens of Puget Sound Energy customers whose electricity flows through underground power lines are the last to get their power back following this week’s snow and windstorm.

The underground lines, found in Winslow on Bainbridge and in parts of Port Orchard, Bremerton and Silverdale, are the last place you might think would be affected by such a storm. Dorothy Bracken, Puget Sound Energy spokeswoman, said the underground problems actually developed after the storm, which at its height knocked out power to up to 60,000 customers.

As it repaired overhead lines, Puget Sound Energy re-energized the power supply to the affected area, Braken said. But when the power came back on — sometimes hundreds of homes at a time, each using a full complement of power for appliances, furnace, lights and other purposes — the system was overloaded. Fuses and transformers were blown, Bracken said.

The system is designed to accommodate that much power use, but the sudden surge of having everything flipped on at once caused problems.

As a result, some customers got power back for a few minutes, then lost it again, Bracken said.

Recognizing that issue, power crews started to focus on the blown fuses and transformers. And power was restored to smaller groups at one time to ensure the system would not overload again.

Bracken said it’s more time-consuming to repair blown fuses on underground lines.

“We know where our fuses are,” she said, “It’s just finding which fuse blew.”

Puget Sound Energy plans to have everyone’s power back on by the end of Friday. Those without power are asked to call (888) 225-5773 to confirm crews are repairing the outage.

Friday, Nov. 26, 2010

In Kitsap, people with underground lines are the last to get power back

By ERIC NALDER, HEARST NEWSPAPER

A few dozen Kitsap County residents remained without power Friday morning, and it was a surprising group.

Customers served by underground power lines -- not the type of wires that get blown down in a windstorm -- were the last to get their power restored, said Puget Sound Energy spokesperson Dorothy Bracken.

Otherwise, everybody had juice after a week-long crisis caused by high winds Monday night, trees crashing into power lines and temperatures in the teens on Tuesday and Wednesday.

At the height of the outage, half of Puget Sound Energy's customers in Kitsap County were without power. So were residents of Vashon Island and others scattered around the Puget Sound region -- a total of more than 100,000 customers.

On Thanksgiving, "a few hundred" customers were without power, Bracken said. Seattle was mostly spared.

Why were underground power lines still out in scattered neighborhoods on Bainbridge Island and in Silverdale, Port Orchard and Bremerton on Friday?

The answer to that question contains a lesson for homeowners.

The problem is a phenomenon known in the power industry as "cold load pickup."

You could also call it "shock and awe" hitting a power system, even underground, where the repair is more difficult.

Big wires carrying tens of thousands of volts to neighborhoods can't handle the shock when the power is switched on during a deep freeze, and when homeowners have left their electric heaters, big screen TVs and other energy gobblers turned on. When temperatures are low, the wires need to be warmed slowly. They can't handle the hit from a huge, sudden load, Bracken explained.

So circuit breakers pop and transformers blow. It is the reason many Kitsap residents experienced disappointment on Wednesday; their power came on for a few minutes -- warming the heart and the home -- only to flip off again for a few hours.

When that happens, crews must restore the circuit breakers and transformers. It is a quicker job with overhead wires than with underground systems. On Friday, crews were still descending into underground vaults to take care of the subterranean problem, Bracken said.

Homeowners could help their neighborhood avoid such problems. When the power goes out, turn off the big stuff and the lights in your house. You'll reduce the load and avoid damage to your appliances caused by power surges.

Of course, in the long run, you should also be sure that your water pipes are insulated.

Though nearly everyone now has power, the water pipe trouble caused by the Thanksgiving Week Storm of 2010 is just emerging.

"We are extremely busy with frozen pipes in Kitsap County," said Wayne Bolton, manager of Roto-Rooter in Tacoma, on Friday morning.

Friday, Nov. 26, 2010

- It's back to Seattle's signature rainy weather

Posted by By Jill Kimball

After this week's snow-induced traffic headaches and freezing temperatures, many might feel relief when they hear this blissfully predictable weekend forecast: clouds, rain and highs in the 40s.

Lows will stay above freezing all weekend and likely all next week, National Weather Service meteorologist Johnny Burg said, and the weekend's only idiosyncrasy is a possible thunderstorm Saturday afternoon.

Highs are expected to be in the low 40s and lows in the low 30s both Saturday and Sunday, with clouds and a chance of showers.

It's a good weekend for snow sports, Burg said: In the mountains east of Seattle, snow will fall throughout the weekend, tapering off a little Sunday. At Snoqualmie and Stevens passes, high temperatures will be in the mid to upper 20s.

So far, November has been a month characterized by extremes. The first week of the month, a summery sun shone and the temperature reached a record 74 degrees at Sea-Tac Airport on Nov. 3.

Then, less than three weeks later, 2.5 inches of snow blew through town, and Tuesday's low was a bone-chilling 14 degrees at Sea-Tac.

Days of below-freezing temperatures resulted in two hypothermia deaths in the area. Jerry M. Fitzgerald, 76, died Friday in Redmond and James R. Furseth, 56, died Saturday in Issaquah, according to the King County Medical Examiner's Office.

The snowstorm Monday backed up traffic everywhere, and for many, commutes home were longer than the workday itself. According to Puget Sound Energy, 100,000 customers in Kitsap, King and Jefferson counties lost power.

Now, the roads are clear, all PSE customers' power has been restored, and Seattle has returned to the clouds and rain for which it is known.

The storm was "definitely one to remember for most people," Burg said, and only longtime Seattleites remember the last time November got so cold: 1985. Bottom line: "This was definitely not a normal November."

Burg can't predict whether December has as many ups and downs in store, but Seattleites can count on a wetter-than-normal holiday season with slightly colder temperatures than usual, as it's a La Niña year.

Friday, Nov. 26, 2010

- Kitsap residents, businesses continue to recover from storm

By KIPP ROBERTSON

The aftermath of a storm that left 50,000 Kitsap County residents without power is keeping businesses busy.

Stranded vehicles have kept the phones ringing at local businesses such as Kitsap Towing and company owner Ron Madler said the storm was one of the worst in terms of accidents.

"The fact that it came during a holiday week was a big factor," Madler said.

Because the storm hit three days before Thanksgiving, the increased traffic due to holiday travel caused more accidents than usually, he said. Madler could not give an exact estimate on how many calls the company responded to, but he said the company has responded to more than 300 calls in the past five days.

With the warming temperatures and rain melting the remaining ice on the roads, it has made it possible for tow truck drivers to tow vehicles that were previously unreachable. The areas in Kitsap drivers have the most difficulty with are Bainbridge Island - because of steep driveways going to waterfront homes-Jefferson Point and Hansville.

Drivers worked well into the night on Nov. 22 and Madler said most exceeded 12 hour shifts and he said the power outage significantly slowed the company's response time. One of the repeater towers the company uses for two-way radios went down for 36 hours, forcing workers to use cell phones that are not as reliable as the radios.

As of Friday afternoon, Madler said the company still had about 50 calls to respond to.

Towing cars stranded by the storm is not the only work still being done. Puget Sound Energy continues to work on small pockets of the county and burst pipes keep the phones ringing at Swift Plumbing & Heating in Kingston.

Though phone calls mean more business, which Bev Swift can't complain about, she said the office has been empty except for her because the staff is so busy.

"It's a real boost for us, but its crazy right now. Our phones are ringing off the hook," Swift said.

The majority of power was restored by Wednesday night, but areas-mainly in Silverdale, Port Orchard and Bremerton-are still without power, said Puget Sound Energy spokesperson Dorothy Bracken.

"This was a tough one," Bracken said referring to the storm.

Work crews responded to more than 200 hundred locations since Monday. The company was so overloaded with calls that it brought in 80 work crews-50 from Puget Sound Energy and 30 from Oregon and Canada.

Because of the cars strewn about the roads, crews had difficulty accessing some of the locations that needed service, Bracken said.

Additional problems arrived when power began to be restored. Because of the combination of freezing temperatures and an increased need for electricity, fuses attached to power lines blew, Bracken said. The fuses that blew were primarily attached to underground power lines, which could not handle the demand.

The day after the storm hit, a meeting was held to discuss how Puget Sound Energy could respond more efficiently, but Bracken said there is only so much the company can prepare for.

"Every storm is different," Bracken said. "They always cause new challenges, but we learn from every storm."

The National Weather Service is predicting rain showers through the weekend with temperatures dropping to the mid to low 30s at night, with highs in the lower 40s. Winds are expected to pick up to 15 MPH Saturday afternoon.

Schools will be open next week, but the district buildings are experiencing technical issues with internet capabilities according to a press release received on Nov. 24. For information on school closures call the school emergency line: (360) 779-3971.