2010

Qualifying Storm Events

December 14, 2010

# Table of Contents

Table of Contents	2

Event Description	3

Date of Event	3

Event Type	3

Service Areas Affected	3

Number of Customers Affected	3

Summary of System Impacts	3

Mobilization Summary	3

Major Event Day – Qualification	5

Qualified Events - 2010	5

Current Event – Calculation Detail	5

Cumulative list of events that have qualified	5

Event Restoration – Cost Summary	6

Restoration Cost Detail by Qualifying Event	6

YTD Storm Restoration Cost Detail – Through December 14, 2010	6

Detail Documents	7

Restoration Cost Detail – Current Event	8

IEEE-1366 - Detailed List of Distribution Circuits with Outages	9

Terms, Codes and Definitions Used on Detail Reports	15

Media Coverage	16

# Event Description

### Date of Event

December 14, 2010

### Event Type

Windstorm.

### Service Areas Affected

This weather event affected King, Pierce, Thurston, and Kitsap Counties.

### Number of Customers Affected

Approximately 69,500 customers were without power over the course of this outage event.

### Summary of System Impacts

| Total Number of Outages | 241 |
| --- | --- |
| Distribution Circuits Totally Out | 1 |
| Distribution Circuits Partially Out | 240 |

| Transmission Circuits Affected | 5 |
| --- | --- |
| Substations Totally Off-line | 1 |

### Mobilization Summary

#### Operating Bases

| Base | Date Opened | Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
| South King | 12/14/2010 | 02:15 | 12/14/2010 | 22:00 |
| North King | 12/14/2010 | 02:00 | 12/14/2010 | 21:30 |
| Pierce | 12/14/2010 | 01:30 | 12/14/2010 | 21:00 |
| Thurston | 12/14/2010 | 01:30 | 12/14/2010 | 20:45 |
| Kitsap | 12/14/2010 | 04:45 | 12/14/2010 | 24:00 |
| Vashon | 12/14/2010 | 04:45 | 12/14/2010 | 24:00 |

#### Emergency Operations Center

| EOC | Date Opened | #### Time Opened | Date Closed | Time Closed |
| --- | --- | --- | --- | --- |
|  | 12/14/2010 | 05:45 | 12/14/2010 | 18:00 |

# Major Event Day – Qualification

- IEEE 1366 Method

IEEE 1366 was established to present a set of terms and definitions which can be used to foster uniformity in the development of distribution service reliability indices, to identify factors which affect the indices, and to aid in consistent reporting practices among utilities.  Also, it provides guidance for new personnel in the reliability area, and tools for internal as well as external comparisons.  The Major Event Day definition was created as part of IEEE 1366 to allow for consistent calculation of reliability metrics between utilities, and enable more valid comparisons with other utility reliability metrics.

IEEE Major Event Day Calculation (2.5 BETA METHOD) - A threshold on daily SAIDI is computed once a year, following year end. - Assemble the 5 most recent years of historical values of SAIDI/day. - Discard any days in the data set that has a SAIDI/day of zero. - Find the natural logarithm of each value in the data set. - Compute the average Alpha and the standard deviation (Beta) of the natural logarithms computed in step 3. - Compute the threshold Tmed where Tmed = exp (Alpha + 2.5 * Beta) - Any day in the next year with SAIDI > Tmed is a major event day.

Puget Sound Energy’s Major Event Threshold for 2010: 7.21 Minutes

# Qualified Events - 2010

### Current Event – Calculation Detail

| Event Date | Total Customer Minutes | Average Customer Count | Daily SAIDI – Customer Minutes /Customer Count |
| --- | --- | --- | --- |
| 12/14/2010 | 21,560,985 | 1,085,427 | 19.86 |

### Cumulative list of events that have qualified

| Date(s) | T-med Score | O&M – Deferrable Accumulation |
| --- | --- | --- |
| 01/17/2010 | 29.25 | $862,417 |
| 03/16/2010 | 10.61 | $481,430 |
| 05/03/2010 | 13.55 | $721,305 |
| 11/15/2010 | 101.18 | $5,016,951 |
| 11/22/2010 | 124.14 | $917,897 |
| 12/14/2010 | 19.86 | $0 |

# Event Restoration – Cost Summary

### Restoration Cost Detail by Qualifying Event

| Date | Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M – Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01/17/2010 | $0 | $50,785 | $0 | $79,959 | $862,417 | $942,376 | $993,161 |
| 03/16/2010 | $0 | $110,581 | $0 | $43,339 | $481,430 | $524,769 | $635,349 |
| 05/03/2010 | $0 | $154,017 | $0 | $44,568 | $721,305 | $765,872 | $919,889 |
| 11/15/2010 | $0 | $578,471 | $0 | $261,686 | $5,016,951 | $5,278,638 | $5,857,108 |
| 11/22/2010 | $7,837,044 | $932,518 | $0 | $342,190 | $917,897 | $1,260,087 | $10,029,649 |
| 12/14/2010 | $1,542,934 | $462,136 | $0 | $100,375 | $0 | $100,375 | $2,105,445 |

### YTD Storm Restoration Cost Detail – Through December 14, 2010

| Qualified Events Deferred Account | Capital | C&D Costs Recoverable from Direct Billings (Costs Not Yet Billed) | O&M – Not Deferrable | O&M Deferrable Accumulation | Total O&M | Total |
| --- | --- | --- | --- | --- | --- | --- |
| $9,379,978 | $2,288,507 | $0 | $872,117 | $8,000,000 | $8,872,117 | $20,540,602 |

# Detail Documents

- Restoration Cost Detail – Current Event

- Detailed List of Distribution Circuits with Outages

- Terms, Codes & Definitions Used on Detail Reports

- Newsprint Media Coverage

### Restoration Cost Detail – Current Event

|  |  |  | Puget Sound Energy |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | December 14, 2010 Storm Damage Repair Costs |  |  |  |  |  |  |
|  |  | Qualifying Events Deferred Account | Capital | C&D Recoverable from Direct Billings (Costs Not Yet Billed) | O&M - Not Deferrable | O&M - Deferrable Accumulation | Total O&M | Total |  |
|  | Labor |  |  |  |  |  |  |  |  |
|  | ST |  | $ 1,422 |  | $ 36,012 | $ 26,135 | $ 62,147 | $ 63,568 |  |
|  | OT |  |  |  |  | $ 140,780 | $ 140,780 | $ 140,780 |  |
|  | Total Labor | $ - | $ 1,422 | $ - | $ 36,012 | $ 166,915 | $ 202,927 | $ 204,349 |  |
|  | Labor OH |  | $ 834 |  | $ 25,671 | $ 75,441 | $ 101,112 | $ 101,945 |  |
|  | Materials |  | $ 69,833 |  | $ 17,703 | $ 59,311 | $ 77,014 | $ 146,847 |  |
|  | Contractors |  | $ 321,112 |  | $ 1,433 | $ 1,198,656 | $ 1,200,089 | $ 1,521,201 |  |
|  | Other Direct Charges |  |  |  |  | $ 11,767 | $ 11,767 | $ 11,767 |  |
|  | Fleet |  | $ 94 |  |  | $ 30,845 | $ 30,845 | $ 30,939 |  |
|  | Other Assessments |  | $ 68,842 |  | $ 19,556 | $ 0 | $ 19,556 | $ 88,398 |  |
|  | Deferred Expenses | $ 1,542,934 |  |  |  | $ (1,542,934) | $ (1,542,934) | $ - |  |
|  |  | $ 1,542,934 | $ 462,136 | $ - | $ 100,375 | $ - | $ 100,375 | $ 2,105,445 |  |

### IEEE-1366 - Detailed List of Distribution Circuits with Outages

| NUMBER | DATE | TIME | CKT | MPG | CAZ | EQT | CUST.OUT | CUST.MIN |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| E391946857 | 12/14/2010 | 12:00:07 AM | GRI-16 | ECC | TV | OCO | 1,264 | 189,453 |
| E875930123 | 12/14/2010 | 12:10:58 AM | PLG-13 | ECC | TV | OPO | 1,124 | 446,993 |
| E715779450 | 12/14/2010 | 12:11:42 AM | CHA-15 | ECC | TV | OCO | 2 | 1,743 |
| E959238383 | 12/14/2010 | 12:12:25 AM | DEC-17 | ECC | TV | OCO | 12 | 8,959 |
| E646288481 | 12/14/2010 | 12:13:01 AM | PRI-13 | ECC | TV | OCO | 160 | 102,557 |
| E127743239 | 12/14/2010 | 12:15:55 AM | SWI-15 | ECC | TF | OCO | 2,739 | 570,451 |
| E028866082 | 12/14/2010 | 12:18:33 AM | FRG-24 | ECC | TV | OCO | 43 | 55,962 |
| E675408994 | 12/14/2010 | 12:19:44 AM | CHA-16 | ECC | TV | OCO | 1,413 | 1,247,796 |
| E175334448 | 12/14/2010 | 12:21:31 AM | WOL-25 | ECC | TV | OCO | 1,419 | 406,520 |
| E129942731 | 12/14/2010 | 12:25:00 AM | FRA-12 | ECD | TV | OPO | 21 | 25,914 |
| E558946198 | 12/14/2010 | 12:25:08 AM | FRA-12 | ECD | TV | OCO | 1,063 | 749,447 |
| E265278551 | 12/14/2010 | 12:26:00 AM | KAP-16 | ECA | TF | CDH | 1,321 | 506,316 |
| E473680875 | 12/14/2010 | 12:28:22 AM | SWI-16 | ECC | TV | OCO | 12 | 13,700 |
| E562807109 | 12/14/2010 | 12:30:27 AM | AIR-23 | ECC | TV | OCO | 1,311 | 152,797 |
| E463143915 | 12/14/2010 | 12:31:00 AM | FCH-24 | ECA | TF | OCO | 1,802 | 499,154 |
| E707798317 | 12/14/2010 | 12:31:00 AM | HEM-17 | ECA | TF | OCO | 1,705 | 373,395 |
| E766656188 | 12/14/2010 | 12:31:26 AM | TAN-16 | ECC | TV | OCO | 177 | 73,555 |
| E037838568 | 12/14/2010 | 12:31:52 AM | FRG-23 | ECC | TV | OCO | 77 | 67,616 |
| E643022607 | 12/14/2010 | 12:33:20 AM | LOL-21 | ECD | TV | OCO | 1,484 | 349,729 |
| E972093561 | 12/14/2010 | 12:33:56 AM | HAW-12 | ECC | TV | OCO | 18 | 12,151 |
| E533011232 | 12/14/2010 | 12:34:12 AM | PAT-15 | ECC | TV | OCO | 62 | 59,818 |
| E907536575 | 12/14/2010 | 12:36:25 AM | FRA-16 | ECD | TO | OCO | 1,315 | 392,637 |
| E148692363 | 12/14/2010 | 12:37:00 AM | RHO-16 | ECA | TV | OCO | 2,369 | 594,619 |
| E710475014 | 12/14/2010 | 12:37:10 AM | FRA-13 | ECD | TV | OFU | 52 | 44,763 |
| E591528141 | 12/14/2010 | 12:40:31 AM | PMA-13 | ECE | TV | OFU | 18 | 11,151 |
| E835516279 | 12/14/2010 | 12:41:19 AM | PRI-23 | ECC | TV | OSV | 8 | 3,205 |
| E210959401 | 12/14/2010 | 12:41:45 AM | CHI-12 | ECD | TV | OFC | 78 | 53,372 |
| E612237394 | 12/14/2010 | 12:42:00 AM | WLK-13 | ECA | TV | OCO | 1,049 | 463,662 |
| E901996125 | 12/14/2010 | 12:44:32 AM | EDG-12 | ECA | TV | OCO | 24 | 19,571 |
| E104788652 | 12/14/2010 | 12:44:52 AM | MAN-16 | ECD | TF | OCO | 629 | 151,673 |
| E254549437 | 12/14/2010 | 12:45:47 AM | MVW-13 | EBJ | TV | OCO | 1,483 | 336,962 |
| E338467794 | 12/14/2010 | 12:46:11 AM | KAP-13 | ECA | TV | CDH | 97 | 118,482 |
| E200918129 | 12/14/2010 | 12:46:23 AM | WOL-23 | ECC | TV | OCO | 112 | 79,589 |
| E927240059 | 12/14/2010 | 12:47:34 AM | FWD-16 | EBJ | TV | OCO | 1,776 | 222,770 |
| E662797723 | 12/14/2010 | 12:47:54 AM | MAN-12 | ECD | TV | OFU | 204 | 97,532 |
| E304036196 | 12/14/2010 | 12:48:03 AM | FNW-16 | ECD | TV | OFU | 535 | 167,598 |
| E677011682 | 12/14/2010 | 12:48:21 AM | OSC-23 | EBI | TV | OFU | 36 | 11,579 |
| E171327517 | 12/14/2010 | 12:50:50 AM | MAP-16 | EBF | TF | OPO | 1,519 | 157,592 |
| E129454736 | 12/14/2010 | 12:50:54 AM | SHE-16 | ECE | TV | OTH | 990 | 289,917 |
| E469163127 | 12/14/2010 | 12:51:21 AM | SPA-16 | ECA | TV | OSV | 1 | 1,172 |
| E384361455 | 12/14/2010 | 12:52:00 AM | FCR-13 | EBI | TV | OCO | 72 | 93,456 |
| E812199316 | 12/14/2010 | 12:52:00 AM | TLN-0085 | EBD | TV | OCO | 4,187 | 92,114 |
| E783033734 | 12/14/2010 | 12:53:17 AM | KCR-17 | EBJ | EF | OFU | 1,003 | 245,451 |
| E163364346 | 12/14/2010 | 12:54:11 AM | TAN-13 | ECC | TV | OCO | 186 | 78,830 |
| E585174252 | 12/14/2010 | 12:55:20 AM | SIL-15 | ECD | TV | OCO | 143 | 86,181 |
| E386658458 | 12/14/2010 | 12:55:35 AM | YEL-27 | ECC | TV | OCO | 535 | 316,943 |
| E898277726 | 12/14/2010 | 12:56:04 AM | VAS-13 | EBL | TV | OCO | 669 | 347,289 |
| E493066097 | 12/14/2010 | 12:57:08 AM | VAS-12 | EBL | TV | OCO | 5 | 7,314 |
| E058913878 | 12/14/2010 | 12:58:00 AM | PAN-14 | EBJ | UN | OCO | 1,337 | 216,282 |
| E811620100 | 12/14/2010 | 12:58:01 AM | NBO-26 | EBD | TF | OCO | 863 | 187,257 |
| E311127965 | 12/14/2010 | 12:58:27 AM | HIG-16 | EBE | TV | OSV | 3 | 3,695 |
| E581561003 | 12/14/2010 | 12:59:28 AM | BDI-13 | EBJ | TV | OCO | 758 | 636,366 |
| E331016940 | 12/14/2010 | 12:59:56 AM | HOL-13 | ECA | TV | OTF | 8 | 6,081 |
| E808263894 | 12/14/2010 | 1:00:33 AM | WAY-15 | EBD | TV | OCO | 1,539 | 189,755 |
| E460794947 | 12/14/2010 | 1:00:41 AM | ROS-21 | EBD | TV | OCO | 148 | 79,967 |
| E178396133 | 12/14/2010 | 1:00:59 AM | HOB-15 | EBI | TV | OCO | 1,261 | 1,135,499 |
| E058661712 | 12/14/2010 | 1:01:28 AM | VAS-23 | EBL | TV | OFU | 6 | 1,484 |
| E938752752 | 12/14/2010 | 1:02:02 AM | SOO-25 | EBI | TV | OTR | 1,078 | 350,568 |
| E018617274 | 12/14/2010 | 1:02:13 AM | FRG-22 | ECC | TV | OCO | 68 | 25,213 |
| E786856259 | 12/14/2010 | 1:02:15 AM | PIK-23 | EBF | TV | OCO | 73 | 22,831 |
| E235522386 | 12/14/2010 | 1:02:25 AM | ROS-22 | EBD | TF | OCO | 937 | 99,869 |
| E217388322 | 12/14/2010 | 1:02:25 AM | CUM-15 | EBI | TF | OFU | 587 | 151,788 |
| E650498775 | 12/14/2010 | 1:03:51 AM | PIN-27 | EBF | TV | OPO | 300 | 246,045 |
| E373015591 | 12/14/2010 | 1:04:09 AM | BON-13 | ECA | TV | OCO | 1,241 | 563,863 |
| E590922188 | 12/14/2010 | 1:04:15 AM | ING-13 | EBD | TV | OCO | 36 | 34,011 |
| E119029752 | 12/14/2010 | 1:05:12 AM | KCR-16 | EBJ | TV | OCO | 8 | 6,286 |
| E234234238 | 12/14/2010 | 1:05:35 AM | SEQ-22 | EBI | TV | OCO | 263 | 166,794 |
| E578004344 | 12/14/2010 | 1:06:17 AM | WIN-12 | ECE | TV | OFU | 36 | 13,814 |
| E030669635 | 12/14/2010 | 1:06:35 AM | SOO-23 | EBJ | TF | OCO | 1,676 | 262,154 |
| E916423595 | 12/14/2010 | 1:06:38 AM | HWD-23 | EBD | TV | OCO | 13 | 12,199 |
| E691919467 | 12/14/2010 | 1:07:25 AM | RDO-16 | EBJ | TV | OSV | 9 | 8,123 |
| E882864608 | 12/14/2010 | 1:07:50 AM | KWH-25 | EBD | UN | OCO | 1,954 | 252,392 |
| E019293581 | 12/14/2010 | 1:07:56 AM | VIT-23 | EBD | TV | OCO | 257 | 152,161 |
| E104583343 | 12/14/2010 | 1:08:21 AM | VAS-13 | EBL | TV | OCO | 10 | 8,527 |
| E685086415 | 12/14/2010 | 1:08:34 AM | EDG-16 | ECA | TV | OCO | 23 | 10,383 |
| E498115101 | 12/14/2010 | 1:10:01 AM | HOB-16 | EBI | TV | OCO | 259 | 309,906 |
| E729356380 | 12/14/2010 | 1:10:45 AM | EDG-16 | ECA | TV | OCO | 20 | 15,163 |
| E049936010 | 12/14/2010 | 1:12:30 AM | HOL-12 | ECA | TV | OCO | 26 | 18,187 |
| E520285529 | 12/14/2010 | 1:13:11 AM | BDI-13 | EBI | TV | OCO | 236 | 183,329 |
| E494354957 | 12/14/2010 | 1:13:17 AM | LAC-13 | ECC | TV | OFC | 15 | 7,676 |
| E136509852 | 12/14/2010 | 1:13:48 AM | CWD-25 | EBD | TF | OCO | 780 | 195,936 |
| E702747390 | 12/14/2010 | 1:14:13 AM | MTH-13 | EBJ | TV | OPO | 425 | 198,165 |
| E568558764 | 12/14/2010 | 1:14:18 AM | EGT-27 | EBE | TV | OCO | 38 | 32,061 |
| E347134885 | 12/14/2010 | 1:15:01 AM | PLA-23 | EBD | TV | OFC | 32 | 30,047 |
| E265125872 | 12/14/2010 | 1:15:27 AM | LLT-16 | EBD | TV | OCO | 17 | 13,932 |
| E849945101 | 12/14/2010 | 1:16:59 AM | LYO-12 | EBJ | TV | OCO | 3 | 2,049 |
| E790612380 | 12/14/2010 | 1:17:00 AM | BTR-22 | EBE | TF | OCO | 651 | 178,374 |
| E435849510 | 12/14/2010 | 1:19:29 AM | KAP-15 | ECA | TV | OCO | 16 | 6,712 |
| E086967824 | 12/14/2010 | 1:20:55 AM | DUV-12 | EBD | TV | OCO | 186 | 233,260 |
| E504969812 | 12/14/2010 | 1:22:58 AM | MVW-15 | EBJ | TV | OFU | 23 | 9,109 |
| E315102986 | 12/14/2010 | 1:26:01 AM | POU-16 | ECE | TV | OCO | 158 | 82,947 |
| E035679603 | 12/14/2010 | 1:26:17 AM | SME-15 | EBE | TV | OCO | 58 | 17,616 |
| E385515718 | 12/14/2010 | 1:27:35 AM | HAZ-16 | EBE | TV | OCO | 80 | 73,553 |
| E776115133 | 12/14/2010 | 1:28:12 AM | COT-15 | EBD | TV | OCO | 49 | 40,366 |
| E313970728 | 12/14/2010 | 1:30:23 AM | WAB-13 | EBI | TV | OFU | 17 | 6,453 |
| E885137492 | 12/14/2010 | 1:32:17 AM | MWD-16 | EBE | TV | OCO | 13 | 3,090 |
| E988722410 | 12/14/2010 | 1:34:45 AM | PIP-22 | EBI | TV | OCO | 29 | 16,682 |
| E866334358 | 12/14/2010 | 1:35:14 AM | STA-16 | EBJ | TV | OFU | 1 | 865 |
| E830157207 | 12/14/2010 | 1:35:16 AM | BDI-15 | EBI | TV | OCO | 29 | 18,117 |
| E137954036 | 12/14/2010 | 1:35:24 AM | CWD-24 | EBD | TV | OCN | 1 | 935 |
| E590496500 | 12/14/2010 | 1:37:06 AM | PLA-23 | EBF | TV | OCO | 8 | 8,583 |
| E793615438 | 12/14/2010 | 1:38:58 AM | BHS-11 | EAA | TV | OCO | 10 | 3,170 |
| E406306081 | 12/14/2010 | 1:39:34 AM | LOL-23 | ECD | TV | OCO | 40 | 17,617 |
| E018064695 | 12/14/2010 | 1:41:52 AM | AIR-22 | ECC | TV | OTF | 1 | 591 |
| E721277845 | 12/14/2010 | 1:44:53 AM | ROC-16 | ECC | TV | OCO | 1 | 434 |
| E300863053 | 12/14/2010 | 1:49:30 AM | SAH-16 | EBD | TV | OCO | 3 | 2,543 |
| E311387132 | 12/14/2010 | 1:53:27 AM | GRV-15 | ECA | TV | CDH | 42 | 41,645 |
| E848823106 | 12/14/2010 | 1:55:12 AM | KIN-21 | ECE | TV | OFU | 9 | 3,688 |
| E156282465 | 12/14/2010 | 1:55:28 AM | NOB-23 | EBD | TV | OTF | 2 | 1,329 |
| E831030353 | 12/14/2010 | 1:55:29 AM | FAL-15 | EBF | TV | OCO | 7 | 4,803 |
| E471351234 | 12/14/2010 | 1:56:17 AM | LON-17 | ECC | TV | OCO | 29 | 18,958 |
| E156657611 | 12/14/2010 | 1:56:36 AM | BRE-21 | ECE | TV | OCO | 36 | 29,822 |
| E001060644 | 12/14/2010 | 1:56:44 AM | VIS-26 | EAA | TV | OFU | 10 | 966 |
| E454556588 | 12/14/2010 | 1:57:08 AM | LYO-15 | EBJ | TV | OCN | 6 | 4,517 |
| E773141933 | 12/14/2010 | 1:57:26 AM | BLA-13 | EAA | EF | OCO | 48 | 19,179 |
| E101980652 | 12/14/2010 | 2:00:00 AM | BUC-16 | ECA | TV | OTF | 13 | 6,266 |
| E394998364 | 12/14/2010 | 2:00:04 AM | TOL-15 | EBD | TV | OCO | 15 | 11,169 |
| E415765181 | 12/14/2010 | 2:00:16 AM | NHL-13 | EBD | TV | OCO | 8 | 6,478 |
| E829975475 | 12/14/2010 | 2:03:29 AM | LWS-13 | EBI | TV | OCO | 66 | 60,490 |
| E786923712 | 12/14/2010 | 2:03:47 AM | SEM-15 | EAA | TV | UTC | 15 | 1,630 |
| E495283225 | 12/14/2010 | 2:03:48 AM | ROS-15 | EBD | TV | OSV | 5 | 2,531 |
| E258516066 | 12/14/2010 | 2:04:03 AM | SKY-25 | EBD | TV | OCO | 2 | 1,552 |
| E751079618 | 12/14/2010 | 2:04:09 AM | HAP-16 | EAA | TV | OFU | 3 | 523 |
| E966653323 | 12/14/2010 | 2:04:24 AM | MAN-13 | ECD | TV | OFU | 8 | 3,965 |
| E694548935 | 12/14/2010 | 2:07:40 AM | WCA-16 | EBJ | TV | OFU | 1 | 467 |
| E456521990 | 12/14/2010 | 2:08:08 AM | MWD-15 | EBE | TV | OCO | 24 | 5,565 |
| E868196047 | 12/14/2010 | 2:18:45 AM | YEL-25 | ECC | TV | OCO | 37 | 12,367 |
| E127163222 | 12/14/2010 | 2:19:00 AM | KNT-23 | EBJ | TV | OCO | 12 | 14,052 |
| E001682725 | 12/14/2010 | 2:28:51 AM | LLT-17 | EBD | TV | OCO | 32 | 25,957 |
| E947676183 | 12/14/2010 | 2:29:13 AM | SHA-13 | ECA | TV | OCO | 7 | 6,053 |
| E630376048 | 12/14/2010 | 2:33:37 AM | DUT-16 | ECA | TV | OCO | 2,349 | 1,527,301 |
| E375222471 | 12/14/2010 | 2:37:51 AM | GAR-13 | ECA | TV | CDH | 1 | 1,049 |
| E994451061 | 12/14/2010 | 2:40:39 AM | RAI-12 | ECC | TV | OCO | 34 | 17,386 |
| E844732294 | 12/14/2010 | 2:52:54 AM | ORC-13 | EBJ | TV | OCO | 4 | 4,068 |
| E957651033 | 12/14/2010 | 2:54:40 AM | BIG-15 | EAC | TV | UTC | 15 | 2,285 |
| E246400893 | 12/14/2010 | 3:01:47 AM | FWD-16 | EBJ | TV | OHR | 973 | 314,490 |
| E724005158 | 12/14/2010 | 3:04:11 AM | YEL-23 | ECC | TV | OSV | 1 | 786 |
| E203646756 | 12/14/2010 | 3:20:06 AM | WLK-15 | ECA | TV | OPO | 1 | 1,590 |
| E036196709 | 12/14/2010 | 3:22:09 AM | NRU-01 | EBE | TV | OCO | 2,528 | 304,570 |
| E165063282 | 12/14/2010 | 3:24:05 AM | KNM-26 | EBD | TV | OCO | 9 | 863 |
| E800725948 | 12/14/2010 | 3:29:48 AM | PAN-12 | EBJ | TV | OCO | 275 | 24,000 |
| E059663306 | 12/14/2010 | 3:30:45 AM | LMC-25 | EBF | TV | OCO | 18 | 4,307 |
| E784644691 | 12/14/2010 | 3:32:06 AM | ROS-17 | EBD | TV | OCO | 59 | 18,107 |
| E707304207 | 12/14/2010 | 3:39:09 AM | MER-16 | EBE | EF | OCO | 10 | 9,499 |
| E022208916 | 12/14/2010 | 3:51:11 AM | PAN-15 | EBJ | TV | OTF | 2 | 920 |
| E910307048 | 12/14/2010 | 4:24:50 AM | FAL-13 | EBF | TV | OTF | 3 | 826 |
| E653724830 | 12/14/2010 | 4:26:13 AM | MIR-15 | EBF | TV | OCR | 462 | 345,104 |
| E480945800 | 12/14/2010 | 4:28:16 AM | MIR-16 | EBF | TV | OCO | 51 | 37,573 |
| E392478681 | 12/14/2010 | 4:29:53 AM | SOO-23 | EBI | TV | OTR | 5 | 4,401 |
| E153400655 | 12/14/2010 | 4:32:31 AM | ELL-13 | EBI | TV | OCO | 558 | 234,072 |
| E532194200 | 12/14/2010 | 4:36:52 AM | KWH-25 | EBE | TV | OCO | 278 | 109,291 |
| E294089321 | 12/14/2010 | 4:37:28 AM | CUM-13 | EBI | TV | OFU | 5 | 1,288 |
| E437430381 | 12/14/2010 | 4:43:04 AM | MVW-13 | EBJ | TV | OFC | 144 | 68,246 |
| E901085818 | 12/14/2010 | 4:48:58 AM | WIN-13 | ECE | TV | OTF | 1 | 455 |
| E011216574 | 12/14/2010 | 4:56:59 AM | SIN-25 | ECD | TV | OCO | 28 | 11,648 |
| E696109025 | 12/14/2010 | 5:27:38 AM | LAT-14 | EBJ | TV | OCO | 6 | 4,334 |
| E923421699 | 12/14/2010 | 5:41:19 AM | GRV-16 | ECA | TV | OSV | 4 | 2,875 |
| E159356165 | 12/14/2010 | 5:47:47 AM | NBE-12 | EBF | TV | OCO | 10 | 4,022 |
| E810178918 | 12/14/2010 | 5:49:59 AM | WAY-15 | EBD | TV | OCO | 45 | 9,001 |
| E027649353 | 12/14/2010 | 5:50:19 AM | KNM-23 | EBD | TV | OCO | 3 | 1,694 |
| E705458143 | 12/14/2010 | 5:56:59 AM | SHE-17 | ECE | TV | OCO | 34 | 20,503 |
| E388848832 | 12/14/2010 | 6:02:24 AM | MOT-14 | ECC | TV | OCO | 40 | 11,544 |
| E958424900 | 12/14/2010 | 6:09:00 AM | LAC-17 | ECC | TV | OTR | 2 | 1,904 |
| E592600185 | 12/14/2010 | 6:13:54 AM | HAP-16 | EAA | EF | OCO | 160 | 38,576 |
| E453120696 | 12/14/2010 | 6:16:01 AM | SHA-15 | ECA | TV | OCO | 8 | 5,504 |
| E358931937 | 12/14/2010 | 6:17:32 AM | PLG-16 | ECC | TV | OCO | 41 | 11,499 |
| E269172269 | 12/14/2010 | 6:17:51 AM | COT-13 | EBD | TV | OCR | 5 | 2,436 |
| E728248409 | 12/14/2010 | 6:26:46 AM | AIR-23 | ECC | TV | OCO | 11 | 7,230 |
| E470582657 | 12/14/2010 | 6:27:56 AM | CUM-15 | EBI | TV | OPO | 19 | 15,619 |
| E264551148 | 12/14/2010 | 6:28:55 AM | SEM-15 | EAA | TV | OCO | 7 | 2,038 |
| E648752865 | 12/14/2010 | 6:31:17 AM | MIR-17 | EBF | TV | OCO | 12 | 10,953 |
| E980330119 | 12/14/2010 | 6:44:35 AM | LMD-12 | EBJ | TV | OTF | 5 | 577 |
| E395348045 | 12/14/2010 | 6:57:27 AM | KCR-17 | EBJ | TV | OCO | 6 | 3,315 |
| E777739778 | 12/14/2010 | 7:03:33 AM | LWS-16 | EBI | TV | OCO | 1 | 366 |
| E841858237 | 12/14/2010 | 7:08:49 AM | FCR-14 | EBJ | TV | OPO | 5 | 4,891 |
| E495802932 | 12/14/2010 | 7:14:50 AM | GAR-16 | ECA | TV | OSV | 1 | 564 |
| E978702391 | 12/14/2010 | 7:18:00 AM | LMD-16 | EBJ | TV | OTF | 4 | 408 |
| 10990796 | 12/14/2010 | 7:22:00 AM | SIL-15 | ECD | TV | OCO | 51 | 11,016 |
| E782538046 | 12/14/2010 | 7:27:22 AM | ORT-22 | ECA | TV | CDH | 1 | 378 |
| E449136190 | 12/14/2010 | 7:28:48 AM | EVE-23 | EBD | TV | OSV | 1 | 271 |
| E813280118 | 12/14/2010 | 7:39:35 AM | SWI-17 | ECC | TV | OSV | 1 | 241 |
| 10987094 | 12/14/2010 | 7:43:00 AM | ANA-16 | EAC | EF | OFU | 1 | 14 |
| 10990743 | 12/14/2010 | 7:44:00 AM | BLU-17 | ECC | TV | OCO | 298 | 52,746 |
| E014873190 | 12/14/2010 | 7:53:16 AM | DUV-15 | EBD | TV | OCO | 49 | 12,405 |
| E661413106 | 12/14/2010 | 7:55:03 AM | PRI-23 | ECC | TV | OCO | 5 | 1,665 |
| E452659790 | 12/14/2010 | 8:09:42 AM | EGT-16 | EBE | TV | OSV | 1 | 496 |
| E939084969 | 12/14/2010 | 8:13:51 AM | KIT-25 | EBH | EF | OJU | 5 | 701 |
| E614988073 | 12/14/2010 | 8:15:09 AM | SAH-17 | EBD | TV | OCO | 13 | 9,943 |
| E766042197 | 12/14/2010 | 8:17:51 AM | FNW-16 | ECD | TV | OCO | 56 | 22,352 |
| E567319097 | 12/14/2010 | 8:28:12 AM | FAC-14 | EBE | TV | OCO | 18 | 4,352 |
| E602169515 | 12/14/2010 | 8:43:52 AM | MTH-15 | EBJ | TV | OCO | 2 | 312 |
| E567391515 | 12/14/2010 | 8:55:03 AM | WAU-22 | EBI | TV | OSW | 1,004 | 129,466 |
| E106388013 | 12/14/2010 | 9:04:34 AM | LEA-17 | EBI | TV | OCO | 35 | 5,901 |
| E013388006 | 12/14/2010 | 9:08:11 AM | FCR-12 | EBI | TV | OCO | 9 | 7,756 |
| E200491533 | 12/14/2010 | 9:12:38 AM | GRI-13 | ECC | TV | OSV | 2 | 253 |
| E010705222 | 12/14/2010 | 9:13:37 AM | PIK-21 | EBF | TV | OCO | 17 | 10,666 |
| E386027894 | 12/14/2010 | 9:16:05 AM | WAY-15 | EBD | TV | OSV | 5 | 1,670 |
| 10986891 | 12/14/2010 | 9:19:00 AM | KLA-15 | EBE | TV | OCO | 7 | 84 |
| E202110928 | 12/14/2010 | 9:24:08 AM | WAY-13 | EBD | TV | OSV | 1 | 416 |
| E467578709 | 12/14/2010 | 9:27:13 AM | KAP-15 | ECA | TV | OCO | 16 | 4,301 |
| E999068909 | 12/14/2010 | 9:28:10 AM | VIS-26 | EAA | EF | OPO | 1 | 272 |
| E473944226 | 12/14/2010 | 9:33:29 AM | KCR-16 | EBJ | TV | OCO | 27 | 7,736 |
| E472854497 | 12/14/2010 | 9:46:41 AM | HWD-22 | EBD | LI | OCO | 66 | 17,901 |
| E377583679 | 12/14/2010 | 9:54:09 AM | NOR-23 | EBD | TV | OSV | 1 | 479 |
| E266897829 | 12/14/2010 | 9:55:30 AM | WAB-13 | EBI | TV | OCO | 7 | 2,867 |
| E059075932 | 12/14/2010 | 10:16:37 AM | BLU-13 | ECC | TV | OCO | 4 | 1,570 |
| E955093724 | 12/14/2010 | 10:20:39 AM | ROS-21 | EBD | TV | OCO | 62 | 24,760 |
| E690910261 | 12/14/2010 | 10:21:18 AM | FAL-13 | EBF | TV | OCO | 1 | 519 |
| E506541694 | 12/14/2010 | 10:29:00 AM | RHO-16 | ECA | TF | OFC | 2,369 | 133,035 |
| E852808313 | 12/14/2010 | 10:40:35 AM | ENU-17 | EBI | TV | OFU | 2 | 209 |
| E061208976 | 12/14/2010 | 10:41:25 AM | HAP-13 | EAA | EF | USV | 1 | 99 |
| E702044430 | 12/14/2010 | 10:46:30 AM | LOL-21 | ECD | TV | OCO | 12 | 2,094 |
| E853456461 | 12/14/2010 | 10:48:11 AM | ELD-25 | ECC | TV | OCO | 9 | 331 |
| E668243150 | 12/14/2010 | 10:50:05 AM | POU-16 | ECE | TV | OCO | 165 | 117,466 |
| E478946023 | 12/14/2010 | 10:54:13 AM | GRI-15 | ECC | TV | OCO | 50 | 8,639 |
| E636185370 | 12/14/2010 | 10:57:32 AM | VAS-13 | EBL | TV | OFU | 72 | 14,434 |
| E387869619 | 12/14/2010 | 11:03:56 AM | MIL-22 | ECE | TV | OSV | 1 | 66 |
| E127911718 | 12/14/2010 | 11:14:09 AM | YEL-27 | ECC | TV | OCO | 40 | 8,434 |
| E322122865 | 12/14/2010 | 11:21:59 AM | PRI-13 | ECC | TV | OFU | 132 | 14,126 |
| 10986962 | 12/14/2010 | 11:37:00 AM | MAP-13 | EBE | EF | USV | 1 | 482 |
| E721625036 | 12/14/2010 | 12:04:42 PM | PRE-14 | EBE | TV | OCO | 3 | 1,630 |
| E136581578 | 12/14/2010 | 12:05:21 PM | MIR-13 | EBF | TV | OCO | 706 | 69,647 |
| E846895292 | 12/14/2010 | 12:10:41 PM | BLU-16 | ECC | TV | OCO | 55 | 17,892 |
| E814559792 | 12/14/2010 | 12:10:45 PM | SIN-25 | ECD | TV | OCO | 1 | 862 |
| E223450407 | 12/14/2010 | 12:13:56 PM | PAT-17 | ECC | TV | OSV | 1 | 126 |
| E667513593 | 12/14/2010 | 12:17:56 PM | BAR-15 | ECC | TV | OTF | 4 | 396 |
| E109127130 | 12/14/2010 | 12:22:52 PM | MIL-22 | ECE | TV | OCO | 7 | 6,161 |
| E223308610 | 12/14/2010 | 12:25:04 PM | FRA-12 | ECD | TV | OCO | 107 | 29,418 |
| E302179909 | 12/14/2010 | 12:28:17 PM | OVE-15 | EBE | TV | OCO | 1 | 557 |
| E530284235 | 12/14/2010 | 12:33:21 PM | CLY-27 | EBE | TV | OCO | 113 | 29,453 |
| E419478626 | 12/14/2010 | 12:42:00 PM | PRE-13 | EBE | TV | OCO | 328 | 70,848 |
| E343165523 | 12/14/2010 | 12:42:27 PM | NBE-13 | EBF | TV | OPO | 1 | 228 |
| E863706864 | 12/14/2010 | 1:04:48 PM | FRA-12 | ECD | TV | OPO | 14 | 13,387 |
| E765406417 | 12/14/2010 | 1:06:23 PM | SHE-25 | ECE | TV | OCO | 9 | 1,923 |
| E109588094 | 12/14/2010 | 1:08:21 PM | BTR-22 | EBD | TV | OCO | 2 | 833 |
| E772966638 | 12/14/2010 | 1:08:33 PM | HKX-16 | EAC | EF | OTF | 5 | 257 |
| E250299217 | 12/14/2010 | 1:12:46 PM | WOB-26 | EAA | EF | USV | 1 | 47 |
| E993680852 | 12/14/2010 | 1:16:31 PM | LON-17 | ECC | TV | OCO | 19 | 2,669 |
| E411024954 | 12/14/2010 | 1:17:11 PM | CHI-12 | ECD | TV | OCO | 20 | 10,756 |
| E285847958 | 12/14/2010 | 1:20:08 PM | NBE-16 | EBF | TV | OCO | 2 | 140 |
| E390633159 | 12/14/2010 | 1:22:22 PM | KWH-25 | EBE | EF | OTF | 7 | 2,328 |
| E418335087 | 12/14/2010 | 1:28:02 PM | FAC-12 | EBE | PO | USV | 1 | 285 |
| E119371332 | 12/14/2010 | 1:33:39 PM | BRW-15 | EAC | TV | OCO | 26 | 10,551 |
| E684435478 | 12/14/2010 | 1:40:16 PM | SWD-12 | ECE | TV | OCO | 32 | 9,335 |
| E210127886 | 12/14/2010 | 1:41:13 PM | LAT-17 | EBJ | TV | OCO | 174 | 54,598 |
| E830686804 | 12/14/2010 | 1:55:11 PM | BIG-15 | EAC | TV | OFU | 25 | 3,345 |
| 10987098 | 12/14/2010 | 2:05:00 PM | NUG-26 | EAA | TV | OFU | 1 | 62 |
| E450892656 | 12/14/2010 | 2:18:26 PM | DUV-13 | EBD | TV | OCO | 7 | 1,180 |
| E794572568 | 12/14/2010 | 2:24:21 PM | NLM-15 | EAC | TV | OFU | 50 | 3,133 |
| E323657053 | 12/14/2010 | 2:24:58 PM | MVW-13 | EBJ | TV | OSV | 7 | 1,085 |
| E715533964 | 12/14/2010 | 2:25:25 PM | VAS-13 | EBL | TV | OCO | 41 | 33,119 |
| E320042023 | 12/14/2010 | 2:26:18 PM | MAN-13 | ECD | TV | OSV | 3 | 332 |
| E792196689 | 12/14/2010 | 2:33:47 PM | MHT-15 | EBJ | TV | OSV | 9 | 1,496 |
| E745882474 | 12/14/2010 | 2:58:02 PM | PLU-25 | ECC | TV | OCO | 5 | 2,110 |
| E039564474 | 12/14/2010 | 2:58:07 PM | KAP-16 | ECA | TV | CDH | 30 | 3,507 |
| 10987105 | 12/14/2010 | 3:01:00 PM | HAZ-16 | EBE | TV | OCO | 13 | 1,475 |
| E347179742 | 12/14/2010 | 3:27:25 PM | PRI-13 | ECC | TV | OSV | 1 | 153 |
| E915066670 | 12/14/2010 | 3:28:21 PM | SHE-15 | ECE | TV | OPO | 21 | 12,488 |
| E015375963 | 12/14/2010 | 3:35:35 PM | PHA-13 | EBE | TV | OTF | 3 | 262 |
| E578015235 | 12/14/2010 | 3:59:10 PM | ROC-17 | ECC | TV | OTR | 1 | 238 |
| E201264307 | 12/14/2010 | 4:22:56 PM | BRE-11 | ECD | TV | OSV | 2 | 570 |
| E440582899 | 12/14/2010 | 4:25:25 PM | PGA-12 | ECE | TV | OCO | 1 | 127 |
| E079119399 | 12/14/2010 | 4:29:17 PM | PHA-16 | EBE | PO | OSV | 2 | 601 |
| E196696001 | 12/14/2010 | 4:39:17 PM | PAT-15 | ECC | TV | OCO | 22 | 2,656 |
| E269906992 | 12/14/2010 | 4:40:08 PM | MKI-14 | ECC | TV | OSV | 1 | 63 |
| E331776978 | 12/14/2010 | 4:49:29 PM | PAN-13 | EBJ | TV | UHH | 11 | 6,001 |
| E037357965 | 12/14/2010 | 4:50:00 PM | MIR-16 | EBF | EF | OCO | 60 | 6,420 |
| E461177699 | 12/14/2010 | 4:53:29 PM | BUC-16 | ECA | TV | CDH | 36 | 4,706 |
| E238146073 | 12/14/2010 | 5:05:19 PM | FNW-13 | ECD | TV | OCO | 4 | 1,495 |
| E685698719 | 12/14/2010 | 5:13:41 PM | ROS-21 | EBD | TV | OCO | 6 | 1,034 |
| E162402636 | 12/14/2010 | 5:16:04 PM | SKE-22 | ECE | TV | OCO | 50 | 6,697 |
| E312462149 | 12/14/2010 | 5:17:29 PM | PTR-14 | EAA | TV | OTF | 1 | 137 |
| E194602412 | 12/14/2010 | 5:18:01 PM | FNW-15 | ECD | TV | OCO | 22 | 9,526 |
| E265204808 | 12/14/2010 | 5:27:51 PM | KAP-16 | ECA | TV | CDH | 4 | 2,770 |
| E873350811 | 12/14/2010 | 5:41:07 PM | FRA-12 | ECD | TV | OFU | 23 | 4,781 |
| E224353785 | 12/14/2010 | 5:49:00 PM | LWS-13 | EBI | TV | OFU | 16 | 1,680 |
| E906595122 | 12/14/2010 | 5:56:54 PM | MIR-15 | EBF | TV | OCO | 49 | 12,892 |
| E749362469 | 12/14/2010 | 5:58:39 PM | FAL-15 | EBF | TV | OTF | 1 | 275 |
| E379873265 | 12/14/2010 | 6:13:51 PM | SWE-23 | EBJ | TV | OTF | 6 | 757 |
| E079693416 | 12/14/2010 | 6:14:25 PM | EDG-15 | ECA | EF | USV | 1 | 193 |
| E028805099 | 12/14/2010 | 6:18:37 PM | WAB-13 | EBI | TV | OTF | 2 | 223 |
| E462808915 | 12/14/2010 | 6:19:17 PM | FRG-23 | ECC | TV | OTF | 3 | 113 |
| 10986989 | 12/14/2010 | 7:00:00 PM | KNT-37 | EBJ | EF | USV | 1 | 80 |
| E579552255 | 12/14/2010 | 7:12:39 PM | GBK-13 | EAD | PO | USV | 1 | 196 |
| E459830938 | 12/14/2010 | 7:13:11 PM | WOD-13 | EBH | TV | OTF | 2 | 344 |
| E379723373 | 12/14/2010 | 7:24:48 PM | WAY-15 | EBD | TV | OSV | 1 | 205 |
| E658990061 | 12/14/2010 | 7:35:50 PM | SOO-25 | EBI | TV | OSV | 7 | 799 |
| E711366445 | 12/14/2010 | 9:17:28 PM | BLU-16 | ECC | TV | OFC | 10 | 1,594 |
| E530435736 | 12/14/2010 | 9:47:41 PM | YEL-25 | ECC | TV | OFC | 5 | 967 |
| E420847297 | 12/14/2010 | 10:09:56 PM | ELD-25 | ECC | TV | OFC | 1 | 630 |
| E860630234 | 12/14/2010 | 10:13:05 PM | AIR-22 | ECC | EF | OFU | 20 | 2,703 |
| 10987026 | 12/14/2010 | 10:33:00 PM | LAC-17 | ECC | TV | OPO | 1 | 239 |

### Terms, Codes and Definitions Used on Detail Reports

| #### Notification | [Notification Number] A number assigned by SAP, identifying the outage record |
| --- | --- |
| Date | The date of the outage |
| Time | The time of the outage |
| Circuit | [Reference Circuit] The circuit identifier for the affected circuit |

|  | Area | [Maintenance Planner Group] A code representing the energy, region and service center |  |
| --- | --- | --- | --- |
|  |  | EAA – Bellingham | EBJ – South King |
|  |  | EAB – Lynden | EBK – Southwest King |
|  |  | EAC – Skagit | EBL – Vashon |
|  |  | EAD – Whidbey | ECA – Puyallup |
|  |  | EBD – Redmond | ECC – Olympia |
|  |  | EBE – Factoria | ECD – Port Orchard |
|  |  | EBF – Snoqualmie | ECE – Poulsbo |
|  |  | EBI – Enumclaw | ECF – Port Townsend |
|  | Cause | Cause of Outage |  |
|  |  | AO – Accident Other | EF – Equipment Failure |
|  |  | BA – Bird or Animal | EO – Electrical Overload |
|  |  | CP – Car Pole | FI – Faulty Installation |
|  |  | CR – Customer Request | TF – Tree Off Right-of-Way |
|  |  | DU – Dig-up Underground | TO – Tree On Right-of-Way |
|  |  | TV – Trees/Vegetation | SO – Scheduled Outage |
|  |  | UN – Unknown |  |
| Equipment |  | Affected by, or involved in the outage |  |
|  |  | OCN – Connector | OSW – Overhead Switch |
|  |  | OCO – Overhead Conductor | OTF – Overhead Transformer Fuse |
|  |  | OCR – Crossarm | OTR – Overhead Transformer |
|  |  | OFC – Overhead Cut-out | OUP – OH to UG Primary |
|  |  | OFS – Overhead Fire Signal | OUS – OH to UG Secondary Service |
|  |  | OFU – Fuse Link/OH Line Fuse | SBF – High-side Bank Fuse |
|  |  | OGS – Span Guy | SCB – Power Circuit Breaker |
|  |  | OHR – Overhead Recloser | UOT – Underground Outdoor Term |
|  |  | OIN – Insulator | UPC – Underground Primary Cable |
|  |  | OJU- Jump Wire | UPT – Padmount Transformer |
|  |  | OPI – Overhead Pin Insulator | USV – Underground Service |
|  |  | OPO – Pole | UTC – Underground Terminal Fuse |
|  |  | OSV – Overhead Service | UTR – Submersible Transformer |
|  |  | ORE – Regulator |  |

| CUST OUT | [Customer Out] The number of customers without power for any given outage record |
| --- | --- |
| CUST MIN | [Customer Minutes] The total number of minutes customers were without power for any given record |

### Media Coverage

Tuesday, December 14, 2010 - Page updated at 04:46 PM

ALAN BERNER / THE SEATTLE TIMES

Steve Glass, father of Chaya Glass who lives in this brick home in North Seattle, checks storm damage Tuesday.

- 3 trees clobber N. Seattle house; another hits next door

By Susan Gilmore

Seattle Times staff reporter

Brian Pennington had just gone to bed about midnight, with the wind blowing fiercely outside and the power out, when he joked that maybe a tree will fall down in his back yard.

Not one, but three trees fell onto Pennington's house on Northeast 120th Street near Northgate, smashing windows, burying his car and blocking his front door.

Pennington and roommate Chaya Glass escaped unhurt by opening a window and crawling out.

Pennington then called his grandfather, William Pennington, who owns the brick home.

"The fact that no one got hurt is what really counts," said William Pennington, standing outside his broken house in the rain. "The rest is just sticks and stones. It was such good news. The only thing I cared about were the people inside."

One tree split the roof, wedging between the two bedrooms shared by Pennington, Glass and another roommate.

"It was really scary," said Glass, who escaped with her frightened dog. She grabbed a flashlight, her cellphone, some clothes and her laptop computer before fleeing the house.

Sue Elrum, Glass' mother, said she was awakened early Tuesday by a phone call from her daughter and rushed to Seattle from her home in Mill Creek. "Thankfully everyone's OK," she said. "It sure makes you want to go out and get a brick home."

William Pennington said the house, which used to belong to his mother, was built in 1951 and there's never been any problems with fallen trees. "There's been a lot of fallen branches, but nothing like this."

Next door, a tree fell on David Wu's house, punching a hole through the bedroom where his disabled father was sleeping. There are cracks in the walls and blood on the carpet where Wu hit his head trying to reach his father. Wu ended up in the emergency room to get stitches for his head injury.

"It was really loud," said Wu's mother, Grace Wu, who was also in the house when the storm hit.

Susan Gilmore: 206-464-2054 or sgilmore@seattletimes.com

Copyright © The Seattle Times Company

Tuesday, December 14, 2010 - Page updated at 08:15 AM

- Storm cuts power to thousands; teen dies in house hit by car

By Jack Broom

A fierce storm system tore through Western Washington early Tuesday, toppling trees, cutting power to tens of thousands and possibly contributing to a fatal accident in which a car ran off a road in Lacey, hitting a house and killing a teenager inside.

The storm hit even as rivers were receding and crews were making progress reopening flooded roads.

Lacey neighbors KOMO Radio that power was out at the time of the crash there at 12:30 a.m. and the driver may have not seen the street end near the mobile home park. A 16-year-old boy sleeping in the house was killed. Police reported that the two occupants of the car had fled the scene.

In other outages, Puget Sound Energy reported 30,000 customers losty power in the storm, mostly in King and Thurston counties. By 8 a.m., the number without power was down to 12,000, and the utility said it hoped to restore the rest later Tuesday.

Seattle City Light reported more than 8,600 customers without power, with all but about 750 back on line by 7 a.m. Grays Harbor PUD had 2,300 outages around midnight, according to The Associated Press.

Copyright © The Seattle Times Company

December 14, 2010 at 5:04 AM

- Thunderstorms rumble through Western Washington

Posted by Seattle Times staff

Already soggy from heavy weekend rains, Western Washington was hit by a squall line of thunderstorms overnight that knocked out power in places with gusty winds and falling limbs.

The National Weather Service reports peak gusts of 70 mph at Hoquiam, 51 at Sea-Tac Airport, 45 at the Tacoma Narrows, and 35 at Chehalis.

Puget Sound Energy reports 30,000 outages early Tuesday at 190 locations, mostly in King and Thurston counties. Spokeswoman MacKenzie McDowell told KIRO-TV the utility hoped to have service restored later Tuesday.

Seattle City Light reported 8,600 outages, and restored most of them in a few hours.

Grays Harbor PUD had 2,300 outages around midnight. Spokeswoman Liz Anderson told KBKW most were quickly restored.

---

With information from: KIRO-TV, KBKW

December 14, 2010 at 10:29 AM

- Falling tree kills woman in Kitsap County

Posted by Jack Broom

A Kitsap County woman was killed early Tuesday when a large tree crashed onto her single-wide mobile home in the Southworth area.

South Kitsap Fire and Rescue Capt. Nathan Post said neighbors reported the tree falling at about 12:30 a.m.

The tree landed directly on the back end of the mobile home, where the woman's bedroom is, Post said. She was dead by the time firefighters reached her, Post said.

The Kitsap County Coroner's Office identified the woman as Diane Walker, 55.

Post said she was the only occupant of the mobile home.