## Elec-Gas
Heating Fuel Cost Comparison
The purpose of this calculator is to show how Avista determines the cost savings that can be expected when a customer converts their heating system from electric resistance to natural gas. The example below is for an average residential customer with a 2,000 square foot home (1,000 square feet on the main floor with a full basement). The annual heating load for the home is calculated on a seperate tab using heat loss and gain equations along with heating degree day information for Spokane, WA. It is generally accpeted that electric resistive heat is 100% efficient, 90% gas efficiency was chosen as that is the minimum efficieny required to qualify for an incentive through our prescriptive HVAC incentive program.
Fuel Heating Value |  | Equipment Information |  |  |  | User Input Cells
Electric(BTU/KWH) | 3412 |  | Efficiency | Fuel Type |  | Calculated Cells
Natural gas (BTU/Therm) | 100000 | Existing | 100% | Electric
|  | Proposed | 90% | Natural Gas
Fuel Costs
Electric ($/KWH) | 0.1008 | Equipment Energy Usage
Electric Monthly service charge | 8.5 |  | Fuel Usage | Cost | BTU's consumed | BTU's delivered to home
Natural gas ($/Therm) | 0.7898 | Existing (KWH) | 14308 | 1544.2464 | 48818896 | 48818896
Gas Monthly service charge | 9 | Proposed (Therm) | 542.4322 | 536.4129 | 54243217.7778 | 48818896
|  | Annual Savings: |  | 1007.8335
|  | Annual Savings %: |  | 65.26%

## Home Use Estimator
This calculator is used to estimate the annual heating costs for a building based on the criteria listed in the cells below. Heat loss and gain calculations are calculated using the provided information along with WA State Non-Res Energy code values (Insulation R-values, widow U-values, lighting density, etc) that correspond with the selected remodel dates in addition to the heating degree days associated with the selected location. All calculations can be seen on the 'Calculations' tab.
Home Heating Use Estimator
Customer Information |  |  |  |  | Inputs | Degree Days | Heating | Cooling | Building Type | SF/person | BTU/h per person (Sensible) | Lighting Density W/SF | Estimated annual hours | HVAC Type |  | Cooling Efficiency | Heating Efficiency | Year Remodeled | Roof Component U (BTU/hr*ºF*ft2) | Wall U (BTU/hr*ºF*ft2) | Window U (BTU/hr*ºF*ft2) | HVAC Type |  | Cooling Efficiency | Heating Efficiency
| Name: | Average Electric Heat Customer |  |  | Output | CDA | 6820 | 823 | Office | 200 | 245 | 0.66 | 2080 | Existing | Proposed | COP | AFUE | 1984 or older | 0.07 | 0.08 | 0.75 | Existing | Proposed | COP | AFUE
| Account Number: |  |  |  |  | Spokane | 5166 | 681 | School | 75 | 250 | 0.7 | 1950 | Gas | Gas | SEER | HSPF | 1985-1991 | 0.05 | 0.07 | 0.6 | Gas | Gas | SEER | HSPF
Building Specifications | [5 empty] | Lewiston | 5166 | 1246 | Church | 50 | 225 | 0.8 | 600 | Electric Resistance | Electric Resistance | EER | COP | 1992-1994 | 0.031 | 0.062 | 0.6 | Electric Resistance | Electric Resistance | EER | COP
| Area (Square Feet) |  | 2000 |  |  | Pullman | 6683 | 690 | Service-Food | 150 | 275 | 0.71 | 4368 | Heat Pump | Heat Pump | kW/Ton |  | 1995-1997 | 0.031 | 0.062 | 0.6 | Heat Pump | Heat Pump | kW/Ton
| Roof Area (Square Feet) |  | 1000 |  |  | Sandpoint | 7419 | 525 | Health-Care | 200 | 305 | 0.7 | 4368 |  |  |  |  | 1998-2000 | 0.031 | 0.062 | 0.6
| Exterior Wall Area (Square Feet) |  | 1000 |  |  | Colville | 6996 | 924 | Manufacturing | 200 | 580 | 0.89 | 4368 |  |  |  |  | 2001-2003 | 0.031 | 0.044 | 0.44
| % Glazing (estimate for all sides) |  | 30% | [5 empty] | Warehouse | 500 | 250 | 0.4 | 4368 |  |  |  |  | 2004-2006 | 0.031 | 0.044 | 0.44
| Last Year Remodeled |  | 1992-1994 | [5 empty] | Residential | 624 | 250 | 0.66 | 4380 |  |  |  |  | 2007-2009 | 0.031 | 0.044 | 0.44
| Project Cost | [7 empty] | Retail | 300 | 250 | 1.01 | 4368 |  |  |  |  | 2010-2012 | 0.03 | 0.084 | 0.44
| Project Type |  | Residential | [14 empty] | 2013-2015 | 0.028 | 0.07 | 0.415
| Location |  | Spokane | [14 empty] | >2016 | 0.027 | 0.066 | 0.3
Heating
| Existing System Type | Electric Resistance
Existing Efficiency
|  | Heating | 14308.0311 | kWh
#REF!

## Calculations
| Name: |  | 0 |  |  |  | Degree Days | Heating | Cooling | Building Type | SF/person | BTU/h per person (Sensible) | Lighting Density W/SF | Estimated annual hours (Heating season) | Estimated annual hours (Cooling Season) | HVAC Type |  | Cooling Efficiency | Heating Efficiency
| Account Number: |  | 0 |  |  |  | CDA | 6820 | 681 | Office | 200 | 245 | 0.66 | 1248 | 832 | Existing | Proposed | COP | AFUE
| Area (Square Feet) |  | 10000 | <10,000 SF |  |  | Spokane | 6589 | 823 | School | 75 | 250 | 0.7 | 1170 | 780 | Gas | Gas | SEER | HSPF
| Annual Energy Cost |  | 1 |  |  |  | Lewiston | 5166 | 1246 | Church | 50 | 225 | 0.8 | 360 | 240 | Electric Resistance | Electric Resistance | EER | COP
| Project Cost |  | 1 |  |  |  | Pullman | 6683 | 690 | Service-Food | 150 | 275 | 0.71 | 2620.8 | 1747.2 | Heat Pump | Heat Pump | kW/Ton
| Project Type |  | Service-Food |  |  | FALSE | Sandpoint | 7419 | 525 | Health-Care | 200 | 305 | 0.7 | 2620.8 | 1747.2
| Location |  | Spokane |  |  |  | Colville | 6996 | 924 | Manufacturing | 200 | 580 | 0.89 | 2620.8 | 1747.2
| Existing System Type |  | Gas | [6 empty] | Warehouse | 500 | 250 | 0.4 | 2620.8 | 1747.2
| Original Heating Efficiency |  | 75 | AFUE | [5 empty] | Residential | 624 | 250 | 0.66 | 2628 | 1752
| Proposed Heating Efficiency |  | 80 | AFUE | [5 empty] | Retail | 300 | 250 | 1.01 | 2620.8 | 1747.2
[7 empty] | Thermal Conductivity of Air (BTU/ft3*ºF) | 0.0157
| Existing Cooling Efficiency |  | 7.5 | EER | [5 empty] | Year Remodeled | Roof Component U (BTU/hr*ºF*ft2) | Wall Component U (BTU/hr*ºF*ft2) | Window U (BTU/hr*ºF*ft2) | SHGC | Infiltration (ACH)
| Proposed Cooling Efficiency |  | 11 | EER |  |  | Average Daily Solar Irradiance |  |  | 1984 or older | 0.07 | 0.3 | 0.75 | 0.7 | 0.25
[10 empty] | 1985-1991 | 0.05 | 0.2 | 0.6 | 0.7 | 0.25
[7 empty] | Direction | ED |  | 1992-1994 | 0.035 | 0.062 | 0.6 | 0.7 | 0.25
[7 empty] | North | 0.071484 |  | 1995-1997 | 0.031 | 0.062 | 0.6 | 0.6 | 0.25
| Energy Savings |  | #REF! | Therms |  |  | NE/NW | 0.1235 |  | 1998-2000 | 0.031 | 0.062 | 0.6 | 0.6 | 0.2
|  |  | #REF! | kWh |  |  | E/W | 0.23988 |  | 2001-2003 | 0.031 | 0.054 | 0.44 | 0.6 | 0.2
[7 empty] | SE/SW | 0.34322 |  | 2004-2006 | 0.031 | 0.054 | 0.44 | 0.6 | 0.2
[7 empty] | South | 0.37539 |  | 2007-2009 | 0.031 | 0.054 | 0.44 | 0.4 | 0.2
[7 empty] | Horizontal | 0.36741 |  | 2010-2012 | 0.031 | 0.054 | 0.44 | 0.4 | 0.2
[7 empty] | Values found in the 1997 ASHRAE Fundamentals Handbook. Chapter 29, tables 17 & 18. |  |  | 2013-2015 | 0.031 | 0.054 | 0.415 | 0.4 | 0.2
[10 empty] | >2016 | 0.031 | 0.054 | 0.3 | 0.4 | 0.2
Home Estimator
Window Square Footage | 300
Window SF per direction | 75
HDD | 6589
CDD | 823
Internal Heat Gains
Building Population | 3.2051
Heating Season
People Heat gain | 1750000 | BTU |  | Energy Savings
Lighting Gain | 1734480 | BTU |  | Existing Heating Eff. | 3412 | BTU/kWh
Cooling Season
People Heat gain | 842307.6923 | BTU |  | Existing Annual Heat | 14308.0311 | kWh
Lighting Gain | 1156320 | BTU
Shell Losses
Roof U-Value | 0.035 | (BTU/hr*ºF*ft2)
Wall U-Value | 0.062 | (BTU/hr*ºF*ft2)
Window U-Value | 0.5 | (BTU/hr*ºF*ft2)
Window SHGC | 0.4
Heating Season
Roof Heat Loss | 6364974 | BTU
Wall Heat Loss | 9804432 | BTU
Window Heat Loss | 23720400 | BTU
Cooling Season
Roof Heat Gain | 691320 | BTU
Wall Heat Gain | 1224624 | BTU
Window Heat Gain | 15138809.127 | BTU
Infiltration Losses
Infiltration Rate | 0.25 | ACH
Infiltration Losses (Heating) | 12413676 | BTU
Infiltration Losses (Cooling) | 1550532 | BTU