- EXHIBIT NO. ___(SML-1T)
DOCKET NO. PG-041624
WITNESS:  SUSAN MCLAIN

BEFORE THE

WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION

| WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION, Complainant, v. PUGET SOUND ENERGY, INC., Respondent. |  | Docket No. PG-041624 |
| --- | --- | --- |

PREFILED DIRECT TESTIMONY OF
SUSAN MCLAIN 
ON BEHALF OF PUGET SOUND ENERGY, INC.

AUGUST 15, 2005

# PUGET SOUND ENERGY, INC.

# PREFILED DIRECT TESTIMONY OF SUSAN MCLAIN

# CONTENTS

I.	INTRODUCTION	1

II.	SCOPE OF TESTIMONY	2

III.	SUMMARY OF TESTIMONY	2

III.	BACKGROUND ON PSE'S GAS DISTRIBUTION SYSTEM	3

IV.	PSE'S RESPONSE TO THE SEPTEMBER 2 EXPLOSION	5

V.	CONTINUED PERFORMANCE OF EMERGENCY ORDER ACTION ITEMS	9

VI.	PSE'S RESPONSE TO THE WUTC'S STAFF'S RECOMMENDATIONS	10

VII.	THE ALLEGED VIOLATION OF FEDERAL AND STATE LAW	15

EXHIBIT LIST

| Exhibit No. _____ (SML-2) | Susan McLain's Resume |
| --- | --- |
| Exhibit No. _____ (SML-3) | September 17, 2004 Order Requiring Emergency Action |
| Exhibit No. _____ (SML-4) | Graphic Illustration of PSE Gas Distribution System |
| Exhibit No. _____ (SML-5) | September 2, 2004 "Walk Around Letter" for Spiritridge Customers |
| Exhibit No. _____ (SML-6) | September 29, 2004 Letter to Customers with an Investigation Status Report |
| Exhibit No. _____ (SML-7) | September 29, 2004 Frequently Asked Questions Document |
| Exhibit No. _____ (SML-8) | PSE Scratch 'n Sniff Pamphlet |
| Exhibit No. _____ (SML-9) | Spiritridge Neighborhood Association Handout Materials |
| Exhibit No. _____ (SML-10) | PSE Pre-Recorded Messages for Neighborhood-Wide Telephone Updates |
| Exhibit No. _____ (SML-11) | Collection of Weekly Status Reports |

# PUGET SOUND ENERGY, INC.

# PREFILED DIRECT TESTIMONY OF SUSAN MCLAIN

# 1	INTRODUCTION

Q.	Please state your name, business address and present position with Puget Sound Energy, Inc.

A.	My name is Susan McLain.  My business address is 10885 N.E. Fourth Street, P.O. Box 97034, Bellevue, Washington 98009-9734.  I am the Senior Vice President, Operations, for Puget Sound Energy, Inc. ("PSE" or "the Company").

Q.	What is your educational and professional experience?

A.	Exhibit No. ___(SML-2) describes my educational and professional experience.

Q.	What are your duties as Senior Vice President for Operations?

A.	I am responsible for all activities associated with the Company's gas and electricity delivery systems.  This includes:  system and maintenance planning; safety and standards; system design and engineering; gas and electric system construction and maintenance; substation construction, operations and maintenance; contractor and project management; system controls and protection; dispatch; emergency response; system mapping; quality assurance and control; operations performance measurement; purchasing and materials management; fleet management; and electric control center and electric transmission contracts.

# 2	SCOPE OF TESTIMONY

Q.	What is the scope of your testimony in this proceeding?

A.	I will provide: (1) an overview of PSE's gas distribution system; (2) an assessment of the current state of the system and an explanation of our efforts to maintain its integrity; (3) a description of PSE's efforts to investigate and take remedial action after the September 2, 2004, Bellevue house explosion; (4) PSE's response to the WUTC Staff's recommendations articulated in the prefiled testimony of Messrs. Rathbun and Chu; and (5) PSE's response to the alleged violation of RCW 80.28.210 and 49 CFR § 192.463.

# III.	SUMMARY OF TESTIMONY

Q.	Please summarize your testimony.

A.	PSE's gas distribution system is safe, well maintained and operating in accordance with federal and state gas regulations.  Due to the unique factual circumstances, PSE could not predict the chain of events that led to the September 2, 2004, explosion and ultimately the tragic death of Mrs. Frances Schmitz.  After the explosion, PSE immediately undertook a thorough investigation, consistently communicated with all stakeholders about the status of the investigation, and took prompt action within the time allowed by law to remedy any identified deficiencies.  In the final analysis, the results of the investigation have shown that PSE did not violate any laws that gave rise to this complaint, that PSE should not be penalized for this unforeseeable and tragic event, and that PSE should not be forced to deviate from a state regulatory scheme that was created for the purpose of ensuring the safe and uniform operation of all gas distribution systems.  Moreover, because PSE's system is safe and no emergency exists, there is no need for the continuing obligations imposed in the Commission's September 17, 2004, Order Requiring Emergency Action ("Emergency Order"), which is Exhibit No. __ (SML-3) to my testimony.

# 3	BACKGROUND ON PSE'S GAS DISTRIBUTION SYSTEM

Q.	Can you provide us with an overview of PSE's gas distribution system?

A.	Yes.  PSE is Washington's largest energy utility, serving more than one million electric customers and more than 680,000 natural gas customers, primarily in the Puget Sound region.  PSE's priorities are to provide safe, reliable, reasonably priced energy service for the customers and communities we serve.  With respect to natural gas, we provide service in six counties (i.e., King, Kittitas, Lewis, Pierce, Snohomish and Thurston) and we maintain over 11,000 miles of gas pipeline and approximately 12,000 miles of gas service lines.  Notwithstanding the size and complexity of our gas distribution systems, safety is and will always be our top priority.

Q.	Can you describe how PSE distributes gas to its customers?

A.	Yes.  Natural gas is a combustible fossil fuel composed almost entirely of methane.  It is found in deep underground reservoirs formed by porous rock.  From the wellhead of a drill, natural gas can be transported thousands of miles through large-diameter interstate pipelines.  The gas is sent along the interstate pipeline through compressor stations that are located every 50 to 60 miles.  Eventually, the gas reaches a city gate station, where it is metered and delivered to our customers through a distribution network of local gas mains, small-diameter service lines, and ultimately the customer's meter.  Exhibit No. _____ (SML-4) of my testimony provides a graphic illustration of this process.

Q.	What kind of pipes are used to deliver gas to the customers' meters?

A.	Originally, cast iron was commonly used because of its excellent resistance to corrosion.  Steel generally replaced cast iron in the 1950's because of its strength and flexibility.  In the late 1950's, gas companies all over the country began using wrapped steel to help prevent pipe corrosion.  Since the early 1980's, plastic pipe has become the material of choice for low-pressure service lines because it is strong, flexible and corrosion-resistant.

Q.	How long do gas service and main lines normally last?

A.	Unless a gas service or main line is somehow damaged, it will perform safely for many decades.  We are aware of service and main lines that have functioned safely for over 70 years without a need for replacement.

Q.	Is one type of gas service or main line safer than another?

A.	Not necessarily.  Both metal and plastic service and main lines have different attributes.  The key benefit of plastic over metal is the absence of corrosion.  Corrosion is a concern because, over long periods of time, holes can be created in unprotected steel gas service and main lines when the corrosion becomes excessive.  There are federal and state laws that require constant corrosion control for wrapped steel pipe in the form of "cathodic protection" and periodic surveys of gas pipelines to detect leaks.  The testimony of Harry Shapiro and Kevin Garrity elaborate on this.  Corrosion, however, is merely one of the dangers faced by gas pipelines and is not the most likely cause of leaks.  By far, we have found the most common cause of a leak is due to excavation damage.  It routinely occurs as a result of inadvertent homeowner actions or the actions of other utilities (e.g., cable, water, sewer, etc.) whose workers may not be knowledgeable about the location or significance of our gas service and main lines.  In fact, in the last four months, 52% of leaks were caused by third-party damage; the remaining leaks were caused by a number of factors, including mechanical failure (e.g., loosened fitting) or material failure, corrosion, or an unknown cause.  In any event, whether the gas service and main lines are metal or plastic, PSE takes steps to ensure pipeline integrity and to alert the public if there is a leak.

Q.	How do you alert the public to and protect the public from gas leaks?

A.	The first safety device we have is the injection of a strong, noticeable odor into the natural gas we sell.  Natural gas, on its own, is colorless and odorless.  What you smell in our product is a harmless, but sour-smelling, odorant commonly called "mercaptan."  We inject mercaptan at the city gate stations to make it easy for people to quickly identify gas leaks.  Second, we have dedicated personnel on duty 24-hours a day to respond telephonically to any customer questions or concerns about gas leaks.  The third safety procedure we have is the gas First Response Leak Inspection Team ("First Response Team") that is sent to the leak site if a customer's report is not readily explainable.  Our First Response Team is staffed by experienced gas technicians who are equipped to identify where a gas leak is coming from.  The First Response Team is also on 24-hour duty.

Q.	In your view, is the PSE gas distribution system safe?

A.	Yes, we believe that it is a safe system and we have heard that statement publicly confirmed by the WUTC Staff.

# 4	PSE'S RESPONSE TO THE SEPTEMBER 2 EXPLOSION

Q.	Are you familiar with the September 2, 2004 explosion that is the subject of this matter?

A.	Yes.

Q.	How did PSE respond to the explosion?

A.	As soon as the explosion occurred, PSE reached out to the Spiritridge neighborhood with "walk-around letters" that were distributed to the residents.  These letters were intended to quickly inform about the explosion and the status of the investigation.  Exhibit No. __ (SML-5) is an example of those letters.  A recorded message on the event was also delivered to any neighborhood resident who had provided us with a current and active telephone number.  We also immediately began working cooperatively with the WUTC Staff and the City of Bellevue ("City") on the investigation and an action plan to ensure the integrity of our gas distribution system.

Q.	Please explain how PSE worked with Staff and the City to respond.

A.	After the September 2 explosion, PSE, with the approval of the WUTC and in partnership with the City, implemented the nine-point emergency "Action Plan" intended, in part, to communicate important information to PSE customers and key audiences about the ongoing investigation, the status of the gas-distribution system, and system remediation steps being taken.  That Action Plan is reflected in the Emergency Order.  As stated in the Staff's Pre-filed testimony, PSE has performed all nine of the Action Plan points.  The Company also brought in third-party investigators and periodically briefed both Staff and the City of the investigation methodology and progress.

Q.	Did PSE do anything to communicate with its gas customers about the explosion?

A.	Yes.  One of the most important aspects of the Action Plan was the first item, which required PSE to prepare and implement a "Communications Plan to educate all customers in the area served by the rectifier."  Our Plan's objectives were to, among other things, provide factual, timely and up-to-date information to PSE customers within the affected area about the status of the investigation, the safety condition of their gas-delivery system, and the proper actions to take in the event gas odor is detected in or around their premises.  To accomplish these goals, PSE employed the following tactics:

- Creation of Mail Packets of Information.  PSE, in cooperation with the WUTC Staff and the City, sent packets of information to customers within the service area covered by the cross-wired rectifier (a description of which is covered in the testimony of James Hogan).  These packets included:

  - Letters describing key known facts of the incident, status of the investigation, activity that residents may be seeing in their neighborhoods (e.g., digging, detecting, etc.), what to do if resident smells gas, and key-contact information for PSE, WUTC and the City.  Exhibit No. _____ (SML-6).

  - Frequently Asked Questions Document on gas safety, the basics of a gas distribution system and the identity of whom to call.  Exhibit No. _____ (SML-7).

  - PSE Scratch 'n' Sniff Pamphlets that were sent along with customer bills to make them familiar with the smell of natural gas.  Exhibit No. _____ (SML-8).

- Creation of a Dedicated PSE Email Box.  This email box was dedicated solely to handling direct correspondence with PSE customers on the explosion.

- Prominent Publication of All Communications Documents.  PSE published everything on its website and created direct links to PSE's site from the WUTC's and the City's websites.

- Joint Review and Approval of All Updated Communications.  To ensure complete accuracy and coordination with the WUTC Staff and the City, PSE provided a minimum of one day for them to review all proposed communication materials.

- Direct Consultation With the Spiritridge Neighborhood Association.  PSE consulted with the Association to continue and expand in-person communication opportunities and interaction with its customers.  For example, PSE participated in two community meetings sponsored by the Association, held weekly "Coffee Klatch" hours in the Spiritridge neighborhood to update residents, answer questions and hand out information similar to that attached as Exhibit No. __ (SML-9) to my testimony.  PSE also encouraged participation in these meetings by the WUTC Staff and the Bellevue Fire Department.

- Recorded Neighborhood-Wide Telephone Updates.  On an as-needed basis, PSE set up recordings that would provide informational updates via telephone.  Exhibit No. __ (SML-10).

- Regular Informational Updates in Local Newspapers.  PSE consistently presented information on the investigation's status, community meeting announcements, etc., in the Eastside Journal, The Seattle Times and Seattle Post-Intelligencer.

- Informational Insert for the City.  PSE created informational inserts for the publication called "It's Your City," which was distributed in late October of 2004.

- Weekly Progress Reports.  PSE created weekly status reports on PSE's execution of the Action Plan to keep WUTC Staff and the City fully informed of all activities related to the investigation.  Exhibit No. __ (SML-11).

Q.	What did PSE do to manage, coordinate and track customer communications to you?

A.	We did several things.  We established an internal process to document the number and nature of customer inquiries and PSE's response.  We provided weekly written reports to the WUTC Staff and City on our communication efforts along with information on key gas-operations activities.  We also provided the WUTC Staff and the City with copies of all PSE customer inquiries and correspondence.

Q.	Aside from your efforts to execute on the Communication Plan, what else did you do in response?

A.	PSE was and still is concerned with the public's peace of mind as well as its safety.  As a consequence, we took some steps that were not required but were approved of by WUTC Staff.  First, to alleviate the public's concerns over the safety of the system, PSE announced on October 29, 2004 that it intended to replace all of the Spiritridge area steel mains and service lines with plastic natural gas mains and service lines for the 600 customers who were connected to the mis-wired rectifier.  Second, to prevent future inadvertent mis-wiring, PSE assured that all rectifier units and associated wiring had permanent labeling and were securely locked.  Third, in addition to the investigative testing performed on the Spiritridge piping in September and October 2004, PSE undertook a system-wide investigation of all like and similar cathodic protection rectifier units to ascertain whether any additional units had been mis-wired.  No additional wiring reversals were found during this investigation.

# 5	CONTINUED PERFORMANCE OF EMERGENCY ORDER ACTION ITEMS

Q.	Does PSE believe that the Spiritridge neighborhood is safe from service and main line corrosion?

A.	Yes.

Q.	Please explain why.

A.	As described in the testimony of James Hogan and Kevin Garrity, PSE has thoroughly investigated the cause of the explosion and determined that it was a series of anomalies of that specific residence, and not any corrosion caused by the rectifier.  Additionally, PSE has replaced all of the metal pipes in the Spiritridge neighborhood with plastic pipe that will not corrode.

Q.	Are you familiar with the September 17, 2004 Emergency Order?

A.	Yes.

Q.	Do you believe that PSE's continued performance of any of the Action Items is necessary to maintain the gasline safety of the Spiritridge neighborhood?

A.	No.

Q.	Please explain why.

A.	The federal and state codes and regulations provide adequate protection for gas line safety in the Spiritridge neighborhood.  The additional and ongoing requirements imposed by the Action Items, such as the requirement of leak surveys every 30 days in the Spiritridge neighborhood, are simply unnecessary and will drive up the cost of gas operations without significant safety benefits.  PSE wishes to return to normal operations in the Spiritridge neighborhood by complying with applicable federal and state codes and regulations.

# 6	PSE'S RESPONSE TO THE WUTC'S STAFF'S RECOMMENDATIONS

Q.	Have you had an opportunity to review the pre-filed testimony of Alan E. Rathbun and the attached exhibit, which contains the list of Staff recommendations for repairs, changes or other improvement PSE should make?

A.	Yes.

Q.	In Recommendation No. 1(a), Mr. Rathbun suggests that the Commission order PSE to develop an inventory of properties with similar vintage of construction as Mrs. Schmitz's.  What is PSE's position on that?

A.	In an abundance of caution and to provide peace of mind to all of PSE's customers who have service lines that may be of a vintage similar to Mrs. Schmitz's, PSE is prepared to develop an inventory of such properties.  To ensure the comprehensiveness of our inventory, however, PSE would go beyond the WUTC Staff's recommendation of five years prior to application of impressed current cathodic protection.  Instead, PSE would identify all homes with gas service lines that were installed at any point before 1971.  By doing this, PSE can ensure that any service lines that were installed prior to mandatory cathodic protection have been identified.  Since PSE will have to review the maps and records of almost 700,000 gas service lines to be certain as to the material for each, the creation of this inventory will take a substantial amount of time.

Q.	In Recommendation No. 1, Mr. Rathbun also asks the Commission to order PSE to (b) assess the condition of the systems in a manner similar to that used at Spiritridge (i.e., increased leak surveys, detailed cathodic protection surveys with direct examinations of positive and negative indications, and scrutiny and analysis of details of cathodic protection data); (c) prioritize the areas for digital monitoring, and create a plan for rehabilitation and eventual replacement of the aging portions of the distribution system; (d) increase leak monitoring activities during the periods PSE is in the inventory, assessment and prioritization process (e.g., annual leak surveys); and (e) continue to use Direct Current Voltage Gradient (DCVG) and Close Interval Survey (CIS) methods to indirectly assess pipeline condition.  Please tell us PSE's position on these parts of Recommendation 1.

A.	PSE disagrees with all recommendations in 1(b)-(e) because they have several fundamental flaws.

Q.	What flaws have you identified in Staff Recommendations 1(b)-(e)?

A.	First, the recommendations assume that there is a systemic problem within PSE's gas distribution system.  That assumption is based upon the testimony of the WUTC Staff's expert, Dr. Bell, who speculates that the unusual circumstances of the Schmitz home are representative of those that will be found in other homes serviced by PSE.  The investigation of the Spiritridge incident looked for and did not find any evidence of similar circumstances anywhere else.  The second flaw in the recommendations is the assumption that a gas distribution system must never leak.  While a laudable goal, it is technologically impossible to attain.  No such system exists and the federal and state codes and regulations anticipate that various kinds of leaks will inevitably occur.  Third, the recommendations assume that leaks in a gas distribution system are routinely the result of corrosion and that those leaks will result in an explosion or similar dangerous incident.  The truth is that the vast majority of gas leaks in PSE's gas distribution system are resolved without incident and are caused by the actions of third parties who have inadvertently damaged the gas pipeline during an excavation.  The final flaw in the recommendations is the suggestion that PSE perform additional surveys and inspections throughout the entire gas distribution system without there being any evidence that the action would improve public safety or that PSE should be treated any differently from all of the other gas distribution companies in Washington.  The guidelines for surveying gas pipelines for leaks were created with the public's safety in mind and are uniform throughout Washington.  The Staff has not articulated any reason why the isolated events at Mrs. Schmitz's home would justify the Commission throwing out the CFR and the WAC requirements for leak surveys and pipeline inspections.

Q.	Are there any other concerns about the Staff's recommendations?

A.	Yes.  In addition to the flawed assumptions in Recommendation No. 1, PSE does not believe that implementation of those items would improve public safety or be cost effective if ordered by the Commission.

Q.	How many steel service lines would be implicated by Recommendation No. 1?

A.	Our cursory review of records indicates between 70,000 and 100,000.

Q.	What are the costs of doing annual leak surveys on 100,000 steel-wrapped services contemplated by Recommendation No. 1?

A	There will be a one time cost of $100,000 to locate all of the relevant service lines.  In addition, we estimate spending an additional $300,000 - $400,000 each year to comply with the recommendations.  That amount would be on top of the regular leak survey costs incurred for inspecting service lines for 1/5 of the customers each year as required by law.  There will also be substantial costs associated with continuing the Direct Current Voltage Gradient and Close Internal Survey methods (coating survey) to indirectly assess pipeline condition.

Q.	How much would a coating survey as proposed cost?

A	PSE estimates it spent $275,000 on the Spiritridge coating survey.  We would expect to pay an average of $450 per service line in a fairly small geographic area, but are unable to accurately estimate the total cost (as recommended by Staff) at this point without more information about the specific location of the service lines.

Q.	What is PSE's position with respect to Recommendation No. 2, which seeks to require PSE to change its operating manual to initiate remediation without undue delay after a zero or positive voltage cathodic protection reading is taken?

A.	PSE agrees with this recommendation and has already changed our gas field procedures to reflect the heightened urgency called for when a cathodic protection reading is more positive than -200 mV.

Q.	What is PSE's position on Recommendation No. 3, which requires PSE to amend its operating manual to include a standardized process of taking pipe-to-soil potential measurements, including specific provisions described and the significance of the zero voltage cathodic protection readings, and indicating that remedial action must be initiated without undue delay where such readings are found?

A.	PSE agrees with this recommendation and has discussed the significance of a zero or positive read and an appropriate response in staff meetings.

Q.	What is PSE's position on Recommendation No. 4, which would require PSE to secure its rectifiers against unauthorized access and maintain a log showing when each rectifier is accessed and what was done to it?

A.	PSE agrees with this recommendation.  Two days after the explosion occurred, PSE checked all of the rectifiers within its gas distribution system.  It has already begun the process of enhancing the security of each.  All of the "long shank" locks have been replaced and it is no longer possible to gain access to the controls of a rectifier without removing the lock.  In addition, logs are maintained to track access to PSE's rectifiers.

Q.	What is PSE's position with respect to Recommendation No. 5, which would relieve PSE from the requirements of Order 1 regarding leak repair and leak regrades because the new Commission rules now provide adequate protection?

A.	PSE agrees that the Commission should relieve PSE of the requirements currently in place regarding leak repair and leak regrades.

Q.	With respect to that portion of Recommendation No. 5, which would require the Commission to change Order 1 to require that PSE perform leak surveys in the area served by the Rectifier from monthly to an interval of annually, what is PSE's position?

A.	PSE rejects that recommendation for the same reasons mentioned in my testimony regarding Recommendation No. 1(b)-(e).

# 7	THE ALLEGED VIOLATION OF FEDERAL AND STATE LAW

Q.	Have you had an opportunity to review that portion of Mr. Rathbun's prefiled testimony which requests that the Commission assess a monetary penalty of $125,000 against PSE for alleged violations of RCW 80.28.210 and/or 49 CFR § 192.463(a).

A.	Yes.

Q.	What is PSE's position with respect to the claimed violation and penalty?

A.	PSE has not violated either the RCW or the CFR and, as a consequence, asks that the Commission not impose a monetary fine of any kind.  As will be shown in the prefiled testimony of James Hogan and Dennis Burke, PSE, by law, had ninety (90) days to take remedial action from the point at which it discovered the mis-wired Rectifier.  Additionally, as PSE was operating under the codes and regulations, it was not operating an unsafe system.  By the WUTC Staff's own admission, PSE repaired the cross-wired rectifier immediately upon discovery.  Additionally, PSE knew of the cathodic protection problem no sooner than sixty-four (64) days prior to repairing the cross-wired Rectifier.  Thus, under any factual scenario, the conduct, as alleged in this docket, cannot constitute the basis for a violation.  Because PSE fixed the Rectifier as soon as the cross-wiring was discovered and did not delay the repair or notification of WUTC Staff, PSE respectfully requests that the Commission reject the Staff's claim for a $125,000 fine.

Q.	Does this conclude your testimony?

A.	Yes, it does.