

**2015**

**Qualifying Events Report**

**August 29, 2015 Event**

Filed on December 2, 2015

# **Table of Contents**

Table of Contents 2

Event Description 3

**Event Date and Time** 3

**Event Type** 3

**Service Areas Significantly Affected** 3

**Number of Customers Affected** 3

**Summary of System Impacts** 3

**Mobilization Summary** 3

Active Outage Event Chart 4

Major Event Day – Qualification 5

Qualified Events - 2015 5

**Current Event – Calculation Detail** 5

**YTD Daily SAIDI Detail** 5

Event Restoration – Cost Summary 6

**2015 Restoration Costs Detail by Qualifying Event (updated)** 6

**2015 YTD Storm Restoration Costs Detail** 6

Detail Documents 7

**Restoration Cost Detail – Current Event** 8

**Detailed List of Outages - First TMED-Exceeding Day** 9

**Terms, Codes and Definitions Used on Detail Reports** 50

Media & Communication Coverage 51

# **Event Description**

### **Event Date and Time**

August 29, 2015, 01:00 – September 4, 2015. 15:00

### **Event Type**

Wind

### **Service Areas Significantly Affected**

All Service territories were impacted with the most significant impact in North King County and Skagit County

### **Number of Customers Affected**

System wide, approximately 404,693 customers were without power during the course of this event.

### **Summary of System Impacts**

|  |  |
| --- | --- |
| **Total Number of Outages** | **1,003** |
| Distribution Circuits Totally Out | 28 |
| Distribution Circuits Partially Out | 975 |

|  |  |
| --- | --- |
| Transmission Circuits Affected | 20 |
| Substations Offline | 5 |

### **Mobilization Summary**


#### Operating Bases Placed In Emergency Status

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Base** | **Date Opened** | **Time Opened** | **Date Closed** | **Time Closed** |
| Whatcom/Skagit/Island | 8/29/2015 | 11:00 | 9/3/2015 | 03:00 |
| North King | 8/29/2015 | 13:00 | 9/01/2015 | 01:30 |
| South King | 8/29/2015 | 13:00 | 8/30/2015 | 19:00 |
| Pierce | 8/29/2015 | 11:00 | 8/31/2015 | 16:30 |
| Thurston | 8/29/2015 | 10:00 | 8/31/2015 | 01:00 |
| Kitsap | 8/29/2015 | 13:00 | 9/01/2015 | 19:00 |
| Vashon | 8/29/2015 | 13:00 | 9/01/2015 | 19:00 |
| Kittitas | 8/29/2015 | 11:00 | 9/01/2015 | 01:30 |

#### Emergency Coordination Center (ECC)

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **ECC** | **Date Opened** | **Time Opened** | **Date Closed** | **Time Closed** |
|  | 8/29/2015 | 11:00 | 9/2/2015 | 07:00 |

# **Active Outage Event Chart**



# **Major Event Day – Qualification**

**IEEE[[1]](#footnote-1) Standard 1366**

IEEE Standard 1366 was established to present a set of terms and definitions which can be used to foster uniformity in the development of electric system service reliability indices, to identify factors which affect the indices, and to aid in consistent reporting practices among utilities. Also, it provides guidance for new personnel in the reliability area and tools for internal as well as external comparisons. The Major Event Day definition was created as part of IEEE Standard 1366 to allow for consistent calculation of reliability metrics between utilities and enable more valid comparisons with other utility reliability metrics.

|  |
| --- |
| **IEEE Major Event Day Calculation (2.5 BETA METHOD)**   1. A threshold on daily SAIDI[[2]](#footnote-2) is computed once a year, following year end 2. Assemble the 5 most recent years of historical values of SAIDI/day 3. Discard any days in the data set that has a SAIDI/day of zero 4. Find the natural logarithm of each value in the data set 5. Compute the average (Alpha) and the standard deviation (Beta) of the natural logarithms computed in step 4 6. Compute the threshold TMED where TMED = exp (Alpha + 2.5 \* Beta) 7. Any day in the next year with SAIDI > Tmed is a major event day |
| **Puget Sound Energy’s IEEE Major Event Threshold (TMED ) for 2015: 6.1 Minutes** |

# **Qualified Events - 2015**

### **Current Event – Calculation Detail**

|  |  |  |  |
| --- | --- | --- | --- |
| **Event Date, Time Range** | **Total Customer Minutes** | **Average Customer Count** | **Event SAIDI**  (Customer Minutes /Customer Count) |
| 8/29/2015, 08:00 – 9/4/2015, 15:00 | 252,924,888 | 1,114,164 | 227.0 |

### **YTD Daily SAIDI Detail**

(first day that daily SAIDI exceeded PSE’s TMED of 6.1 Minutes by qualifying event)

|  |  |  |
| --- | --- | --- |
| **Date** | **Daily SAIDI**  **(from midnight to midnight)** | **O&M[[3]](#footnote-3) Costs– Deferrable** |
| 1/18/2015 | 25.8 | $2,011,173(r) |
| 8/29/2015 | 208.8 | $11,456,963 |

# **Event Restoration – Cost Summary**

### **2015 Restoration Costs Detail by Qualifying Event (updated)**

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Event Date** | **Qualified Events Deferred Account** | **Capital Costs** | **O&M Costs Not Deferrable** | **O&M Costs**  **Deferrable**  **Accumulation** | **Total O&M Costs** | **Total** |
| 1/18/2015 | $0 | $255,457(r) | $159,839(r) | $2,011,173(r) | $ 2,171,012(r) | $ 2,426,469(r) |
| 8/29/2015 | $ 5,468,136 | $917,209 | $1,001,092 | $5,988,827 | $12,458,054 | $13,375,263 |

(r) Revised

### **2015 YTD Storm Restoration Costs Detail**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **Qualifying Events Deferred Account** | **Capital** | **O&M - Not Deferrable** | **O&M - Deferrable Accumulation** | **Total O&M** | **Total** |
| $5,468,136 | $1,172,665 | $1,160,931 | $8,000,000 | $9,160,931 | $15,801,732 |

# **Detail Documents**

**Restoration Cost Detail – Current Event**

**Detailed List of Distribution Circuits with Outages**

**Terms, Codes and Definitions Used on Detail Reports**

**Newsprint Media Coverage**

### **Restoration Cost Detail – Current Event**



### **Detailed List of Outages** **- First TMED-Exceeding Day**

**August 29, 2015**

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00201887-1 | 8/29/2015 | 3:38:30 AM | NLM-16 | EAC | TV | OCO | 16 | 4,196 |  |  |  |
| P00201888-1 | 8/29/2015 | 3:42:46 AM | HAN-13 | EAA | TV | OCO | 37 | 2,961 |  |  |  |
| P00201891-1 | 8/29/2015 | 5:25:49 AM | SCH-15 | EAA | TV | OFU | 50 | 4,229 |  |  |  |
| P00201900-1 | 8/29/2015 | 5:26:46 AM | DGR-15 | ECA | TV | OCO | 1,249 | 119,542 |  |  |  |
| P00201902-1 | 8/29/2015 | 5:47:40 AM | LEA-16 | EBJ | TV | SCB | 1,189 | 95,358 |  |  |  |
| P00201917-1 | 8/29/2015 | 5:55:45 AM | MTH-21 | EBJ | UN | UTC | 118 | 12,948 |  |  |  |
| P00201982-1 | 8/29/2015 | 5:55:45 AM | LEA-16 | EBJ | TV | OHR | 667 | 62,620 |  |  |  |
| P00201916-1 | 8/29/2015 | 5:58:28 AM | OSC-23 | EBI | TV | OTH | 42 | 7,166 |  |  |  |
| P00201918-1 | 8/29/2015 | 5:59:00 AM | SWD-11 | ECE | TV | OCO | 2,474 | 295,494 |  |  |  |
| P00201936-1 | 8/29/2015 | 6:03:46 AM | MTH-15 | EBJ | TF | UTC | 178 | 17,459 |  |  |  |
| P00201928-1 | 8/29/2015 | 6:06:19 AM | MCA-13 | ECC | EF | OFU | 22 | 28,590 |  |  |  |
| P00201929-1 | 8/29/2015 | 6:07:08 AM | MIL-17 | ECE | TV | OCO | 7 | 1,322 |  |  |  |
| P00201933-1 | 8/29/2015 | 6:11:24 AM | GRV-12 | ECA | TV | OFU | 4 | 444 |  |  |  |
| P00201934-1 | 8/29/2015 | 6:13:15 AM | PIN-26 | EBD | TV | OTF | 4 | 255 |  |  |  |
| P00201937-1 | 8/29/2015 | 6:27:59 AM | CLY-23 | EBE | TV | OCO | 539 | 59,919 |  |  |  |
| P00201939-1 | 8/29/2015 | 6:32:00 AM | HKX-16 | EAC | TV | OPO | 156 | 259,412 |  |  |  |
| P00205785-1 | 8/29/2015 | 6:32:00 AM | HKX-16 | EAC | TV | OPO | 967 | 1,171,901 |  |  |  |
| P00202073-1 | 8/29/2015 | 6:45:00 AM | LON-17 | ECC | EF | OCO | 1,870 | 578,151 |  |  |  |
| 11202357 | 8/29/2015 | 6:47:00 AM | BIG-16 | EAC | TV | OCO | 105 | 36,645 |  |  |  |
| P00201962-1 | 8/29/2015 | 6:48:00 AM | BIG-16 | EAC | TV | OCO | 105 | 36,709 |  |  |  |
| P00201964-1 | 8/29/2015 | 6:50:44 AM | BIG-15 | EAC | TV | OFU | - | 9,571 |  |  |  |
| P00201968-1 | 8/29/2015 | 6:53:20 AM | NLM-12 | EAC | TV | OHR | 114 | 32,874 |  |  |  |
| P00202104-1 | 8/29/2015 | 6:54:33 AM | HKX-16 | EAC | TV | OCO | - | 50,069 |  |  |  |
| P00201977-1 | 8/29/2015 | 7:07:39 AM | RIT-17 | EAC | TV | OCO | 2 | 10,055 |  |  |  |
| P00201983-1 | 8/29/2015 | 7:12:41 AM | WOO-25 | ECA | BA | OTF | 4 | 249 |  |  |  |
| P00202868-1 | 8/29/2015 | 7:16:00 AM | HAM-13 | EAC | TV | OPO | 64 | 840,117 |  |  |  |
| P00201987-1 | 8/29/2015 | 7:16:35 AM | PHA-16 | EBE | TV | OCO | 1,334 | 147,985 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00201992-1 | 8/29/2015 | 7:18:00 AM | KAP-16 | ECA | TV | OTF | - | 451 |  |  |  |
| P00201998-1 | 8/29/2015 | 7:22:05 AM | MLK-12 | EBE | TV | OCO | 3 | 315 |  |  |  |
| P00202001-1 | 8/29/2015 | 7:26:00 AM | NUG-26 | EAA | TV | OCO | 20 | 4,849 |  |  |  |
| P00202063-1 | 8/29/2015 | 7:26:46 AM | NUG-26 | EAA | TV | OFU | 47 | 4,062 |  |  |  |
| P00202005-1 | 8/29/2015 | 7:27:00 AM | NLM-16 | EAC | TV | OCO | - | 1,904 |  |  |  |
| P00210007-1 | 8/29/2015 | 7:27:00 AM | BIG-15 | EAC | TV | OCO | 150 | 569,050 |  |  |  |
| P00202004-1 | 8/29/2015 | 7:27:27 AM | BKB-12 | EAC | TV | OSV | 1 | 4,413 |  |  |  |
| P00203914-1 | 8/29/2015 | 7:27:27 AM | NLM-16 | EAC | TV | OHR | 1,026 | 758,946 |  |  |  |
| P00202012-1 | 8/29/2015 | 7:38:34 AM | CPV-15 | EAD | TV | OTF | 2 | 98 |  |  |  |
| P00202065-1 | 8/29/2015 | 7:41:14 AM | NUG-26 | EAA | TV | OTF | 2 | 452 |  |  |  |
| P00202027-1 | 8/29/2015 | 7:43:55 AM | GLA-01 | EAA | TV | SBF | 1,263 | 124,266 |  |  |  |
| P00202034-1 | 8/29/2015 | 7:51:19 AM | RAI-14 | ECC | EF | OPO | 66 | 53,004 |  |  |  |
| P00202042-1 | 8/29/2015 | 7:57:00 AM | ROC-15 | ECC | EF | UPC | 15 | 37,235 |  |  |  |
| P00201991-1 | 8/29/2015 | 8:18:40 AM | MUR-17 | ECE | EF | UPC | 18 | 3,888 |  |  |  |
| P00202052-1 | 8/29/2015 | 8:19:53 AM | FWY-11 | EBJ | TV | OFU | 4 | 380 |  |  |  |
| P00202055-1 | 8/29/2015 | 8:24:46 AM | CRE-12 | EAD | TV | OTF | 1 | 44 |  |  |  |
| P00202070-1 | 8/29/2015 | 8:42:00 AM | SUM-22 | EAC | TV | OCO | 16 | 37,523 |  |  |  |
| P00202075-1 | 8/29/2015 | 8:57:13 AM | SIL-16 | ECE | TV | OCO | 1,987 | 104,947 |  |  |  |
| P00202076-1 | 8/29/2015 | 8:57:22 AM | SOM-17 | EBE | TV | OCO | 24 | 829 |  |  |  |
| P00202080-1 | 8/29/2015 | 8:57:55 AM | SCH-15 | EAA | TV | OCO | 5 | 11,333 |  |  |  |
| P00206308-1 | 8/29/2015 | 9:00:00 AM | LMC-25 | EBE | TV | OCO | 14 | (1) |  |  |  |
| P00202102-1 | 8/29/2015 | 9:03:27 AM | LAC-17 | ECC | TV | OFU | 33 | 42,060 |  |  |  |
| P00202105-1 | 8/29/2015 | 9:06:03 AM | MOT-14 | ECC | TV | OCO | 964 | 121,175 |  |  |  |
| P00202046-1 | 8/29/2015 | 9:09:11 AM | NBO-25 | EBD | EF | OFC | 18 | 29,385 |  |  |  |
| P00208625-1 | 8/29/2015 | 9:09:23 AM | GRV-16 | ECA | TV | OCO | 1,460 | 239,905 |  |  |  |
| P00202114-1 | 8/29/2015 | 9:14:00 AM | CRE-16 | EAD | TV | OPO | 2 | 13,218 |  |  |  |
| P00204226-1 | 8/29/2015 | 9:17:46 AM | LAB-25 | EAA | TV | OHR | 738 | 1,322,074 |  |  |  |
| P00202118-1 | 8/29/2015 | 9:18:43 AM | PRI-13 | ECC | TV | OTF | 1 | 1,556 |  |  |  |
| P00202136-1 | 8/29/2015 | 9:19:00 AM | ROC-26 | ECC | TV | OCO | 195 | 376,902 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00202121-1 | 8/29/2015 | 9:20:05 AM | MVW-16 | EBJ | TV | OFU | 9 | 1,511 |  |  |  |
| P00202133-1 | 8/29/2015 | 9:20:05 AM | MVW-16 | EBJ | TV | OFU | 7 | 1,175 |  |  |  |
| P00202122-1 | 8/29/2015 | 9:20:20 AM | RAI-12 | ECC | TV | OCO | 97 | 81,616 |  |  |  |
| P00202297-1 | 8/29/2015 | 9:26:50 AM | MOT-15 | ECC | EF | OHR | 496 | 114,336 |  |  |  |
| P00202130-1 | 8/29/2015 | 9:26:58 AM | CHA-12 | ECC | TV | OFU | 40 | 118,233 |  |  |  |
| P00204729-1 | 8/29/2015 | 9:27:00 AM | SLA-16 | EAA | TV | OCO | 1,029 | 3,062,968 |  |  |  |
| P00202132-1 | 8/29/2015 | 9:27:00 AM | YEL-26 | ECC | TF | OCO | 118 | 221,434 |  |  |  |
| P00205189-1 | 8/29/2015 | 9:33:16 AM | PRI-13 | ECC | TV | OFU | 15 | 22,811 |  |  |  |
| P00202191-1 | 8/29/2015 | 9:34:17 AM | PAT-13 | ECC | EF | OTF | 43 | 27,469 |  |  |  |
| P00202148-1 | 8/29/2015 | 9:35:36 AM | MCA-16 | ECC | TV | OCO | 1,858 | 598,895 |  |  |  |
| P00202150-1 | 8/29/2015 | 9:36:01 AM | SPA-16 | ECA | TV | OCO | 1,970 | 110,976 |  |  |  |
| P00202151-1 | 8/29/2015 | 9:37:13 AM | ELD-25 | ECC | TF | OCO | 46 | 56,435 |  |  |  |
| P00202152-1 | 8/29/2015 | 9:37:28 AM | LOL-21 | ECD | EF | OTF | 2 | 1,488 |  |  |  |
| P00202154-1 | 8/29/2015 | 9:37:36 AM | MOT-17 | ECC | TV | OCO | 601 | 56,384 |  |  |  |
| P00202155-1 | 8/29/2015 | 9:37:41 AM | MCA-13 | ECC | TV | OCO | 939 | 449,652 |  |  |  |
| P00209205-1 | 8/29/2015 | 9:40:58 AM | LAB-23 | EAA | TV | SCB | 614 | 1,237,903 |  |  |  |
| P00205193-1 | 8/29/2015 | 9:42:00 AM | BAR-17 | ECC | TV | OFU | 9 | 19,800 |  |  |  |
| P00204511-1 | 8/29/2015 | 9:45:00 AM | PAT-15 | ECC | TV | OFU | 27 | 67,359 |  |  |  |
| P00202210-1 | 8/29/2015 | 9:47:00 AM | HOL-01 | ECA | TV | OCO | 527 | (1) |  |  |  |
| P00202481-1 | 8/29/2015 | 9:47:00 AM | HOL-12 | ECA | TV | OCO | 1,233 | 746,561 |  |  |  |
| P00202488-1 | 8/29/2015 | 9:47:00 AM | HOL-15 | ECA | TV | OCO | 1,266 | 467,154 |  |  |  |
| P00202180-1 | 8/29/2015 | 9:47:00 AM | NLM-13 | EAC | TV | OCO | 1,367 | 472,502 |  |  |  |
| P00202183-1 | 8/29/2015 | 9:48:00 AM | ORT-22 | ECA | TV | OIN | 1,245 | 948,046 |  |  |  |
| P00208314-1 | 8/29/2015 | 9:48:22 AM | LON-23 | ECC | TV | OCO | 954 | 762,824 |  |  |  |
| P00202190-1 | 8/29/2015 | 9:49:00 AM | CUS-13 | EAA | TV | OCO | 133 | 313,975 |  |  |  |
| P00206037-1 | 8/29/2015 | 9:49:00 AM | BIG-12 | EAC | TV | OIN | 801 | 1,919,969 |  |  |  |
| P00202204-1 | 8/29/2015 | 9:49:17 AM | BON-13 | ECA | TV | OCO | 1,222 | 108,208 |  |  |  |
| P00202197-1 | 8/29/2015 | 9:49:34 AM | PRI-13 | ECC | TV | OSV | 3 | 6,913 |  |  |  |
| P00211994-1 | 8/29/2015 | 9:49:55 AM | CUS-13 | EAA | TV | OCR | 37 | 178,281 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00202221-1 | 8/29/2015 | 9:52:00 AM | KAP-13 | ECA | TV | OCO | 1 | 904 |  |  |  |
| P00202238-1 | 8/29/2015 | 9:53:02 AM | SLA-17 | EAA | TV | SCB | 1,758 | 229,653 |  |  |  |
| P00209940-1 | 8/29/2015 | 9:53:50 AM | ORT-23 | ECA | TV | OCO | 7 | 10,291 |  |  |  |
| P00202250-1 | 8/29/2015 | 9:54:23 AM | BLU-13 | ECC | TV | OCO | 1,130 | 607,922 |  |  |  |
| P00202271-1 | 8/29/2015 | 9:55:33 AM | BIG-15 | EAC | TV | SCB | 3,110 | 724,970 |  |  |  |
| P00202273-1 | 8/29/2015 | 9:55:38 AM | RAI-12 | ECC | TV | OCO | 820 | 452,366 |  |  |  |
| P00202262-1 | 8/29/2015 | 9:56:37 AM | MSI-24 | EBF | TV | OCO | 28 | 1,923 |  |  |  |
| P00202264-1 | 8/29/2015 | 9:56:42 AM | ROE-13 | EAA | TV | OHR | 146 | 54,564 |  |  |  |
| P00202276-1 | 8/29/2015 | 9:57:41 AM | OSC-23 | EBI | TV | OHR | 770 | 42,389 |  |  |  |
| P00202299-1 | 8/29/2015 | 9:57:46 AM | LON-25 | ECC | TF | OCO | 1,218 | 1,126,229 |  |  |  |
| P00207001-1 | 8/29/2015 | 9:58:00 AM | AIR-26 | ECC | TV | OCO | 428 | 171,500 |  |  |  |
| P00204109-1 | 8/29/2015 | 9:58:02 AM | GWR-16 | EBI | TV | OHR | 323 | 280,585 |  |  |  |
| P00201875-1 | 8/29/2015 | 9:58:48 AM | AIR-26 | ECC |  |  | 428 | 86 |  |  |  |
| P00202295-1 | 8/29/2015 | 9:59:11 AM | CAP-13 | ECC | EF | OTF | 7 | 3,360 |  |  |  |
| P00202323-1 | 8/29/2015 | 10:01:00 AM | WLS-16 | EAC | TV | OPO | 5 | 30,183 |  |  |  |
| P00202330-1 | 8/29/2015 | 10:01:00 AM | CHA-12 | ECC | TV | OCO | 23 | 45,970 |  |  |  |
| P00202404-1 | 8/29/2015 | 10:01:51 AM | PLG-13 | ECC | TV | OCO | 1,117 | 238,331 |  |  |  |
| P00202339-1 | 8/29/2015 | 10:03:00 AM | CHA-16 | ECC | EF | OFU | 20 | 22,000 |  |  |  |
| P00202353-1 | 8/29/2015 | 10:03:38 AM | GRV-12 | ECA | TV | OCO | 879 | 411,431 |  |  |  |
| P00202355-1 | 8/29/2015 | 10:03:53 AM | TAN-13 | ECC | TV | OCO | 2,134 | 566,933 |  |  |  |
| P00202346-1 | 8/29/2015 | 10:03:58 AM | PRI-13 | ECC | TV | OTF | 4 | 6,144 |  |  |  |
| P00202349-1 | 8/29/2015 | 10:04:14 AM | TOL-17 | EBD | BA | OTF | 2 | 113 |  |  |  |
| P00202352-1 | 8/29/2015 | 10:05:00 AM | CAP-13 | ECC | EF | OTF | 7 | 3,317 |  |  |  |
| P00202365-1 | 8/29/2015 | 10:05:00 AM | ALG-12 | EAC | TV | OIN | 31 | 93,210 |  |  |  |
| P00202360-1 | 8/29/2015 | 10:05:25 AM | CHA-12 | ECC | EF | OFU | 11 | 6,628 |  |  |  |
| P00203690-1 | 8/29/2015 | 10:05:31 AM | PRI-23 | ECC | TV | OCO | 63 | 77,655 |  |  |  |
| P00202376-1 | 8/29/2015 | 10:06:09 AM | BAR-13 | ECC | TV | OCO | 1,518 | 230,964 |  |  |  |
| P00202366-1 | 8/29/2015 | 10:06:40 AM | ROC-16 | ECC | TV | OFU | 209 | 26,564 |  |  |  |
| P00202803-1 | 8/29/2015 | 10:07:25 AM | VAS-13 | EBL | TV | OCO | 208 | 83,200 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00202393-1 | 8/29/2015 | 10:09:15 AM | BHL-16 | ECE | TV | OCO | 2 | 965 |  |  |  |
| P00202447-1 | 8/29/2015 | 10:09:43 AM | SWI-13 | ECC | TV | OCO | 983 | 500,332 |  |  |  |
| P00202398-1 | 8/29/2015 | 10:10:01 AM | PMA-15 | ECE | TV | OCO | 13 | 16,618 |  |  |  |
| P00211995-1 | 8/29/2015 | 10:10:20 AM | CUS-13 | EAA | TV | OCO | 22 | 80,707 |  |  |  |
| P00202689-1 | 8/29/2015 | 10:10:46 AM | BAR-17 | ECC | TV | OCO | 111 | 90,232 |  |  |  |
| P00202448-1 | 8/29/2015 | 10:12:00 AM | SWD-13 | ECE | TV | OCO | - | 59,867 |  |  |  |
| P00202408-1 | 8/29/2015 | 10:12:21 AM | SIL-16 | ECE | TV | OCO | 744 | 65,956 |  |  |  |
| P00202832-1 | 8/29/2015 | 10:13:58 AM | TIL-01 | ECA |  |  | 2,598 | 530,987 |  |  |  |
| P00202432-1 | 8/29/2015 | 10:14:09 AM | MIL-17 | ECE | TV | OCO | 3,232 | 223,661 |  |  |  |
| P00202423-1 | 8/29/2015 | 10:14:41 AM | PET-13 | EAC | TV | OFU | 26 | 72,244 |  |  |  |
| P00202438-1 | 8/29/2015 | 10:15:09 AM | PLU-25 | ECC | TV | OCO | 127 | 29,849 |  |  |  |
| P00202427-1 | 8/29/2015 | 10:15:17 AM | MKI-14 | ECC | TV | OFU | 2 | 3,008 |  |  |  |
| P00202429-1 | 8/29/2015 | 10:15:28 AM | PEA-15 | EBJ | BA | OFU | 3 | 158 |  |  |  |
| P00202445-1 | 8/29/2015 | 10:17:00 AM | RAI-14 | ECC | EF | OTF | 3 | 5,428 |  |  |  |
| P00202633-1 | 8/29/2015 | 10:17:00 AM | PLG-17 | ECC | TV | OCO | 21 | 34,144 |  |  |  |
| P00206660-1 | 8/29/2015 | 10:17:49 AM | CAP-15 | ECC | TV | OCO | 110 | 130,269 |  |  |  |
| P00202466-1 | 8/29/2015 | 10:18:05 AM | LAC-13 | ECC | TV | OCO | 3,509 | 1,153,584 |  |  |  |
| P00202840-1 | 8/29/2015 | 10:18:07 AM | GRI-15 | ECC | TV | OCO | 23 | 11,240 |  |  |  |
| P00202474-1 | 8/29/2015 | 10:19:30 AM | GAR-16 | ECA | TV | OCO | 4,196 | 275,608 |  |  |  |
| P00202468-1 | 8/29/2015 | 10:19:49 AM | GWR-16 | EBI | TV | OHR | 1 | 1,690 |  |  |  |
| P00202472-1 | 8/29/2015 | 10:20:00 AM | PLA-23 | EBD | TV | OTR | 4 | 6,845 |  |  |  |
| P00202644-1 | 8/29/2015 | 10:20:44 AM | LUH-14 | ECC | TF | OCO | 172 | 92,047 |  |  |  |
| P00205113-1 | 8/29/2015 | 10:20:48 AM | KIN-22 | ECE | TV | OCO | 1,378 | 784,261 |  |  |  |
| P00202483-1 | 8/29/2015 | 10:21:00 AM | LUH-14 | ECC | TF | OCO | 65 | 61,656 |  |  |  |
| P00202490-1 | 8/29/2015 | 10:23:25 AM | FRG-24 | ECC | TV | OCO | 950 | 167,921 |  |  |  |
| P00202491-1 | 8/29/2015 | 10:23:30 AM | LMC-25 | EBE | TV | OCO | 33 | 3,841 |  |  |  |
| P00212618-1 | 8/29/2015 | 10:26:10 AM | CUS-13 | EAA | TV | OCO | - | 297,438 |  |  |  |
| P00202540-1 | 8/29/2015 | 10:26:21 AM | PIK-24 | EBF | TV | OCO | 209 | 16,501 |  |  |  |
| P00202544-1 | 8/29/2015 | 10:27:00 AM | MSI-24 | EBF | TV | OCO | 11 | 34,280 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00202569-1 | 8/29/2015 | 10:28:05 AM | VAS-13 | EBL | TV | OCO | 204 | 18,802 |  |  |  |
| P00202579-1 | 8/29/2015 | 10:29:31 AM | LMD-16 | EBJ | TV | OFU | 32 | 5,199 |  |  |  |
| P00202572-1 | 8/29/2015 | 10:30:00 AM | SWI-17 | ECC | TV | OCO | 1 | 2,511 |  |  |  |
| P00207605-1 | 8/29/2015 | 10:30:37 AM | LAC-17 | ECC | TV | OCO | 25 | 27,210 |  |  |  |
| P00202728-1 | 8/29/2015 | 10:32:00 AM | KIN-24 | ECE | TV | OCO | - | 106,373 |  |  |  |
| P00209197-1 | 8/29/2015 | 10:32:36 AM | WLK-15 | ECA | TO |  | 22 | 24,981 |  |  |  |
| P00209188-1 | 8/29/2015 | 10:32:42 AM | FLD-12 | EAD | TV | OCO | 889 | 1,486,441 |  |  |  |
| P00208949-1 | 8/29/2015 | 10:33:15 AM | LON-22 | ECC | TV | OCO | 568 | 432,289 |  |  |  |
| P00202629-1 | 8/29/2015 | 10:35:00 AM | LAC-17 | ECC | TV | OCO | 5 | 6,086 |  |  |  |
| P00202635-1 | 8/29/2015 | 10:35:06 AM | SWI-16 | ECC | TV | OCO | 2,656 | 913,975 |  |  |  |
| P00206093-1 | 8/29/2015 | 10:35:55 AM | CLV-16 | EAD | TV | OCO | 946 | 932,083 |  |  |  |
| P00202638-1 | 8/29/2015 | 10:36:44 AM | CPV-12 | EAD | TV | OTF | 1 | 4,810 |  |  |  |
| P00202640-1 | 8/29/2015 | 10:37:14 AM | PIK-21 | EBF | TV | OSV | 6 | 1,052 |  |  |  |
| P00202654-1 | 8/29/2015 | 10:37:32 AM | OSC-26 | EBI | TV | SCB | 1,041 | 74,808 |  |  |  |
| P00202676-1 | 8/29/2015 | 10:38:00 AM | LMC-23 | EBE | TV | OTR | 133 | 31,754 |  |  |  |
| P00203584-1 | 8/29/2015 | 10:38:05 AM | OSC-22 | EBI | TV | OFU | 60 | 22,877 |  |  |  |
| P00202674-1 | 8/29/2015 | 10:38:17 AM | LAC-17 | ECC | TV | OCO | 1,817 | 553,671 |  |  |  |
| P00202666-1 | 8/29/2015 | 10:39:00 AM | KAP-16 | ECA | TV |  | 34 | 32,896 |  |  |  |
| P00202693-1 | 8/29/2015 | 10:39:00 AM | SLA-15 | EAA | TV | OFU | 214 | 452,824 |  |  |  |
| P00202660-1 | 8/29/2015 | 10:39:14 AM | SIL-15 | ECE | TV | OCO | 73 | 7,923 |  |  |  |
| P00209878-1 | 8/29/2015 | 10:39:29 AM | FLD-15 | EAD | TV | OCO | 23 | 37,937 |  |  |  |
| P00202683-1 | 8/29/2015 | 10:41:09 AM | OSC-22 | EBI | TV | OHR | 520 | 109,321 |  |  |  |
| P00202773-1 | 8/29/2015 | 10:41:55 AM | MIR-15 | EBF | TV | OCO | 84 | 17,931 |  |  |  |
| P00202718-1 | 8/29/2015 | 10:44:17 AM | RDO-15 | EBJ | TV | SCB | 1,656 | 129,802 |  |  |  |
| P00208178-1 | 8/29/2015 | 10:44:44 AM | SWI-15 | ECC | TV | OCO | 189 | 127,499 |  |  |  |
| P00202740-1 | 8/29/2015 | 10:45:08 AM | RIT-18 | EAC | TV | OCO | 1,482 | 668,185 |  |  |  |
| P00202870-1 | 8/29/2015 | 10:45:26 AM | YEL-26 | ECC | TV | OCO | 37 | 39,063 |  |  |  |
| P00202765-1 | 8/29/2015 | 10:46:00 AM | ING-13 | EBD | TV | OCO | 4,685 | 2,927,606 |  |  |  |
| P00205468-1 | 8/29/2015 | 10:46:35 AM | PGA-13 | ECE | TV | OCO | 1,190 | 1,848,290 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00208412-1 | 8/29/2015 | 10:46:41 AM | CLE-11 | EBH | TV | OCO | 46 | 21,471 |  |  |  |
| P00202741-1 | 8/29/2015 | 10:46:47 AM | GAR-13 | ECA | TV | OCO | 49 | 63,578 |  |  |  |
| P00207068-1 | 8/29/2015 | 10:47:00 AM | BRE-21 | ECD | TV | OSV | 1 | 1,735 |  |  |  |
| P00202748-1 | 8/29/2015 | 10:47:18 AM | SEM-15 | EAA | TV | OTF | 2 | 10,418 |  |  |  |
| P00202886-1 | 8/29/2015 | 10:47:31 AM | ENU-18 | EBI | TV | OTF | - | 1,713 |  |  |  |
| P00202775-1 | 8/29/2015 | 10:48:00 AM | SPA-16 | ECA | EF | OCR | 1,954 | 914,505 |  |  |  |
| P00202772-1 | 8/29/2015 | 10:49:22 AM | SWE-23 | EBJ | TV | OFU | 52 | 12,431 |  |  |  |
| P00202792-1 | 8/29/2015 | 10:50:49 AM | CUM-15 | EBI | TV | OTF | 1 | 650 |  |  |  |
| P00204313-1 | 8/29/2015 | 10:52:00 AM | WOB-23 | EAA | TV | OFU | 110 | 216,918 |  |  |  |
| P00202810-1 | 8/29/2015 | 10:52:54 AM | VAS-12 | EBL | TV | OCO | 10 | 10,078 |  |  |  |
| P00209879-1 | 8/29/2015 | 10:54:12 AM | EDG-12 | ECA | TV | OCO | 6 | 8,534 |  |  |  |
| P00211496-1 | 8/29/2015 | 10:54:29 AM | BRO-15 | EAD | TV | OCO | 186 | 379,083 |  |  |  |
| P00202857-1 | 8/29/2015 | 10:55:00 AM | BCH-13 | EAA | TV | OIN | 1,719 | 2,200,320 |  |  |  |
| P00213051-1 | 8/29/2015 | 10:55:20 AM | CPV-12 | EAD | TV | OTR | 1 | 4,834 |  |  |  |
| P00203857-1 | 8/29/2015 | 10:55:23 AM | VWY-15 | EAA | TV | OCO | 83 | 315,064 |  |  |  |
| P00202841-1 | 8/29/2015 | 10:56:01 AM | SIN-23 | ECD | TV | OCO | 1 | 702 |  |  |  |
| P00202844-1 | 8/29/2015 | 10:56:22 AM | MKI-17 | ECC | TV | OCO | 219 | 344,230 |  |  |  |
| P00202856-1 | 8/29/2015 | 10:57:00 AM | JHO-12 | ECC | EF | OAR | 8 | 6,052 |  |  |  |
| P00206077-1 | 8/29/2015 | 10:57:06 AM | FLD-13 | EAD | TV | OCO | 91 | 346,590 |  |  |  |
| P00203549-1 | 8/29/2015 | 10:58:00 AM | WCA-16 | EBJ | TV | OCO | 17 | 5,020 |  |  |  |
| P00202860-1 | 8/29/2015 | 10:58:01 AM | KLA-17 | EBD | BA | OTR | 2 | 3,264 |  |  |  |
| P00202867-1 | 8/29/2015 | 10:58:26 AM | HOB-16 | EBI | TV | OCO | 13 | 20,206 |  |  |  |
| P00202876-1 | 8/29/2015 | 10:59:10 AM | NHL-17 | EBD | TV | OCO | 29 | 32,069 |  |  |  |
| P00202897-1 | 8/29/2015 | 11:00:16 AM | LON-26 | ECC | TV | OCO | 9 | 7,363 |  |  |  |
| P00203779-1 | 8/29/2015 | 11:00:30 AM | FLD-13 | EAD | TV | OCO | 299 | 788,010 |  |  |  |
| P00208851-1 | 8/29/2015 | 11:02:29 AM | WOO-26 | ECA | TV | OFC | - | 2,157 |  |  |  |
| P00208671-1 | 8/29/2015 | 11:02:29 AM | WOO-26 | ECA | TV | OCO | 40 | 101,209 |  |  |  |
| P00202919-1 | 8/29/2015 | 11:02:57 AM | NUG-26 | EAA | TV | OTF | 15 | 12,116 |  |  |  |
| P00202941-1 | 8/29/2015 | 11:03:00 AM | CRE-16 | EAD | TV | OCO | 92 | 285,235 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00202987-1 | 8/29/2015 | 11:03:06 AM | HEM-16 | ECA | TV | OCO | 1,033 | 835,881 |  |  |  |
| P00208290-1 | 8/29/2015 | 11:03:16 AM | HEM-16 | ECA | TV | OPO | 343 | 204,266 |  |  |  |
| P00202940-1 | 8/29/2015 | 11:04:00 AM | VWY-12 | EAA | TV | OCO | 25 | 100,673 |  |  |  |
| P00202931-1 | 8/29/2015 | 11:04:18 AM | CED-13 | ECA | TV |  | 17 | 11,841 |  |  |  |
| P00204503-1 | 8/29/2015 | 11:04:20 AM | ING-15 | EBD | TV | OCO | 1,311 | 2,072,281 |  |  |  |
| P00202944-1 | 8/29/2015 | 11:04:57 AM | KAP-16 | ECA | TV | OFU | 4 | 651 |  |  |  |
| P00209309-1 | 8/29/2015 | 11:05:00 AM | NUG-26 | EAA | TV | OCO | 93 | 193,024 |  |  |  |
| P00202947-1 | 8/29/2015 | 11:05:26 AM | EGT-12 | EBE | TV | OCO | 15 | 11,199 |  |  |  |
| P00202960-1 | 8/29/2015 | 11:05:49 AM | PEA-16 | EBJ | TV | SCB | 269 | 13,764 |  |  |  |
| P00203466-1 | 8/29/2015 | 11:06:19 AM | NUG-26 | EAA | TV | OCO | 202 | 63,338 |  |  |  |
| P00202997-1 | 8/29/2015 | 11:07:00 AM | BLU-17 | ECC | TV | OCO | 215 | 366,145 |  |  |  |
| P00206538-1 | 8/29/2015 | 11:07:15 AM | OSC-23 | EBI | TV | OHR | 763 | 406,651 |  |  |  |
| P00202971-1 | 8/29/2015 | 11:07:33 AM | EGT-12 | EBE | TV | OCO | 3 | 2,218 |  |  |  |
| P00210263-1 | 8/29/2015 | 11:07:58 AM | ING-15 | EBD | TV | OCO | 17 | 11,358 |  |  |  |
| P00202994-1 | 8/29/2015 | 11:08:04 AM | BLA-13 | EAA | TV | OCO | 588 | 1,273,499 |  |  |  |
| P00202984-1 | 8/29/2015 | 11:09:48 AM | ALG-12 | EAC | TV | OCO | 52 | 222,915 |  |  |  |
| P00202993-1 | 8/29/2015 | 11:10:00 AM | ORC-17 | EBJ | TV | OCO | 427 | 432,978 |  |  |  |
| P00211781-1 | 8/29/2015 | 11:10:12 AM | BLA-13 | EAA | TV | OFU | 244 | 686,010 |  |  |  |
| P00211426-1 | 8/29/2015 | 11:10:33 AM | ALG-15 | EAA | TV | OCO | 13 | 41,495 |  |  |  |
| P00203023-1 | 8/29/2015 | 11:11:00 AM | ROE-17 | EAA | TV | OCO | 1,859 | 2,488,086 |  |  |  |
| P00203007-1 | 8/29/2015 | 11:11:50 AM | WCA-17 | EBJ | TV | OFU | 158 | 41,809 |  |  |  |
| P00203020-1 | 8/29/2015 | 11:12:00 AM | CWD-24 | EBD | TV | OCO | 74 | 33,592 |  |  |  |
| P00202170-1 | 8/29/2015 | 11:12:01 AM | BTR-21 | EBE | TV | OCO | 13 | 951 |  |  |  |
| P00211270-1 | 8/29/2015 | 11:12:17 AM | BLA-13 | EAA | TV | OCO | 164 | 153,898 |  |  |  |
| P00203025-1 | 8/29/2015 | 11:12:51 AM | WOO-23 | ECA |  |  | 14 | 9,405 |  |  |  |
| P00209966-1 | 8/29/2015 | 11:12:51 AM | WOO-23 | ECA | TV | OCO | - | 9,299 |  |  |  |
| P00203238-1 | 8/29/2015 | 11:13:13 AM | BRO-15 | EAD | TV | OCO | 4,069 | 1,548,067 |  |  |  |
| P00203142-1 | 8/29/2015 | 11:15:00 AM | VAS-23 | EBL | TV | OCR | 1,352 | 1,303,147 |  |  |  |
| P00203052-1 | 8/29/2015 | 11:15:00 AM | CTR-22 | EBJ | TV | OCO | 129 | 149,466 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00203044-1 | 8/29/2015 | 11:15:14 AM | ALG-12 | EAC | TV | OCO | 31 | 99,007 |  |  |  |
| P00207343-1 | 8/29/2015 | 11:15:47 AM | YEL-26 | ECC | TV | OCO | 56 | 67,815 |  |  |  |
| P00203299-1 | 8/29/2015 | 11:15:58 AM | FRA-12 | ECD | TV | OCO | 1,677 | 537,381 |  |  |  |
| P00206637-1 | 8/29/2015 | 11:16:00 AM | VAS-12 | EBL | TV | OCO | 170 | 118,204 |  |  |  |
| P00203096-1 | 8/29/2015 | 11:16:00 AM | CED-13 | ECA | TV | OCO | 3 | 3,881 |  |  |  |
| P00203157-1 | 8/29/2015 | 11:16:18 AM | FRA-15 | ECD | UN | OFU | 96 | 3,890 |  |  |  |
| P00207741-1 | 8/29/2015 | 11:16:31 AM | VAS-13 | EBL | TV | OCO | 117 | 72,966 |  |  |  |
| P00211273-1 | 8/29/2015 | 11:16:38 AM | BLA-13 | EAA | TV | OCO | - | 50,827 |  |  |  |
| P00205835-1 | 8/29/2015 | 11:17:54 AM | SMR-26 | ECA | TV | OCO | 368 | 194,862 |  |  |  |
| P00208871-1 | 8/29/2015 | 11:18:00 AM | HAM-15 | EAC | TV | OCO | 1,273 | 3,818,563 |  |  |  |
| P00203208-1 | 8/29/2015 | 11:18:00 AM | CPV-15 | EAD | TV | OCO | 430 | 264,406 |  |  |  |
| P00209609-1 | 8/29/2015 | 11:18:00 AM | SWA-15 | EAD | TV | OCO | 94 | 141,044 |  |  |  |
| P00203166-1 | 8/29/2015 | 11:18:18 AM | ALG-15 | EAA | TV | OCO | 28 | 89,142 |  |  |  |
| P00203167-1 | 8/29/2015 | 11:18:20 AM | OSC-23 | EBI | TV | OTF | 3 | 782 |  |  |  |
| P00211327-1 | 8/29/2015 | 11:18:47 AM | BTN-36 | EAC | TV | OCO | 11 | 18,603 |  |  |  |
| P00203168-1 | 8/29/2015 | 11:18:54 AM | OSC-23 | EBI | TV | OFU | 30 | 7,808 |  |  |  |
| P00203209-1 | 8/29/2015 | 11:19:21 AM | FLD-13 | EAD | TV | OFU | 58 | 105,543 |  |  |  |
| P00210358-1 | 8/29/2015 | 11:19:21 AM | BCH-12 | EAA | TV | OCO | 128 | 375,863 |  |  |  |
| P00208402-1 | 8/29/2015 | 11:19:26 AM | BEL-17 | EBJ | TV | OCO | 6 | 4,027 |  |  |  |
| P00203260-1 | 8/29/2015 | 11:21:00 AM | FAL-16 | EBF | TV | OTF | 1 | 1,517 |  |  |  |
| P00203261-1 | 8/29/2015 | 11:21:00 AM | YEL-26 | ECC | TV | OCO | 2 | 2,679 |  |  |  |
| P00207869-1 | 8/29/2015 | 11:21:23 AM | VAS-12 | EBL | TV | OCO | 21 | 21,218 |  |  |  |
| P00206857-1 | 8/29/2015 | 11:21:44 AM | VAS-12 | EBL | TV | OCO | 38 | 50,474 |  |  |  |
| P00208930-1 | 8/29/2015 | 11:22:07 AM | WLK-13 | ECA | TV | OCO | 287 | 211,203 |  |  |  |
| P00203286-1 | 8/29/2015 | 11:22:31 AM | KNM-27 | EBD | TV | OCO | 859 | 1,926,325 |  |  |  |
| P00203285-1 | 8/29/2015 | 11:23:42 AM | NLM-16 | EAC | TV | OFU | 191 | 959,654 |  |  |  |
| P00203317-1 | 8/29/2015 | 11:23:43 AM | KIT-22 | EBH | TV | OCO | 229 | 28,919 |  |  |  |
| P00203296-1 | 8/29/2015 | 11:24:38 AM | CUS-13 | EAA | TV | OCO | 187 | 193,499 |  |  |  |
| P00207805-1 | 8/29/2015 | 11:25:42 AM | PGA-12 | ECE | TV | OCO | 854 | 1,279,857 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00203309-1 | 8/29/2015 | 11:26:03 AM | EDG-16 | ECA | TV | OCO | 885 | 33,568 |  |  |  |
| P00203323-1 | 8/29/2015 | 11:26:06 AM | PLU-22 | ECC | TV | OCO | 476 | 104,601 |  |  |  |
| P00203328-1 | 8/29/2015 | 11:27:00 AM | PLG-17 | ECC | TV | OCO | 1 | 2,236 |  |  |  |
| P00203326-1 | 8/29/2015 | 11:27:26 AM | BRO-15 | EAD | TV | OFU | 115 | 188,296 |  |  |  |
| P00203330-1 | 8/29/2015 | 11:27:38 AM | EGT-12 | EBE | TV | OCO | 3 | 2,149 |  |  |  |
| P00203387-1 | 8/29/2015 | 11:28:00 AM | KEN-13 | EAA | TV | OCO | - | 355,500 |  |  |  |
| P00208516-1 | 8/29/2015 | 11:28:15 AM | BUC-26 | ECA | TV | OFU | 59 | 31,133 |  |  |  |
| P00203516-1 | 8/29/2015 | 11:28:30 AM | PEA-17 | EBJ | TV | OCO | 315 | 266,138 |  |  |  |
| P00203343-1 | 8/29/2015 | 11:28:38 AM | LAU-12 | EAA | TV | OFU | 44 | 146,852 |  |  |  |
| P00203442-1 | 8/29/2015 | 11:29:00 AM | RAI-13 | ECC | TV | OCO | 1,437 | 484,819 |  |  |  |
| P00203371-1 | 8/29/2015 | 11:30:41 AM | EGT-12 | EBE | TV | OCO | 6 | 4,316 |  |  |  |
| P00205082-1 | 8/29/2015 | 11:30:50 AM | FWD-01 | EBJ | TV | SBF | - | 2,558,346 |  |  |  |
| P00203495-1 | 8/29/2015 | 11:30:51 AM | SUN-01 | ECA | TV | OCO | 5,658 | 520,536 |  |  |  |
| P00209786-1 | 8/29/2015 | 11:31:04 AM | TLN-0136 | ECE | TV | OCO | 876 | 1,371,309 |  |  |  |
| P00203418-1 | 8/29/2015 | 11:31:52 AM | LGY-12 | EAD | TV | OCO | 9 | 119,987 |  |  |  |
| P00203413-1 | 8/29/2015 | 11:31:57 AM | CPV-13 | EAD | TV | SCB | 577 | 193,414 |  |  |  |
| P00211664-1 | 8/29/2015 | 11:32:00 AM | MIL-23 | ECE | TV | OCO | 3 | 8,593 |  |  |  |
| P00203407-1 | 8/29/2015 | 11:32:41 AM | GRI-15 | ECC | EF | UPC | 9 | 17,111 |  |  |  |
| P00203577-1 | 8/29/2015 | 11:33:00 AM | ANA-01 | EAC | TV | OCO | 4,244 | 2,921,086 |  |  |  |
| P00206048-1 | 8/29/2015 | 11:34:20 AM | HAM-13 | EAC | TV | OCO | - | 5,665 |  |  |  |
| P00203450-1 | 8/29/2015 | 11:34:28 AM | KIT-25 | EBH | TV | OCO | 4 | 343 |  |  |  |
| P00203457-1 | 8/29/2015 | 11:34:37 AM | HEM-15 | ECA | TV | OCO | 807 | 924,849 |  |  |  |
| P00207548-1 | 8/29/2015 | 11:34:53 AM | BUC-16 | ECA | TV | OCO | 124 | 108,491 |  |  |  |
| P00205828-1 | 8/29/2015 | 11:34:53 AM | BUC-16 | ECA | TV | OCO | 525 | 270,699 |  |  |  |
| P00203481-1 | 8/29/2015 | 11:35:00 AM | KIN-23 | ECE | TV | OCO | 3 | 10,812 |  |  |  |
| P00208606-1 | 8/29/2015 | 11:35:07 AM | BDI-13 | EBI | TV | OCO | 23 | 18,240 |  |  |  |
| P00203500-1 | 8/29/2015 | 11:36:00 AM | WLS-16 | EAC | TV | OCO | 27 | 128,951 |  |  |  |
| P00213039-1 | 8/29/2015 | 11:36:40 AM | WLS-16 | EAC | TV |  | - | 6,494 |  |  |  |
| P00207150-1 | 8/29/2015 | 11:37:13 AM | VWY-15 | EAA | TV | OCO | 154 | 336,513 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00209696-1 | 8/29/2015 | 11:38:08 AM | BRI-17 | EAA | TV | OHR | 529 | 668,153 |  |  |  |
| P00203518-1 | 8/29/2015 | 11:38:27 AM | LGY-15 | EAD | TV | OFU | 4 | 8,502 |  |  |  |
| P00203546-1 | 8/29/2015 | 11:38:52 AM | VIC-15 | EBJ | TV | SCB | 1,117 | 1,210 |  |  |  |
| P00203535-1 | 8/29/2015 | 11:39:11 AM | CLV-16 | EAD | TV | OFU | 21 | 14,710 |  |  |  |
| P00203709-1 | 8/29/2015 | 11:40:00 AM | HEM-13 | ECA | TV | OPO | 70 | 130,717 |  |  |  |
| P00203564-1 | 8/29/2015 | 11:40:06 AM | HKX-16 | EAC | TV | OPO | 177 | 255,490 |  |  |  |
| P00209039-1 | 8/29/2015 | 11:40:39 AM | HKX-16 | EAC | TV | OCO | 69 | 57,582 |  |  |  |
| P00203610-1 | 8/29/2015 | 11:41:00 AM | NUG-25 | EAA | TV | OCO | 1,196 | 263,476 |  |  |  |
| P00203579-1 | 8/29/2015 | 11:42:02 AM | CHA-12 | ECC | TV | OFU | 1 | 565 |  |  |  |
| P00203606-1 | 8/29/2015 | 11:42:14 AM | MWD-15 | EBE | TV | OCO | 72 | 53,593 |  |  |  |
| P00203590-1 | 8/29/2015 | 11:42:18 AM | HLC-23 | EAD | TV | OFU | 51 | 170,032 |  |  |  |
| P00210127-1 | 8/29/2015 | 11:42:47 AM | HAP-16 | EAA | TV | OCO | 161 | 637,399 |  |  |  |
| P00207726-1 | 8/29/2015 | 11:42:48 AM | WOB-23 | EAA | TV | OHR | 579 | 601,620 |  |  |  |
| P00213365-1 | 8/29/2015 | 11:43:17 AM | ALG-12 | EAC | TV | OCO | 24 | 103,745 |  |  |  |
| P00212119-1 | 8/29/2015 | 11:43:27 AM | HAP-16 | EAA | TV | OFU | 38 | 171,664 |  |  |  |
| P00203631-1 | 8/29/2015 | 11:44:19 AM | LON-17 | ECC | EF | OFU | 12 | 18,527 |  |  |  |
| P00210342-1 | 8/29/2015 | 11:44:32 AM | VWY-12 | EAA | TV | OFU | 159 | 371,300 |  |  |  |
| P00208014-1 | 8/29/2015 | 11:45:00 AM | PET-13 | EAC | TV | OCO | 1,579 | 4,151,151 |  |  |  |
| P00209651-1 | 8/29/2015 | 11:45:06 AM | LGY-12 | EAD | TV | OCO | 329 | 794,529 |  |  |  |
| P00203644-1 | 8/29/2015 | 11:45:16 AM | HEM-13 | ECA | TV | OPO | - | 1,385 |  |  |  |
| P00206105-1 | 8/29/2015 | 11:45:36 AM | WOB-25 | EAA | TV | SCB | 1,650 | 1,034,001 |  |  |  |
| P00203669-1 | 8/29/2015 | 11:45:48 AM | FRA-12 | ECD | TV | OCO | 277 | 38,494 |  |  |  |
| P00203712-1 | 8/29/2015 | 11:45:53 AM | CLV-16 | EAD | TV | OFU | 135 | 93,987 |  |  |  |
| P00203662-1 | 8/29/2015 | 11:46:42 AM | EGT-12 | EBE | TV | OCO | 2 | 1,403 |  |  |  |
| P00207642-1 | 8/29/2015 | 11:47:35 AM | SCH-13 | EAA | TV | OIN | 1,252 | (1) |  |  |  |
| P00203699-1 | 8/29/2015 | 11:47:53 AM | SLA-13 | EAA | TV | SCB | 35 | 11,726 |  |  |  |
| P00203704-1 | 8/29/2015 | 11:48:23 AM | STA-26 | EBJ | TV | SCB | 3,130 | 323,105 |  |  |  |
| P00203693-1 | 8/29/2015 | 11:48:35 AM | BAK-25 | EAA | TV | OCO | 112 | 208,167 |  |  |  |
| P00203695-1 | 8/29/2015 | 11:48:37 AM | BAK-23 | EAA | TV | OCO | 36 | 180,040 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00203734-1 | 8/29/2015 | 11:49:00 AM | SEM-15 | EAA | TV | OCO | 2,290 | 3,090,528 |  |  |  |
| P00209422-1 | 8/29/2015 | 11:49:00 AM | GBK-15 | EAD | TV | OCO | 36 | 155,887 |  |  |  |
| P00203731-1 | 8/29/2015 | 11:49:28 AM | HAP-16 | EAA | TV | SCB | 404 | 224,790 |  |  |  |
| P00203741-1 | 8/29/2015 | 11:50:00 AM | WOO-25 | ECA | TV | OCO | 1 | 1,431 |  |  |  |
| P00209782-1 | 8/29/2015 | 11:51:00 AM | ALG-15 | EAA | TV | OCO | 238 | 533,108 |  |  |  |
| P00203753-1 | 8/29/2015 | 11:51:00 AM | VIS-23 | EAA | TV | OCO | 1 | 5,250 |  |  |  |
| P00203766-1 | 8/29/2015 | 11:51:00 AM | KIN-21 | ECE | TV | OCO | 29 | 90,597 |  |  |  |
| P00203797-1 | 8/29/2015 | 11:51:34 AM | LAB-23 | EAA | TV | OHR | 195 | 81,149 |  |  |  |
| P00209295-1 | 8/29/2015 | 11:51:39 AM | HKX-16 | EAC | TV | OCO | 41 | 157,333 |  |  |  |
| P00203780-1 | 8/29/2015 | 11:52:00 AM | SUM-21 | EAC | TV | OCO | - | 4,354 |  |  |  |
| P00210305-1 | 8/29/2015 | 11:52:00 AM | BHS-14 | EAA | TV | OCO | 68 | 225,812 |  |  |  |
| P00212290-1 | 8/29/2015 | 11:52:14 AM | BRW-15 | EAC |  |  | 15 | 67,224 |  |  |  |
| P00203802-1 | 8/29/2015 | 11:52:14 AM | HLC-24 | EAD | TV | SCB | 1,380 | 562,281 |  |  |  |
| P00203805-1 | 8/29/2015 | 11:52:24 AM | LAU-12 | EAA | TV | SCB | 539 | 405,049 |  |  |  |
| P00204860-1 | 8/29/2015 | 11:53:00 AM | SLA-16 | EAA | TV | OCO | 776 | 449,162 |  |  |  |
| P00203825-1 | 8/29/2015 | 11:53:00 AM | LYN-14 | EAA | TV | SCB | 644 | 1,134,041 |  |  |  |
| P00203808-1 | 8/29/2015 | 11:53:00 AM | WLS-16 | EAC | TV | OCO | 50 | 214,967 |  |  |  |
| P00203786-1 | 8/29/2015 | 11:53:16 AM | GBK-15 | EAD | TV | OFU | 14 | 47,132 |  |  |  |
| P00212106-1 | 8/29/2015 | 11:54:00 AM | VIS-22 | EAA |  |  | 1,789 | 4,641,839 |  |  |  |
| P00206192-1 | 8/29/2015 | 11:54:29 AM | FRU-25 | ECA | TV | OFU | 47 | 59,512 |  |  |  |
| P00203839-1 | 8/29/2015 | 11:54:59 AM | CRE-15 | EAD | TV | SCB | 1,439 | 1,307,743 |  |  |  |
| P00208182-1 | 8/29/2015 | 11:55:54 AM | OSC-23 | EBI | TV | OCO | 7 | 4,023 |  |  |  |
| P00203874-1 | 8/29/2015 | 11:58:00 AM | PEA-15 | EBJ | TV | OCO | 30 | 27,600 |  |  |  |
| P00203941-1 | 8/29/2015 | 11:58:43 AM | NUG-26 | EAA | TV | OHR | 332 | 88,229 |  |  |  |
| P00204325-1 | 8/29/2015 | 11:59:02 AM | FNW-16 | ECD | TV | OCO | 23 | 10,796 |  |  |  |
| P00204249-1 | 8/29/2015 | 11:59:56 AM | GBK-15 | EAD | TV | OHR | 494 | 306,898 |  |  |  |
| P00208006-1 | 8/29/2015 | 11:59:56 AM | CRE-15 | EAD | TV | OCO | - | 49,121 |  |  |  |
| P00213513-1 | 8/29/2015 | 12:00:18 PM | NLM-12 | EAC | TV | OCO | 103 | 468,366 |  |  |  |
| P00210663-1 | 8/29/2015 | 12:00:41 PM | CUS-15 | EAA | TV | OCO | 108 | 568,554 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00203924-1 | 8/29/2015 | 12:01:09 PM | KIN-23 | ECE | TV | OCO | 1 | 1,981 |  |  |  |
| P00203938-1 | 8/29/2015 | 12:02:00 PM | RIT-16 | EAC | TV | OCO | 67 | 46,450 |  |  |  |
| P00203957-1 | 8/29/2015 | 12:02:40 PM | SLA-15 | EAA | TV | OFU | 659 | 195,415 |  |  |  |
| P00203958-1 | 8/29/2015 | 12:02:45 PM | SUM-21 | EAC | TV | OCO | 820 | 2,784,205 |  |  |  |
| P00203945-1 | 8/29/2015 | 12:02:50 PM | CHI-12 | ECD | TV | OCO | 60 | 32,968 |  |  |  |
| P00211791-1 | 8/29/2015 | 12:03:07 PM | BLA-12 | EAA | TV | OTR | 175 | 527,085 |  |  |  |
| P00206971-1 | 8/29/2015 | 12:04:00 PM | BTN-36 | EAC | TV | OCO | 84 | 340,456 |  |  |  |
| P00205769-1 | 8/29/2015 | 12:04:00 PM | TLN-0157 | EBI | TV | SWT | 2,616 | 281,351 |  |  |  |
| P00203977-1 | 8/29/2015 | 12:04:05 PM | WAY-16 | EBD | TV | OCO | 4,030 | 146,289 |  |  |  |
| P00203980-1 | 8/29/2015 | 12:04:35 PM | LYN-26 | EAA | TV | OCO | 2,362 | 3,052,609 |  |  |  |
| P00203965-1 | 8/29/2015 | 12:04:49 PM | ASB-17 | EBJ | TV | OCO | 18 | 24,433 |  |  |  |
| P00203983-1 | 8/29/2015 | 12:05:00 PM | BHL-15 | ECE | TV | OCO | 41 | 54,620 |  |  |  |
| P00203981-1 | 8/29/2015 | 12:05:41 PM | FNW-17 | ECD | EF | OFU | 41 | 15,616 |  |  |  |
| P00203979-1 | 8/29/2015 | 12:05:45 PM | MUR-13 | ECE | TV | OCO | 6 | 996 |  |  |  |
| P00204001-1 | 8/29/2015 | 12:06:00 PM | EPO-13 | ECD | TV | OCO | 2 | 3,178 |  |  |  |
| P00210191-1 | 8/29/2015 | 12:06:00 PM | CRE-12 | EAD | TV | OCO | 80 | 325,813 |  |  |  |
| P00203990-1 | 8/29/2015 | 12:06:00 PM | SCH-15 | EAA | TV | OCO | 62 | 194,310 |  |  |  |
| P00204005-1 | 8/29/2015 | 12:06:05 PM | BRI-17 | EAA | TV | OPO | 1,715 | 1,236,601 |  |  |  |
| P00204068-1 | 8/29/2015 | 12:06:37 PM | MVW-15 | EBJ | TV | OHR | 447 | 26,127 |  |  |  |
| P00205921-1 | 8/29/2015 | 12:07:00 PM | TLN-0127 | ECA | TV | OCO | 6,019 | (1) |  |  |  |
| P00210434-1 | 8/29/2015 | 12:07:00 PM | SCH-16 | EAA | TV | OCO | - | 241,646 |  |  |  |
| P00208030-1 | 8/29/2015 | 12:07:00 PM | MCA-15 | ECC | TV | OFU | 18 | 46,984 |  |  |  |
| P00204033-1 | 8/29/2015 | 12:07:05 PM | LAB-23 | EAA | TV | SCB | 451 | 302,516 |  |  |  |
| P00204076-1 | 8/29/2015 | 12:07:22 PM | KEN-12 | EAA | TV | SCB | 1,912 | 22,242 |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00204009-1 | 8/29/2015 | 12:07:25 PM | SCH-16 | EAA | TV | OFU | 117 | (1) |  |  |  |
| P00204021-1 | 8/29/2015 | 12:08:09 PM | CLV-16 | EAD | TV | OFU | 57 | 103,598 |  |  |  |
| P00211815-1 | 8/29/2015 | 12:08:23 PM | LYN-24 | EAA | TV | OFU | 32 | 179,214 |  |  |  |
| P00207502-1 | 8/29/2015 | 12:08:33 PM | FNW-16 | ECD | TV | OCO | 21 | 23,889 |  |  |  |
| P00204044-1 | 8/29/2015 | 12:08:37 PM | LOL-21 | ECD | TV | OCO | 505 | 166,818 |  |  |  |
| P00204069-1 | 8/29/2015 | 12:09:00 PM | SUM-22 | EAC | TV | SCB | 311 | 432,254 |  |  |  |
| P00204065-1 | 8/29/2015 | 12:09:00 PM | EDG-15 | ECA | TV | OSV | 2 | 2,716 |  |  |  |
| P00208297-1 | 8/29/2015 | 12:09:05 PM | LAB-23 | EAA | TV | OCO | - | 429,221 |  |  |  |
| P00204072-1 | 8/29/2015 | 12:09:05 PM | NBO-26 | EBD | TV | OPO | 958 | 1,367,573 |  |  |  |
| P00207955-1 | 8/29/2015 | 12:09:16 PM | HKX-13 | EAC | TV | OCR | 563 | 579,844 |  |  |  |
| P00204067-1 | 8/29/2015 | 12:10:04 PM | CLV-16 | EAD | TV | OCO | 30 | 70,111 |  |  |  |
| P00204085-1 | 8/29/2015 | 12:10:50 PM | LLS-15 | EAA | TV | SCB | 1,306 | 1,131,039 |  |  |  |
| P00204756-1 | 8/29/2015 | 12:10:58 PM | PMA-16 | ECE | TV | OCO | 834 | 174,890 |  |  |  |
| P00206729-1 | 8/29/2015 | 12:11:06 PM | LLS-17 | EAA | TV | UTC | 440 | 926,097 |  |  |  |
| P00204125-1 | 8/29/2015 | 12:11:40 PM | ORT-23 | ECA | TV | OCO | 2,656 | 976,478 |  |  |  |
| P00209281-1 | 8/29/2015 | 12:12:22 PM | SCH-16 | EAA | TV | OSW | 156 | 305,613 |  |  |  |
| P00204158-1 | 8/29/2015 | 12:12:45 PM | FWY-12 | EBJ | TV | OCO | 77 | 42,354 |  |  |  |
| P00212573-1 | 8/29/2015 | 12:12:54 PM | SCH-13 | EAA |  |  | 230 | 634,693 |  |  |  |
| P00210274-1 | 8/29/2015 | 12:13:07 PM | BTN-36 | EAC | TV | OCO | 93 | 369,405 |  |  |  |
| P00204139-1 | 8/29/2015 | 12:13:20 PM | SWE-13 | EBJ | EF | OTR | 18 | 28,310 |  |  |  |
| P00204302-1 | 8/29/2015 | 12:13:46 PM | DES-15 | EBJ | TV | OHR | 290 | 325,762 |  |  |  |
| P00211578-1 | 8/29/2015 | 12:14:00 PM | CPV-15 | EAD | TV | OCO | 21 | 75,843 |  |  |  |
| P00204268-1 | 8/29/2015 | 12:14:00 PM | NUG-26 | EAA | TV | OCO | 78 | 119,474 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00208017-1 | 8/29/2015 | 12:14:07 PM | BRI-14 | EAA | TV | OFU | 266 | 81,414 |  |  |  |
| P00207464-1 | 8/29/2015 | 12:14:12 PM | TLN-0089 | ECE | TV | OCO | 4,471 | 1,560,960 |  |  |  |
| P00204255-1 | 8/29/2015 | 12:14:43 PM | SHE-26 | ECE | TV | OCO | 594 | 1,091,396 |  |  |  |
| P00204210-1 | 8/29/2015 | 12:15:00 PM | VIK-25 | EAA | TV | OCO | 2,453 | 2,309,948 |  |  |  |
| P00204656-1 | 8/29/2015 | 12:15:00 PM | BRW-15 | EAC | TV | OCO | 157 | 698,064 |  |  |  |
| P00204185-1 | 8/29/2015 | 12:15:03 PM | CLV-16 | EAD | TV | OFU | 24 | 52,421 |  |  |  |
| P00204179-1 | 8/29/2015 | 12:15:05 PM | SLA-16 | EAA | TV | OCO | 30 | 17,918 |  |  |  |
| P00204183-1 | 8/29/2015 | 12:15:20 PM | CLV-16 | EAD | EF | PTF | 3 | 5,514 |  |  |  |
| P00204196-1 | 8/29/2015 | 12:15:34 PM | SWA-12 | EAD | TV | OFC | 18 | 74,549 |  |  |  |
| P00204220-1 | 8/29/2015 | 12:16:06 PM | VIS-26 | EAA | TV | SCB | 1,065 | 1,418,349 |  |  |  |
| P00204222-1 | 8/29/2015 | 12:16:52 PM | MAP-13 | EBE | TV | OCO | 32 | 16,239 |  |  |  |
| P00204242-1 | 8/29/2015 | 12:17:01 PM | SOM-16 | EBE | TV | OCO | 3,766 | 1,174,378 |  |  |  |
| P00204234-1 | 8/29/2015 | 12:17:43 PM | SLA-17 | EAA | TV | OTF | 2 | 8,347 |  |  |  |
| P00208094-1 | 8/29/2015 | 12:18:00 PM | LON-17 | ECC | TF | OCO | 11 | 17,787 |  |  |  |
| P00204241-1 | 8/29/2015 | 12:18:00 PM | SCH-12 | EAA | EF | OFU | 26 | 117,187 |  |  |  |
| P00211164-1 | 8/29/2015 | 12:18:58 PM | CRE-12 | EAD | TV | OCO | 39 | 67,700 |  |  |  |
| P00204290-1 | 8/29/2015 | 12:20:00 PM | VIS-25 | EAA | OD | OCO | 1,062 | 1,705,048 |  |  |  |
| P00204498-1 | 8/29/2015 | 12:20:37 PM | KAP-16 | ECA | TV | OCO | 297 | 51,302 |  |  |  |
| P00204291-1 | 8/29/2015 | 12:20:41 PM | HAN-13 | EAA | TV | SCB | 1,294 | 927,604 |  |  |  |
| P00204319-1 | 8/29/2015 | 12:22:00 PM | GRI-16 | ECC | TV | OCO | 2 | 2,457 |  |  |  |
| P00204305-1 | 8/29/2015 | 12:22:00 PM | BTN-36 | EAC | TV | OCO | 3 | 14,442 |  |  |  |
| P00204322-1 | 8/29/2015 | 12:22:00 PM | WOB-23 | EAA | TV | OFU | 101 | 430,326 |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00204317-1 | 8/29/2015 | 12:22:00 PM | WLK-13 | ECA | TV | OTR | 36 | 35,874 |  |  |  |
| P00204315-1 | 8/29/2015 | 12:22:20 PM | FRA-13 | ECD | EF | OTF | 1 | 614 |  |  |  |
| P00205320-1 | 8/29/2015 | 12:22:35 PM | POU-13 | ECE | TV | OCO | - | 317,694 |  |  |  |
| P00204334-1 | 8/29/2015 | 12:22:36 PM | CHR-23 | ECE | TV | OCO | 446 | 370,500 |  |  |  |
| P00204343-1 | 8/29/2015 | 12:22:51 PM | SLA-17 | EAA | TV | SCB | 3,227 | (1) |  |  |  |
| P00210789-1 | 8/29/2015 | 12:23:00 PM | BAK-22 | EAA | TV | OCO | 172 | (1) |  |  |  |
| P00204329-1 | 8/29/2015 | 12:23:00 PM | HAP-13 | EAA | TV | OCO | 37 | 108,642 |  |  |  |
| P00204330-1 | 8/29/2015 | 12:23:34 PM | DUV-12 | EBD | TV | OSV | 1 | 2,744 |  |  |  |
| P00204337-1 | 8/29/2015 | 12:23:59 PM | LMC-27 | EBE | TV | OCO | 128 | 21,101 |  |  |  |
| P00204374-1 | 8/29/2015 | 12:24:22 PM | LAB-26 | EAA | TV | OCO | 876 | 307,733 |  |  |  |
| P00204348-1 | 8/29/2015 | 12:24:31 PM | CLV-16 | EAD | EF | UTF | 7 | 12,798 |  |  |  |
| P00204349-1 | 8/29/2015 | 12:24:37 PM | SOO-27 | EBI | TV | OCO | 13 | 11,696 |  |  |  |
| P00204666-1 | 8/29/2015 | 12:24:46 PM | KAP-16 | ECA | TV | OCO | 37 | 112,614 |  |  |  |
| P00208646-1 | 8/29/2015 | 12:25:20 PM | VWY-12 | EAA | TV | OPI | 119 | 330,509 |  |  |  |
| P00212601-1 | 8/29/2015 | 12:25:23 PM | VWY-15 | EAA |  | OFU | 488 | 2,227,999 |  |  |  |
| P00204371-1 | 8/29/2015 | 12:25:25 PM | HAP-16 | EAA | TV | OFU | 113 | 387,057 |  |  |  |
| P00204810-1 | 8/29/2015 | 12:25:29 PM | CED-17 | ECA | TV | OCO | 719 | 281,033 |  |  |  |
| P00204378-1 | 8/29/2015 | 12:25:52 PM | BRW-16 | EAC | TV | OFU | 407 | 761,443 |  |  |  |
| P00204462-1 | 8/29/2015 | 12:26:28 PM | NNO-15 | EBJ | TV | OHR | 483 | 203,053 |  |  |  |
| P00205756-1 | 8/29/2015 | 12:26:39 PM | PLY-13 | EAA | TV | OCO | 538 | 1,422,997 |  |  |  |
| P00204419-1 | 8/29/2015 | 12:27:00 PM | HAN-15 | EAA | TV | OCO | 1 | 760 |  |  |  |
| P00210657-1 | 8/29/2015 | 12:27:00 PM | VIS-23 | EAA | TV | OCO | 114 | 372,953 |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00210679-1 | 8/29/2015 | 12:27:11 PM | HAP-13 | EAA | TV | OCO | 23 | 67,268 |  |  |  |
| P00204189-1 | 8/29/2015 | 12:27:50 PM | KIN-01 | ECE | TV | OCO | 1,475 | 518,263 |  |  |  |
| P00211658-1 | 8/29/2015 | 12:28:14 PM | MIL-23 | ECE | TV | OCO | 32 | 65,216 |  |  |  |
| P00205281-1 | 8/29/2015 | 12:28:14 PM | MIL-23 | ECE | TV | OCO | 1,312 | (1) |  |  |  |
| P00204454-1 | 8/29/2015 | 12:28:27 PM | ROE-13 | EAA | TV | OCO | 478 | 841,771 |  |  |  |
| P00204487-1 | 8/29/2015 | 12:29:00 PM | AVO-17 | EBD | TV | OCO | 283 | 47,358 |  |  |  |
| P00204548-1 | 8/29/2015 | 12:29:00 PM | CUS-16 | EAA | TV | OCO | 106 | 131,053 |  |  |  |
| P00208459-1 | 8/29/2015 | 12:29:29 PM | KNM-25 | EBD | TV | OCO | 1,504 | 1,925,956 |  |  |  |
| P00204526-1 | 8/29/2015 | 12:30:00 PM | NHL-17 | EBD | TV | OCR | 452 | (1) |  |  |  |
| P00204504-1 | 8/29/2015 | 12:30:00 PM | KNM-26 | EBD | TV | OCO | 1,965 | 4,474,166 |  |  |  |
| P00205832-1 | 8/29/2015 | 12:30:00 PM | WIN-13 | ECE | TV | OCO | 1,396 | 723,983 |  |  |  |
| P00204537-1 | 8/29/2015 | 12:30:57 PM | MHT-16 | EBJ | TV | SCB | 670 | 59,217 |  |  |  |
| P00206731-1 | 8/29/2015 | 12:31:00 PM | EPO-13 | ECD | TV | OCO | 7 | 22,711 |  |  |  |
| P00211825-1 | 8/29/2015 | 12:31:36 PM | LYN-24 | EAA | TV | OFU | 149 | 348,191 |  |  |  |
| P00204665-1 | 8/29/2015 | 12:31:57 PM | MCW-14 | ECE | TV | OCO | - | - |  |  |  |
| P00203947-1 | 8/29/2015 | 12:32:42 PM | BLA-12 | EAA | TV | OCO | 35 | 163,728 |  |  |  |
| P00211640-1 | 8/29/2015 | 12:33:07 PM | BAK-25 | EAA | TV | OCO | 260 | 574,808 |  |  |  |
| P00211786-1 | 8/29/2015 | 12:33:16 PM | BLA-12 | EAA | TV | OFU | 131 | 394,260 |  |  |  |
| P00204587-1 | 8/29/2015 | 12:33:32 PM | OLD-23 | EAA | TV | SCB | 594 | 523,116 |  |  |  |
| P00204592-1 | 8/29/2015 | 12:33:37 PM | LEA-15 | EBJ | TV | SCB | 2,377 | 279,535 |  |  |  |
| P00207905-1 | 8/29/2015 | 12:34:00 PM | LGY-12 | EAD | TV | OCO | 583 | 867,343 |  |  |  |
| P00204586-1 | 8/29/2015 | 12:34:00 PM | NBO-22 | EBD | TV | OTF | 2 | 2,994 |  |  |  |
| P00207075-1 | 8/29/2015 | 12:34:23 PM | WAY-15 | EBD | TV | OCO | 17 | 34,912 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00204598-1 | 8/29/2015 | 12:35:02 PM | MST-25 | EBJ | TV | UTC | 39 | 39,224 |  |  |  |
| P00204599-1 | 8/29/2015 | 12:35:06 PM | EAR-17 | EBJ | TV | OCO | 13 | 4,431 |  |  |  |
| P00207620-1 | 8/29/2015 | 12:35:51 PM | ING-17 | EBD | TV | OCO | 768 | 296,346 |  |  |  |
| P00204639-1 | 8/29/2015 | 12:36:00 PM | PTR-14 | EAA | TV | OCO | 31 | 157,316 |  |  |  |
| P00207063-1 | 8/29/2015 | 12:36:33 PM | WOB-23 | EAA | TV | OHR | 90 | 113,116 |  |  |  |
| P00207813-1 | 8/29/2015 | 12:38:00 PM | PLY-13 | EAA | TV | OPO | 34 | 168,371 |  |  |  |
| P00204671-1 | 8/29/2015 | 12:38:24 PM | CHI-12 | ECD | TV | OCO | 115 | 54,771 |  |  |  |
| P00206341-1 | 8/29/2015 | 12:38:54 PM | MED-01 | EBE | TV | OCO | 2,189 | 751,748 |  |  |  |
| P00204705-1 | 8/29/2015 | 12:38:58 PM | FCR-11 | EBI | TV | OFC | 3,307 | 452,515 |  |  |  |
| P00204690-1 | 8/29/2015 | 12:39:18 PM | PAN-15 | EBJ | TV | OFU | 78 | 91,251 |  |  |  |
| P00207622-1 | 8/29/2015 | 12:39:24 PM | WIN-12 | ECE | TV | OCO | 20 | 37,337 |  |  |  |
| P00204719-1 | 8/29/2015 | 12:40:23 PM | MED-35 | EBE | TV | OCO | - | 84,431 |  |  |  |
| P00207076-1 | 8/29/2015 | 12:40:52 PM | JUA-14 | EBD | TV | OCO | 88 | 160,059 |  |  |  |
| P00206815-1 | 8/29/2015 | 12:41:07 PM | TLN-0173 | EBJ |  | SWT | 2,950 | 1,183,072 |  |  |  |
| P00204728-1 | 8/29/2015 | 12:41:08 PM | SWD-13 | ECE | TV | OCO | 392 | 565,942 |  |  |  |
| P00205055-1 | 8/29/2015 | 12:41:13 PM | LLT-16 | EBD | TV | OCO | 558 | 485,432 |  |  |  |
| P00204721-1 | 8/29/2015 | 12:41:17 PM | SHA-01 | ECA | TV | OCO | 4,804 | 1,675,395 |  |  |  |
| P00204730-1 | 8/29/2015 | 12:41:28 PM | OVE-15 | EBE | TV | OCO | 659 | 184,476 |  |  |  |
| P00204752-1 | 8/29/2015 | 12:41:33 PM | BHS-12 | EAA | TV | SCB | 106 | 570,012 |  |  |  |
| P00211454-1 | 8/29/2015 | 12:42:00 PM | WLS-16 | EAC | TV | OCO | 226 | 337,612 |  |  |  |
| P00206829-1 | 8/29/2015 | 12:42:17 PM | KNM-25 | EBD | TV | OCO | - | 244,408 |  |  |  |
| P00206072-1 | 8/29/2015 | 12:42:37 PM | NHL-16 | EBD | TV | OCO | 2,075 | 1,520,560 |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00204786-1 | 8/29/2015 | 12:43:00 PM | SWD-12 | ECE | TV | OCO | 1,431 | 735,124 |  |  |  |
| P00204751-1 | 8/29/2015 | 12:43:00 PM | WLS-15 | EAC | TV | OCO | 1 | 4,214 |  |  |  |
| P00204765-1 | 8/29/2015 | 12:43:39 PM | EDG-15 | ECA | EF | OTF | 3 | 2,053 |  |  |  |
| P00204789-1 | 8/29/2015 | 12:43:53 PM | LMD-13 | EBJ | TV | SCB | 1,938 | 192,876 |  |  |  |
| P00204787-1 | 8/29/2015 | 12:44:00 PM | CHI-12 | ECD | TV | OCO | 6 | 17,593 |  |  |  |
| P00204824-1 | 8/29/2015 | 12:44:48 PM | GAR-16 | ECA | TV | OCO | 2,098 | 50,107 |  |  |  |
| P00206016-1 | 8/29/2015 | 12:44:51 PM | MTH-17 | EBJ | AV | OFU | 15 | 23,682 |  |  |  |
| P00204795-1 | 8/29/2015 | 12:44:51 PM | LMC-25 | EBE | TV | OCO | 13 | 19,495 |  |  |  |
| P00204797-1 | 8/29/2015 | 12:44:59 PM | SME-12 | EBE | TV | OCO | 11 | 33,457 |  |  |  |
| P00204850-1 | 8/29/2015 | 12:45:00 PM | CHI-12 | ECD | TF | OCO | 118 | 361,970 |  |  |  |
| P00204808-1 | 8/29/2015 | 12:45:00 PM | LAU-13 | EAA | TV | OCO | 2 | 11,090 |  |  |  |
| P00204835-1 | 8/29/2015 | 12:45:44 PM | LGY-15 | EAD | TV | OSW | 406 | 258,980 |  |  |  |
| P00206493-1 | 8/29/2015 | 12:46:00 PM | SIL-15 | ECE | TV | OCO | 23 | 69,000 |  |  |  |
| P00204825-1 | 8/29/2015 | 12:46:09 PM | WOO-27 | ECA | TV | OTF | 2 | 2,505 |  |  |  |
| P00211683-1 | 8/29/2015 | 12:46:39 PM | BAK-22 | EAA | TV | OCO | - | 68,978 |  |  |  |
| P00205999-1 | 8/29/2015 | 12:46:41 PM | ING-16 | EBD | TV | OCO | 1,765 | 679,996 |  |  |  |
| P00204876-1 | 8/29/2015 | 12:46:49 PM | LYN-16 | EAA | TV | SCB | 40 | 40,856 |  |  |  |
| P00205413-1 | 8/29/2015 | 12:47:00 PM | LTA-18 | ECA | TF | OCO | 49 | 65,317 |  |  |  |
| P00208723-1 | 8/29/2015 | 12:47:00 PM | MIL-22 | ECE | TV | OCO | 41 | 195,008 |  |  |  |
| P00206811-1 | 8/29/2015 | 12:47:00 PM | TLN-0173 | EBJ | TV | SWT | 7,562 | 509,934 |  |  |  |
| P00204888-1 | 8/29/2015 | 12:47:19 PM | HWD-22 | EBD | TV | OCO | 1,539 | 434,964 |  |  |  |
| P00212617-1 | 8/29/2015 | 12:47:47 PM | CUS-13 | EAA |  |  | - | 53,775 |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00208236-1 | 8/29/2015 | 12:48:11 PM | FLD-15 | EAD | TV | OHR | 809 | 1,111,026 |  |  |  |
| P00204898-1 | 8/29/2015 | 12:48:37 PM | EDG-16 | ECA | TV | OTF | 4 | 3,254 |  |  |  |
| P00207788-1 | 8/29/2015 | 12:48:45 PM | MVW-13 | EBJ | TV | DNO | 1 | 598 |  |  |  |
| P00204938-1 | 8/29/2015 | 12:49:00 PM | LAU-14 | EAA | TV | OCO | 7 | 37,732 |  |  |  |
| P00211091-1 | 8/29/2015 | 12:49:22 PM | FLD-13 | EAD | TV | OCO | 252 | 802,024 |  |  |  |
| P00204973-1 | 8/29/2015 | 12:50:00 PM | HWD-23 | EBD | TV | OCO | 182 | 223,706 |  |  |  |
| P00207833-1 | 8/29/2015 | 12:50:00 PM | KAP-15 | ECA | TV | OCO | 3 | 5,622 |  |  |  |
| P00208447-1 | 8/29/2015 | 12:50:00 PM | PMA-15 | ECE | TV | OCO | 25 | 36,303 |  |  |  |
| P00206509-1 | 8/29/2015 | 12:50:27 PM | POU-15 | ECE | TV | OCO | 1,819 | 1,096,866 |  |  |  |
| P00209788-1 | 8/29/2015 | 12:50:39 PM | BHS-12 | EAA | TV | OSW | 130 | (1) |  |  |  |
| P00210013-1 | 8/29/2015 | 12:50:39 PM | BHS-12 | EAA | TV | OCO | 31 | 121,165 |  |  |  |
| P00208269-1 | 8/29/2015 | 12:51:00 PM | POU-15 | ECE | TV | OCO | 577 | 188,669 |  |  |  |
| P00204996-1 | 8/29/2015 | 12:51:42 PM | FLD-12 | EAD | TV | OTF | 8 | 14,492 |  |  |  |
| P00205059-1 | 8/29/2015 | 12:53:14 PM | PIP-22 | EBI | TV | SCB | 3,928 | 556,008 |  |  |  |
| P00205442-1 | 8/29/2015 | 12:53:43 PM | MIL-22 | ECE | TV | OCO | 569 | 859,935 |  |  |  |
| P00211064-1 | 8/29/2015 | 12:53:51 PM | SWA-16 | EAD | TV | OCO | 41 | 144,039 |  |  |  |
| P00205088-1 | 8/29/2015 | 12:54:00 PM | NLM-12 | EAC | TV | OCO | 12 | 56,727 |  |  |  |
| P00205057-1 | 8/29/2015 | 12:54:05 PM | HOB-17 | EBI | TV | OCO | 5 | 7,445 |  |  |  |
| P00208900-1 | 8/29/2015 | 12:54:25 PM | HKX-16 | EAC | TV | OCO | 45 | 58,440 |  |  |  |
| P00211131-1 | 8/29/2015 | 12:54:44 PM | MIL-22 | ECE | TV | OCO | 93 | 270,656 |  |  |  |
| P00208260-1 | 8/29/2015 | 12:55:31 PM | LLT-15 | EBD | TV | OCO | 44 | 33,500 |  |  |  |
| P00206207-1 | 8/29/2015 | 12:56:07 PM | WAY-13 | EBD | TV | OCO | 834 | 490,865 |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00207195-1 | 8/29/2015 | 12:56:40 PM | SWE-13 | EBJ | EF | OTR | 26 | 39,774 |  |  |  |
| P00205153-1 | 8/29/2015 | 12:56:45 PM | SKE-23 | ECE | TV | OCO | 582 | 247,353 |  |  |  |
| P00205128-1 | 8/29/2015 | 12:56:52 PM | ASB-17 | EBJ | TV | OFU | 35 | 43,128 |  |  |  |
| P00205962-1 | 8/29/2015 | 12:56:57 PM | MIL-17 | ECE | TV | OCO | 62 | 157,858 |  |  |  |
| P00211570-1 | 8/29/2015 | 12:57:00 PM | LGY-16 | EAD | TV | OCO | 21 | 35,088 |  |  |  |
| P00205137-1 | 8/29/2015 | 12:57:00 PM | BRW-15 | EAC | TV | OSW | 108 | 504,304 |  |  |  |
| P00211187-1 | 8/29/2015 | 12:59:47 PM | MIL-22 | ECE | TV | OCO | 15 | 45,707 |  |  |  |
| P00205272-1 | 8/29/2015 | 1:00:45 PM | RIV-16 | EAC | TV | SCB | 1,322 | 657,467 |  |  |  |
| P00205291-1 | 8/29/2015 | 1:01:45 PM | KIN-23 | ECE | TV | OCO | - | 24,567 |  |  |  |
| P00210631-1 | 8/29/2015 | 1:02:00 PM | HWD-25 | EBD | TV | OCO | 6 | 18,769 |  |  |  |
| P00205361-1 | 8/29/2015 | 1:02:10 PM | ROS-15 | EBD | TV | OCO | 121 | 96,361 |  |  |  |
| P00205789-1 | 8/29/2015 | 1:03:35 PM | KNM-23 | EBD | TV | OCO | 686 | 1,247,225 |  |  |  |
| P00208159-1 | 8/29/2015 | 1:04:10 PM | COT-16 | EBD | TV | OCO | 13 | 18,982 |  |  |  |
| P00205471-1 | 8/29/2015 | 1:04:16 PM | BRE-21 | ECE | TV | OCO | 12 | 26,777 |  |  |  |
| P00208592-1 | 8/29/2015 | 1:04:24 PM | KNM-23 | EBD | TV | OCO | 1,587 | 1,919,985 |  |  |  |
| P00205335-1 | 8/29/2015 | 1:05:00 PM | SWD-11 | ECE | EF | UTC | 27 | 80,249 |  |  |  |
| P00205865-1 | 8/29/2015 | 1:05:00 PM | TLN-0037 | ECA | TV | OCO | 5,427 | 487,073 |  |  |  |
| P00205877-1 | 8/29/2015 | 1:05:00 PM | TLN-0037 | ECA | TV | OCO | 2,816 | 636,416 |  |  |  |
| P00205354-1 | 8/29/2015 | 1:05:00 PM | HAP-13 | EAA | TV | OCO | 2 | 12,370 |  |  |  |
| P00205848-1 | 8/29/2015 | 1:05:00 PM | TLN-0037 | ECA | TV | OCO | 2,618 | 233,832 |  |  |  |
| P00210104-1 | 8/29/2015 | 1:05:02 PM | POU-13 | ECE | TV | OCO | 739 | 693,736 |  |  |  |
| P00205359-1 | 8/29/2015 | 1:06:00 PM | PIK-23 | EBF | TV | OTR | 34 | 9,026 |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00205373-1 | 8/29/2015 | 1:06:10 PM | JUA-14 | EBD | TV | OCO | 1,823 | 177,560 |  |  |  |
| P00207289-1 | 8/29/2015 | 1:06:43 PM | SKE-22 | ECE | TV | OCO | 10 | 33,017 |  |  |  |
| P00205379-1 | 8/29/2015 | 1:07:00 PM | SKI-13 | EBD | TV | OSV | 7 | 15,288 |  |  |  |
| P00207318-1 | 8/29/2015 | 1:07:00 PM | HAP-16 | EAA | TV | OCO | 53 | 178,693 |  |  |  |
| P00205414-1 | 8/29/2015 | 1:07:46 PM | PMA-15 | ECE | TV | OCO | 1,243 | 929,806 |  |  |  |
| P00205417-1 | 8/29/2015 | 1:08:21 PM | SKE-26 | ECE | TV | OCO | 1,590 | 421,854 |  |  |  |
| P00205451-1 | 8/29/2015 | 1:08:41 PM | WOB-26 | EAA | TV | SCB | 2,786 | 766,478 |  |  |  |
| P00205438-1 | 8/29/2015 | 1:08:54 PM | LLT-13 | EBD | TV | OCO | 150 | 74,759 |  |  |  |
| P00205453-1 | 8/29/2015 | 1:09:16 PM | ROS-22 | EBD | TV | OCO | 721 | 810,752 |  |  |  |
| P00205478-1 | 8/29/2015 | 1:10:00 PM | PIN-26 | EBD | TV | OCO | 9 | 14,938 |  |  |  |
| P00205484-1 | 8/29/2015 | 1:11:00 PM | BDI-15 | EBI | TV | OCO | 5 | 6,251 |  |  |  |
| P00210062-1 | 8/29/2015 | 1:11:22 PM | NBO-22 | EBD | TV | OCO | 122 | 332,023 |  |  |  |
| P00212970-1 | 8/29/2015 | 1:12:11 PM | CPV-15 | EAD | TV | OTR | 2 | 9,309 |  |  |  |
| P00205514-1 | 8/29/2015 | 1:12:36 PM | PHA-16 | EBE | TV | OCO | 35 | 55,406 |  |  |  |
| P00205539-1 | 8/29/2015 | 1:13:00 PM | SIL-15 | ECE | TV | OCO | 6 | 26,936 |  |  |  |
| P00206353-1 | 8/29/2015 | 1:13:02 PM | ROS-13 | EBD | TV | OCO | 66 | 170,885 |  |  |  |
| P00205524-1 | 8/29/2015 | 1:13:19 PM | GBK-13 | EAD | TV | OCO | 35 | 121,291 |  |  |  |
| P00205595-1 | 8/29/2015 | 1:13:44 PM | STA-26 | EBJ | TV | OFU | 496 | 217,760 |  |  |  |
| P00205549-1 | 8/29/2015 | 1:14:00 PM | WOO-25 | ECA | TV | OTF | 2 | 2,958 |  |  |  |
| P00205573-1 | 8/29/2015 | 1:14:51 PM | CHR-22 | ECE | TV | OCO | 507 | 244,550 |  |  |  |
| P00206182-1 | 8/29/2015 | 1:15:00 PM | GAR-16 | ECA | TO |  | 695 | 311,360 |  |  |  |
| P00209241-1 | 8/29/2015 | 1:15:15 PM | MAP-13 | EBE | TV | OFU | 7 | 19,529 |  |  |  |
| P00205591-1 | 8/29/2015 | 1:15:56 PM | UHL-25 | EBD | TV | OCO | 438 | 113,179 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00205614-1 | 8/29/2015 | 1:17:26 PM | WOB-27 | EAA | TV | SCB | 2,296 | (1) |  |  |  |
| P00205626-1 | 8/29/2015 | 1:17:36 PM | DUV-13 | EBD | TV | OCO | 692 | 741,859 |  |  |  |
| P00205632-1 | 8/29/2015 | 1:18:00 PM | SIL-15 | ECE | TV | OCO | - | 25,421 |  |  |  |
| P00205647-1 | 8/29/2015 | 1:19:00 PM | PAT-13 | ECC | EF | OTF | 3 | 8,505 |  |  |  |
| P00205651-1 | 8/29/2015 | 1:19:00 PM | SCH-13 | EAA | TV | OTF | 2 | 8,972 |  |  |  |
| P00205649-1 | 8/29/2015 | 1:19:00 PM | SIL-13 | ECE | TV | OCO | 13 | 56,163 |  |  |  |
| P00205658-1 | 8/29/2015 | 1:20:25 PM | CWD-23 | EBD | TV | OFU | 10 | 19,341 |  |  |  |
| P00205667-1 | 8/29/2015 | 1:21:07 PM | POU-16 | ECE | TV | OCO | 26 | 15,889 |  |  |  |
| P00205692-1 | 8/29/2015 | 1:22:12 PM | SAH-15 | EBD | TV | OCO | 1,374 | 246,884 |  |  |  |
| P00205696-1 | 8/29/2015 | 1:23:00 PM | CHI-12 | ECD | TV | OCO | 74 | 236,051 |  |  |  |
| P00205722-1 | 8/29/2015 | 1:23:52 PM | SEM-13 | EAA | TV | SCB | 105 | 195,864 |  |  |  |
| P00208041-1 | 8/29/2015 | 1:24:15 PM | ALG-15 | EAC | TV | OFU | 16 | 43,506 |  |  |  |
| P00205730-1 | 8/29/2015 | 1:24:22 PM | FLD-12 | EAD | TV | SCB | 1,451 | 626,590 |  |  |  |
| P00207280-1 | 8/29/2015 | 1:25:00 PM | SIL-15 | ECE | TV | OCO | 13 | 42,304 |  |  |  |
| P00207826-1 | 8/29/2015 | 1:25:17 PM | HWD-26 | EBD | TV | OCO | 111 | 312,729 |  |  |  |
| P00205741-1 | 8/29/2015 | 1:25:42 PM | SIN-23 | ECD | TV | OSV | 1 | 3,083 |  |  |  |
| P00205765-1 | 8/29/2015 | 1:26:02 PM | SHD-18 | EBI | TV | SCB | 1,217 | 371,621 |  |  |  |
| P00205768-1 | 8/29/2015 | 1:26:15 PM | PIN-26 | EBD | TV | OCO | 115 | 178,756 |  |  |  |
| P00205752-1 | 8/29/2015 | 1:26:37 PM | NOR-26 | EBD | TV | OCO | 61 | 114,193 |  |  |  |
| P00205758-1 | 8/29/2015 | 1:26:47 PM | FRA-13 | ECD | TV | OCO | 35 | 6,834 |  |  |  |
| P00205778-1 | 8/29/2015 | 1:28:00 PM | SCH-15 | EAA | TV | OCO | - | 168,122 |  |  |  |
| P00205794-1 | 8/29/2015 | 1:28:00 PM | COT-13 | EBD | TV | OCR | 2,000 | 1,848,136 |  |  |  |
| P00210072-1 | 8/29/2015 | 1:29:38 PM | GAR-13 | ECA |  |  | 27 | 32,618 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00205851-1 | 8/29/2015 | 1:32:00 PM | SIL-13 | ECE | TV | OCO | 5 | 14,207 |  |  |  |
| P00205852-1 | 8/29/2015 | 1:32:41 PM | ENU-18 | EBI | TV | OCO | 27 | 9,124 |  |  |  |
| P00206698-1 | 8/29/2015 | 1:33:00 PM | WAY-16 | EBD | TV | OCO | 2,015 | 859,936 |  |  |  |
| P00208624-1 | 8/29/2015 | 1:33:00 PM | WAY-12 | EBD | TV | OFU | 1,885 | 604,678 |  |  |  |
| P00209670-1 | 8/29/2015 | 1:33:31 PM | SIL-13 | ECE | TV | OCO | 8 | 14,938 |  |  |  |
| P00209253-1 | 8/29/2015 | 1:34:00 PM | HAM-13 | EAC | TV | OPO | 571 | 1,037,411 |  |  |  |
| P00205882-1 | 8/29/2015 | 1:34:21 PM | PET-15 | EAC | TV | OHR | 198 | 144,879 |  |  |  |
| P00206957-1 | 8/29/2015 | 1:34:30 PM | NHL-13 | EBD | TV | OCO | - | 1,231,247 |  |  |  |
| P00205901-1 | 8/29/2015 | 1:35:00 PM | SIL-13 | ECE | TV | OCO | 3 | 9,662 |  |  |  |
| P00208027-1 | 8/29/2015 | 1:35:30 PM | BRW-15 | EAC | TV | OFU | 43 | 189,096 |  |  |  |
| P00209058-1 | 8/29/2015 | 1:37:11 PM | LLS-01 | EAA | TV | OCO | 22 | 609,301 |  |  |  |
| P00205931-1 | 8/29/2015 | 1:37:13 PM | WAY-12 | EBD | TV | OCO | 61 | 51,471 |  |  |  |
| P00205934-1 | 8/29/2015 | 1:37:20 PM | WAY-15 | EBD | TV | OCO | 11 | 5,533 |  |  |  |
| P00205960-1 | 8/29/2015 | 1:37:28 PM | PET-13 | EAC | TV | OCO | 1,413 | 301,722 |  |  |  |
| P00211864-1 | 8/29/2015 | 1:37:53 PM | SEM-13 | EAA | TV | OCO | 32 | 84,140 |  |  |  |
| P00211425-1 | 8/29/2015 | 1:40:00 PM | TLN-0073 | EBD | TV | OCO | 7,781 | 264,554 |  |  |  |
| P00205981-1 | 8/29/2015 | 1:40:08 PM | WAY-15 | EBD | TV | OTF | 5 | 3,864 |  |  |  |
| P00206211-1 | 8/29/2015 | 1:40:55 PM | WAY-15 | EBD | TV | OCO | 156 | 105,966 |  |  |  |
| P00210453-1 | 8/29/2015 | 1:41:22 PM | SWA-12 | EAD | TV | OCO | 365 | 1,246,903 |  |  |  |
| P00209193-1 | 8/29/2015 | 1:42:13 PM | WOO-26 | ECA | TO | OFU | 25 | 98,285 |  |  |  |
| P00206047-1 | 8/29/2015 | 1:43:24 PM | BRO-15 | EAD | TV | OCO | 1,387 | 845,515 |  |  |  |
| P00206030-1 | 8/29/2015 | 1:43:29 PM | COT-16 | EBD | TV | OCO | 56 | 88,119 |  |  |  |
| P00206053-1 | 8/29/2015 | 1:43:59 PM | AVO-24 | EBD | TV | OCO | 2,409 | 244,675 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00206038-1 | 8/29/2015 | 1:44:34 PM | LLT-13 | EBD | TV | OCO | 40 | 68,823 |  |  |  |
| P00206068-1 | 8/29/2015 | 1:44:39 PM | CLV-16 | EAD | TV | SCB | 297 | 40,466 |  |  |  |
| P00206043-1 | 8/29/2015 | 1:44:49 PM | LOL-25 | ECD | TV | OCO | 45 | 19,698 |  |  |  |
| P00206057-1 | 8/29/2015 | 1:45:00 PM | GBK-15 | EAD | TV | OCO | 29 | 114,112 |  |  |  |
| P00206081-1 | 8/29/2015 | 1:47:00 PM | PLY-15 | EAA | TV | OCN | 9 | 50,625 |  |  |  |
| P00206091-1 | 8/29/2015 | 1:48:34 PM | CHI-12 | ECD | TO | OCO | 13 | 37,203 |  |  |  |
| P00206711-1 | 8/29/2015 | 1:48:59 PM | BEL-16 | EBJ | TV | UTC | 21 | 27,059 |  |  |  |
| P00206145-1 | 8/29/2015 | 1:52:15 PM | JUA-25 | EBD | TV | OCO | 1,658 | 266,546 |  |  |  |
| P00206150-1 | 8/29/2015 | 1:53:00 PM | POU-16 | ECE | TV | OCO | 5 | 15,979 |  |  |  |
| P00209705-1 | 8/29/2015 | 1:53:49 PM | LMD-16 | EBJ | TV | OCO | 33 | 26,854 |  |  |  |
| P00206149-1 | 8/29/2015 | 1:53:57 PM | CHA-12 | ECC | EF | OFU | 8 | 3,464 |  |  |  |
| P00207507-1 | 8/29/2015 | 1:54:00 PM | HAP-13 | EAA | TV | OCO | 46 | 134,811 |  |  |  |
| P00206157-1 | 8/29/2015 | 1:54:00 PM | SIL-15 | ECE | TV | OCO | 47 | 137,203 |  |  |  |
| P00206155-1 | 8/29/2015 | 1:54:18 PM | WAY-15 | EBD | TV | UTC | 7 | 3,401 |  |  |  |
| P00206165-1 | 8/29/2015 | 1:54:40 PM | BTN-38 | EAC | TV | SCB | 1,744 | 206,547 |  |  |  |
| P00210234-1 | 8/29/2015 | 1:54:41 PM | BLS-23 | EAA | TV | OCO | 201 | 701,306 |  |  |  |
| P00206168-1 | 8/29/2015 | 1:55:34 PM | WAY-15 | EBD | TV | UTC | 9 | 4,631 |  |  |  |
| P00206206-1 | 8/29/2015 | 1:56:30 PM | SBE-25 | EBE | TV | OCO | 22 | 60,409 |  |  |  |
| P00208662-1 | 8/29/2015 | 1:57:00 PM | PMA-12 | ECE | TV | OCO | 10 | 30,565 |  |  |  |
| P00211587-1 | 8/29/2015 | 1:57:00 PM | LGY-16 | EAD | TV | OCO | 32 | 130,648 |  |  |  |
| P00206200-1 | 8/29/2015 | 1:57:42 PM | KAP-13 | ECA | TV | OPO | 1 | 968 |  |  |  |
| P00210896-1 | 8/29/2015 | 1:58:00 PM | SBE-25 | EBE | TV | OCO | 16 | 46,456 |  |  |  |
| P00206208-1 | 8/29/2015 | 1:58:00 PM | ING-17 | EBD | TV | OSV | 4 | 6,964 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00213101-1 | 8/29/2015 | 1:58:15 PM | HAP-16 | EAA |  |  | 1 | 4,345 |  |  |  |
| P00206226-1 | 8/29/2015 | 1:59:00 PM | MTV-16 | EAC | TV | OSV | 1 | 6,097 |  |  |  |
| P00208704-1 | 8/29/2015 | 1:59:00 PM | CRE-16 | EAD | TV | OCO | 16 | 51,089 |  |  |  |
| P00206234-1 | 8/29/2015 | 2:00:00 PM | VIS-22 | EAA | TV | OTF | 1 | 6,340 |  |  |  |
| P00206233-1 | 8/29/2015 | 2:00:31 PM | HOU-25 | EBD | TV | OCO | 89 | 73,256 |  |  |  |
| P00207232-1 | 8/29/2015 | 2:01:25 PM | HAM-01 | EAC | TV | OCO | 1,984 | 701,509 |  |  |  |
| P00206471-1 | 8/29/2015 | 2:02:00 PM | FNW-13 | ECD | TV | OCO | 575 | 149,606 |  |  |  |
| P00206273-1 | 8/29/2015 | 2:02:37 PM | KAP-16 | ECA | TV | OCO | 1 | 1,078 |  |  |  |
| P00206288-1 | 8/29/2015 | 2:03:47 PM | HWD-25 | EBD | TV | OCO | 8 | 23,396 |  |  |  |
| P00206333-1 | 8/29/2015 | 2:06:00 PM | BTN-36 | EAC | TV | OCO | 2 | 6,989 |  |  |  |
| P00209460-1 | 8/29/2015 | 2:08:18 PM | SUM-21 | EAC | TV | OCO | - | 3,256 |  |  |  |
| P00206360-1 | 8/29/2015 | 2:09:21 PM | UHL-23 | EBD | TV | OTF | 4 | 3,642 |  |  |  |
| P00209734-1 | 8/29/2015 | 2:10:00 PM | HOB-16 | EBI | TV | OPI | 8 | 14,751 |  |  |  |
| P00207544-1 | 8/29/2015 | 2:12:54 PM | MIL-17 | ECE | TV | OCO | - | 19,241 |  |  |  |
| P00206428-1 | 8/29/2015 | 2:15:00 PM | RIT-16 | EAC | TV | OCO | 8 | 20,525 |  |  |  |
| P00206430-1 | 8/29/2015 | 2:15:49 PM | UHL-23 | EBD | TV | OCO | 110 | 34,623 |  |  |  |
| P00207528-1 | 8/29/2015 | 2:16:14 PM | KNM-23 | EBD | TV | OCO | 25 | 55,319 |  |  |  |
| P00206468-1 | 8/29/2015 | 2:18:00 PM | CHI-12 | ECD | TO | OTF | 3 | 9,652 |  |  |  |
| P00207311-1 | 8/29/2015 | 2:18:44 PM | BAR-13 | ECC | EF | PMF | 88 | 78,452 |  |  |  |
| P00206484-1 | 8/29/2015 | 2:19:00 PM | DUV-15 | EBD | TV | OCO | 11 | 29,832 |  |  |  |
| P00206878-1 | 8/29/2015 | 2:21:00 PM | SKE-22 | ECE | TV | OCO | 38 | 79,961 |  |  |  |
| P00206497-1 | 8/29/2015 | 2:21:04 PM | HOB-16 | EBI | TV | OCO | 6 | 1,620 |  |  |  |
| P00206781-1 | 8/29/2015 | 2:22:00 PM | PTR-14 | EAA | TV | OCO | 120 | 593,792 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00206513-1 | 8/29/2015 | 2:22:00 PM | WAY-15 | EBD | TV | OCO | 9 | 4,122 |  |  |  |
| P00207360-1 | 8/29/2015 | 2:24:01 PM | NOR-25 | EBD | TV | OCO | 35 | 58,220 |  |  |  |
| P00206526-1 | 8/29/2015 | 2:24:09 PM | SHD-17 | EBI | TV | OCO | 1 | 835 |  |  |  |
| P00206539-1 | 8/29/2015 | 2:24:13 PM | PAN-15 | EBJ | TV | SCB | 1,732 | 182,409 |  |  |  |
| P00208966-1 | 8/29/2015 | 2:25:00 PM | MCK-15 | EAA | TV | OCO | 4 | 20,714 |  |  |  |
| P00202170-2 | 8/29/2015 | 2:26:53 PM | BTR-21 | EBE | TV | OCO | 11 | 526 |  |  |  |
| P00209539-1 | 8/29/2015 | 2:27:00 PM | WIN-15 | ECE | TV | OCO | 84 | 106,385 |  |  |  |
| P00206569-1 | 8/29/2015 | 2:27:00 PM | RPT-22 | ECD | TV | OSV | 5 | 22,854 |  |  |  |
| P00208762-1 | 8/29/2015 | 2:28:30 PM | DGR-13 | ECA | TO |  | - | 11,347 |  |  |  |
| P00208716-1 | 8/29/2015 | 2:28:30 PM | DGR-13 | ECA | TO | OCO | 8 | 6 |  |  |  |
| P00206597-1 | 8/29/2015 | 2:29:23 PM | PAN-16 | EBJ | TV | SCB | 1,260 | 126,609 |  |  |  |
| P00211154-1 | 8/29/2015 | 2:31:57 PM | PLY-16 | EAA | TV | OFU | 21 | 61,928 |  |  |  |
| P00207129-1 | 8/29/2015 | 2:33:00 PM | MIL-17 | ECE | TV | OCO | 165 | 352,654 |  |  |  |
| P00208866-1 | 8/29/2015 | 2:33:19 PM | CRE-16 | EAD | TV | OFU | 222 | 589,876 |  |  |  |
| P00208234-1 | 8/29/2015 | 2:33:21 PM | STA-26 | EBJ | TV | SCB | 2,613 | 760,311 |  |  |  |
| P00206632-1 | 8/29/2015 | 2:33:54 PM | ALG-12 | EAC | TV | OFU | 11 | 31,912 |  |  |  |
| P00206655-1 | 8/29/2015 | 2:36:44 PM | MSI-25 | EBF | TV | OCO | 12 | 36,774 |  |  |  |
| P00206656-1 | 8/29/2015 | 2:36:45 PM | EGT-12 | EBE | TV | OCO | 5 | 2,836 |  |  |  |
| P00211659-1 | 8/29/2015 | 2:38:33 PM | MIL-23 | ECE | TV | OCO | 3 | 6,218 |  |  |  |
| P00206680-1 | 8/29/2015 | 2:38:38 PM | SIL-13 | ECE | TV | OSV | 1 | 2,972 |  |  |  |
| P00206695-1 | 8/29/2015 | 2:40:00 PM | WLS-13 | EAC | TV | OSV | 1 | 4,658 |  |  |  |
| P00206742-1 | 8/29/2015 | 2:44:58 PM | HWD-25 | EBD | TV | OAR | 17 | 44,777 |  |  |  |
| P00206818-1 | 8/29/2015 | 2:45:46 PM | HIG-16 | EBE | TV | OPO | 218 | 134,400 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00207975-1 | 8/29/2015 | 2:46:00 PM | RIT-16 | EAC | TV | OCO | 20 | 90,911 |  |  |  |
| P00208237-1 | 8/29/2015 | 2:47:44 PM | PET-16 | EAC | TV | OHR | 101 | 423,924 |  |  |  |
| P00206807-1 | 8/29/2015 | 2:51:30 PM | NUG-26 | EAA | TV | SCB | 510 | 18,258 |  |  |  |
| P00207263-1 | 8/29/2015 | 2:55:02 PM | EGT-27 | EBE | TV | OFU | 1,302 | 91,053 |  |  |  |
| P00204846-1 | 8/29/2015 | 2:55:28 PM | SIL-15 | ECE | TV | OCO | 12 | 16,654 |  |  |  |
| P00210053-1 | 8/29/2015 | 2:55:54 PM | CRE-12 | EAD | TV | OFU | 9 | 25,662 |  |  |  |
| P00206852-1 | 8/29/2015 | 2:57:00 PM | WAY-15 | EBD | TV | OSV | 1 | 1,582 |  |  |  |
| P00207990-1 | 8/29/2015 | 2:57:47 PM | ROL-17 | EBJ | TV | OCO | 54 | 51,040 |  |  |  |
| P00207004-1 | 8/29/2015 | 3:00:00 PM | SEH-14 | EAA | TV | OCO | 60 | 294,264 |  |  |  |
| P00210184-1 | 8/29/2015 | 3:01:00 PM | CLY-23 | EBE | TV | OCO | 44 | 105,841 |  |  |  |
| P00206918-1 | 8/29/2015 | 3:04:38 PM | CAM-23 | EBJ | TV | OFU | 122 | 156,941 |  |  |  |
| P00206992-1 | 8/29/2015 | 3:07:00 PM | ARD-12 | EBD | EF | UPC | 77 | 127,515 |  |  |  |
| P00206935-1 | 8/29/2015 | 3:07:11 PM | EGT-28 | EBE | TV | OCO | 244 | 299,547 |  |  |  |
| P00206950-1 | 8/29/2015 | 3:09:02 PM | MAN-16 | ECD | TV | OCO | 2 | 3,074 |  |  |  |
| P00206952-1 | 8/29/2015 | 3:09:09 PM | WAY-15 | EBD | TV | OTF | 4 | 2,835 |  |  |  |
| P00207481-1 | 8/29/2015 | 3:10:00 PM | LAB-26 | EAA | TV | OCO | 104 | 365,020 |  |  |  |
| P00206967-1 | 8/29/2015 | 3:10:00 PM | LAB-25 | EAA | TV | OCO | 7 | 21,350 |  |  |  |
| P00207577-1 | 8/29/2015 | 3:11:00 PM | NUG-25 | EAA | TV | OCO | 11 | 52,131 |  |  |  |
| P00207302-1 | 8/29/2015 | 3:13:40 PM | BAK-23 | EAA | TV | OFU | 101 | 410,600 |  |  |  |
| P00207003-1 | 8/29/2015 | 3:14:07 PM | LUH-17 | ECC | TV | OTF | 1 | 505 |  |  |  |
| P00207023-1 | 8/29/2015 | 3:16:43 PM | CLE-11 | EBH | TV | OTF | 3 | 3,206 |  |  |  |
| P00207093-1 | 8/29/2015 | 3:24:53 PM | LAC-15 | ECC | TV | OSV | 7 | 17,913 |  |  |  |
| P00207118-1 | 8/29/2015 | 3:27:11 PM | UHL-23 | EBD | TV | OTF | 1 | 244 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00207145-1 | 8/29/2015 | 3:31:50 PM | SNQ-17 | EBF | TV | OTF | 2 | 3,445 |  |  |  |
| P00207162-1 | 8/29/2015 | 3:33:00 PM | SIL-16 | ECE | TV | OCO | 4 | 11,462 |  |  |  |
| P00212248-1 | 8/29/2015 | 3:33:16 PM | NUG-25 | EAA |  |  | 99 | 441,127 |  |  |  |
| P00208169-1 | 8/29/2015 | 3:33:30 PM | LMC-25 | EBE | TV | OCO | 53 | 70,429 |  |  |  |
| P00209596-1 | 8/29/2015 | 3:34:06 PM | MIL-17 | ECE | TV | OCO | 28 | 71,879 |  |  |  |
| P00207325-1 | 8/29/2015 | 3:34:15 PM | MIR-16 | EBF | TV | OCO | 117 | 190,639 |  |  |  |
| P00207181-1 | 8/29/2015 | 3:36:00 PM | POU-13 | ECE | TV | OSV | 1 | 4,540 |  |  |  |
| P00207217-1 | 8/29/2015 | 3:38:49 PM | KIN-24 | ECE | TV | OCO | 1,551 | (1) |  |  |  |
| P00207212-1 | 8/29/2015 | 3:39:00 PM | LWS-16 | EBJ | TV | OCO | 8 | 2,911 |  |  |  |
| P00209502-1 | 8/29/2015 | 3:42:49 PM | SUM-21 | EAC | TV | OCO | - | 5,953 |  |  |  |
| P00207234-1 | 8/29/2015 | 3:42:53 PM | DUV-12 | EBD | TV | OTF | 2 | 2,312 |  |  |  |
| P00207241-1 | 8/29/2015 | 3:43:48 PM | NOB-24 | EBE | TV | OSV | 7 | 13,518 |  |  |  |
| P00209066-1 | 8/29/2015 | 3:45:08 PM | PIN-26 | EBD | TV | OCO | 12 | 21,609 |  |  |  |
| P00210900-1 | 8/29/2015 | 3:46:33 PM | CPV-12 | EAD | TV | OFU | 4 | 13,141 |  |  |  |
| P00207275-1 | 8/29/2015 | 3:48:18 PM | SWD-11 | ECE | TV | OCO | 20 | 55,861 |  |  |  |
| P00208348-1 | 8/29/2015 | 3:49:00 PM | GAG-13 | EAC | TV | OCO | 14 | 51,562 |  |  |  |
| P00207641-1 | 8/29/2015 | 3:51:00 PM | VWY-15 | EAA | TV | OCO | - | 25,717 |  |  |  |
| P00207317-1 | 8/29/2015 | 3:53:00 PM | RPT-15 | ECD | TV | OCO | 160 | 129,405 |  |  |  |
| P00207329-1 | 8/29/2015 | 3:54:00 PM | CPV-15 | EAD | TV | OCO | 71 | 273,358 |  |  |  |
| P00207321-1 | 8/29/2015 | 3:54:21 PM | DUV-15 | EBD | TV | OCO | 7 | 9,919 |  |  |  |
| P00207334-1 | 8/29/2015 | 3:55:46 PM | VIS-23 | EAA | TV | OTF | 1 | 3,271 |  |  |  |
| P00210987-1 | 8/29/2015 | 3:56:16 PM | WIN-15 | ECE | TV | OCO | 25 | 65,480 |  |  |  |
| P00212572-1 | 8/29/2015 | 3:57:00 PM | NUG-25 | EAA |  |  | 28 | 120,674 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00207348-1 | 8/29/2015 | 3:57:40 PM | WAY-15 | EBD | TV | OSV | 1 | 1,673 |  |  |  |
| P00209778-1 | 8/29/2015 | 3:59:22 PM | HWD-25 | EBD | TV | OCO | 7 | 15,308 |  |  |  |
| P00207366-1 | 8/29/2015 | 4:00:00 PM | MIL-17 | ECE | TV | OCO | 3 | 5,445 |  |  |  |
| P00210164-1 | 8/29/2015 | 4:00:24 PM | GAR-13 | ECA | TV | OCO | 4 | 3,041 |  |  |  |
| P00207361-1 | 8/29/2015 | 4:00:39 PM | NBE-13 | EBF | TV | OCO | 2 | 2,514 |  |  |  |
| P00207401-1 | 8/29/2015 | 4:06:00 PM | SIL-13 | ECE | TV | OCO | 1 | 4,138 |  |  |  |
| P00208587-1 | 8/29/2015 | 4:07:11 PM | LAC-17 | ECC | TV | OCO | 104 | 101,026 |  |  |  |
| P00207437-1 | 8/29/2015 | 4:11:20 PM | PIK-21 | EBF | TV | OSV | 1 | 1,972 |  |  |  |
| P00207456-1 | 8/29/2015 | 4:13:27 PM | WOL-23 | ECC | TV | OFU | 1 | 728 |  |  |  |
| P00207466-1 | 8/29/2015 | 4:15:29 PM | MIR-15 | EBF | TV | OCO | 1 | 1,588 |  |  |  |
| P00210614-1 | 8/29/2015 | 4:17:00 PM | MIL-16 | ECE | TV | OCO | 25 | 88,069 |  |  |  |
| P00207492-1 | 8/29/2015 | 4:18:00 PM | PIN-26 | EBD | TV | OFC | - | 4,032 |  |  |  |
| P00207497-1 | 8/29/2015 | 4:18:43 PM | TIL-22 | ECA | TV | OSV | 1 | 1,795 |  |  |  |
| P00207506-1 | 8/29/2015 | 4:20:10 PM | PMA-16 | ECE | TV | OCO | 275 | 262,757 |  |  |  |
| P00207515-1 | 8/29/2015 | 4:21:00 PM | KIN-21 | ECE | TV | OCO | 30 | 89,218 |  |  |  |
| P00207532-1 | 8/29/2015 | 4:23:00 PM | TRA-22 | ECE | TV | OCO | 2 | 6,572 |  |  |  |
| P00208196-1 | 8/29/2015 | 4:24:29 PM | NUG-26 | EAA | TV | OFU | 153 | 375,187 |  |  |  |
| P00207560-1 | 8/29/2015 | 4:26:45 PM | KIN-21 | ECE | TV | OCO | 1 | 1,200 |  |  |  |
| P00207576-1 | 8/29/2015 | 4:28:05 PM | BIG-16 | EAC | TV | OFU | 14 | 45,709 |  |  |  |
| P00208698-1 | 8/29/2015 | 4:28:27 PM | HKX-16 | EAC | TV | OCO | 22 | 22,922 |  |  |  |
| P00207598-1 | 8/29/2015 | 4:29:29 PM | FCH-16 | ECA | EF | OCB | 136 | 6,210 |  |  |  |
| P00207600-1 | 8/29/2015 | 4:29:39 PM | FCH-23 | ECA | EF | OCB | 1,796 | 66,513 |  |  |  |
| P00207589-1 | 8/29/2015 | 4:29:53 PM | KNM-25 | EBD | TV | OCO | 14 | 28,013 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00208471-1 | 8/29/2015 | 4:30:14 PM | KIN-21 | ECE | TV | OCO | 49 | 108,986 |  |  |  |
| P00207630-1 | 8/29/2015 | 4:34:34 PM | GBK-15 | EAD | TV | OTF | 5 | 20,626 |  |  |  |
| P00208787-1 | 8/29/2015 | 4:36:02 PM | HKX-16 | EAC | TV | OCR | 12 | 98,694 |  |  |  |
| P00207643-1 | 8/29/2015 | 4:36:39 PM | LLT-16 | EBD | TV | OTF | 3 | 1,512 |  |  |  |
| P00207649-1 | 8/29/2015 | 4:37:08 PM | LAC-13 | ECC | EF | PTF | 11 | 13,100 |  |  |  |
| P00213085-1 | 8/29/2015 | 4:37:17 PM | CUS-15 | EAA |  |  | 12 | 38,198 |  |  |  |
| P00207662-1 | 8/29/2015 | 4:37:32 PM | SKE-23 | ECE | TV | OCO | 43 | 69,198 |  |  |  |
| P00207658-1 | 8/29/2015 | 4:37:34 PM | STA-15 | EBJ | TV | UTC | 2 | 2,459 |  |  |  |
| P00207661-1 | 8/29/2015 | 4:37:51 PM | PMA-13 | ECE | TV | OCO | 33 | 37,766 |  |  |  |
| P00213461-1 | 8/29/2015 | 4:39:00 PM | PTR-14 | EAA | TV | OCO | 16 | 72,850 |  |  |  |
| P00207695-1 | 8/29/2015 | 4:41:58 PM | KIN-23 | ECE | TV | OCO | 2 | 2,072 |  |  |  |
| P00210150-1 | 8/29/2015 | 4:43:00 PM | BKB-14 | EAC | TV | OFU | 21 | 75,012 |  |  |  |
| P00208852-1 | 8/29/2015 | 4:43:00 PM | KIN-21 | ECE | TV | OCO | 18 | 56,195 |  |  |  |
| P00207734-1 | 8/29/2015 | 4:45:00 PM | KAP-13 | ECA | EF | UPC | 18 | 49,465 |  |  |  |
| P00207730-1 | 8/29/2015 | 4:45:00 PM | PMA-13 | ECE | TV | OCO | 2 | 5,457 |  |  |  |
| P00213044-1 | 8/29/2015 | 4:45:35 PM | WLS-16 | EAC | TV |  | 8 | 39,106 |  |  |  |
| P00209426-1 | 8/29/2015 | 4:48:00 PM | RAI-11 | ECC | TV | OTF | 5 | 8,360 |  |  |  |
| P00206931-1 | 8/29/2015 | 4:48:24 PM | EGT-11 | EBE | TV | OCO | 796 | 905,593 |  |  |  |
| P00207790-1 | 8/29/2015 | 4:49:00 PM | VAS-13 | EBL | EF | OPI | 2 | 2,657 |  |  |  |
| P00207794-1 | 8/29/2015 | 4:50:25 PM | EPO-13 | ECD | EF | OTR | 4 | 6,036 |  |  |  |
| P00207814-1 | 8/29/2015 | 4:53:00 PM | MAN-15 | ECD | TV | OCO | 1 | 1,652 |  |  |  |
| P00208143-1 | 8/29/2015 | 4:55:00 PM | BIG-15 | EAC | TV | OCO | 205 | 312,379 |  |  |  |
| P00207849-1 | 8/29/2015 | 4:57:13 PM | WIN-12 | ECE | TV | OCO | 2 | 3,051 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00212301-1 | 8/29/2015 | 4:57:36 PM | LAB-27 | EAA |  |  | 21 | 95,249 |  |  |  |
| P00207863-1 | 8/29/2015 | 4:58:00 PM | KIN-21 | ECE | TV | OCO | 29 | 43,921 |  |  |  |
| P00207865-1 | 8/29/2015 | 4:58:00 PM | FRG-24 | ECC | TV | OSV | 3 | 5,136 |  |  |  |
| P00207876-1 | 8/29/2015 | 4:59:47 PM | FWD-17 | EBJ | TV | SCB | - | 19,695 |  |  |  |
| P00207883-1 | 8/29/2015 | 5:01:42 PM | WAY-15 | EBD | TV | OCO | 9 | 2,958 |  |  |  |
| P00207891-1 | 8/29/2015 | 5:02:00 PM | CHI-12 | ECD | TF | OCO | 1 | 2,675 |  |  |  |
| P00209264-1 | 8/29/2015 | 5:03:14 PM | LAT-14 | EBJ | TV | OCO | 5 | 6,437 |  |  |  |
| P00208653-1 | 8/29/2015 | 5:03:27 PM | WOO-26 | ECA | TO | OCO | 451 | 124,126 |  |  |  |
| P00207900-1 | 8/29/2015 | 5:03:43 PM | BEL-16 | EBJ | TV | OFU | 68 | 69,592 |  |  |  |
| P00207907-1 | 8/29/2015 | 5:04:00 PM | VWY-12 | EAA | TV | OCO | 9 | 34,486 |  |  |  |
| P00210731-1 | 8/29/2015 | 5:04:00 PM | NUG-26 | EAA | TV | OFU | 52 | 226,492 |  |  |  |
| P00207916-1 | 8/29/2015 | 5:04:52 PM | WAY-15 | EBD | TV | OCO | 8 | 2,367 |  |  |  |
| P00210214-1 | 8/29/2015 | 5:06:11 PM | POU-13 | ECE | TV | OCO | 27 | 37,628 |  |  |  |
| P00207928-1 | 8/29/2015 | 5:06:25 PM | FAL-16 | EBF | TV | OFU | 35 | 21,251 |  |  |  |
| P00207949-1 | 8/29/2015 | 5:07:55 PM | FWD-13 | EBJ | TV | SCB | - | 7,933 |  |  |  |
| P00207944-1 | 8/29/2015 | 5:08:36 PM | HIG-16 | EBE | TV | OCO | 21 | 7,456 |  |  |  |
| P00207957-1 | 8/29/2015 | 5:10:53 PM | CHI-12 | ECD | EF | OTF | 2 | 5,968 |  |  |  |
| P00207961-1 | 8/29/2015 | 5:11:28 PM | YEL-27 | ECC | TV | OTF | 2 | 2,005 |  |  |  |
| P00209335-1 | 8/29/2015 | 5:14:21 PM | HAN-16 | EAA | TV | OFU | 23 | 93,931 |  |  |  |
| P00209529-1 | 8/29/2015 | 5:15:14 PM | CWD-22 | EBD | TV | OCO | 23 | 46,747 |  |  |  |
| P00208337-1 | 8/29/2015 | 5:16:00 PM | BIG-15 | EAC | TV | OCO | 80 | 260,012 |  |  |  |
| P00207992-1 | 8/29/2015 | 5:16:48 PM | VAS-23 | EBL | TV | OTF | - | 838 |  |  |  |
| P00209342-1 | 8/29/2015 | 5:16:48 PM | VAS-23 | EBL | TV | OCO | 16 | (1) |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00213068-1 | 8/29/2015 | 5:17:00 PM | BIG-15 | EAC |  |  | 153 | 686,205 |  |  |  |
| P00208009-1 | 8/29/2015 | 5:17:59 PM | LMC-23 | EBE | TV | OTR | 4 | 5,229 |  |  |  |
| P00208028-1 | 8/29/2015 | 5:19:00 PM | RAI-13 | ECC | TV | OFC | 1 | 1,525 |  |  |  |
| P00208054-1 | 8/29/2015 | 5:23:00 PM | RIT-16 | EAC | TV | OPO | 1 | 4,221 |  |  |  |
| P00208108-1 | 8/29/2015 | 5:31:56 PM | MIR-17 | EBF | TV | OCO | 6 | 9,535 |  |  |  |
| P00208115-1 | 8/29/2015 | 5:33:24 PM | PLG-17 | ECC | TV | OTF | 5 | 5,063 |  |  |  |
| P00210629-1 | 8/29/2015 | 5:33:40 PM | BLS-23 | EAA | TV | OCO | 30 | 62,272 |  |  |  |
| P00208122-1 | 8/29/2015 | 5:34:00 PM | KIN-21 | ECE | TV | OCO | 17 | 17,013 |  |  |  |
| P00208132-1 | 8/29/2015 | 5:37:00 PM | CEK-14 | ECE | TV | OCO | 1 | 3,156 |  |  |  |
| P00208141-1 | 8/29/2015 | 5:37:00 PM | WLS-16 | EAC | TV | OFU | - | 47,290 |  |  |  |
| P00208142-1 | 8/29/2015 | 5:38:02 PM | PRE-14 | EBE | TV | OSV | 1 | 302 |  |  |  |
| P00208146-1 | 8/29/2015 | 5:38:32 PM | LAC-13 | ECC | TV | OTF | 1 | 1,127 |  |  |  |
| P00208158-1 | 8/29/2015 | 5:40:23 PM | SOM-16 | EBE | TV | OAR | 22 | 34,091 |  |  |  |
| P00211549-1 | 8/29/2015 | 5:40:53 PM | LGY-16 | EAD | TV | OCO | 5 | 14,953 |  |  |  |
| P00208163-1 | 8/29/2015 | 5:41:02 PM | PHA-13 | EBE | TV | UTC | 6 | 8,224 |  |  |  |
| P00208173-1 | 8/29/2015 | 5:42:39 PM | LMD-16 | EBJ | TV | OFU | 20 | 11,440 |  |  |  |
| P00208187-1 | 8/29/2015 | 5:44:35 PM | GLC-14 | EBJ | TV | UTC | 25 | 45,262 |  |  |  |
| P00208199-1 | 8/29/2015 | 5:46:09 PM | SBE-26 | EBE | TV | OTF | 2 | 2,670 |  |  |  |
| P00211264-1 | 8/29/2015 | 5:46:38 PM | RIV-12 | EAC | TV | OFU | 42 | 125,077 |  |  |  |
| P00208206-1 | 8/29/2015 | 5:46:48 PM | SHD-18 | EBI | SO | DNO | 25 | 7,548 |  |  |  |
| P00208216-1 | 8/29/2015 | 5:48:09 PM | SHD-18 | EBI | TV | OFU | 21 | 3,434 |  |  |  |
| P00208220-1 | 8/29/2015 | 5:48:53 PM | SHD-18 | EBI | TV | OFU | 33 | 5,058 |  |  |  |
| P00209377-1 | 8/29/2015 | 5:49:02 PM | SIL-15 | ECE | TV | OCO | 15 | 45,723 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00211173-1 | 8/29/2015 | 5:51:00 PM | BTN-36 | EAC | TV | OCO | 66 | 186,242 |  |  |  |
| P00213319-1 | 8/29/2015 | 5:52:34 PM | BIG-15 | EAC | TV | UTC | 479 | 2,094,475 |  |  |  |
| P00208247-1 | 8/29/2015 | 5:52:46 PM | WAY-12 | EBD | TV | OTF | 7 | 4,125 |  |  |  |
| P00208645-1 | 8/29/2015 | 5:52:46 PM | WAY-16 | EBD | TV | OCO | 2,088 | 258,630 |  |  |  |
| P00208251-1 | 8/29/2015 | 5:53:36 PM | SKE-22 | ECE | EF | OFU | 3 | 2,168 |  |  |  |
| P00208262-1 | 8/29/2015 | 5:56:00 PM | SLA-17 | EAA | TV | OCO | 27 | 124,718 |  |  |  |
| P00208281-1 | 8/29/2015 | 6:00:02 PM | MED-37 | EBE | TV | OCO | - | 377,475 |  |  |  |
| P00213117-1 | 8/29/2015 | 6:01:54 PM | SLA-17 | EAA |  |  | 3 | 13,657 |  |  |  |
| P00211101-1 | 8/29/2015 | 6:08:41 PM | CRE-12 | EAD | TV | OFU | 6 | 15,947 |  |  |  |
| P00208339-1 | 8/29/2015 | 6:12:00 PM | MIL-17 | ECE | TV | OCO | 12 | 28,183 |  |  |  |
| P00208349-1 | 8/29/2015 | 6:13:32 PM | NHL-15 | EBD | TV | OCR | 29 | 77,183 |  |  |  |
| P00208352-1 | 8/29/2015 | 6:14:00 PM | BRI-15 | EAA | TV | OTF | 2 | 11,301 |  |  |  |
| P00208358-1 | 8/29/2015 | 6:16:09 PM | HOB-17 | EBI | TV | OTR | 2 | 2,739 |  |  |  |
| P00209449-1 | 8/29/2015 | 6:16:21 PM | EDG-15 | ECA | TO | OCO | 68 | 52,873 |  |  |  |
| P00210023-1 | 8/29/2015 | 6:16:51 PM | PET-16 | EAC | TV | OHR | 17 | 17,242 |  |  |  |
| P00208742-1 | 8/29/2015 | 6:21:06 PM | RIT-18 | EAC | TV | SCB | 1,451 | 420,882 |  |  |  |
| P00207105-1 | 8/29/2015 | 6:21:14 PM | ALG-12 | EAC | TV | OCO | 2 | 9,950 |  |  |  |
| P00208418-1 | 8/29/2015 | 6:22:44 PM | WOB-23 | EAA | TV | SCB | 463 | 105,124 |  |  |  |
| P00208414-1 | 8/29/2015 | 6:22:54 PM | NBO-22 | EBD | TV | OFU | 3 | 2,082 |  |  |  |
| P00208431-1 | 8/29/2015 | 6:26:00 PM | SKE-26 | ECE | TV | OCO | 4 | 16,496 |  |  |  |
| P00208438-1 | 8/29/2015 | 6:27:00 PM | MUR-13 | ECE | TV | OPO | 20 | 42,526 |  |  |  |
| P00208448-1 | 8/29/2015 | 6:27:00 PM | POU-15 | ECE | TV | OCO | 20 | 53,942 |  |  |  |
| P00208437-1 | 8/29/2015 | 6:27:07 PM | ORT-23 | ECA | TV | OFU | 38 | 37,502 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00208446-1 | 8/29/2015 | 6:27:56 PM | KCR-17 | EBJ | TV | OTF | 3 | 3,348 |  |  |  |
| P00208449-1 | 8/29/2015 | 6:28:00 PM | CPV-15 | EAD | TV | OCO | 1 | 3,299 |  |  |  |
| P00208461-1 | 8/29/2015 | 6:31:02 PM | PIN-26 | EBD | TV | OFC | 14 | 13,522 |  |  |  |
| P00208470-1 | 8/29/2015 | 6:32:15 PM | LYN-23 | EAA | TV | SCB | 757 | 494,132 |  |  |  |
| P00208479-1 | 8/29/2015 | 6:33:31 PM | ORC-13 | EBJ | TV | OFU | 1 | 613 |  |  |  |
| P00208816-1 | 8/29/2015 | 6:34:16 PM | BAR-13 | ECC | TV | OCO | 544 | 282,155 |  |  |  |
| P00211311-1 | 8/29/2015 | 6:34:31 PM | NUG-26 | EAA | TV | OFU | 26 | 37,955 |  |  |  |
| P00208491-1 | 8/29/2015 | 6:36:21 PM | SWA-12 | EAD | EF | OSV | 1 | 4,411 |  |  |  |
| P00208499-1 | 8/29/2015 | 6:36:52 PM | WAY-15 | EBD | TV | OCO | 1 | 1,270 |  |  |  |
| P00208504-1 | 8/29/2015 | 6:38:52 PM | LAB-23 | EAA | TV | OCO | 2 | 6,239 |  |  |  |
| P00208547-1 | 8/29/2015 | 6:47:17 PM | RIT-16 | EAC | TV | OSV | 1 | 5,173 |  |  |  |
| P00208570-1 | 8/29/2015 | 6:51:18 PM | LOL-25 | ECD | EF | UTC | 16 | 13,061 |  |  |  |
| P00208572-1 | 8/29/2015 | 6:51:38 PM | WAY-15 | EBD | TV | OCO | 4 | 2,065 |  |  |  |
| P00208593-1 | 8/29/2015 | 6:54:59 PM | HWD-25 | EBD | TV | OCO | 1 | 2,834 |  |  |  |
| P00208613-1 | 8/29/2015 | 6:59:00 PM | JUA-14 | EBD | TV | OSV | 1 | 2,881 |  |  |  |
| P00208614-1 | 8/29/2015 | 6:59:41 PM | WAY-15 | EBD | TV | OCO | 1 | 1,246 |  |  |  |
| P00210100-1 | 8/29/2015 | 7:01:30 PM | CEK-14 | ECE | TV | OCO | 23 | 68,041 |  |  |  |
| P00208623-1 | 8/29/2015 | 7:02:25 PM | LMC-25 | EBE | TV | OCO | 13 | 404 |  |  |  |
| P00208636-1 | 8/29/2015 | 7:05:00 PM | SHD-18 | EBI | EF | UPC | 95 | 48,362 |  |  |  |
| P00208632-1 | 8/29/2015 | 7:05:14 PM | EDG-13 | ECA | TV | OCO | 2 | 1,646 |  |  |  |
| P00209310-1 | 8/29/2015 | 7:05:20 PM | ING-17 | EBD | TV | OCO | 52 | 67,238 |  |  |  |
| P00208640-1 | 8/29/2015 | 7:07:15 PM | RIT-16 | EAC | TV | OFU | 3 | 15,479 |  |  |  |
| P00208650-1 | 8/29/2015 | 7:08:49 PM | NUG-26 | EAA | TV | OFU | 20 | 23,797 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00209394-1 | 8/29/2015 | 7:10:53 PM | RIT-18 | EAC | TV | OCO | 31 | 40,496 |  |  |  |
| P00208660-1 | 8/29/2015 | 7:11:00 PM | CRE-15 | EAD | TV | OCO | 40 | 149,601 |  |  |  |
| P00208670-1 | 8/29/2015 | 7:13:00 PM | CED-17 | ECA | TV | OCO | 4 | 4,853 |  |  |  |
| P00208669-1 | 8/29/2015 | 7:13:18 PM | LYN-24 | EAA | TV | SCB | 756 | 459,056 |  |  |  |
| P00208672-1 | 8/29/2015 | 7:13:37 PM | HEM-13 | ECA | TV | OTR | 4 | 9,418 |  |  |  |
| P00211051-1 | 8/29/2015 | 7:15:08 PM | BIG-15 | EAC | TV | OCO | 15 | 44,826 |  |  |  |
| P00209875-1 | 8/29/2015 | 7:18:56 PM | GBK-13 | EAD | TV | OFU | 10 | 25,935 |  |  |  |
| P00208703-1 | 8/29/2015 | 7:19:00 PM | ALG-12 | EAC | TV | OCO | 2 | 8,881 |  |  |  |
| P00210551-1 | 8/29/2015 | 7:19:09 PM | EDG-13 | ECA | EF | OFU | 23 | 24,531 |  |  |  |
| P00209895-1 | 8/29/2015 | 7:19:09 PM | EDG-13 | ECA | TV | OCO | - | 5,837 |  |  |  |
| P00208705-1 | 8/29/2015 | 7:19:58 PM | ING-16 | EBD | TV | OCO | 82 | 122,800 |  |  |  |
| P00208717-1 | 8/29/2015 | 7:20:05 PM | HAN-12 | EAA | TV | SCB | 1,365 | 249,368 |  |  |  |
| P00208708-1 | 8/29/2015 | 7:20:30 PM | HOB-16 | EBI | TV | OGS | 3 | 1,011 |  |  |  |
| P00208729-1 | 8/29/2015 | 7:21:20 PM | BHS-11 | EAA | TV | SCB | 1,717 | 1,195,446 |  |  |  |
| P00208727-1 | 8/29/2015 | 7:22:36 PM | LAB-27 | EAA | TV | UTC | - | 22,642 |  |  |  |
| P00208764-1 | 8/29/2015 | 7:28:01 PM | VAS-13 | EBL | TV | OCO | 24 | 2,872 |  |  |  |
| P00208765-1 | 8/29/2015 | 7:31:00 PM | LAB-26 | EAA | TV | OFU | 23 | 107,080 |  |  |  |
| P00208779-1 | 8/29/2015 | 7:33:00 PM | GRI-13 | ECC | TV | OCO | 177 | 3,072 |  |  |  |
| P00208773-1 | 8/29/2015 | 7:33:34 PM | SEQ-17 | EBJ | TV | OTF | 2 | 2,765 |  |  |  |
| P00208170-1 | 8/29/2015 | 7:40:37 PM | MAN-16 | ECD | TV | OCO | 2 | 2,967 |  |  |  |
| P00208805-1 | 8/29/2015 | 7:45:05 PM | SIL-15 | ECE | TV | OCO | 3 | 8,463 |  |  |  |
| P00209032-1 | 8/29/2015 | 7:50:59 PM | NLM-16 | EAC | TV | OCO | 127 | 228,689 |  |  |  |
| P00208834-1 | 8/29/2015 | 7:51:21 PM | SME-13 | EBE | TV | OTF | 2 | 5,421 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00208842-1 | 8/29/2015 | 7:52:00 PM | NLM-16 | EAC | TV | OCO | 64 | 251,491 |  |  |  |
| P00211589-1 | 8/29/2015 | 7:53:41 PM | MIL-17 | ECE | TV | OFU | 52 | 137,673 |  |  |  |
| P00209720-1 | 8/29/2015 | 7:55:00 PM | RIT-16 | EAC | TV | OJU | 158 | 342,768 |  |  |  |
| P00208854-1 | 8/29/2015 | 7:55:11 PM | GWR-13 | EBI | TV | OTF | 2 | 959 |  |  |  |
| P00208857-1 | 8/29/2015 | 7:56:00 PM | NLM-16 | EAC | TV | OCO | 57 | 230,920 |  |  |  |
| P00208861-1 | 8/29/2015 | 7:56:58 PM | RAI-13 | ECC | TV | OCO | 4 | 5,255 |  |  |  |
| P00212312-1 | 8/29/2015 | 8:00:13 PM | LAB-27 | EAA |  |  | - | 4,928 |  |  |  |
| P00208897-1 | 8/29/2015 | 8:00:18 PM | LYN-23 | EAA | TV | SCB | - | 52,223 |  |  |  |
| P00208908-1 | 8/29/2015 | 8:04:00 PM | HAZ-15 | EBE | TV | OCO | 9 | 9,246 |  |  |  |
| P00208929-1 | 8/29/2015 | 8:07:00 PM | SIL-15 | ECE | TV | OCO | 3 | 4,992 |  |  |  |
| P00208946-1 | 8/29/2015 | 8:10:50 PM | OSC-23 | EBI | TV | OFU | 15 | 3,588 |  |  |  |
| P00211881-1 | 8/29/2015 | 8:11:49 PM | POU-13 | ECE | TV | OCO | 34 | 51,131 |  |  |  |
| P00213200-1 | 8/29/2015 | 8:12:00 PM | VWY-13 | EAA | TV | OCO | 13 | 60,086 |  |  |  |
| P00208973-1 | 8/29/2015 | 8:13:25 PM | MIL-16 | ECE | TV | OCO | 244 | 22,887 |  |  |  |
| P00208975-1 | 8/29/2015 | 8:14:50 PM | HLC-24 | EAD | TV | OCO | 3 | 1,626 |  |  |  |
| P00209359-1 | 8/29/2015 | 8:17:09 PM | BUC-26 | ECA | TV | OCO | 59 | 38,374 |  |  |  |
| P00209052-1 | 8/29/2015 | 8:21:00 PM | NLM-16 | EAC | TV | OPO | 69 | 194,948 |  |  |  |
| P00209013-1 | 8/29/2015 | 8:22:24 PM | HLC-24 | EAD | TV | OFU | 33 | 17,010 |  |  |  |
| P00209024-1 | 8/29/2015 | 8:23:05 PM | POU-15 | ECE | EF | OCR | 1,129 | 252,889 |  |  |  |
| P00209021-1 | 8/29/2015 | 8:23:17 PM | CRE-15 | EAD | TV | OSV | 1 | 4,072 |  |  |  |
| P00209028-1 | 8/29/2015 | 8:24:39 PM | LYO-15 | EBJ | TV | UTC | 9 | 1,801 |  |  |  |
| P00212324-1 | 8/29/2015 | 8:26:27 PM | LAB-27 | EAA |  |  | - | 59,001 |  |  |  |
| P00209038-1 | 8/29/2015 | 8:27:00 PM | VWY-13 | EAA | TV | OTF | 2 | 10,917 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00209047-1 | 8/29/2015 | 8:29:00 PM | NLM-13 | EAC | EF | UPC | 104 | 209,234 |  |  |  |
| P00210534-1 | 8/29/2015 | 8:30:21 PM | NUG-26 | EAA | TV | OFU | 14 | 31,561 |  |  |  |
| P00209054-1 | 8/29/2015 | 8:31:00 PM | PET-12 | EAC | TV | OSV | 2 | 8,579 |  |  |  |
| P00209068-1 | 8/29/2015 | 8:34:26 PM | OSC-22 | EBI | TV | OFU | 25 | 10,650 |  |  |  |
| P00209077-1 | 8/29/2015 | 8:35:00 PM | PIN-26 | EBD | TV | OCO | 4 | 5,288 |  |  |  |
| P00209071-1 | 8/29/2015 | 8:35:00 PM | POU-16 | ECE | TV | OCO | 3 | 5,331 |  |  |  |
| P00209085-1 | 8/29/2015 | 8:37:35 PM | FRA-15 | ECD | TV | OCO | 838 | 757,678 |  |  |  |
| P00209089-1 | 8/29/2015 | 8:38:24 PM | SKE-23 | ECE | TV | OCO | 17 | 67,424 |  |  |  |
| P00209108-1 | 8/29/2015 | 8:40:00 PM | MCA-13 | ECC | TF | OCO | 25 | 12,276 |  |  |  |
| P00209106-1 | 8/29/2015 | 8:40:41 PM | CHI-12 | ECD | TV | OCO | 56 | 137,602 |  |  |  |
| P00209113-1 | 8/29/2015 | 8:41:10 PM | TLN-0126 | EAA | TV | OCO | - | 55,037 |  |  |  |
| P00209120-1 | 8/29/2015 | 8:43:35 PM | LAB-26 | EAA | TV | OTF | 1 | 4,585 |  |  |  |
| P00209127-1 | 8/29/2015 | 8:44:59 PM | UHL-23 | EBD | TV | OCO | 4 | 8,934 |  |  |  |
| P00209130-1 | 8/29/2015 | 8:45:12 PM | FRG-23 | ECC | TV | OTF | 6 | 4,055 |  |  |  |
| P00209245-1 | 8/29/2015 | 8:45:27 PM | GAR-16 | ECA | TV | OCO | 695 | 193,118 |  |  |  |
| P00209149-1 | 8/29/2015 | 8:49:00 PM | CHI-12 | ECD | TV | OCO | - | - |  |  |  |
| P00209155-1 | 8/29/2015 | 8:50:59 PM | LLT-16 | EBD | TV | OTF | 2 | 3,404 |  |  |  |
| P00209160-1 | 8/29/2015 | 8:51:00 PM | EDG-13 | ECA | TV | OFU | 3 | 3,696 |  |  |  |
| P00209161-1 | 8/29/2015 | 8:51:41 PM | PAN-14 | EBJ | TV | OTF | 3 | 2,953 |  |  |  |
| P00209190-1 | 8/29/2015 | 8:58:00 PM | GBK-13 | EAD | TV | OCO | 3 | 10,245 |  |  |  |
| P00211239-1 | 8/29/2015 | 9:00:11 PM | VAS-22 | EBL | EF | UPC | 4 | 9,370 |  |  |  |
| P00210251-1 | 8/29/2015 | 9:00:44 PM | NBO-22 | EBD | TV | OTF | 97 | 83,614 |  |  |  |
| P00212309-1 | 8/29/2015 | 9:01:39 PM | LAB-27 | EAA |  |  | - | 16,827 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00209463-1 | 8/29/2015 | 9:10:49 PM | LYO-15 | EBJ | TV | OFU | 14 | 4,082 |  |  |  |
| P00212294-1 | 8/29/2015 | 9:14:30 PM | LAB-27 | EAA |  |  | - | 7,227 |  |  |  |
| P00209272-1 | 8/29/2015 | 9:16:39 PM | ROS-21 | EBD | TV | OCO | 65 | 85,556 |  |  |  |
| P00209283-1 | 8/29/2015 | 9:20:00 PM | SIL-15 | ECE | TV | OCO | 1 | 4,202 |  |  |  |
| P00209291-1 | 8/29/2015 | 9:23:12 PM | SIL-13 | ECE | EF | OFC | 6 | 14,330 |  |  |  |
| P00212308-1 | 8/29/2015 | 9:24:09 PM | LAB-27 | EAA |  |  | - | 7,194 |  |  |  |
| P00210208-1 | 8/29/2015 | 9:24:27 PM | HAN-16 | EAA | TV | OFU | 184 | 297,537 |  |  |  |
| P00211993-1 | 8/29/2015 | 9:24:45 PM | HAN-16 | EAA | TV | OCO | 29 | 78,845 |  |  |  |
| P00209548-1 | 8/29/2015 | 9:27:20 PM | WOO-26 | ECA | TV | OCO | 297 | 52,254 |  |  |  |
| P00209323-1 | 8/29/2015 | 9:35:28 PM | PGA-13 | ECE | TV | OSV | 1 | 1,966 |  |  |  |
| P00209333-1 | 8/29/2015 | 9:38:00 PM | MCA-15 | ECC | TF | OCO | 1 | 5,081 |  |  |  |
| P00209334-1 | 8/29/2015 | 9:38:51 PM | VAS-13 | EBL | TV | OCO | 1 | 1,039 |  |  |  |
| P00209336-1 | 8/29/2015 | 9:39:28 PM | KIN-24 | ECE | TV | OSV | - | 68 |  |  |  |
| P00209347-1 | 8/29/2015 | 9:42:00 PM | BIG-15 | EAC | TV | OTF | 2 | 11,666 |  |  |  |
| P00209345-1 | 8/29/2015 | 9:42:00 PM | BAS-13 | EBJ | TV | OCO | 3 | 688 |  |  |  |
| P00209348-1 | 8/29/2015 | 9:43:43 PM | LAB-27 | EAA | EF | OJU | - | 14,268 |  |  |  |
| P00209350-1 | 8/29/2015 | 9:44:02 PM | KLA-15 | EBD | TV | OCO | 1 | 2,289 |  |  |  |
| P00209561-1 | 8/29/2015 | 9:46:10 PM | VWY-15 | EAA | TV | OCO | - | 6,681 |  |  |  |
| P00209371-1 | 8/29/2015 | 9:50:30 PM | GRV-12 | ECA | TV | OFU | 4 | 4,708 |  |  |  |
| P00209384-1 | 8/29/2015 | 9:55:19 PM | MIL-16 | ECE | TV | OCO | 244 | 9,706 |  |  |  |
| P00209405-1 | 8/29/2015 | 10:03:00 PM | MIL-17 | ECE | TV | OCO | 2 | 7,325 |  |  |  |
| P00209415-1 | 8/29/2015 | 10:08:00 PM | SIL-15 | ECE | TV | OCO | 1 | 1,647 |  |  |  |
| P00209418-1 | 8/29/2015 | 10:09:23 PM | EAR-17 | EBJ | TV | OSV | 3 | 4,025 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00209433-1 | 8/29/2015 | 10:14:48 PM | HAN-12 | EAA | TV | OCO | 113 | 505,500 |  |  |  |
| P00209812-1 | 8/29/2015 | 10:15:47 PM | WOB-25 | EAA | TV | OHR | 381 | 320,664.00 |  |  |  |
| P00209444-1 | 8/29/2015 | 10:18:00 PM | PLA-21 | EBD | TV | OCO | 24 | 50,854 |  |  |  |
| P00209443-1 | 8/29/2015 | 10:18:00 PM | ALG-15 | EAA | TV | OTR | 1 | 10,310 |  |  |  |
| P00211662-1 | 8/29/2015 | 10:19:21 PM | MIL-23 | ECE | TV | OCO | 31 | 73,200 |  |  |  |
| P00209461-1 | 8/29/2015 | 10:25:58 PM | MAP-15 | EBE | TV | OCO | 32 | 2,712 |  |  |  |
| P00209467-1 | 8/29/2015 | 10:27:00 PM | VWY-12 | EAA | TV | OTF | 1 | 5,721 |  |  |  |
| P00209466-1 | 8/29/2015 | 10:27:18 PM | MED-36 | EBE | EF | OTF | 4 | 9,536 |  |  |  |
| P00209473-1 | 8/29/2015 | 10:27:37 PM | BCH-15 | EAA | TV | OCO | 1,516 | 1,096,693 |  |  |  |
| P00209475-1 | 8/29/2015 | 10:30:11 PM | LLT-13 | EBD | TV | OCO | 3 | 3,589 |  |  |  |
| P00210131-1 | 8/29/2015 | 10:34:00 PM | FRA-13 | ECD | TV | OCO | 2 | 5,747 |  |  |  |
| P00209481-1 | 8/29/2015 | 10:34:00 PM | FRA-13 | ECD | TV | OCO | 3 | 8,622 |  |  |  |
| P00209486-1 | 8/29/2015 | 10:36:45 PM | ZEN-26 | EBJ | TV | UTC | 1 | 860 |  |  |  |
| P00209493-1 | 8/29/2015 | 10:39:00 PM | PLY-13 | EAA | TV | OTF | 7 | 35,568 |  |  |  |
| P00209562-1 | 8/29/2015 | 10:39:18 PM | VWY-15 | EAA | TV | OTF | - | 1 |  |  |  |
| P00209499-1 | 8/29/2015 | 10:42:16 PM | JUA-25 | EBD | TV | OTF | 2 | 5,217 |  |  |  |
| P00209738-1 | 8/29/2015 | 10:43:00 PM | LON-25 | ECC | TV | OPO | 3 | 2,616 |  |  |  |
| P00209505-1 | 8/29/2015 | 10:43:00 PM | LON-25 | ECC | TV | OFU | 57 | 2,974 |  |  |  |
| P00207554-1 | 8/29/2015 | 10:44:20 PM | MVW-13 | EBJ | TV | DNO | 12 | 398 |  |  |  |
| P00209628-1 | 8/29/2015 | 10:45:00 PM | LON-25 | ECC | TV | OTR | 93 | 175,485 |  |  |  |
| P00203400-1 | 8/29/2015 | 10:54:51 PM | MAP-15 | EBE | TV | OCO | 18 | 258 |  |  |  |
| P00209947-1 | 8/29/2015 | 10:57:00 PM | SHA-15 | ECA | EF | UPC | 11 | 23,941 |  |  |  |
| P00210133-1 | 8/29/2015 | 11:02:00 PM | WAY-13 | EBD | TV | OCO | 127 | 215,236 |  |  |  |
| **NUMBER** | **DATE** | **TIME** | **CKT** | **MPG** | **CAZ** | **EQT** | **CUST.OUT** | **CUST.MIN** |  |  |  |
| P00210371-1 | 8/29/2015 | 11:05:38 PM | ZEN-26 | EBJ | EF | UPC | 15 | 12,401 |  |  |  |
| P00209540-1 | 8/29/2015 | 11:07:42 PM | FAB-15 | EAD | TV | UTC | 24 | 97,397 |  |  |  |
| P00209244-1 | 8/29/2015 | 11:12:44 PM | HWD-25 | EBD | TV | OCO | 28 | 24,145 |  |  |  |
| P00210383-1 | 8/29/2015 | 11:13:24 PM | ORT-22 | ECA | TV | OCO | 55 | 73,231 |  |  |  |
| P00209552-1 | 8/29/2015 | 11:14:12 PM | ROL-17 | EBJ | EF | UFJ | 4 | 4,889 |  |  |  |
| P00209567-1 | 8/29/2015 | 11:17:56 PM | RHO-15 | ECA | TV | OCO | 3 | 2,400 |  |  |  |
| P00213038-1 | 8/29/2015 | 11:24:00 PM | ALG-15 | EAA |  |  | 1 | 5,048 |  |  |  |
| P00209587-1 | 8/29/2015 | 11:28:20 PM | HWD-26 | EBD | TV | OTF | 1 | 2,495 |  |  |  |
| P00209590-1 | 8/29/2015 | 11:28:52 PM | BUC-16 | ECA | TV | OSV | 3 | 2,490 |  |  |  |
| P00210134-1 | 8/29/2015 | 11:39:54 PM | SWD-12 | ECE | TV | OCO | - | 23,431 |  |  |  |
| P00209616-1 | 8/29/2015 | 11:40:21 PM | LTA-18 | ECA | TV | OTR | 1 | 1,317 |  |  |  |
| P00209639-1 | 8/29/2015 | 11:44:00 PM | POU-13 | ECE | TV | OCO | 1,445 | 94,166 |  |  |  |
| P00209625-1 | 8/29/2015 | 11:47:13 PM | PLY-13 | EAA | TV | OCO | - | 77,580 |  |  |  |
| P00209632-1 | 8/29/2015 | 11:51:00 PM | LUH-14 | ECC | TV | OFU | 1 | 1,036 |  |  |  |
| P00209652-1 | 8/29/2015 | 11:54:29 PM | MST-25 | EBJ | TV | OPI | 72 | 19,247 |  |  |  |

### **Terms, Codes and Definitions Used on Detail Reports**

|  |  |  |
| --- | --- | --- |
| Notification (NUMBER) | A number assigned by SAP, identifying the outage record | |
| **Date (DATE)** | The date of the outage | |
| **Time (TIME)** | The time of the outage | |
| **Circuit (CKT)** | The circuit identifier for the affected circuit | |
| **Area (MPG)** | **Maintenance Planner Group** A code representing the energy, region and service center | |
| EAA – Bellingham | EBJ – South King |
| EAC – Skagit | EBL – Vashon |
| EAD – Whidbey | ECA – Puyallup |
| EBD – Redmond | ECC – Olympia |
| EBE – Factoria | ECD – Port Orchard |
| EBF – Snoqualmie | ECE – Poulsbo |
| EBI – Enumclaw |  |
| **Cause (CAZ)** | **Cause of Outage** | |
| AO – Accident Other | EF – Equipment Failure |
| BA – Bird or Animal | EO – Electrical Overload |
| CP – Car Pole | FI – Faulty Installation |
| CR – Customer Request | TF – Tree Off Right-of-Way |
| DU – Dig-up Underground | TO – Tree On Right-of-Way |
| TV – Trees/Vegetation | SO – Scheduled Outage |
| UN – Unknown |  |
| Equipment (EQT) | | **Affected by, or involved in the outage** | |
| OCN – Connector | OSW – Overhead Switch |
| OCO – Overhead Conductor | OTF – Overhead Transformer Fuse |
| OCR – Crossarm | OTR – Overhead Transformer |
| OFC – Overhead Cut-out | OUP – OH to UG Primary |
| OFS – Overhead Fire Signal | OUS – OH to UG Secondary Service |
| OFU – Fuse Link/OH Line Fuse | SBF – High-side Bank Fuse |
| OGS – Span Guy | SCB – Power Circuit Breaker |
| OHR – Overhead Recloser | UOT – Underground Outdoor Term |
| OIN – Insulator | UPC – Underground Primary Cable |
| OJU- Jump Wire | UPT – Padmount Transformer |
| OPI – Overhead Pin Insulator | USV – Underground Service |
| OPO – Pole | UTC – Underground Terminal Fuse |
| OSV – Overhead Service | UTR – Submersible Transformer |
| ORE – Regulator |  |
| **CUST OUT (CUST.OUT)** | | **Customer Out,** The number of customers without power for any given outage record | |
| **CUST MIN (CUST. MIN)** | | **Customer Minutes,** The total number of minutes customers were without power for any given record | |

# **Media & Communication Coverage**

**Seattle PI-8/29/15**

**Storm toll: 2 dead, 4 hurt, 450,000 lose power**

http://ww4.hdnux.com/photos/40/50/42/8554643/3/920x920.jpg

A block-long length of power lines and poles are shown in Lake City after they were knocked down during a windstorm that caused damage across the Pacific Northwest on Saturday, Aug. 29, 2015.

A powerful and rare summertime windstorm packing 50-70 mph winds is being blamed for two deaths, four injuries and knocking out power to our 450,000 people Saturday afternoon.

A father driving in Gig Harbor with his 3-year-old son [**was killed when a tree fell on his car**](http://www.komonews.com/news/local/Man-dies-after-tree-falls-atop-car-in-Gig-Harbor-323323201.html). He died at the scene; his son was not hurt. In Federal Way, [**a 10-year-old girl was struck and killed**](http://www.komonews.com/news/local/Man-dies-after-tree-falls-atop-car-in-Gig-Harbor-323323201.html) by a falling branch while attending a sleepover.

[**Four others were hurt**](http://www.komonews.com/news/local/4-injured-by-falling-debris-at-JBLM-triathlon--323330141.html) during the Deuces Wild Triathlon at Joint Base Lewis-McChord on Saturday morning when three trees fell. The injured were taken to Madigan Army Medical Center for treatment of non-life-threatening injuries, officials said. Two have since been released while two more are being held overnight for observation.

There were many other tales of close calls amid dozens of reports of downed trees and power lines across much of the Western Washington lowlands, damaging homes and wreaking havoc on roads and freeways.

Crews working to restore power were taxed by the storm's breadth. It tore trees out of the ground across a vast swatch of the Pacific Northwest, stretching manpower and equipment thin.

"If it just hits one part of our service area, you can maybe send crews down from another area. But this is a service-area-wide event," said Christina Donegan, a spokeswoman for Puget Sound Energy, which reported 224,000 customers without power by early evening.

In the North Sound, a large tree fell across the northbound lanes of Interstate 5 near 196th Street Southwest in Lynnwood, striking one car, but no one was hurt. I-5 was also shut down in the southbound direction for a time near Northeast 145th Street in Shoreline due to downed trees.

Over on Interstate 405, eight trees toppled along the southbound lanes just south of state Route 527 in Bothell, according to the state Department of Transportation. There have been multiple reports of trees down on local roads across the region. Several trees toppled in the Olympic National Park, prompting park rangers to close all roads into the park and campgrounds. Puyallup closed all its parks in the city and ordered the closure of the Farmers Market in Pioneer Park.

In Shoreline, power lines fell on a truck at North 185th Street and Dayton Avenue North, setting the truck on fire. No one was hurt. In Lacey, firefighters had to board water rescue craft to save two people whose boat overturned on Long Lake. They were safely rescued.

At the peak of the storm, Puget Sound Energy reported more than 223,000 people without power while Snohomish PUD estimated over 175,000 outages and Seattle City Light had about 59,000 at their peak. Tacoma Public Utilities reported 20,000 around midday but had restored more than 10,000 of those by late afternoon.

Wind speeds were on par with some of the stronger storms Western Washington typically receives in the late fall and winter, with gusts in the Seattle-Tacoma area reaching 40-50 mph, while gusts to 60-70 mph were common in the North Sound and along the coast. Whidbey Island Naval Air Station reported a gust of 70 mph, while Everett's Paine Field had multiple gusts around 60 mph, peaking at 61 mph. The Coast Guard took a report from a boat in the Rosario Strait that recorded a gust of 81 mph. Lopez Island clocked in at 66 mph and Bellingham hit 58 mph.

Closer to the metro area, Tacoma reported a gust of 54 mph, while Gig Harbor hit 51 mph and Seattle hit a gust of 46 mph. Over on the coast, Westport hit 63 mph while Forks, Hoquiam and Astoria all hit 62 mph. But the largest gust recorded in the western half of the state belonged to Destruction Island just off the north coast, which measured a sustained wind of 79 mph gusting to 87 mph.

Those kinds of wind speeds would do damage in any month, but the damage with this storm was particularly severe because the trees were still heavy and full of leaves. The first windstorm of a season tends to be the one to break off the most susceptible branches that weakened over the summer, which was especially an issue this summer with our recent dry weather.

1. IEEE: Institute of Electrical and Electronics Engineers [↑](#footnote-ref-1)
2. SAIDI: System Average Interruption Duration Index [↑](#footnote-ref-2)
3. O&M: Operations and Maintenance

   (r): Revised [↑](#footnote-ref-3)