## Growth Stats NG EIA US
Natural Gas Delivered to Consumers in the U.S.
https://www.eia.gov/dnav/ng/hist/n3060us2a.htm
19:01:24 PST
Source: U.S. Energy Information Administration
Year | Natural Gas Delivered to Consumers in the U.S. Million Cubic Feet | Annual Growth %
2018 | 27402138 | 10.38%
2017 | 24824284 | -1.538%
2016 | 25212159 | 0.8919%
2015 | 24989285 | 2.495%
2014 | 24381082 | 2.274%
2013 | 23838925 | 1.826%
2012 | 23411423 | 4.203%
2011 | 22467053 | 1.537%
2010 | 22127046 | 5.544%
2009 | 20964665 | -2.077%
2008 | 21409349
2007 | 21256042
2006 | 19972881
2005 | 20318892
2004 | 20738454
2003 | 20562727
2002 | 21247016
2001 | 20495108
2000 | 21539964
1999 | 20680843
1998 | 20437798
1997 | 20782693
| Total Growth 2014-2018 | 14.95%
| Average Annual Growth | 2.901%

## Growth Stats ELEC EIA US
https://www.eia.gov/electricity/annual/
(From Table 2.1.) Number of Ultimate Customers
Year | Residential | Commer-cial | Industrial | Transpor-tation | Other | Total | Annual Growth %
2007 | 123949916 | 17377219 | 793767 | 750 | N/A | 142121652
2008 | 125037837 | 17582382 | 774808 | 726 | N/A | 143395753 | 0.8965%
2009 | 125208829 | 17562235 | 757537 | 704 | N/A | 143529305 | 0.09314%
2010 | 125717935 | 17674338 | 747747 | 239 | N/A | 144140259 | 0.4257%
2011 | 126143072 | 17638062 | 727920 | 92 | N/A | 144509146 | 0.2559%
2012 | 126832343 | 17729029 | 732385 | 83 | N/A | 145293840 | 0.543%
2013 | 127777153 | 17679562 | 831790 | 75 | N/A | 146288580 | 0.6846%
2014 | 128680416 | 17853995 | 839212 | 79 | N/A | 147373702 | 0.7418%
2015 | 129811718 | 17985690 | 835536 | 78 | N/A | 148633022 | 0.8545%
2016 | 131068760 | 18148353 | 838059 | 86 | N/A | 150055258 | 0.9569%
2017 | 132579747 | 18359427 | 840329 | 86 | N/A | 151779589 | 1.149%
[6 empty] | Total Growth 2014-2017 | 3.754%
[6 empty] | Average Annual Growth (2014-2017) | 0.9256%

## Gas & Elec Damages
Gas and Electric Damages: 2015 - 2018
| 2015 | 2016 | 2017 | 2018
Damages
Gas | 1020 | 1011 | 976 | 1035
Elec | 330 | 311 | 318 | 293
Total damages | 1350 | 1322 | 1294 | 1328
Locates
Gas Locates | 169879 | 185497 | 256325 | 302118
Total locates | 298298 | 329950 | 444044 | 514048
Ratios
Gas damage ratio (to enable comparison with AGA data) | 6.0043 | 5.4502 | 3.8077 | 3.4258
Damage ratio--total damages (Damages per 1,000 locates) | 4.5257 | 4.0067 | 2.9141 | 2.5834
|  |  | Gas and Electric Damage Reduction, 2015-2018: | -42.92%
`

## Cable_Repl_Hist Outages
Year | CRP_Miles_Repl | CRP_Miles_Inj | No.Cables_Inj | Total CRP_Miles_Repl | Actual Outages
1990 | 37 | 0 | 0 | 37 | 1094
1991 | 53 | 2 | 26 | 53 | 1113
1992 | 82 | 4 | 52.1481 | 82 | 1469
1993 | 152 | 0 | 0 | 152 | 1263
1994 | 157 | 0 | 0 | 157 | 1380
1995 | 119 | 1 | 13.037 | 140 | 1464
1996 | 183 | 12 | 156.4444 | 185 | 1397
1997 | 123 | 23 | 299.8519 | 146 | 1279
1998 | 128 | 5 | 65.1852 | 133 | 1139
1999 | 95 | 3 | 39.1111 | 98 | 1129
2000 | 56 | 42 | 547.5556 | 98 | 1086
2001 | 47 | 41 | 534.5185 | 88 | 1076
2002 | 15 | 61 | 795.2593 | 76 | 1156
2003 | 19 | 59 | 769.1852 | 78 | 1383
2004 | 78 | 106 | 1381.9259 | 184 | 1333
2005 | 47 | 77 | 1003.8519 | 124 | 1139
2006 | 56 | 40 | 521.4815 | 96 | 1094
2007 | 55 | 5 | 65.1852 | 60 | 1065
2008 | 90 | 0 |  | 90 | 948
2009 | 92.12 | 0 |  | 92.12 | 994
2010 | 57.6 | 0 |  | 57.6 | 888
2011 | 75 | 0 |  | 75 | 895
2012 | 25.7 | 0 |  | 25.7 | 974
2013 | 27 | 0 |  | 27 | 994
2014 | 47.9 | 0 |  | 47.9 | 1086
2015 | 70 | 0 |  | 70 | 1243
2016 | 128.4404 | 0 |  | 128.4404 | 1063
2017 | 144 | 0 |  | 118.6 | 813
2018 | 163 | 0 |  | 151 | 773
|  |  |  | Outage reduction due to failing cable: | -37.81%

## PSE Growth Stats Gas County
SAP - Counts by County |  | Customer Counts | [10 empty] | Customer Additions
| Division | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas
Fiscal year/period | Serv County Code | King | Kitsap | Kittitas | Lewis | Pierce | Snohomish | Thurston | Whatcom | Total Assigned | US/WA/Not assigned | Result | King | Kitsap | Kittitas | Lewis | Pierce | Snohomish | Thurston | Whatcom | Total Assigned | US/WA/Not assigned | Result
012/2015 | Customer Counts | 454066 | 1 | 1486 | 4252 | 153397 | 136245 | 50658 |  | 800105 | 221 | 800326
001/2016 | Customer Counts | 454933 | 1 | 1495 | 4269 | 153789 | 136583 | 50730 |  | 801800 | 221 | 802021 | 867 | 0 | 9 | 17 | 392 | 338 | 72 | 0 | 1695 | 0 | 1695
002/2016 | Customer Counts | 455360 | 1 | 1506 | 4271 | 154004 | 136789 | 50770 |  | 802701 | 224 | 802925 | 427 | 0 | 11 | 2 | 215 | 206 | 40 | 0 | 901 | 3 | 904
003/2016 | Customer Counts | 455819 | 1 | 1504 | 4290 | 154253 | 136954 | 50861 |  | 803682 | 227 | 803909 | 459 | 0 | -2 | 19 | 249 | 165 | 91 | 0 | 981 | 3 | 984
004/2016 | Customer Counts | 455911 | 1 | 1511 | 4283 | 154260 | 136911 | 50918 |  | 803795 | 200 | 803995 | 92 | 0 | 7 | -7 | 7 | -43 | 57 | 0 | 113 | -27 | 86
005/2016 | Customer Counts | 457245 | 1 | 1530 | 4276 | 154682 | 137456 | 51060 | 1 | 806251 | 209 | 806460 | 1334 | 0 | 19 | -7 | 422 | 545 | 142 | 1 | 2456 | 9 | 2465
006/2016 | Customer Counts | 457828 | 1 | 1539 | 4280 | 154852 | 137668 | 51165 | 1 | 807334 | 214 | 807548 | 583 | 0 | 9 | 4 | 170 | 212 | 105 | 0 | 1083 | 5 | 1088
007/2016 | Customer Counts | 457895 | 1 | 1543 | 4265 | 154909 | 137757 | 51210 | 1 | 807581 | 214 | 807795 | 67 | 0 | 4 | -15 | 57 | 89 | 45 | 0 | 247 | 0 | 247
008/2016 | Customer Counts | 458199 | 1 | 1541 | 4250 | 155031 | 137910 | 51325 |  | 808257 | 222 | 808479 | 304 | 0 | -2 | -15 | 122 | 153 | 115 | -1 | 676 | 8 | 684
009/2016 | Customer Counts | 458620 | 1 | 1551 | 4244 | 155266 | 138185 | 51447 |  | 809314 | 224 | 809538 | 421 | 0 | 10 | -6 | 235 | 275 | 122 | 0 | 1057 | 2 | 1059
010/2016 | Customer Counts | 459363 | 1 | 1559 | 4264 | 155564 | 138498 | 51555 |  | 810804 | 225 | 811029 | 743 | 0 | 8 | 20 | 298 | 313 | 108 | 0 | 1490 | 1 | 1491
011/2016 | Customer Counts | 460183 | 1 | 1570 | 4270 | 155916 | 138867 | 51693 |  | 812500 | 225 | 812725 | 820 | 0 | 11 | 6 | 352 | 369 | 138 | 0 | 1696 | 0 | 1696
012/2016 | Customer Counts | 461069 | 1 | 1595 | 4288 | 156349 | 139287 | 51782 |  | 814371 | 222 | 814593 | 886 | 0 | 25 | 18 | 433 | 420 | 89 | 0 | 1871 | -3 | 1868
001/2017 | Customer Counts | 461649 | 1 | 1598 | 4286 | 156547 | 139472 | 51870 |  | 815423 | 225 | 815648 | 580 | 0 | 3 | -2 | 198 | 185 | 88 | 0 | 1052 | 3 | 1055
002/2017 | Customer Counts | 462063 | 1 | 1607 | 4281 | 156774 | 139724 | 51938 |  | 816388 | 223 | 816611 | 414 | 0 | 9 | -5 | 227 | 252 | 68 | 0 | 965 | -2 | 963
003/2017 | Customer Counts | 462283 | 1 | 1606 | 4282 | 156895 | 139896 | 51966 |  | 816929 | 225 | 817154 | 220 | 0 | -1 | 1 | 121 | 172 | 28 | 0 | 541 | 2 | 543
004/2017 | Customer Counts | 462432 | 1 | 1608 | 4284 | 157032 | 139978 | 52049 |  | 817384 | 230 | 817614 | 149 | 0 | 2 | 2 | 137 | 82 | 83 | 0 | 455 | 5 | 460
005/2017 | Customer Counts | 462701 | 1 | 1616 | 4264 | 157160 | 140107 | 52105 |  | 817954 | 232 | 818186 | 269 | 0 | 8 | -20 | 128 | 129 | 56 | 0 | 570 | 2 | 572
006/2017 | Customer Counts | 462740 | 1 | 1626 | 4258 | 157156 | 140161 | 52161 |  | 818103 | 234 | 818337 | 39 | 0 | 10 | -6 | -4 | 54 | 56 | 0 | 149 | 2 | 151
007/2017 | Customer Counts | 462622 | 1 | 1628 | 4247 | 157126 | 140219 | 52200 |  | 818043 | 233 | 818276 | -118 | 0 | 2 | -11 | -30 | 58 | 39 | 0 | -60 | -1 | -61
008/2017 | Customer Counts | 462762 | 1 | 1641 | 4229 | 157261 | 140407 | 52283 |  | 818584 | 235 | 818819 | 140 | 0 | 13 | -18 | 135 | 188 | 83 | 0 | 541 | 2 | 543
009/2017 | Customer Counts | 463238 | 1 | 1646 | 4219 | 157573 | 140691 | 52393 |  | 819761 | 235 | 819996 | 476 | 0 | 5 | -10 | 312 | 284 | 110 | 0 | 1177 | 0 | 1177
010/2017 | Customer Counts | 464233 | 1 | 1654 | 4241 | 157942 | 141031 | 52462 |  | 821564 | 234 | 821798 | 995 | 0 | 8 | 22 | 369 | 340 | 69 | 0 | 1803 | -1 | 1802
011/2017 | Customer Counts | 465344 | 1 | 1667 | 4269 | 158436 | 141472 | 52565 |  | 823754 | 241 | 823995 | 1111 | 0 | 13 | 28 | 494 | 441 | 103 | 0 | 2190 | 7 | 2197
012/2017 | Customer Counts | 466015 | 1 | 1678 | 4284 | 158854 | 141874 | 52648 |  | 825354 | 245 | 825599 | 671 | 0 | 11 | 15 | 418 | 402 | 83 | 0 | 1600 | 4 | 1604
001/2018 | Customer Counts | 466548 | 1 | 1678 | 4295 | 159103 | 142105 | 52722 |  | 826452 | 238 | 826690 | 533 | 0 | 0 | 11 | 249 | 231 | 74 | 0 | 1098 | -7 | 1091
002/2018 | Customer Counts | 467087 | 1 | 1687 | 4287 | 159372 | 142369 | 52792 |  | 827595 | 238 | 827833 | 539 | 0 | 9 | -8 | 269 | 264 | 70 | 0 | 1143 | 0 | 1143
003/2018 | Customer Counts | 467515 | 1 | 1691 | 4276 | 159546 | 142531 | 52851 |  | 828411 | 224 | 828635 | 428 | 0 | 4 | -11 | 174 | 162 | 59 | 0 | 816 | -14 | 802
004/2018 | Customer Counts | 467543 | 1 | 1704 | 4267 | 159686 | 142686 | 52886 |  | 828773 | 217 | 828990 | 28 | 0 | 13 | -9 | 140 | 155 | 35 | 0 | 362 | -7 | 355
005/2018 | Customer Counts | 467879 | 1 | 1710 | 4254 | 159815 | 142807 | 52935 |  | 829401 | 217 | 829618 | 336 | 0 | 6 | -13 | 129 | 121 | 49 | 0 | 628 | 0 | 628
006/2018 | Customer Counts | 467951 | 1 | 1710 | 4246 | 159828 | 142934 | 52966 |  | 829636 | 219 | 829855 | 72 | 0 | 0 | -8 | 13 | 127 | 31 | 0 | 235 | 2 | 237
007/2018 | Customer Counts | 467952 | 1 | 1721 | 4233 | 159883 | 142994 | 53002 |  | 829786 | 218 | 830004 | 1 | 0 | 11 | -13 | 55 | 60 | 36 | 0 | 150 | -1 | 149
008/2018 | Customer Counts | 468146 | 1 | 1722 | 4223 | 160009 | 143078 | 53133 |  | 830312 | 216 | 830528 | 194 | 0 | 1 | -10 | 126 | 84 | 131 | 0 | 526 | -2 | 524
009/2018 | Customer Counts | 468399 | 1 | 1739 | 4223 | 160162 | 143149 | 53207 |  | 830880 | 219 | 831099 | 253 | 0 | 17 | 0 | 153 | 71 | 74 | 0 | 568 | 3 | 571
010/2018 | Customer Counts | 469588 | 1 | 1746 | 4232 | 160601 | 143638 | 53318 |  | 833124 | 221 | 833345 | 1189 | 0 | 7 | 9 | 439 | 489 | 111 | 0 | 2244 | 2 | 2246
011/2018 | Customer Counts | 470871 | 1 | 1774 | 4248 | 161027 | 144114 | 53394 |  | 835429 | 223 | 835652 | 1283 | 0 | 28 | 16 | 426 | 476 | 76 | 0 | 2305 | 2 | 2307
012/2018 | Customer Counts | 471566 | 1 | 1792 | 4260 | 161388 | 144421 | 53460 |  | 836888 | 224 | 837112 | 695 | 0 | 18 | 12 | 361 | 307 | 66 | 0 | 1459 | 1 | 1460
Year End | Customer Counts | [11 empty] | Annual Customer Additions |  |  |  |  | snohomish
| 2015 | 454066 | 1 | 1486 | 4252 | 153397 | 136245 | 50658 | 0 | 800105 | 221 | 800326
| 2016 | 461069 | 1 | 1595 | 4288 | 156349 | 139287 | 51782 | 0 | 814371 | 222 | 814593 | 7003 | 0 | 109 | 36 | 2952 | 3042 | 1124 | 0 | 14266 | 1 | 14267
| 2017 | 466015 | 1 | 1678 | 4284 | 158854 | 141874 | 52648 | 0 | 825354 | 245 | 825599 | 4946 | 0 | 83 | -4 | 2505 | 2587 | 866 | 0 | 10983 | 23 | 11006
| 2018 | 471566 | 1 | 1792 | 4260 | 161388 | 144421 | 53460 | 0 | 836888 | 224 | 837112 | 5551 | 0 | 114 | -24 | 2534 | 2547 | 812 | 0 | 11534 | -21 | 11513
Customer Additions
[11 empty] | Jan 16 thru Dec 18 |  | 17500 | 0 | 306 | 8 | 7991 | 8176 | 2802 | 0 | 36783 | 3 | 36786
[11 empty] | Oct 16 thru Dec 18 |  | 12946 | 0 | 241 | 16 | 6122 | 6236 | 2013 | 0 | 27574 | 0 | 27574
[12 empty] | Total growth Jan16 thru Dec18 | 3.854% | 0% | 20.59% | 0.1881% | 5.209% | 6.001% | 5.531% | 0% | 4.597% | 1.357% | 4.596%
[12 empty] | Total growth Oct16 thru Dec18 | 2.823% | 0% | 15.54% | 0.377% | 3.943% | 4.513% | 3.913% | 0% | 3.407% | 0% | 3.406%
Total Customer Annual Growth
[11 empty] | 2016 |  | 1.542% | 0% | 7.335% | 0.8467% | 1.924% | 2.233% | 2.219% | 0% | 1.783% | 0.4525% | 1.783%
[11 empty] | 2017 |  | 1.073% | 0% | 5.204% | -0.09328% | 1.602% | 1.857% | 1.672% | 0% | 1.349% | 10.36% | 1.351%
[11 empty] | 2018 |  | 1.191% | 0% | 6.794% | -0.5602% | 1.595% | 1.795% | 1.542% | 0% | 1.397% | -8.571% | 1.395%
[12 empty] | Average Annual Growth (2017-2018) | 1.132% | 0% | 5.999% | -0.3268% | 1.599% | 1.826% | 1.607% | 0% | 1.373% | 0.8945% | 1.373%
[12 empty] | Average Annual Growth (2016-2018) | 1.269% | 0% | 6.444% | 0.06438% | 1.707% | 1.962% | 1.811% | 0% | 1.51% | 0.7471% | 1.509%

## Public Improvement Projects
Gas and Electric Public Improvement Project Counts by month
| YEAR | 2017 | [12 empty] | 2018
| WBS Element | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | 2017 TOTAL | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | 2018 TOTAL | TOTAL
Electric PI | R.10008.01.01.01 | 2017 Aug: 1; 2017 Sep: 1; 2017 Nov: 2 | 4 |  | 1 |  | 1 | 1 |  |  | 2 | 2 | 5 | 2 | 1 | 15 | 19
Electric PI | R.10008.01.01.02 | 17 | 13 | 18 | 11 | 16 | 19 | 12 | 18 | 13 | 12 | 6 | 9 | 164 | 11 | 9 | 7 | 18 | 16 | 10 | 13 | 14 | 18 | 12 | 9 | 8 | 145 | 309
Electric PI | R.10008.03.01.01 | [12 empty] | 8 | 3 | 2 | 1 |  | 1 | 3 |  | 1 |  | 1 | 2 |  | 14 | 22 | bar: 2017 Mar to 2017 Jun; 2017 Aug to 2017 Nov
Electric PI | R.10008.03.01.03 |  | 1 | 2 | 3 | 2 | 1 | 6 | 4 | 4 | 3 | 1 | 1 | 28 | 2 | 4 | 3 | 4 | 4 | 3 | 4 | 5 | 4 | 4 | 4 | 1 | 42 | 70
Electric PI | R.10008.03.01.04 | 2017 Jun: 3 | 3 |  |  | 1 |  | 2 | 4 | 1 | 1 | 2 | 1 | 1 |  | 13 | 16
Electric PI | R.10008.03.01.05 | 2017 Mar: 1; 2017 Apr: 3; 2017 Jun: 2; 2017 Sep: 1; 2017 Dec: 1 | 8 |  | 2 |  |  | 1 | 1 | 1 |  |  | 1 | 2 | 1 | 9 | 17
Electric PI | R.10009.07.03.01 | [12 empty] | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 2 | 2
| Sub Total | 17 | 14 | 22 | 18 | 19 | 26 | 18 | 24 | 20 | 16 | 10 | 11 | 215 | 16 | 18 | 13 | 23 | 25 | 21 | 19 | 24 | 26 | 24 | 20 | 11 | 240 | 455
Gas PI | R.10013.04.01.01 | 2 | 3 | 5 | 5 | 4 | 11 | 3 | 3 | 10 | 4 | 5 | 1 | 56 | 1 | 3 | 9 | 5 | 13 | 10 | 9 | 6 | 6 | 6 | 5 | 4 | 77 | 133
Gas PI | R.10013.04.01.02 | 2017 Aug: 2 | 2 |  |  | 1 | [5 empty] | 1 |  |  |  | 2 | 4
Gas PI | R.10013.07.01.01 | [12 empty] | 1 | [12 empty] | 0 | 1 | bar: 2017 Jun
Gas PI | R.10013.07.01.02 | 2017 Jan: 1; 2017 Mar: 1; 2017 Apr: 1; 2017 Jun: 1; 2017 Aug: 1; 2017 Nov: 2 | 7 |  |  |  | 2 | [8 empty] | 2 | 9
| Sub Total | 3 | 3 | 6 | 6 | 4 | 13 | 3 | 6 | 10 | 4 | 7 | 1 | 66 | 1 | 3 | 10 | 7 | 13 | 10 | 9 | 6 | 7 | 6 | 5 | 4 | 81 | 147

## PSE Growth Stats Elec County
|  | Customer Counts | [14 empty] | Customer Additions
| Division | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Total ELECTRIC | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Electric | Total ELECTRIC | Electric | Electric
Fiscal year/period | Serv County Code | Island | King | Kitsap | Kittitas | Lewis | Pierce | San Juan | Skagit | Snohomish | Stevens | Thurston | Whatcom | Assigned | US/WA/Not assigned | Result | Island | King | Kitsap | Kittitas | Lewis | Pierce | San Juan | Skagit | Snohomish | Stevens | Thurston | Whatcom | Assigned | US/WA/Not assigned | Result
012/2015 | Customer Counts | 36090 | 541503 | 117699 | 13009 | 21 | 115267 | 1 | 59081 | 55 |  | 125415 | 100816 | 1108957 | 1084 | 1110041
001/2016 | Customer Counts | 36118 | 542167 | 117696 | 13020 | 21 | 115369 | 1 | 59178 | 55 |  | 125452 | 100955 | 1110032 | 1187 | 1111219 | 28 | 664 | -3 | 11 | 0 | 102 | 0 | 97 | 0 | 0 | 37 | 139 | 1075 | 103 | 1178
002/2016 | Customer Counts | 36146 | 542515 | 117751 | 13036 | 21 | 115509 | 1 | 59187 | 54 |  | 125568 | 101133 | 1110921 | 1191 | 1112112 | 28 | 348 | 55 | 16 | 0 | 140 | 0 | 9 | -1 | 0 | 116 | 178 | 889 | 4 | 893
003/2016 | Customer Counts | 36158 | 543305 | 117960 | 13036 | 21 | 115660 | 1 | 59243 | 55 |  | 125820 | 101267 | 1112526 | 1192 | 1113718 | 12 | 790 | 209 | 0 | 0 | 151 | 0 | 56 | 1 | 0 | 252 | 134 | 1605 | 1 | 1606
004/2016 | Customer Counts | 36181 | 543594 | 117969 | 13082 | 20 | 115799 | 1 | 59343 | 54 |  | 126021 | 101372 | 1113436 | 1104 | 1114540 | 23 | 289 | 9 | 46 | -1 | 139 | 0 | 100 | -1 | 0 | 201 | 105 | 910 | -88 | 822
005/2016 | Customer Counts | 36246 | 545136 | 118190 | 13196 | 19 | 116093 | 1 | 59454 | 54 | 5 | 126405 | 101495 | 1116294 | 1115 | 1117409 | 65 | 1542 | 221 | 114 | -1 | 294 | 0 | 111 | 0 | 5 | 384 | 123 | 2858 | 11 | 2869
006/2016 | Customer Counts | 36354 | 546349 | 118413 | 13263 | 20 | 116431 | 1 | 59610 | 54 | 7 | 126715 | 101832 | 1119049 | 1217 | 1120266 | 108 | 1213 | 223 | 67 | 1 | 338 | 0 | 156 | 0 | 2 | 310 | 337 | 2755 | 102 | 2857
007/2016 | Customer Counts | 36327 | 546500 | 118491 | 13283 | 20 | 116564 | 1 | 59662 | 53 | 7 | 126847 | 101784 | 1119539 | 1216 | 1120755 | -27 | 151 | 78 | 20 | 0 | 133 | 0 | 52 | -1 | 0 | 132 | -48 | 490 | -1 | 489
008/2016 | Customer Counts | 36386 | 547004 | 118571 | 13305 | 20 | 116714 | 1 | 59712 | 52 | 7 | 127037 | 101925 | 1120734 | 1217 | 1121951 | 59 | 504 | 80 | 22 | 0 | 150 | 0 | 50 | -1 | 0 | 190 | 141 | 1195 | 1 | 1196
009/2016 | Customer Counts | 36403 | 547881 | 118731 | 13349 | 22 | 116842 | 1 | 59768 | 54 | 7 | 127267 | 102060 | 1122385 | 1229 | 1123614 | 17 | 877 | 160 | 44 | 2 | 128 | 0 | 56 | 2 | 0 | 230 | 135 | 1651 | 12 | 1663
010/2016 | Customer Counts | 36402 | 548837 | 118864 | 13331 | 22 | 117057 | 1 | 59820 | 54 | 7 | 127425 | 102290 | 1124110 | 1224 | 1125334 | -1 | 956 | 133 | -18 | 0 | 215 | 0 | 52 | 0 | 0 | 158 | 230 | 1725 | -5 | 1720
011/2016 | Customer Counts | 36471 | 549848 | 118984 | 13311 | 22 | 117154 | 1 | 59869 | 54 | 7 | 127608 | 102455 | 1125784 | 1218 | 1127002 | 69 | 1011 | 120 | -20 | 0 | 97 | 0 | 49 | 0 | 0 | 183 | 165 | 1674 | -6 | 1668
012/2016 | Customer Counts | 36497 | 550393 | 119159 | 13322 | 22 | 117659 | 1 | 59905 | 54 | 11 | 127895 | 102564 | 1127482 | 1222 | 1128704 | 26 | 545 | 175 | 11 | 0 | 505 | 0 | 36 | 0 | 4 | 287 | 109 | 1698 | 4 | 1702
001/2017 | Customer Counts | 36524 | 550936 | 119252 | 13336 | 22 | 117866 | 1 | 59996 | 55 | 11 | 128070 | 102584 | 1128653 | 1229 | 1129882 | 27 | 543 | 93 | 14 | 0 | 207 | 0 | 91 | 1 | 0 | 175 | 20 | 1171 | 7 | 1178
002/2017 | Customer Counts | 36554 | 551359 | 119402 | 13331 | 22 | 118018 | 1 | 60033 | 55 | 11 | 128251 | 102615 | 1129652 | 1226 | 1130878 | 30 | 423 | 150 | -5 | 0 | 152 | 0 | 37 | 0 | 0 | 181 | 31 | 999 | -3 | 996
003/2017 | Customer Counts | 36557 | 551355 | 119449 | 13330 | 22 | 118129 | 1 | 60034 | 54 | 11 | 128258 | 102695 | 1129895 | 1230 | 1131125 | 3 | -4 | 47 | -1 | 0 | 111 | 0 | 1 | -1 | 0 | 7 | 80 | 243 | 4 | 247
004/2017 | Customer Counts | 36544 | 551615 | 119493 | 13345 | 23 | 118241 | 1 | 60087 | 55 | 20 | 128536 | 102834 | 1130794 | 1232 | 1132026 | -13 | 260 | 44 | 15 | 1 | 112 | 0 | 53 | 1 | 9 | 278 | 139 | 899 | 2 | 901
005/2017 | Customer Counts | 36584 | 552128 | 119605 | 13434 | 22 | 118438 | 1 | 60101 | 56 | 22 | 128728 | 102898 | 1132017 | 1232 | 1133249 | 40 | 513 | 112 | 89 | -1 | 197 | 0 | 14 | 1 | 2 | 192 | 64 | 1223 | 0 | 1223
006/2017 | Customer Counts | 36599 | 552290 | 119635 | 13481 | 23 | 118513 | 1 | 60150 | 56 | 25 | 128888 | 102957 | 1132618 | 1226 | 1133844 | 15 | 162 | 30 | 47 | 1 | 75 | 0 | 49 | 0 | 3 | 160 | 59 | 601 | -6 | 595
007/2017 | Customer Counts | 36601 | 552426 | 119689 | 13509 | 23 | 118715 | 1 | 60210 | 56 | 25 | 129007 | 103017 | 1133279 | 1233 | 1134512 | 2 | 136 | 54 | 28 | 0 | 202 | 0 | 60 | 0 | 0 | 119 | 60 | 661 | 7 | 668
008/2017 | Customer Counts | 36615 | 552919 | 119824 | 13574 | 24 | 119035 | 1 | 60233 | 56 | 25 | 129222 | 103164 | 1134692 | 1240 | 1135932 | 14 | 493 | 135 | 65 | 1 | 320 | 0 | 23 | 0 | 0 | 215 | 147 | 1413 | 7 | 1420
009/2017 | Customer Counts | 36656 | 553551 | 119988 | 13585 | 24 | 119192 | 1 | 60303 | 56 | 28 | 129408 | 103326 | 1136118 | 1240 | 1137358 | 41 | 632 | 164 | 11 | 0 | 157 | 0 | 70 | 0 | 3 | 186 | 162 | 1426 | 0 | 1426
010/2017 | Customer Counts | 36688 | 554235 | 120126 | 13589 | 24 | 119512 | 1 | 60378 | 57 | 28 | 129554 | 103575 | 1137767 | 1241 | 1139008 | 32 | 684 | 138 | 4 | 0 | 320 | 0 | 75 | 1 | 0 | 146 | 249 | 1649 | 1 | 1650
011/2017 | Customer Counts | 36736 | 554895 | 120316 | 13568 | 24 | 119728 | 1 | 60445 | 57 | 28 | 129950 | 103677 | 1139425 | 1240 | 1140665 | 48 | 660 | 190 | -21 | 0 | 216 | 0 | 67 | 0 | 0 | 396 | 102 | 1658 | -1 | 1657
012/2017 | Customer Counts | 36798 | 555407 | 120454 | 13595 | 24 | 120022 | 1 | 60579 | 56 | 30 | 130069 | 103778 | 1140813 | 1240 | 1142053 | 62 | 512 | 138 | 27 | 0 | 294 | 0 | 134 | -1 | 2 | 119 | 101 | 1388 | 0 | 1388
001/2018 | Customer Counts | 36813 | 556106 | 120503 | 13593 | 23 | 120172 | 1 | 60613 | 57 | 33 | 130179 | 103811 | 1141904 | 1238 | 1143142 | 15 | 699 | 49 | -2 | -1 | 150 | 0 | 34 | 1 | 3 | 110 | 33 | 1091 | -2 | 1089
002/2018 | Customer Counts | 36853 | 556811 | 120640 | 13611 | 24 | 120408 | 1 | 60654 | 57 | 33 | 130281 | 103950 | 1143323 | 1244 | 1144567 | 40 | 705 | 137 | 18 | 1 | 236 | 0 | 41 | 0 | 0 | 102 | 139 | 1419 | 6 | 1425
003/2018 | Customer Counts | 36852 | 557296 | 120655 | 13633 | 23 | 120568 | 1 | 60718 | 57 | 33 | 130377 | 104056 | 1144269 | 1231 | 1145500 | -1 | 485 | 15 | 22 | -1 | 160 | 0 | 64 | 0 | 0 | 96 | 106 | 946 | -13 | 933
004/2018 | Customer Counts | 36892 | 557555 | 120750 | 13672 | 24 | 120649 | 1 | 60778 | 57 | 33 | 130537 | 104177 | 1145125 | 1235 | 1146360 | 40 | 259 | 95 | 39 | 1 | 81 | 0 | 60 | 0 | 0 | 160 | 121 | 856 | 4 | 860
005/2018 | Customer Counts | 36882 | 558191 | 120802 | 13766 | 24 | 120815 | 1 | 60845 | 58 | 33 | 130630 | 104407 | 1146454 | 1237 | 1147691 | -10 | 636 | 52 | 94 | 0 | 166 | 0 | 67 | 1 | 0 | 93 | 230 | 1329 | 2 | 1331
006/2018 | Customer Counts | 36918 | 559011 | 120901 | 13792 | 24 | 120973 | 1 | 60898 | 58 | 33 | 130719 | 104504 | 1147832 | 1227 | 1149059 | 36 | 820 | 99 | 26 | 0 | 158 | 0 | 53 | 0 | 0 | 89 | 97 | 1378 | -10 | 1368
007/2018 | Customer Counts | 36916 | 559198 | 120887 | 13827 | 24 | 121070 | 1 | 60937 | 58 | 33 | 130795 | 104550 | 1148296 | 1293 | 1149589 | -2 | 187 | -14 | 35 | 0 | 97 | 0 | 39 | 0 | 0 | 76 | 46 | 464 | 66 | 530
008/2018 | Customer Counts | 36970 | 559757 | 121008 | 13875 | 24 | 121220 | 1 | 61027 | 58 | 33 | 130934 | 104593 | 1149500 | 1317 | 1150817 | 54 | 559 | 121 | 48 | 0 | 150 | 0 | 90 | 0 | 0 | 139 | 43 | 1204 | 24 | 1228
009/2018 | Customer Counts | 36994 | 560879 | 121158 | 13888 | 24 | 121404 | 1 | 61080 | 59 | 33 | 131093 | 104772 | 1151385 | 1317 | 1152702 | 24 | 1122 | 150 | 13 | 0 | 184 | 0 | 53 | 1 | 0 | 159 | 179 | 1885 | 0 | 1885
010/2018 | Customer Counts | 37041 | 561545 | 121290 | 13917 | 24 | 121580 | 1 | 61153 | 59 | 33 | 131255 | 104992 | 1152890 | 1342 | 1154232 | 47 | 666 | 132 | 29 | 0 | 176 | 0 | 73 | 0 | 0 | 162 | 220 | 1505 | 25 | 1530
011/2018 | Customer Counts | 37088 | 562881 | 121421 | 13896 | 24 | 121742 | 1 | 61224 | 59 | 33 | 131431 | 105140 | 1154940 | 1376 | 1156316 | 47 | 1336 | 131 | -21 | 0 | 162 | 0 | 71 | 0 | 0 | 176 | 148 | 2050 | 34 | 2084
012/2018 | Customer Counts | 37110 | 563382 | 121555 | 13914 | 24 | 121947 | 1 | 61267 | 59 | 33 | 131554 | 105274 | 1156120 | 1376 | 1157496 | 22 | 501 | 134 | 18 | 0 | 205 | 0 | 43 | 0 | 0 | 123 | 134 | 1180 | 0 | 1180
Year End | Customer Counts | [15 empty] | Annual Customer Additions
| 2015 | 36090 | 541503 | 117699 | 13009 | 21 | 115267 | 1 | 59081 | 55 | 0 | 125415 | 100816 | 1108957 | 1084 | 1110041
| 2016 | 36497 | 550393 | 119159 | 13322 | 22 | 117659 | 1 | 59905 | 54 | 11 | 127895 | 102564 | 1127482 | 1222 | 1128704 | 407 | 8890 | 1460 | 313 | 1 | 2392 | 0 | 824 | -1 | 11 | 2480 | 1748 | 18525 | 138 | 18663
| 2017 | 36798 | 555407 | 120454 | 13595 | 24 | 120022 | 1 | 60579 | 56 | 30 | 130069 | 103778 | 1140813 | 1240 | 1142053 | 301 | 5014 | 1295 | 273 | 2 | 2363 | 0 | 674 | 2 | 19 | 2174 | 1214 | 13331 | 18 | 13349
| 2018 | 37110 | 563382 | 121555 | 13914 | 24 | 121947 | 1 | 61267 | 59 | 33 | 131554 | 105274 | 1156120 | 1376 | 1157496 | 312 | 7975 | 1101 | 319 | 0 | 1925 | 0 | 688 | 3 | 3 | 1485 | 1496 | 15307 | 136 | 15443
King Co portion of Total
| Customer Additions | [14 empty] | Customer Additions
| Jan 16 thru Dec 18 | [14 empty] | Jan 16 thru Dec 19 | 1020 | 21879 | 3856 | 905 | 3 | 6680 | 0 | 2186 | 4 | 33 | 6139 | 4458 | 47163 | 292 | 47455
| Oct 16 thru Dec 18 | [14 empty] | Oct 16 thru Dec 19 | 707 | 15501 | 2824 | 565 | 2 | 5105 | 0 | 1499 | 5 | 26 | 4287 | 3214 | 33735 | 147 | 33882 | 45.75% | King Co portion of Total
| Total growth Jan16 thru Dec18 | [14 empty] | Total growth Jan16 thru Dec19 | 2.826% | 4.04% | 3.276% | 6.957% | 14.29% | 5.795% | 0% | 3.7% | 7.273% | #DIV/0! | 4.895% | 4.422% | 4.253% | 26.94% | 4.275%
| Total growth Oct16 thru Dec18 | [14 empty] | Total growth Oct16 thru Dec19 | 1.942% | 2.829% | 2.378% | 4.233% | 9.091% | 4.369% | 0% | 2.508% | 9.259% | 371.4% | 3.369% | 3.149% | 3.006% | 11.96% | 3.015%
| Total Customer Annual Growth | [14 empty] | Total Customer Annual Growth
| 2016 | [14 empty] | 2016 | 1.128% | 1.642% | 1.24% | 2.406% | 4.762% | 2.075% | 0% | 1.395% | -1.818% | #DIV/0! | 1.977% | 1.734% | 1.67% | 12.73% | 1.681%
| 2017 | [14 empty] | 2017 | 0.8247% | 0.911% | 1.087% | 2.049% | 9.091% | 2.008% | 0% | 1.125% | 3.704% | 172.7% | 1.7% | 1.184% | 1.182% | 1.473% | 1.183%
| 2018 | [14 empty] | 2018 | 0.8479% | 1.436% | 0.914% | 2.346% | 0% | 1.604% | 0% | 1.136% | 5.357% | 10% | 1.142% | 1.442% | 1.342% | 10.97% | 1.352%
| Avg Annual Growth (2017-2018) | [14 empty] | Average Annual Growth (2017-2018) | 0.8363% | 1.173% | 1% | 2.198% | 4.545% | 1.806% | 0% | 1.13% | 4.53% | 91.36% | 1.421% | 1.313% | 1.262% | 6.22% | 1.267%
| Avg Annual Growth (2016-2018) | [14 empty] | Average Annual Growth (2016-2018) | 0.9334% | 1.33% | 1.08% | 2.267% | 4.618% | 1.896% | 0% | 1.219% | 2.414% | #DIV/0! | 1.606% | 1.453% | 1.398% | 8.39% | 1.405%

## IWM Ops Per Worker Per Day
Month | Operations Completed | Worker Days | Operations Completed Per Worker Per Day
2018-10-01 | 1644 | 358 | 4.5922
2018-11-01 | 1777 | 404 | 4.3985
2018-12-01 | 1552 | 350 | 4.4343
2019-01-01 | 2192 | 447 | 4.9038
2019-02-01 | 1336 | 318 | 4.2013
2019-03-01 | 2238 | 471 | 4.7516
2019-04-01 | 2509 | 481 | 5.2162
Total | 13248 | 2829 | 4.6829
|  | 2016-2017 Baseline | 4.2072
|  | % Change over Baseline | 11.31%

## Cust Satisfaction Survey
Customer satisfaction for new customer construction
Online - Survey Monkey Response Baseline | 2018 | 2017 | Baseline: Pre-SPA (6-16-15 survey) for complex
Project Application | 8.45 | 8.25 | 6.24
Planning & Coordination | 8.2 | 7.98 | 6
Project Estimates & Pricing | 8.75 | 8.46 | 5.44
Construction | 8.92 | 8.99 | 6.78
Customer Service | 8.67 | 8.46 | 6.34
Sub Total Average of Above Catagories: | 8.598 | 8.428 | 6.16
Overall Satisfaction of Performance: | 8.46 | 8.29 | 6.32
Online - Survey Monkey Response Baseline | Variance 2017 – 2018 | Variance 2016 – 2017
Project Application | 0.2 | 2.01
Planning & Coordination | 0.22 | 1.98
Project Estimates & Pricing | 0.29 | 3.02
Construction | -0.07 | 2.21
Customer Service | 0.21 | 2.12
Overall Satisfaction of Performance | 0 | 0
Planning & Coordination - lowest
coordinating project designs & plans to meet your timelines
communication & maintaining clear, accurate & detailed project schedule
providing clear information on the construction process
providing the correct project design the first time
overall performance of planning
Customer Service - 2nd lowest
responding promptly to your questions
providing communicaton & feedback trhoughout the project
including notifications and status updates
overall performance of PSE in meeting your needs and expectations

## 20 yr Model - Truss comparison
Pricing Model
|  | O&M | Capital
Avg Inspect/Treat Dist | 40.86 | 19.0408 | 21.8192
Avg Inspect/Treat Trans | 64.71 | 64.71 | 0
Avg Truss - Dist | 1062.03 |  | 1062.03
Avg Truss - Tran | 2127.31 |  | 2127.31
Avg Replace - Dist | 10000 | 600 | 9400
Avg Replace - Trans | 35000 | 5600 | 29400
O&M | 46.6% | 6% | 16%
Capital | 53.4% | 94% | 84%
|  | D | T
Distribution
Avg Truss - Dist | 1062.03
Avg Replace - Dist | 10000
Cost savings per pole - Dist | -89.38%
Transmission
Avg Truss - Tran | 2127.31
Avg Replace - Trans | 35000
Cost savings per pole - Trans | -93.92%
Avg Cost Savings per pole - T&D | -91.65%

## DA circuits enabled
DA Enabled Circuits
| Ckt | Date Enabled
| ALG-15 | 2019-01-17
1 | ARD-43 | 2018-10-03
2 | BCH-13 | 2016-12-09
3 | BCH-15 | 2016-12-09
4 | BDI-13 | 2017-12-22
| BKB-12 | 2019-04-01
5 | BKB-13 | 2018-11-07
6 | BTR-24 | 2018-10-03
7 | CAM-25 | 2018-05-23
8 | CAM-26 | 2018-11-20
9 | CPV-13 | 2017-12-19
10 | CTR-22 | 2018-05-23
11 | CUM-13 | 2018-09-22
12 | ELD-27 | 2018-05-12
13 | EVE-13 | 2018-10-03
14 | EVE-26 | 2018-10-03
| FWD-17 | 2019-01-31
15 | GLA-13 | 2017-01-01
| GLC-15 | 2019-01-31
16 | GRI-13 | 2018-05-12
| HAP-16 | 2019-01-17
17 | HKX-13 | 2017-12-19
18 | HKX-16 | 2017-12-19
19 | HLC-23 | 2017-12-19
20 | HOB-15 | 2018-09-22
21 | HWD-25 | 2018-04-18
22 | ING-13 | 2018-04-18
23 | ING-15 | 2018-04-18
24 | KNM-23 | 2018-04-18
25 | KWH-24 | 2018-10-03
26 | LLT-15 | 2018-04-18
27 | MTV-17 | 2018-11-07
28 | MVW-13 | 2018-05-23
29 | PAD-15 | 2018-08-31
| PAN-12 | 2019-01-31
| PAN-14 | 2019-01-31
| PET-16 | 2019-04-01
30 | PRI-13 | 2018-04-10
31 | PRI-23 | 2018-04-10
32 | RDO-13 | 2018-11-20
33 | ROS-17 | 2018-10-03
34 | SHD-18 | 2017-12-22
35 | SOO-25 | 2017-12-22
36 | SUM-23 | 2018-08-31
37 | SWA-16 | 2017-12-19
38 | VAS-12 | 2018-01-05
39 | VAS-13 | 2018-01-05
40 | VAS-22 | 2018-01-05
41 | VAS-23 | 2018-01-05
| WOB-23 | 2019-01-17
42 | WOO-23 | 2017-11-12
43 | WOO-26 | 2017-11-12
44 | WOO-27 | 2017-11-12

## DA Event Tracking Overview
Year | # Of Operations | Successful | Success % | Partial | Partial % | Unsuccessful | Unsuccessful % | Customer Interruptions Saved | Customer Minutes Saved | Missed Opportunity Customer Interruptions | Missed Opportunity Customer Minutes | Operations Missed due to Work Practices | Missed Opportunity Customer Interruptions due to Work Practices | Missed Opportunity Customer Minutes due to Work Practices
2018 | 25 | 12 | 48% | 3 | 12% | 10 | 40% | 9627 | 2302894 | 8470 | 1474714 | * | * | *
2019 | 3 | 2 | 66.67% | 0 | 0% | 1 | 33.33% | 1401 | 29508 | 597 | 87162 | 2 | 1499 | 850821
2020
Total | 28 | 14 | 50% | 3 | 10.71% | 11 | 39.29% | 11028 | 2332402 | 9067 | 1561876
*Not Tracked
Sucessful Operation = All possible customers restored
Partial Operation = Some customers restored, but not all that could have been
Unsuccessful = No customers restored

## DA 2018 Operations
Date of Event | Time | Event # | Substation | Feeder | Device Locked Out | # of Customers on Device Locked Out | Outage Length (Minutes) | Sequence of Operation | Automatic Restoration Time | Customers Automatically Restored | Customer Minutes Saved | OMS Single Order (Yes/No) | Missed Opportunity (# of Customers Could of Restored) | Missed Opportunity (# of Customers Minutes PSE could of Saved) | Follow Up Actions | Follow Up Complete | Operation Classification
2018-01-18 | 0:45 |  | ING | 13 | X420 | 1177 | 113 | X420 locked out at 00:45 due to a fallen tree limb, YFA isolated the faulted area by issuing open commands to reclosers X1424 and X5408. YFA then issue a closed command to X636, restoring 418 customers up to device X1424. Due to a communication error YFA was not able to restore the 313 customers downstream of X5408. Therefore a partially successful operation. | 1 minute 45 seconds | 418 | 47234 | No | 313 | 35369 | Follow up on communication errors process to ensure communication problems are handled in a timely manner. OMS also didn't issue all orders in one due to a point name mismatch the process will be improved with DA Team identifying point name changes to DA Devices to the OMS team. The DA Display had issues with resetting YFA targets as well. | DA Diplay Fixed Feb 2018, OMS/ECS Point Name Changes process identifeid, Communication Tracking On Going | Partial
2018-01-21 | 15:59 | O#426882-1 | VAS | 13 | X307 | 1114 | 0:00 | X307 locked out due to a fault downstream. YFA then sent a Open command to X6358 to Isolated the faulted area. YFA then stopped automation, as there wasn't a restoration path available. | N/A | 0 | 0 | Yes | 0 | 0 | N/A | N/A | Successful
2018-01-21 | 1:40 | O#426551-1 | HLC | 23 | HLC-23 CB | 1119 | 42 | HLC-23 Circuit Breaker locekd out due to fault downstream. YFA then issue a open command to recloser 2910 to Isoalte the fault. YFA then stopped automation because a modeling error showed that the area behind 2910 was energized still. This occurred becasue of source/load voltages were flipped on recloser 2162. System Ops closed in 2162 remotely after 18 minutes to restore customers up to recloser 2910. | N/A | 0 | 0 | Yes | 697 | 12546 | Have system protection reissue a DNP map with correct source/load side voltages. This was identified during the point to point of the device, but never corrected. The end to end test doesn't test voltages, due to the resources required to do such tests. | 2018-01-29 | Unsuccessful
2018-01-27 | 10:01 | O#428015-1 | GRI | 13 | T-Line | 1479 | 7824:00 | At 10:01 the transmission line feeding the GRI and ELD locked out, ELD was restored at 10:06. YFA started processing a voltage management event for GRI at 10:07, it opened O-1116 and issued a comamnd to closed O-287. This command failed due to a ICCP point name not being correct. Therefore YFA automation stopped. | 0:00 | 0 | 0 | Yes | 1063 | 346538 | Started Process to get ICCP error corrected, will be corrected by ECS Group by the 2/7 Release Date | 2018-02-07 | Unsuccessful
2018-01-27 | 15:27 |  | GRI | 13 |  | 1063 | 395 | At 15:27 GRI-13 was closed, and YFA detected it did not have voltages on O-1116, therefore processed another voltage management event. It opened O-1116 and tried to issue a close on O-287. The command failed due to a ICCP point name not being correct. Therefore automation stopped. | 0 | 0 | 0 | Yes | 1063 | 419885 | Started Process to get ICCP error corrected, will be corrected by ECS Group by the 2/7 Release Date | 2018-02-07 | Unsuccessful
2018-01-27 | 13:11 | 428539-1 | HLC | 23 | HLC-23 CB | 1119 | 1752:00 | HLC-23 CB locked out due to a fault downstream of it, YFA then issued a command to open 2910 to isolate the faulted area. Due to an YFA Modeling error, the source and load side voltages on the normal open 2162 prevented YFA from automatically restoring. At 13:16 System Operations sent a SCADA close to 2913, restoring 697 customers. | 0:00 | 0 | 0 | Yes | 697 | 50881 | The team was aware of the issue on 2162 voltages, from the 1/21/18 operation of this scheme. This issue was followed up on and fixed on 1/29/18. | 2018-01-29 | Unsuccessful
2018-01-27 | 14:24 | 428539-2 | HLC | 23 | N/A | 278 | 141 | Most likely during the fault at 13:11, an A phase jumper was damaged/open. Therefore when the system was restored to normal 14:24, most of the feeder only had 2 of 3 phases. YFA detected this event, but had conflicting information due to the miss modeled voltages on 2162. Then at 14:57 a communication failure removed the conflicting information that 2162 was providing the model, which allowed YFA to declare a loss of voltage event at 14:58 at 2910. Due to a communication error at 2910, it moved to the next upstream device and issued an open for 1106, to isolate voltage issue. Since there was a communication problem on the feeder YFA did not restore, as designed. | 0 | 0 | 0 | Yes | 277 | 39057 | The team was aware of the issue on 2162 voltages, from the 1/21/18 operation of this scheme. This issue was followed up on and fixed on 1/29/18. Communication errors are being tracked, and will need further discussions on the drop outs. This one had 3 devices drop out at once. | Recloser 1/29/2018 Communication TBD | Unsuccessful
2018-01-28 | 19:05 |  | HWD | 25 | X8617 | 439 |  | X8617 Locked out due to a fault downstream, since this device protects the area between the Normal Open and itself. There is no restoration path for Automation to restore. | N/A | 0 | 0 | Yes | N/A | N/A | None |  | Successful
2018-02-17 | 13:48 | O#432671-1 | HLC | 23 | T-Line | 1116 | 13 | At 13:48:29 the Hillcrest substation lost it's transmission source. YFA declared a loss of voltage event and issued a command to open Recloser 2910 at 13:49:02. Since Swantown had already lost transmission source as well, YFA sent a close command to recloser 2162 at 13:49:54, restoring 697 customers from CPV-13. | 1 minute 26 seconds | 694 | 9022 | Yes | N/A | N/A | Discuss Implentation of Restoring up to SCADA feeder breakers via Eaton recommended fix (YFA Work) | On Going - Estimated Completion Date June 2018 | Partial
2018-02-17 | 11:22 | O#431996-1 | HOB | 15 | X286 | 1093 | 344 | At 11:22:08 X286 locked out due to a fault downstream of it. At 11:24 AM YFA issued open commands to X856 and X11473 to isolate the faulted area. YFA then stopped automation, due to a point missing in the ICCP model for the Cumberland Transformer, since YFA couldn't determine loading there, YFA didn't restore. | N/A | 0 | 0 | Yes | 764 | 262816 | Transformer Points added to ICCP Model - 3/2/18 Better point to point process for Substation Points/YFA Points - Josh/Joe (3/31/18) - Subsytem Health Activity Report Checks - Josh (3/9/18) | Heath Reports Checks Completed, XTR Points Completed (3/2) New P2P Process Starated | Unsuccessful
2018-02-17 | 13:10 | O#431996-1 | HOB | 15 | Circuit Breaker | 284 | 114 | At 13:10 HOB-15 CB locked out due to a fault downstream of it. Since the scheme was already in a abnormal state, YFA didn't issue any new commands as there were no restoration paths through a non faulted area. Although it would of failed due to the same transformer error at Cumberland. | N/A | N/A | 0 | Yes | N/A | N/A | Transformer Points added to ICCP Model - 3/2/18 Better point to point process for Substation Points/YFA Points - Josh/Joe (3/31/18) - Subsytem Health Activity Report Checks - Josh (3/9/18) | Heath Reports Checks Completed, XTR Points Completed (3/2) New P2P Process Starated | Successful
2018-02-17 | 10:54 | 431902-1 | SHD | 18 | X1902 | 1118 | 75 | At 10:53:50 recloser X1902 locked out due to fault downstream, YFA then issued a command to isolate the faulted area by opening up recloser X2123. YFA then issued command to NO X942 to restore up to X2123 from BDI-13. | 1 minute 50 seconds | 707 | 53025 |  | N/A | N/A | Ensure communication calculation in ICCP has arguments, this will prevent the health issue that stops restoration from SOO-25. Submitted to ECS team, will be included in release targeted for:2/28/18 | Health Issues are Cleared, Communication Calculaitons On Going Fixes and Discussion | Successful
2018-02-17 | 12:12 | 431902-1 | BDI | 13 | X77668 | 1048 | 98 | At 12:11:53 a second fault happened after the first restoration that resulted in a lock out at recloser X77668. YFA then issued a command to open recloser X942 that was closed due to the first restoration event. Due to a error in the ICCP DA Communication calculation, YFA was unable to close X958 to restore the customers that were out. | N/A | 0 | 0 |  | 707 | 69286 |  |  | Unsuccessful
2018-02-17 | 13:24 | 431902-1 | SHD | 18 | X1902 | 707 | 4 | X1902 declared a lost of voltage event and YFA issued a open command, to X1902. Then YFA determiend X1902 had correct voltages and closed it back in. Eaton is investigating as indication is the voltage never dropped below 66% for devices. Nor does YFA logs indicate it did. | [6 empty] | Eaton investigation results, Joel indicated operations hadn't done anything to cause a loss of voltage. Also YFA wasn't logging values, we enabled logging on 2/28/18. | Eaton Investigation - Unclear - PI Showed Voltage Dropped - Logging Enabled 2/28/18 in YFA | Unsuccessful
2018-04-28 | 1:20 |  | CUM | 13 | CUM-13 CB | 489 | 86 | At 1:19AM on 4/28 CUM-13 CB locked out due to a fault downstream, YFA didn't receive fault indication. Therefore automation didn't occur because it perceived this an manual open as designed. Root cause of YFA not receiving fault indication, was the backup relay had incorrect settings and it operated first. System protection will be issuing new settings, so this does not occur again. | N/A | N/A | 0 | N/A | 281 | 24166 | System Protection Issuing New Settings for Backup Relay and recomending installation of Relay to Relay communications. System Protection also did a review of past DA projects and didn't find any other instance of this issue. | 2018-05-01 | Unsuccessful
2018-06-18 | 10:47 |  | MVW | 13 | High Side Switch/MVW-13 CB | 2913 | 96 | At 10:47 MVW Substation locked out, de-energizing MVW-13. At 10:48 Automation declared a loss of voltage on recloser X2576, it then issued a open on recloser X2576. Automation then issued a close command for X10186 at 10:48:54 restoring up to the open recloser X2576. | 1 minute 58 seconds | 1679 | 161184 | Yes | 655 | 62880 | Automation did not restore up to the breaker due to known issue with breaker not reporting loss of voltage. A fix is identified, and will be tested during the End to End Test for BKB-13. The project was delayed due to material issuse and is expected to be tested by End of August/Early September | Looking into Training Issues with Wiremen Sub Ops | Partial
2018-07-14 | 17:53 | O-4656886 | CTR | 22 | CTR-22 CB | 1585 | 138 | At 17:53:09 CTR-22 CB indicated it locked out in EMS, and at 17:53:12 X700 EMS received indication that X700 also indicated a lockout. Due to both devices targeting and locking out Automation interpreted it as a mis-coordinated fault, therefore it placed the fault location downstream of X700. Since it assumed the fault was downstream of X700, it closed in CTR-22 CB at 17:54:53 this created a new fault event due to a failed arrestor and cutout and locked CTR-22 CB out again. Automation reprocessed this new fault event and ended up issuing a open to relocser X735 to isolate the faulted area and close in X2115 at 17:55:34 to restore customers that were downstream of X735. | 2 mins 55 secs | 1510 | 208380 | Yes | None | N/A | X695 Recloser Headunit is being replaced, due ot the flash over on the B Phase contacts. (System Protection request) | Completed | Successful
2018-09-17 | 13:23 | 466337-1 | CAM | 25 | CAM-25 CB | 1479 | 82 | At 13:22:35 CAM-25 CB Tripped due to protective settings and X77046 tripped due to protective settings. Then at 13:22:59 EMS received a close trip for CAM-26 CB resulting in a lockout. Automation proceeded to treat this fault as a mis-coordinated fault since it received a fault trip downstream from the locked out device. At this point Automation proceeded to isolate the fault area by issuing a open to X77406 at 13:24 and an open to X11413 at 13:25. After isolation Automation, proceeded with restoration by closing CAM-26 CB at 13:25 and closing recloser X695 at 13:25 restoring a total of 875 customers. | 3 min 7 seconds | 875 | 71750 | No | N/A | N/A | OMS to follow up on Issue with X11413 Status coming into OMS correctly - Completed System Protection to check on coordination with CAM-25 CB and X77046 | Completed | Successful
2018-10-09 | 19:08 | O-469292 | SHD | 18 | X1902 | 1029 | 74 | At 19:08 SHD-18 circuit breaker tripped, as well as recloser X1902 due to a fault downstream. SHD-18 CB reclosed and locked out and X1902 reported lockout, since it had no source voltage to reclose. Automation then issued an open to X2123 at 19:09 to isolate the faulted area. Automation then determined that BDI was the highest capacity route to restore from, so automation issued a closed to X942 at 19:11 to restore customers up to the open recloser X2123. | 3 min 24 secs | 614 | 45436 | Yes | N/A | N/A | System Protection to Review SOE, due to possible miscordinated fault - Completed 10/10 SCADA - YFA Configuraiton Change for Non SCADA Breakers - Disabling Voltage Management at Device Level to prevent future issues with sending closes to Non SCADA Devices (10/24) | Completed | Successful
2018-10-27 | 21:01 |  | HOB | 15 | X286 | 1105 | 75 | At 21:00:32 recloser X286 locked out due to protective settings. Recloser X856 had also targeted for the fault, but did not operate since it was in its correct settings group 2, therefore DA logic placed the permanent between reclosers X856 and X458. DA issued open commands to recloser X856 and X458 to isolate the faulted area. Then DA procceded with restoration by closing in recloser X286 restoring those customers from HOB-15 and closing in X6320 restoring up to open recloser X458 from CUM-13. | 3 mins 21 secs | 596 | 44700 | No | N/A | N/A | OMS Team to investigate why signals did not come into OMS correctly on return to normal |  | Successful
2018-11-02 | 8:09 | O-473158 | HLC | 23 | HLC-23 CB | 1119 | 188 | At 08:08 HLC-23 Circuit Breaker locked out, due to its protective settings for a fault downstream. Automation then issued an open to recloser 2910 at 08:10:27, to isolate the faulted area. Restoration was achieved by automation issuing a close for recloser 2162 at 08:10:54, restoring customers up to open recloser 2910 from Coupeville 13. | 2mins 11secs | 699 | 131412 | Yes | N/A | N/A | HLC-23 CB Lockout Timer (Mechanical Timer at CB), is longer than the stability timer in Automation. This isn't a Automation stopping event, but discussions with System Protection should occur to see if we can adjust the timers, to provide feedback faster and which will allow for faster restoration times. This is a issue with all mechanical lockout timers. |  | Successful
2018-11-04 | 1:56 | O-473884 | SHD | 18 | X1902 | 1029 | 86 | At 1:56:26 Recloser X1902 locked out, due to protective settings for a fault downstream. Automation then issued an open to recloser X2123 at 01:57:51, to isolate the faulted area. Restoration was achieved by automation issuing a close for recloser X942 at 01:58:13, restoring customers up to open recloser X2123 from Black Diamond 13. | 1 min 47 secs | 614 | 52804 | Yes | N/A | N/A | None | N/A | Successful
2018-11-05 | 1:34 |  | ING | 13 | ING-13 CB | 1861 | 149 | (System Protection) The initial momentary fault was downstream of ING-13 X5408 at approximately 2000A from A-B phase. ING-13 X420 and X5408 and ING-13 CB all saw this fault. 3 seconds after the initial momentary fault cleared ING-13 saw a new A-B fault at approx. 1000A from EMS. This is most likely line slap since the phases and fault type match exactly. The ING-13 CB never recovered from the fault and eventually went into L/O after the reclose. (DA) Automation treated this fault as a Mis-Coordinated Fault and issued a open to X5408. X1424 during restoration relay rebooted, causing a communication failure along with incohrent data, stoping any restoration. | N/A | 0 | 0 | N/A | 870 | 129630 | System Protection following up on X1424 Root Cause of Reboot |  | Unsuccessful
2018-12-14 | 18:21 | 481840 | SHD | 18 | X1902 | 1031 | 1200 | On 12/14/2018 at 18:21 X1902 locked out, due to its protective settings for a fault downstream. At 18:23 automation issued an open to recloser X2123 to isolate the faulted area. Automation then determined the highest capacity route to restore was by closing X942 at 18:24, restoring the customers downstream of X2123 from BDI-13. | 2 minutes 20 seconds | 614 | 736800 | Yes | N/A | N/A | None |  | Successful
2018-12-20 | 11:49 |  | SHD | 18 | X2123 | 614 | 1221 | At 11:49 Recloser X2123 locked out due to protective settings for a fault downstream, recloser X1724 sent in fault targets, but didn't open by design as it was in its settings group 2 (non-protective) settings. Automation sent an open to recloser X1724 at 11:51 to isolate the faulted area. Then automation issued a close to X2123 at 11:51:28 restoring the customers up to open recloser X1724 from SHD-18. | 2 minutes 2 seconds | 607 | 741147 |  | N/A | N/A | None | N/A | Successful
2018-12-20 | 13:56 |  | HOB | 15 | Transmission Line | 1369 | 20 | *Tracking Purposes Only* At 13:56 the transmission line feeding the HOB-15 feeder locked out, leaving the HOB-15 feeder de-energized. Loss of Voltage was disabled for this scheme at the time, therefore automation didn't take any action. If loss of voltage had been enabled Distribution Atuomation would have opened X286 and restored by closing in X11468. | N/A | N/A | N/A | N/A | 1083 | 21660 | None | N/A | Tracking

## DA 2019 Operations
Date of Event | Time | Event # | Substation | Feeder | Device Locked Out | # of Customers on Device Locked Out | Outage Length (Minutes) | Sequence of Operation | Automatic Restoration Time | Customers Automatically Restored | Customer Minutes Saved | OMS Single Order (Yes/No) | Missed Opportunity (# of Customers Could of Restored) | Missed Opportunity (# of Customers Minutes PSE could of Saved) | Follow Up Actions | Follow Up Complete | Operation Classification | Missed Opportunity Customer Interruptions due to Work Practices | Missed Opportunity Customer Minutes due to Work Practices
2019-01-06 | 1:16 |  | SOO | 25 | SOO-25 CB | 1732 | 18 | At 1:16 SOO-25 CB locked out for a fault downstream, due to protective settings at the circuit breaker. Automation issued an open for recloser X1362 at 1:18, to isolate the faulted area. Restoration was achieved up to open recloser X1367 from SHD-18, when automation closed recloser X958 at 1:18. A subsequent fault occurred downstream of recloser X2123 on SHD-18 at 1:36, which de-energized the customers that were just restored. Due to another prior fault on BDI-13, no other restoration paths were available, leaving the customers de-energized. *Recommend looking at the Diagram* | 2 minutes 35 secs | 1135 | 20430 |  | N/A | N/A | *Note OMS SCADA Link was down Recloser Lockout and Position Change timing coming into automation, is causing the manual operation to trigger which shuts off automation on the assoicated feeder. This could stop a future automation event, but didn't impact this one, investigation underway. | 2019-01-23 | Successful
2019-01-06 |  |  | ING | 13 | X420 | 1180 | 628 | At 4:01 X420 Recloser locked out due to protective settings for a fault downstream. Automation was disabled at System level, therefore it took no further action. If it was enabled it could have issued opens for Recloser X1424 / X5408 to isolate the faulted area. Than it would have close recloser X636 and X1829 restoring customers downstream of X1424 and X5408. *Tracking Purposes Only* | N/A | N/A | N/A | N/A | 0 | 0 |  |  | Tracking | 786 | 493608
2019-01-06 | 4:16 |  | WOO | 23 | WOO-23 CB | 996 | 501 | 4:16 WOO-23 CB Locked out due to a fault downstream. Automation was disabled on the system level. If it had been enabled Automation would have issued an open to P-422 to isolate the faulted area and restored the customers downstream of P-422 by closing in P-662. *Tracking Purposes Only* | N/A | N/A | N/A | N/A | 0 | 0 |  |  | Tracking | 713 | 357213
2019-01-06 | 1:55 |  | HOB | 15 | X286 / HOB-15 CB | 1369 |  | 1:55 Recloser X286 Locked Out due to protective settings for a fault downstream, recloser X856 sent in fault target information but didn’t open as designed, due to it being in switch mode (Settings Group 2). CB HOB-15 also locked out at 1:56 for a separate fault downstream of it as well. Automation then issued opens at 1:58 to recloser X11473 and X458 to isolate the faulted areas. Restoration occurred when automation issued close(s) to reclosers X11468 and X6320. At 2:02 recloser X11468 locked out, due to its protective settings for a third fault downstream. At 4:46 System Operations issued a SCADA Open to CUM-13 CB de-energizing the rest of the scheme. | 4 min 28 seconds | 266 | 9078 | N/A | N/A | N/A | *OMS SCADA Link was down during this event |  | Successful | 0 | 0
2019-02-04 | 6:56 |  | HOB | 15 | X286 | 1111 | 146 | 06:56 Recloser X286 locked out due its protective settings for a fault downstream, recloser X856 also sent in fault targets as designed (Settings Group 2). Due to how the lockout and position change signals came into the automation software, the software treated these changes as a "manual operation" which automation is set to disable itself. This is a safety setting to prevent automation from restoring in case of an emergency de-energization. Therefore no restoration occurred. Automation should have isolated the faulted area by opening reclosers X856 and X458. Then it should have restored by closing reclosers X286 and X6320. *See follow-up action items for more information* | N/A | N/A | N/A | N/A | 597 | 87162 | The position changes and lock out signal issue was observed during events that occurred on 1/6, although it did not stop any events that day. After the initial investigation the DA Team changed communication settings between EMS and the automation software, we ran multiple scheme tests after these changes and did not observe the issue again, so it was assumed to be fixed. Therefore the DA Team will follow up again on how position and lockout signals come into the automation software. In the interim the DA Team has disabled all lockout points in the automation software to prevent the inadvertent "manual operations" from occurring. This will delay future DA restoration by up to 40 seconds, until a viable solution has been created to ensure lockouts do not come in before position changes. It is also important to note the automation software will still automatically disable for manual operations, with the lockout points disabled. The lockout point is only used to speed up restoration time. |  | Unsuccessful
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0