## Slide 1: San Juan Islands Transport Systems Measurement, Maintenance and Inspection
March 2016
Docket UT-132234
San Juan Submarine Fiber Cable Inspection and Maintenance
Attachment 1

## Slide 2: Agreement Terms
By March 31 of each year, CenturyLink will report to the Commission all inspections and maintenance performed during the preceding year for both the underwater fiber cable and microwave systems.
In each report for each underwater fiber facility, CenturyLink will: identify the baseline measurements of decibel and signal strength; identify any loss of decibel or signal strength; and describe ongoing monitoring for each underwater facility.
In each report for each microwave system, CenturyLink will state whether it followed its current Antenna and Tower Routine Inspection, which is attached as Appendix A to this Settlement Agreement. … CenturyLink will report to the Commission the ability of both San Juan microwave systems to provide redundant capacity between the various island customers to the host switch located in Friday Harbor and the redundant capacity between Friday Harbor and Bellingham, Washington. CenturyLink will also affirm in this report that the two microwave systems have sufficient capacity to maintain CenturyLink’s intrastate voice and critical services traffic on a diverse route between the islands and the mainland at normal call volumes.

## Slide 3: Submarine Fiber Cable Lopez, WA to La Conner, WA
November 10, 2015

## Slide 4: Lopez, WA to La Conner, WA.
This report regards loss measurement between the Coriant 7100 Nano equipment located at Lopez Island and at LaConner Washington
  Loss was calculated as the difference between the transmitted (Tx) level and the received (Rx) level.
  These levels were seen on the Optical Service Channels (OSCs) of the 7100N Optical Add/Drop Multiplexer (OADM) High Speed cards.

## Slide 5: Lopez, WA to La Conner, WA.
Tx = -0.2db
Rx = -12.9db
LOPZWAXXO02010025
Degree A
LACNWAAXKRC01CUST06B
Degree A
Tx = +2.0db
Rx = -15.7db
Overall fiber loss: -15.5db
Overall fiber loss: -14.9db

## Slide 6: San Juan Island fiber results.
Tx = +2.8db
Rx = -13.0db
LOPZWAXXO02010025
Degree B
LACNWAAXKRC01CUST06A
Degree A
Tx = +2.8db
Rx = -12.6db
Overall fiber loss: -15.4db
Overall fiber loss: -15.8db

## Slide 7: Lopez, WA to La Conner, WA
Coriant 7100 Optical Specifications
Lopez 7100N is equipped with OADM-LR High-speed cards
  The OADM88-LR supports span loss of 14 dB to 26 dB
La Conner 7100N is equipped with Long Range Amplifier Modules (LRAM-88) in both Optical Line Amplifier shelves
  The LRAM-88 can support span loss of 14 dB to 26 dB

## Slide 8: Submarine Fiber Cable Lopez Island to Friday Harbor
November 10, 2015

## Slide 9: Lopez Island to Friday Harbor.
This report regards loss measurement between the Fujitsu FW7420 equipment located at Lopez Island and at Friday Harbor.
  Fiber loss was calculated as the difference between the transmitted (Tx) level and the received (Rx) level.
  These levels were seen on the working channels of the FW7420 High Speed cards.

## Slide 10: Lopez Island to Friday Harbor.
Tx = +2.0db
Rx = -16.6db
FRHRWAXAO02
Mod 1-15
CH-1-15-NW
LOPZWAXXO01
Mod 1-7
CH-1-7-NW F2488
Tx = +2.4db
Rx = -15.7db
Overall fiber loss: -17.5db
Overall fiber loss: -19.0db

## Slide 11
Field operations technicians conducted site surveys where submarine cable first appears on land and is accessible. The surveys involved visual examination.
  fiber optic cable
  vault and pedestal
  surrounding environment
No defects, faults or significant changes were observed.
Submarine Fiber Cable Landings