## Market Potential
|  |  |  | Number of Sites | [11 empty] | Total Capacity MWAC
|  | Customer | Market Potential Basis | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | Notes
1 | 3rd Party Customer-Sited Distributed Battery PPA | C-B | Aggregator Economics | 33 | 33 | 34 | 35 | 36 | 37 | 37 | 38 | 38 | 39 | 39 |  | 6.6 | 6.6 | 6.8 | 7 | 7.2 | 7.4 | 7.4 | 7.6 | 7.6 | 7.8 | 7.8
2 | 3rd Party Utility-scale Distributed Battery PPA | U-B | Aggregator Economics | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5
3 | C&I Battery Install Incentive | C-B | Customer Economics | 1 | 2 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 17 |  | 0.2 | 0.4 | 0.4 | 0.6 | 0.8 | 1.2 | 1.6 | 2 | 2.4 | 2.8 | 3.4
4 | C&I Space Leasing for Batteries | C-B | Utility Market Access/Strategy | 2 | 9 | 18 | 36 | 36 | 36 | 72 | 72 | 144 | 180 | 180 |  | 0.4 | 1.8 | 3.6 | 7.2 | 7.2 | 7.2 | 14.4 | 14.4 | 28.8 | 36 | 36 | BV to provide inputs - Connor to refine
5 | Multi-Family Unit Battery Program | M-B | Utility Market Access/Strategy | 0 | 1 | 2 | 3 | 3 | 3 | 7 | 7 | 13 | 17 | 17 |  | 0 | 0.25 | 0.5 | 0.75 | 0.75 | 0.75 | 1.75 | 1.75 | 3.25 | 4.25 | 4.25
6 | PSE Mobile Batteries | U-B | Utility Market Access/Strategy | Number of Sites 2020: Unlimited | [12 empty] | Unconstrained
7 | PSE Substation Batteries | U-B | Utility Market Access/Strategy | Number of Sites 2020: Unlimited | [12 empty] | Unconstrained | Number of substations? Connor to follow up.
8 | PSE Utility-Scale Distributed Battery Stations | U-B | Utility Market Access/Strategy | Number of Sites 2020: Unlimited | [12 empty] | Unconstrained
9 | Residential Battery Install Incentive | R-B | Customer Economics | 34 | 43 | 53 | 63 | 74 | 86 | 99 | 112 | 126 | 139 | 153 |  | 0.17 | 0.215 | 0.265 | 0.315 | 0.37 | 0.43 | 0.495 | 0.56 | 0.63 | 0.695 | 0.765
10 | Residential PSE Battery Leasing | R-B | Customer Economics | 214 | 219 | 224 | 229 | 233 | 237 | 240 | 243 | 246 | 249 | 252 |  | 1.07 | 1.095 | 1.12 | 1.145 | 1.165 | 1.185 | 1.2 | 1.215 | 1.23 | 1.245 | 1.26
11 | Residential PSE Battery Leasing - Low Income | RLI-B | Customer Economics | 21.9511 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 0.10976 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
12 | Net Metering (Existing) | R-S | Customer Economics | 1710 | 1774 | 1839 | 1839 | 1839 | 1839 | 1871 | 1871 | 1903 | 1920 | 1952 |  | 10.26 | 10.644 | 11.034 | 11.034 | 11.034 | 11.034 | 11.226 | 11.226 | 11.418 | 11.52 | 11.712
13 | Net Metering (Successor) | R-S | Customer Economics | 1161 | 1242 | 1355 | 1355 | 1355 | 1355 | 1371 | 1436 | 1452 | 1468 | 1484 |  | 6.966 | 7.452 | 8.13 | 8.13 | 8.13 | 8.13 | 8.226 | 8.616 | 8.712 | 8.808 | 8.904
14 | PSE Community Solar | R-S | Customer Economics | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 |  | 15.2 | 19 | 19 | 19 | 19 | 19 | 19 | 22.8 | 22.8 | 22.8 | 22.8
15 | PSE Community Solar - Low Income | RLI-S | Customer Economics | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 0 | 0 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
16 | 3rd Party Distributed Solar PPA (or Solar Lease) | C-S | Customer Economics | 0 | 0 | 7 | 7 | 7 | 7 | 12 | 17 | 22 | 28 | 33 |  | 0 | 0 | 2.8 | 2.8 | 2.8 | 2.8 | 4.8 | 6.8 | 8.8 | 11.2 | 13.2
17 | C&I Roof-top Solar Incentive | C-S | Customer Economics | 0 | 3 | 17 | 17 | 17 | 17 | 23 | 28 | 33 | 38 | 43 |  | 0 | 0.921 | 5.219 | 5.219 | 5.219 | 5.219 | 7.061 | 8.596 | 10.131 | 11.666 | 13.201
18 | C&I Roof-top Solar Leasing | C-S | Utility Market Access/Strategy | 11 | 11 | 21 | 32 | 43 | 54 | 54 | 54 | 54 | 54 | 54 |  | 4.4 | 4.4 | 8.4 | 12.8 | 17.2 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6
19 | Multi-Family Solar Partnership | M-S | Utility Market Access/Strategy | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 3 | 4 |  | 0 | 0 | 0.083 | 0.083 | 0.083 | 0.083 | 0.083 | 0.166 | 0.249 | 0.249 | 0.332 | BV to provide inputs - Connor to refine
20 | Multi-Family Roof-top Solar Incentive | M-S | Customer Economics | 2 | 3 | 5 | 5 | 5 | 5 | 6 | 6 | 7 | 8 | 8 |  | 0.166 | 0.249 | 0.415 | 0.415 | 0.415 | 0.415 | 0.498 | 0.498 | 0.581 | 0.664 | 0.664
21 | PSE Customer-Sited Solar+Storage Offering | R-S | Customer Economics | 316 | 392 | 478 | 576 | 686 | 807 | 940 | 1084 | 1239 | 1403 | 1576 | Solar | 1.896 | 2.352 | 2.868 | 3.456 | 4.116 | 4.842 | 5.64 | 6.504 | 7.434 | 8.418 | 9.456
|  | R-B | [12 empty] | Storage | 1.58 | 1.96 | 2.39 | 2.88 | 3.43 | 4.035 | 4.7 | 5.42 | 6.195 | 7.015 | 7.88
22 | Residential Roof-top Solar Leasing | R-S | Utility Market Access/Strategy | 46 | 75 | 108 | 163 | 230 | 298 | 411 | 546 | 697 | 881 | 1113 |  | 0.276 | 0.45 | 0.648 | 0.978 | 1.38 | 1.788 | 2.466 | 3.276 | 4.182 | 5.286 | 6.678 | BV to provide inputs - Connor to refine
23 | Residential Roof-top Solar Leasing - Low Income | RLI-S | Utility Market Access/Strategy | 7 | 11 | 15 | 23 | 33 | 42 | 58 | 77 | 99 | 125 | 158 |  | 0.042 | 0.066 | 0.09 | 0.138 | 0.198 | 0.252 | 0.348 | 0.462 | 0.594 | 0.75 | 0.948 | BV to provide inputs - Connor to refine
24 | C&I BYO Battery | C-B | Customer Economics | 1 | 1 | 1 | 2 | 2 | 3 | 4 | 5 | 6 | 7 | 9 |  | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.6 | 0.8 | 1 | 1.2 | 1.4 | 1.8

## Estimation Basis
Estimation Basis
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Cost Estimate | $ Per System (2020$) | General (Storage) | General (Solar) | 3rd Party Customer-Sited Distributed Battery PPA | 3rd Party Utility-scale Distributed Battery PPA | C&I Battery Install Incentive | C&I Space Leasing for Batteries | Multi-Family Unit Battery Program | PSE Mobile Batteries | PSE Substation Batteries | PSE Utility-Scale Distributed Battery Stations | Residential Battery Install Incentive | Residential PSE Battery Leasing | Residential PSE Battery Leasing - Low Income | Net Metering (Existing) | Net Metering (Successor) | PSE Community Solar | PSE Community Solar - Low Income | 3rd Party Distributed Solar PPA (or Solar Lease) | C&I Roof-top Solar Incentive | C&I Roof-top Solar Leasing | Multi-Family Solar Partnership | Multi-Family Roof-top Solar Incentive | PSE Customer-Sited Solar+Storage Offering | Residential Roof-top Solar Leasing | Residential Roof-top Solar Leasing - Low Income | C&I BYO Battery
Utility Cost |  | Installed Cost: - Aggregated data based on market data , BV installation costs, and BESS proposal bids - BESS equipment costs based on confidential bids received in the last year. - Labor costs were reflective of WA state - Tax included at 10.5% for WA state - Dev, Financing and Profit based on benchmark data | Installed Cost: - Internal database of historical prices - Equipment costs are based on national averages - Labor are specific to WA state, based on historic data - Taxes included at 10.5% for WA state - Dev, Financing and Profit based on benchmark data
Installed Cost |  |  |  | 4: Utility Owned; 5: Utility Owned; 6: Utility Owned; 7: Utility Owned; 8: Utility Owned; 10: Utility Owned; 11: Utility Owned; 14: Utility Owned; 15: Utility Owned; 18: Utility Owned; 22: Utility Owned; 23: Utility Owned
Equipment |  |  |  | 4: Estimated C&I BESS System; 5: Estimated at 50 in-unit Powerwall systems; 6: Vendor quote; 7: Estimated Substation BESS System; 8: Estimated Utility Scale BESS System; 10: Estimated Residential BESS System; 11: Estimated Residential BESS System; 14: Estimated Groundmount, utility scale solar system; 15: Estimated Groundmount, utility scale solar system; 18: Estimated commercial rooftop PV system; 22: Estimated residential rooftop PV system; 23: Estimated residential rooftop PV system
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year) |  |  |  | 4: Utility Operated; 5: Third-Party Operated; 6: Utility Operated; 7: Utility Operated; 8: Utility Operated; 10: Utility Operated; 11: Utility Operated; 14: Utility Operated; 15: Utility Operated; 18: Utility Operated; 22: Utility Operated; 23: Utility Operated
Equipment O&M |  |  |  | 4: BV benchmarks and market reports (3); 5: BV benchmarks and market reports (3); 6: BV benchmarks and market reports (3); 7: BV benchmarks and market reports (3); 8: BV benchmarks and market reports (3); 10: BV benchmarks and market reports (3); 11: BV benchmarks and market reports (3); 14: BV benchmarks and market data (6); 15: BV benchmarks and market data (6); 18: BV benchmarks and market data (6); 22: BV benchmarks and market data (6); 23: BV benchmarks and market data (6)
Insurance |  |  |  | 4: Benchmarked at 0.3% total installed cost; 5: Benchmarked at 0.3% total installed cost; 6: Benchmarked at 0.4% total installed cost; 7: Benchmarked at 0.3% total installed cost; 8: Benchmarked at 0.3% total installed cost; 10: Benchmarked at 0.3% total installed cost; 11: Benchmarked at 0.3% total installed cost; 14: Benchmarked at 0.3% total installed cost; 15: Benchmarked at 0.3% total installed cost; 18: Benchmarked at 0.3% total installed cost; 22: Incremental, based on aggregator data; 23: Incremental, based on aggregator data
Technology Fees |  |  |  | 4: Energy management cost benchmarks and market reports (4); 5: Energy management cost benchmarks and market reports (4); 6: Energy management cost benchmarks and market reports (4); 7: Energy management cost benchmarks and market reports (4); 8: Energy management cost benchmarks and market reports (4); 10: Energy management cost benchmarks and market reports (4); 11: Energy management cost benchmarks and market reports (4); 12: Provided by PSE; 13: Provided by PSE; 14: Energy management cost benchmarks and market reports (4); 15: Energy management cost benchmarks and market reports (4); 18: Energy management cost benchmarks and market reports (4); 22: Energy management cost benchmarks and market reports (4); 23: Energy management cost benchmarks and market reports (4)
Land / Lease Costs |  |  |  | 4: Land needs - estimated 1260 sqft needed at $30/sqft/year; 5: Assumed provided by customer to third party, at 0 cost; 6: Assumed at 0 cost; 7: Assumed at 0 cost; 8: Land needs - estimated 2100 sqft needed at $30/sqft/year; 10: Assumed provided to utility at 0 cost; 11: Assumed provided to utility at 0 cost; 14: Assume annual lease for 20 acres (rural); 15: Assume annual lease for 20 acres (rural); 18: Assumed payment to customer for rooftop space, for 400 sqft; 22: Estimated based on aggregator data; 23: Assumed offered at 133% of market-rate customer offering (22)
Program Costs (per Year)
Marketing |  |  |  | Benchmark costs for DR programs (1) | Benchmark costs for DR programs (1) | Benchmark costs for Incentive programs (C&I) (5) | Estimated based on thirdparty overhead benchmarks (solar) | Benchmark costs for Incentive programs (C&I) (5) |  |  |  | Benchmark costs for Incentive programs (Res) (5) | Estimated based on thirdparty overhead benchmarks (solar) | Estimated based on thirdparty overhead benchmarks (solar) |  |  | Estimated based on thirdparty overhead benchmarks (solar) | Estimated based on thirdparty overhead benchmarks (solar) |  | Benchmark costs for Incentive programs (C&I) (5) | Estimated based on thirdparty overhead benchmarks (solar) | Benchmark costs for consultative programs (MF) (5) | Benchmark costs for incentive programs (MF) (5) | Benchmark costs for Incentive programs (Res) (5) | Estimated based on thirdparty overhead benchmarks (solar) | Estimated based on thirdparty overhead benchmarks (solar) | Benchmark costs for Incentive programs (C&I) (5)
Administration |  |  |  | Benchmark costs for DR programs | Benchmark costs for DR programs | Benchmark costs for Incentive programs (C&I) (5) | Estimated based on thirdparty overhead benchmarks (solar) | Benchmark costs for Incentive programs (C&I) (5) | Estimated at 12% of comparable leased revenue (Delete if N/A) | Estimated PSE asset management as % of installed cost (Delete if N/A) | Estimated PSE asset management as % of installed cost (Delete if N/A) | Benchmark costs for Incentive programs (Res) (5) | Estimated based on thirdparty overhead benchmarks (solar) | Estimated based on thirdparty overhead benchmarks (solar) | Provided by PSE | Provided by PSE | Estimated at 12% anticipated revenue (Delete if N/A) | Estimated at 12% anticipated revenue (Delete if N/A) | Estimated FTE to support billing and admin (Delete if N/A) | Benchmark costs for Incentive programs (C&I) (5) | Estimated at 12% anticipated revenue | Benchmark costs for consultative programs (MF) (5) | Benchmark costs for incentive programs (MF) (5) | Benchmark costs for Incentive programs (Res) (5) | Estimated based on thirdparty overhead benchmarks (solar) | Estimated based on thirdparty overhead benchmarks (solar) | Benchmark costs for Incentive programs (C&I) (5)
Incentives (One Time) |  |  |  | 1: DR value outlined in IRP (2); 2: DR value outlined in IRP (2); 3: Comparable BESS Incentive (CA-SGIP); 5: One time cost for siting allowance, calculated based on additional spacing and enclosure costs; 9: Comparable BESS Incentive (CA-SGIP); 14: No REC pricing was included - $10/MWh guidance was provided by PSE; 15: No REC pricing was included - $10/MWh guidance was provided by PSE; 17: Comparable Solar Incentive (OR-Pacific Power); 19: Estimated based on similar technlogy subscription products; 20: Comparable incentive, note that incentive is reflective of income qualified MF only - none appeared available for market MF (CA); 21: Comparable BESS Incentive (CA-SGIP) and Solar Incentive (OR-Pacific Power); 24: Comparable BESS Incentive (CA - PGE CBP)
PPA / Recurring Payment |  |  |  | 1: Calculated to provide aggregator 9% IRR; 2: N/A; 3: N/A; 5: N/A; 9: N/A; 14: N/A; 15: N/A; 16: Assumed at $80/MWh based on comparables in PNW; 24: N/A
Non-Utility Costs
Installed Cost |  |  |  | 1: Third-party Owned; 2: Third-party Owned; 3: Customer Owned; 9: Customer Owned; 12: Customer Owned; 13: Customer Owned; 16: Third Party Owned; 17: Customer Owned; 19: Customer Owned; 20: Customer Owned; 21: Customer Owned; 24: Customer Owned
Equipment |  |  |  | 1: Estimated C&I BESS System; 2: Estimated Utility Scale BESS System; 3: Estimated C&I BESS System; 9: Estimated Residential BESS System; 12: Estimated residential rooftop PV; 13: Estimated residential rooftop PV; 16: Estimated commercial rooftop PV; 17: Estimated commerical rooftop PV; 19: Estimated multfamily rooftop PV; 20: Estimated multfamily rooftop PV; 21: Estimated residential rooftop PV and single Powerwall system; 24: Estimated C&I BESS System
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year) |  |  |  | 1: Third-Party Operated; 2: Third-Party Operated; 3: Customer Supplied O&M; 9: Customer Supplied O&M; 12: Customer Supplied O&M; 13: Customer Supplied O&M; 16: Third Party Operated; 17: Customer Supplied O&M; 19: Customer Supplied O&M; 20: Customer Supplied O&M; 21: Customer Supplied O&M; 24: Customer Owned
Equipment O&M |  |  |  | 1: BV benchmarks and market reports (3); 2: BV benchmarks and market reports (3); 3: BV benchmarks and market reports (3); 9: BV benchmarks and market reports (3); 12: BV benchmarks and market data (6); 13: BV benchmarks and market data (6); 16: BV benchmarks and market data (6); 17: BV benchmarks and market data (6); 19: BV benchmarks and market data (6); 20: BV benchmarks and market data (6); 21: BV benchmarks and market data (6); 24: BV benchmarks and market data (6)
Insurance |  |  |  | 1: Benchmarked at 0.3% total installed cost; 2: Benchmarked at 0.3% total installed cost; 3: Benchmarked at 0.3% total installed cost; 9: Benchmarked at 0.3% total installed cost; 12: Incremental, based on aggregator data; 13: Incremental, based on aggregator data; 16: Benchmarked at 0.3% total installed cost; 17: Benchmarked at 0.3% total installed cost; 19: Benchmarked at 0.3% total installed cost; 20: Benchmarked at 0.3% total installed cost; 21: Benchmarked at 0.3% total installed cost; 24: Benchmarked at 0.3% total installed cost
Technology Fees |  |  |  | 1: Energy management cost benchmarks and market reports (4); 2: Energy management cost benchmarks and market reports (4); 3: Energy management cost benchmarks and market reports (4); 9: Energy management cost benchmarks and market reports (4); 12: Energy management cost benchmarks and market reports (4); 13: Energy management cost benchmarks and market reports (4); 16: Energy management cost benchmarks and market reports (4); 17: Energy management cost benchmarks and market reports (4); 19: Energy management cost benchmarks and market reports (4); 20: Energy management cost benchmarks and market reports (4); 21: Energy management cost benchmarks and market reports (4); 24: Energy management cost benchmarks and market reports (4)
Land / Lease Costs |  |  |  | 1: Land needs - estimated 1110 sqft needed at $30/sqft/year; 2: Land needs - estimated 3735 sqft needed at $30/sqft/year; 3: Assumed customer-owned, 0 cost; 9: Assumed customer-owned, 0 cost; 12: Assumed customer-owned, 0 cost; 13: Assumed customer-owned, 0 cost; 16: Assumed payment to customer for rooftop space, for 400 sqft; 17: Assumed customer-owned, 0 cost; 19: Assumed customer-owned, 0 cost; 20: Assumed customer-owned, 0 cost; 21: Assumed customer-owned, 0 cost; 24: Assumed customer-owned, 0 cost
Developer SG&A |  |  |  | 1: Estimated at 12% anticipated revenue; 2: Estimated at 12% anticipated revenue; 3: N/A; 9: N/A; 16: Estimated based on thirdparty overhead benchmarks (solar); 24: N/A
Subscription Costs |  |  |  | 10: Set to 60/kW per guidance from PSE; 11: Set to 10/kW per guidance from PSE; 14: Customer monthly subscription fee at $20/month/customer paid to PSE; 15: Customer subscription fee waived for low-income customers
Participant
Turnkey design and Implementation ($/kWh)
Maintenance Costs ($/kW/y)
EOL replacement costs (% of initial)
(1) SDGE 2017 Demand Response Program Proposal
(2) Final 2021 Integrated Resource Plan, PSE
(3) Energy Storage Technology and Cost Characterization Report, Department of Energy, 2019
(4) Comparison of Actual Costs to Integrate Commercial Buildings with the Grid, LBNL (2016)
(5) 2020 EE Annual Report Tables Public - SDGE, SCE, PGE
(6) U.S. Solar Photovoltaic System and Energy Storage Cost Benchmark: Q1 2020, NREL (2020)

## Energy Storage IRP
|  | Category | Units | PSE Mobile Batteries | [8 empty] | PSE Mobile Batteries | PSE Substation Batteries | [8 empty] | PSE Substation Batteries | PSE Utility-Scale Distributed Battery Stations | [8 empty] | PSE Utility-Scale Distributed Battery Stations | 3rd Party Utility Scale Distributed Battery PPA | [8 empty] | 3rd Party Utility Scale Distributed Battery PPA | 3rd Party Customer-Sited Distributed Battery PPA | [8 empty] | 3rd Party Customer-Sited Distributed Battery PPA | C&I Battery Install Incentive | [8 empty] | C&I Battery Install Incentive | C&I Space Leasing for Batteries | [8 empty] | C&I Space Leasing for Batteries | Multi-Family Unit Battery Program | [8 empty] | Multi-Family Unit Battery Program | Residential Battery Install Incentive | [8 empty] | Residential Battery Install Incentive | Residential PSE Battery Leasing - Low Income | [8 empty] | Residential PSE Battery Leasing - Low Income | Residential PSE Battery Leasing | [8 empty] | Residential PSE Battery Leasing | C&I BYO Battery | [8 empty] | C&I BYO Battery | PSE Customer-Sited Solar+Storage Offering (Storage) | [8 empty] | PSE Customer-Sited Solar+Storage Offering (Storage)
|  |  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  | Nameplate Capacity | MW | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 |  | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 |  | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital | Fixed | IT/Programmatic | $/year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable | EPC | $/KW | 1469.6902 | 1323.8611 | 1185.5825 | 1097.0487 | 1066.5334 | 1036.4453 | 1006.7845 | 977.551 | 933.1487 |  | 1050.9499 | 946.6701 | 847.7895 | 784.4805 | 762.6595 | 741.144 | 719.9341 | 699.0298 | 667.2785 |  | 1063.2887 | 957.7846 | 857.743 | 793.6908 | 771.6136 | 749.8455 | 728.3866 | 707.2368 | 675.1127 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3758.2919 | 3385.3777 | 3031.7718 | 2805.3731 | 2727.3392 | 2650.398 | 2574.5494 | 2499.7935 | 2386.2481 |  | 2960.1406 | 2666.4224 | 2387.9121 | 2209.5939 | 2148.1321 | 2087.5309 | 2027.7904 | 1968.9105 | 1879.4787 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2960.1406 | 2666.4224 | 2387.9121 | 2209.5939 | 2148.1321 | 2087.5309 | 2027.7904 | 1968.9105 | 1879.4787 |  | 2960.1406 | 2666.4224 | 2387.9121 | 2209.5939 | 2148.1321 | 2087.5309 | 2027.7904 | 1968.9105 | 1879.4787 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Interconnection | $/KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | AFUDC | $/KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 63.7854 | 63.7854 | 63.7854 | 63.7854 | 63.7854 | 63.7854 | 63.7854 | 63.7854 | 63.7854 |  | 74.214 | 74.214 | 74.214 | 74.214 | 74.214 | 74.214 | 74.214 | 74.214 | 74.214 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240.105 | 240.105 | 240.105 | 240.105 | 240.105 | 240.105 | 240.105 | 240.105 | 240.105 |  | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 |  | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 | 189.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Capital Cost | $/MW X1000 | 1469.6902 | 1323.8611 | 1185.5825 | 1097.0487 | 1066.5334 | 1036.4453 | 1006.7845 | 977.551 | 933.1487 | 0 | 1114.7353 | 1010.4555 | 911.5749 | 848.2659 | 826.4449 | 804.9294 | 783.7195 | 762.8151 | 731.0638 | 0 | 1137.5027 | 1031.9986 | 931.957 | 867.9048 | 845.8276 | 824.0595 | 802.6006 | 781.4508 | 749.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3998.3969 | 3625.4827 | 3271.8768 | 3045.4781 | 2967.4442 | 2890.503 | 2814.6544 | 2739.8985 | 2626.3531 | 0 | 3149.3406 | 2855.6224 | 2577.1121 | 2398.7939 | 2337.3321 | 2276.7309 | 2216.9904 | 2158.1105 | 2068.6787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3149.3406 | 2855.6224 | 2577.1121 | 2398.7939 | 2337.3321 | 2276.7309 | 2216.9904 | 2158.1105 | 2068.6787 | 0 | 3149.3406 | 2855.6224 | 2577.1121 | 2398.7939 | 2337.3321 | 2276.7309 | 2216.9904 | 2158.1105 | 2068.6787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | O&M Fixed | $/KW-yr | 46.6336 | 46.6336 | 46.6336 | 46.6336 | 46.6336 | 46.6336 | 46.6336 | 46.6336 | 46.6336 |  | 38.4261 | 38.4261 | 38.4261 | 38.4261 | 38.4261 | 38.4261 | 38.4261 | 38.4261 | 38.4261 |  | 118.0327 | 118.0327 | 118.0327 | 118.0327 | 118.0327 | 118.0327 | 118.0327 | 118.0327 | 118.0327 |  | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 |  | 305.4 | 305.4 | 305.4 | 305.4 | 305.4 | 305.4 | 305.4 | 305.4 | 305.4 |  | 63.36 | 63.36 | 63.36 | 63.36 | 63.36 | 63.36 | 63.36 | 63.36 | 63.36 |  | 293.9814 | 293.9814 | 293.9814 | 293.9814 | 293.9814 | 293.9814 | 293.9814 | 293.9814 | 293.9814 |  | 72.2 | 72.2 | 72.2 | 72.2 | 72.2 | 72.2 | 72.2 | 72.2 | 72.2 |  | 70.2 | 70.2 | 70.2 | 70.2 | 70.2 | 70.2 | 70.2 | 70.2 | 70.2 |  | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 |  | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 | 137.853 |  | 7.4484 | 7.4484 | 7.4484 | 7.4484 | 7.4484 | 7.4484 | 7.4484 | 7.4484 | 7.4484 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | O&M Fixed | $/MW-wk | 896.7992 | 896.7992 | 896.7992 | 896.7992 | 896.7992 | 896.7992 | 896.7992 | 896.7992 | 896.7992 | 0 | 738.9626 | 738.9626 | 738.9626 | 738.9626 | 738.9626 | 738.9626 | 738.9626 | 738.9626 | 738.9626 | 0 | 2269.8596 | 2269.8596 | 2269.8596 | 2269.8596 | 2269.8596 | 2269.8596 | 2269.8596 | 2269.8596 | 2269.8596 | 0 | 969.2308 | 969.2308 | 969.2308 | 969.2308 | 969.2308 | 969.2308 | 969.2308 | 969.2308 | 969.2308 | 0 | 5873.0769 | 5873.0769 | 5873.0769 | 5873.0769 | 5873.0769 | 5873.0769 | 5873.0769 | 5873.0769 | 5873.0769 | 0 | 1218.4615 | 1218.4615 | 1218.4615 | 1218.4615 | 1218.4615 | 1218.4615 | 1218.4615 | 1218.4615 | 1218.4615 | 0 | 5653.4894 | 5653.4894 | 5653.4894 | 5653.4894 | 5653.4894 | 5653.4894 | 5653.4894 | 5653.4894 | 5653.4894 | 0 | 1388.4615 | 1388.4615 | 1388.4615 | 1388.4615 | 1388.4615 | 1388.4615 | 1388.4615 | 1388.4615 | 1388.4615 | 0 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 0 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 0 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 2651.0192 | 0 | 143.2385 | 143.2385 | 143.2385 | 143.2385 | 143.2385 | 143.2385 | 143.2385 | 143.2385 | 143.2385 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | O&M Variable | $/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Degredation | %/year | [10 empty] | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | bar: PSE Mobile Batteries 2022 to PSE Mobile Batteries 2030
|  | Operating Range | % | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | R/T Efficiency | % | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% |  | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% |  | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% |  | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% |  | 88% | 88% | 88% | 88% | 88% | 88% | 88% | 88% | 88% |  | 88% | 88% | 88% | 88% | 88% | 88% | 88% | 88% | 88% |  | 88% | 88% | 88% | 88% | 88% | 88% | 88% | 88% | 88% |  | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% |  | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% |  | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% |  | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% |  | 88% | 88% | 88% | 88% | 88% | 88% | 88% | 88% | 88% |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Discharge at Nominal Power | Hours | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Maximum Storage | MWh | [10 empty] | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 |  | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 |  | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 |  | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: PSE Mobile Batteries 2022 to PSE Mobile Batteries 2030
|  | First Year Available |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022
|  | Economic Life | Years | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Greenfield Dev. & Const. Leadtime | Years | [10 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: PSE Mobile Batteries 2022 to PSE Mobile Batteries 2030
|  | Upfront 1-Time Incentive | $/KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 62.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Customer Payments to PSE | $/MW-wk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 192.3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1153.8462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes
Formula

## Renewables IRP
|  | Category | Units | Net Metering (Existing) | [8 empty] | Net Metering (Existing) | Net Metering (Successor) | [8 empty] | Net Metering (Successor) | PSE Community Solar | [8 empty] | PSE Community Solar | PSE Community Solar - Low Income | [8 empty] | PSE Community Solar - Low Income | PSE Customer-Sited Solar+Storage Offering (Solar) | [8 empty] | PSE Customer-Sited Solar+Storage Offering (Solar) | 3rd Party Distributed Solar PPA (or Solar Lease) | [8 empty] | 3rd Party Distributed Solar PPA (or Solar Lease) | C&I Roof-top Solar Incentive | [8 empty] | C&I Roof-top Solar Incentive | C&I Roof-top Solar Leasing | [8 empty] | C&I Roof-top Solar Leasing | Multi-Family Solar Partnership | [8 empty] | Multi-Family Solar Partnership | Multi-Family Roof-top Solar Incentive | [8 empty] | Multi-Family Roof-top Solar Incentive | Residential Roof-top Solar Leasing | [8 empty] | Residential Roof-top Solar Leasing | Residential Roof-top Solar Leasing - Low Income | [8 empty] | Residential Roof-top Solar Leasing - Low Income
|  |  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  | Nameplate Capacity | MW | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 |  | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 |  | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 |  | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 | 3.8462 |  | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 |  | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 |  | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 |  | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 | 0.30769 |  | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 |  | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 |  | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 |  | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333 | 0.0058333
|  | Capacity Factor | % | 13.7% | 0.13699 | 0.13699 | 0.13699 | 0.13699 | 0.13699 | 0.13699 | 0.13699 | 0.13699 |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% |  | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7% | 13.7%
Capital | Fixed | IT/Programmatic | $/KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable | EPC | $/KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1094.34 | 1094.34 | 1094.34 | 1094.34 | 1076.8105 | 1059.2811 | 1041.7516 | 1024.2221 | 1006.6926 |  | 1094.34 | 1094.34 | 1094.34 | 1094.34 | 1076.8105 | 1059.2811 | 1041.7516 | 1024.2221 | 1006.6926 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1420.848 | 1420.848 | 1420.848 | 1420.848 | 1398.0884 | 1375.3288 | 1352.5693 | 1329.8097 | 1307.0501 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2389.056 | 2389.056 | 2389.056 | 2389.056 | 2350.7874 | 2312.5187 | 2274.2501 | 2235.9815 | 2197.7128 |  | 3209.1703 | 3209.1703 | 3209.1703 | 3209.1703 | 3157.7648 | 3106.3593 | 3054.9539 | 3003.5484 | 2952.1429
|  | Interconnection | $/KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | AFUDC | $/KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 |  | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 620.1 | 620.1 | 620.1 | 620.1 | 620.1 | 620.1 | 620.1 | 620.1 | 620.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 950.4 | 950.4 | 950.4 | 950.4 | 950.4 | 950.4 | 950.4 | 950.4 | 950.4 |  | 950.4 | 950.4 | 950.4 | 950.4 | 950.4 | 950.4 | 950.4 | 950.4 | 950.4
|  | Total Capital Cost | $/MW X1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.74 | 1312.74 | 1312.74 | 1312.74 | 1295.2105 | 1277.6811 | 1260.1516 | 1242.6221 | 1225.0926 |  | 1312.74 | 1312.74 | 1312.74 | 1312.74 | 1295.2105 | 1277.6811 | 1260.1516 | 1242.6221 | 1225.0926 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2040.948 | 2040.948 | 2040.948 | 2040.948 | 2018.1884 | 1995.4288 | 1972.6693 | 1949.9097 | 1927.1501 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3339.456 | 3339.456 | 3339.456 | 3339.456 | 3301.1874 | 3262.9187 | 3224.6501 | 3186.3815 | 3148.1128 |  | 4159.5703 | 4159.5703 | 4159.5703 | 4159.5703 | 4108.1648 | 4056.7593 | 4005.3539 | 3953.9484 | 3902.5429
|  | O&M Fixed | $/KW-yr | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 |  | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 | 24.8571 |  | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 |  | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 | 40.924 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101.759 | 101.759 | 101.759 | 101.759 | 101.759 | 101.759 | 101.759 | 101.759 | 101.759 |  | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 |  | 76.0731 | 76.0731 | 76.0731 | 76.0731 | 76.0731 | 76.0731 | 76.0731 | 76.0731 | 76.0731 |  | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 | 406.8 |  | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 |  | 209.184 | 209.184 | 209.184 | 209.184 | 209.184 | 209.184 | 209.184 | 209.184 | 209.184 |  | 250.3269 | 250.3269 | 250.3269 | 250.3269 | 250.3269 | 250.3269 | 250.3269 | 250.3269 | 250.3269
|  | O&M Fixed | $/MW-wk | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 |  | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 | 478.022 |  | 787 | 787 | 787 | 787 | 787 | 787 | 787 | 787 | 787 |  | 787 | 787 | 787 | 787 | 787 | 787 | 787 | 787 | 787 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1956.9038 | 1956.9038 | 1956.9038 | 1956.9038 | 1956.9038 | 1956.9038 | 1956.9038 | 1956.9038 | 1956.9038 |  | 162.5 | 162.5 | 162.5 | 162.5 | 162.5 | 162.5 | 162.5 | 162.5 | 162.5 |  | 1462.945 | 1462.945 | 1462.945 | 1462.945 | 1462.945 | 1462.945 | 1462.945 | 1462.945 | 1462.945 |  | 7823.0769 | 7823.0769 | 7823.0769 | 7823.0769 | 7823.0769 | 7823.0769 | 7823.0769 | 7823.0769 | 7823.0769 |  | 3300 | 3300 | 3300 | 3300 | 3300 | 3300 | 3300 | 3300 | 3300 |  | 4022.7692 | 4022.7692 | 4022.7692 | 4022.7692 | 4022.7692 | 4022.7692 | 4022.7692 | 4022.7692 | 4022.7692 |  | 4813.978 | 4813.978 | 4813.978 | 4813.978 | 4813.978 | 4813.978 | 4813.978 | 4813.978 | 4813.978
|  | O&M Variable | $/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Land Area | acres/MW | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 |  | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 |  | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 |  | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 |  | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 |  | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 |  | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 |  | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 |  | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 |  | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 |  | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 |  | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76 | 2.76
|  | Degradation | %/year | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% |  | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05%
|  | First Year Available |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 |  | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022
|  | Economic Life | Years | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | Greenfield Dev. & Const. Leadtime | Years | [10 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Net Metering (Existing) 2022 to Net Metering (Existing) 2030
| Storage | Nameplate Capacity | MW | [40 empty] | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005
|  | Operating Range (e) | % | [40 empty] | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
|  | R/T Efficiency | % | [40 empty] | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
|  | Discharge at Nominal Power | Hours | [40 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | Maximum Storage | MWh | [40 empty] | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
|  | Upfront 1-Time Incentive | $/KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes
Formula

## 1
#1 - 3rd Party Customer-Sited Distributed Battery PPA
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 0.2
Operating Range (e) | % | 50%
R/T Efficiency | % | 88%
Discharge at Nominal Power | Hours | 2
Maximum Storage | MWh | 0.4
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Program Costs (per Year)
Marketing | 180
Administration | 900
Incentives
PPA / Recurring Payment | 60000 |  | Annual cost
Non-Utility Costs
Installed Cost
Equipment | 342555
Design and Construction | 155793
Taxes | 35968
Development & Financing | 30723
Profit | 49424
Operating Cost (per year)
Equipment O&M | 2575
Insurance | 1843.389
Technology Fees | 240
Land / Lease Costs | 33300 |  | Assumed 1,110 sqft needed
Developer SG&A | 15000
Subscription Costs
Participant | Third Party
Turnkey design and Implementation ($/kWh) | 1536.1575
Maintenance Costs ($/kW/y) | 12.875
EOL replacement costs (% of initial)

## 2
#2 - 3rd Party Utility-scale Distributed Battery PPA
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 2
Storage
Nameplate Capacity | MW | 5
Operating Range (e) | % | 50%
R/T Efficiency | % | 85%
Discharge at Nominal Power | Hours | 4
Maximum Storage | MWh | 20
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Program Costs (per Year)
Marketing | 4500
Administration | 22500
Incentives
PPA / Recurring Payment | 225000 |  | Annual cost
Non-Utility Costs
Installed Cost
Equipment | 6587151
Design and Construction | 2688249
Taxes | 691650.8824
Development & Financing | 498352.5722
Profit | 996705.1443
Operating Cost (per year)
Equipment O&M | 64380
Insurance | 34386.3258
Technology Fees | 12500
Land / Lease Costs | 112050 |  | 3735 sqft needed
Developer SG&A | 114000
Subscription Costs
Participant | Third Party
Turnkey design and Implementation ($/kWh) | 573.1054
Maintenance Costs ($/kW/y) | 12.876
EOL replacement costs (% of initial)

## 3
#3 -C&I Battery Install Incentive
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 0.2
Operating Range (e) | % | 50%
R/T Efficiency | % | 88%
Discharge at Nominal Power | Hours | 2
Maximum Storage | MWh | 0.4
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Program Costs (per Year)
Marketing | 2112
Administration | 10560
Incentives | 105600 |  | BESS Incentive (CA), One time cost
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment | 342555
Design and Construction | 155793
Taxes | 35968
Development & Financing | 30723
Profit | 49424
Operating Cost (per year)
Equipment O&M | 2575
Insurance | 1843.389
Technology Fees | 240
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kWh) | 1536.1575
Maintenance Costs ($/kW/y) | 12.875
EOL replacement costs (% of initial)

## 4
#4 -C&I Space Leasing for Batteries
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 0.2
Operating Range (e) | % | 50%
R/T Efficiency | % | 88%
Discharge at Nominal Power | Hours | 4
Maximum Storage | MWh | 0.8
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 535426
Design and Construction | 243511
Taxes | 56220
Development & Financing | 48021
Profit | 77252
Operating Cost (per year)
Equipment O&M | 2575
Insurance | 2881.29
Technology Fees | 240
Land / Lease Costs | 37800 |  | 1260 sqft required
Program Costs (per Year)
Marketing | 300
Administration | 15000
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant
Turnkey design and Implementation ($/kWh)
Maintenance Costs ($/kW)
EOL replacement costs (% of initial)
Participant
Turnkey design and Implementation ($/kWh)
Maintenance Costs ($/kW/y)
EOL replacement costs (% of initial)

## 5
#5 -Multi-Family Unit Battery Program
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 2
Storage
Nameplate Capacity | MW | 0.25
Operating Range (e) | % | 50%
R/T Efficiency | % | 90%
Discharge at Nominal Power | Hours | 3
Maximum Storage | MWh | 0.75
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 457550
Design and Construction | 302600
Taxes | 48050
Development & Financing | 47300
Profit | 90100
Operating Cost (per year)
Equipment O&M | 0
Insurance | 0
Technology Fees | 2750
Land / Lease Costs
Program Costs (per Year)
Marketing | 300
Administration | 15000
Incentives | 40000 |  | One time cost for siting allowance
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant
Turnkey design and Implementation ($/kWh)
Maintenance Costs ($/kW/y) | 0
EOL replacement costs (% of initial)

## 6
#6 - PSE Mobile Batteries
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 0.5
Operating Range (e) | % | 50%
R/T Efficiency | % | 80%
Discharge at Nominal Power | Hours | 2
Maximum Storage | MWh | 1.3
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 892000 |  | Based on Vendor Quotes
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M | 5150
Insurance | 3686.778
Technology Fees | 480
Land / Lease Costs
Program Costs (per Year)
Marketing
Administration | 14000
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant
Turnkey design and Implementation ($/kWh)
Maintenance Costs ($/kW)
EOL replacement costs (% of initial)
Participant
Turnkey design and Implementation ($/kWh)
Maintenance Costs ($/kW/y)
EOL replacement costs (% of initial)

## 7
#7 - PSE Substation Batteries
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 3.3
Operating Range (e) | % | 50%
R/T Efficiency | % | 85%
Discharge at Nominal Power | Hours | 2
Maximum Storage | MWh | 6.6
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 2521798.1093
Design and Construction | 1423247.6383
Taxes | 264788.8015
Development & Financing | 210491.7275
Profit
Operating Cost (per year)
Equipment O&M | 41045
Insurance | 13260.9788
Technology Fees | 12500
Land / Lease Costs
Program Costs (per Year)
Marketing
Administration | 60000
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant
Turnkey design and Implementation ($/kWh)
Maintenance Costs ($/kW/y)
EOL replacement costs (% of initial)

## 8
#8 - PSE Utility-Scale Distributed Battery Stations
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 1
Operating Range (e) | % | 50%
R/T Efficiency | % | 85%
Discharge at Nominal Power | Hours | 2
Maximum Storage | MWh | 2
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 778048
Design and Construction | 430942
Taxes | 81695
Development & Financing | 74214
Profit
Operating Cost (per year)
Equipment O&M | 12438
Insurance | 4094.697
Technology Fees | 12500
Land / Lease Costs | 63000 |  | Assumed 2100 sqft at $30/sqft
Program Costs (per Year)
Marketing
Administration | 26000
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant
Turnkey design and Implementation ($/kWh)
Maintenance Costs ($/kW/y)
EOL replacement costs (% of initial)

## 9
#9 -Residential Battery Install Incentive
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 0.005
Operating Range (e) | % | 50%
R/T Efficiency | % | 90%
Discharge at Nominal Power | Hours | 3
Maximum Storage | MWh | 0.014
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Program Costs (per Year)
Marketing | 81
Administration | 270
Incentives | 2700 |  | BESS Incentive (CA), One time cost
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment | 9151
Design and Construction | 6052
Taxes | 961
Development & Financing | 946
Profit | 1802
Operating Cost (per year)
Equipment O&M | 137.265
Insurance | 17
Technology Fees | 55
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kWh) | 1350.8571
Maintenance Costs ($/kW/y) | 27.453
EOL replacement costs (% of initial)

## 10
#10 - Residential PSE Battery Leasing
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 0.005
Operating Range (e) | % | 50%
R/T Efficiency | % | 90%
Discharge at Nominal Power | Hours | 3
Maximum Storage | MWh | 0.014
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 9151
Design and Construction | 6052
Taxes | 961
Development & Financing | 946
Profit | 1802
Operating Cost (per year)
Equipment O&M | 137.265
Insurance | 17
Technology Fees | 55
Land / Lease Costs
Program Costs (per Year) |  |  | Using LMI Program Costs as B&V did not include any for this concept
Marketing | 80
Administration | 400 |  | Assume SGA = 12% of revenue
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs | 0 |  | -
Developer SG&A
Subscription Costs | 300 |  | Set to $60/kW
Participant | Customer
Turnkey design and Implementation ($/kWh) | 0
Maintenance Costs ($/kW/y) | 0
EOL replacement costs (% of initial)

## 11
#11 - Residential PSE Battery Leasing - Low Income
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 0.005
Operating Range (e) | % | 50%
R/T Efficiency | % | 90%
Discharge at Nominal Power | Hours | 3
Maximum Storage | MWh | 0.014
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 9151
Design and Construction | 6052
Taxes | 961
Development & Financing | 946
Profit | 1802
Operating Cost (per year)
Equipment O&M | 137.265
Insurance | 17
Technology Fees | 55
Land / Lease Costs
Program Costs (per Year)
Marketing | 80
Administration | 400
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs | - |  | -
Developer SG&A
Subscription Costs | 50 |  | Set to $10/kW
Participant | Customer
Turnkey design and Implementation ($/kWh) | 0
Maintenance Costs ($/kW/y) | 0
EOL replacement costs (% of initial)

## 12
#12 - Net Metering (Existing)
Nameplate Capacity (AC) | MW | 0.0058333 |  | ILR | 1.2
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.76
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 30
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 7000 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees | 55
Land / Lease Costs
Program Costs (per Year)
Marketing
Administration | 90
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment | 5894
Design and Construction | 3493
Taxes | 2023
Development & Financing | 5544
Profit | 3738
Operating Cost (per year)
Equipment O&M | 157.5 |  | Removed replacement costs
Insurance | 17
Technology Fees | 55
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 3547.2 |  | 2956
Maintenance Costs ($/kW/y) | 27
EOL replacement costs (% of initial) | 7.1% |  | Lifetime Inverter Replacement Cost

## 13
#12 - Net Metering (Successor)
Nameplate Capacity (AC) | MW | 0.0058333 |  | ILR | 1.2
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.76
Degradation | %/year | 0.05%
First Year Available |  | 2025
Economic Life | Years | 30
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 7000 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees | 55
Land / Lease Costs
Program Costs (per Year)
Marketing
Administration | 90
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment | 5894
Design and Construction | 3493
Taxes | 2023
Development & Financing | 5544
Profit | 3738
Operating Cost (per year)
Equipment O&M | 157.5 |  | Removed replacement costs
Insurance | 17
Technology Fees | 55
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 3547.2
Maintenance Costs ($/kW/y) | 27
EOL replacement costs (% of initial) | 7.1% |  | Lifetime Inverter Replacement Cost

## 14
#14 - PSE Community Solar
Nameplate Capacity (AC) | MW | 3.8462 |  | ILR | 1.3
Capacity Factor | % | 13.7%
Land Area | acres/MW | 5.2
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 35
Greenfield Dev. & Const. Leadtime | Years | 2
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 4615384.6154 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 2610000
Design and Construction | 1530000
Taxes | 295000
Development & Financing | 840000
Profit | 140000
Operating Cost (per year)
Equipment O&M | 33150 |  | Removed replacement costs
Insurance | 15750
Technology Fees | 12500
Land / Lease Costs | 18000 |  | Incl. Property Tax
Program Costs (per Year)
Marketing | 18000
Administration | 60000
Incentives |  |  | REC's estimated at $10/MWh, not included in reported costs
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs | 120000
Participant | Customer
Turnkey design and Implementation ($/kW) | 0
Maintenance Costs ($/kW/y) | 0
EOL replacement costs (% of initial) | 6.4% |  | Lifetime Inverter Replacement Cost

## 15
#15 - PSE Community Solar - Low Income
Nameplate Capacity (AC) | MW | 3.8462 |  | ILR | 1.3
Capacity Factor | % | 13.7%
Land Area | acres/MW | 5.2
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 35
Greenfield Dev. & Const. Leadtime | Years | 2
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 4615384.6154 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 2610000
Design and Construction | 1530000
Taxes | 295000
Development & Financing | 840000
Profit | 140000
Operating Cost (per year)
Equipment O&M | 33150 |  | Removed replacement costs
Insurance | 15750
Technology Fees | 12500
Land / Lease Costs | 18000 |  | Incl. Property Tax
Program Costs (per Year)
Marketing | 18000
Administration | 60000
Incentives |  |  | REC Per TMB Guidance
PPA / Recurring Payment |  |  | Sch 134 Tariff
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 0
Maintenance Costs ($/kW/y) | 0
EOL replacement costs (% of initial) | 6.4% |  | Lifetime Inverter Replacement Cost

## 16
#16 - 3rd Party Distributed Solar PPA
Nameplate Capacity (AC) | MW | 0.30769 |  | ILR | 1.3
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.99
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 30
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 369230.7692 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees | -
Land / Lease Costs
Program Costs (per Year)
Marketing
Administration | 1772
Incentives
PPA / Recurring Payment | 29538.4615 |  | Assume $80/MWh based on recent PPAs signed in PNW, Annual Cost
Non-Utility Costs
Installed Cost
Equipment | 241600
Design and Construction | 122000
Taxes | 55200
Development & Financing | 190800
Profit | 56400
Operating Cost (per year)
Equipment O&M | 7689.12 |  | Removed replacement costs
Insurance | 1998 |  | 0.3%
Technology Fees | 1200
Land / Lease Costs | 4000
Developer SG&A | 12000
Subscription Costs
Participant | Third Party
Turnkey design and Implementation ($/kW) | 2164.5
Maintenance Costs ($/kW/y) | 24.9896
EOL replacement costs (% of initial) | 5.4% |  | Lifetime Inverter Replacement Cost

## 17
#17 - C&I Roof-top Solar Incentive
Nameplate Capacity (AC) | MW | 0.30769 |  | ILR | 1.3
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.99
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 30
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 369230.7692 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost Multiplier | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Program Costs (per Year)
Marketing | 600
Administration | 2000
Incentives | 20000 |  | One time cost
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment | 241600
Design and Construction | 122000
Taxes | 55200
Development & Financing | 190800
Profit | 56400
Operating Cost (per year)
Equipment O&M | 7689.12 |  | Removed replacement costs
Insurance | 1998
Technology Fees | 120
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 2164.5
Maintenance Costs ($/kW/y) | 24.9896
EOL replacement costs (% of initial) | 5.4% |  | Lifetime Inverter Replacement Cost

## 18
#18 - C&I Roof-top Solar Leasing
Nameplate Capacity (AC) | MW | 0.30769 |  | ILR | 1.3
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.99
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 30
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 369230.7692 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost Multiplier | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate
Utility Cost
Installed Cost
Equipment | 241600
Design and Construction | 122000
Taxes | 55200
Development & Financing | 190800
Profit | 56400
Operating Cost (per year)
Equipment O&M | 7689.12 |  | Removed replacement costs
Insurance | 1998
Technology Fees | 120
Land / Lease Costs | 4000 |  | Commercial roof lease at $10*kWdc
Program Costs (per Year)
Marketing | 1600
Administration | 8000 |  | Based on comparable CA program
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 0
Maintenance Costs ($/kW/y) | 0
EOL replacement costs (% of initial) | 5.4% |  | Lifetime Inverter Replacement Cost

## 19
#19 - Multi-Family Solar Partnership
Nameplate Capacity (AC) | MW | 0.083333 |  | ILR | 1.2
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.76
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 30
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 100000 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost Multiplier | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Program Costs (per Year)
Marketing | 900
Administration | 3000
Incentives
PPA / Recurring Payment | 30000 |  | Annual Payment
Non-Utility Costs
Installed Cost
Equipment | 84200
Design and Construction | 89900
Taxes | 28900
Development & Financing | 79200
Profit | 53400
Operating Cost (per year)
Equipment O&M | 7689.12 |  | Removed replacement costs
Insurance | 1006.8
Technology Fees | 1200
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 4027.2
Maintenance Costs ($/kW/y) | 92.2694
EOL replacement costs (% of initial) | 2.7% |  | Lifetime Inverter Replacement Cost

## 20
#20 - Multi-Family Roof-top Solar Incentive
Nameplate Capacity (AC) | MW | 0.083333 |  | ILR | 1.2
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.76
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 30
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 100000 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost Multiplier | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Program Costs (per Year)
Marketing | 3300
Administration | 11000
Incentives | 110000 |  | Incentives typically only provided for Income Qualified MF buildings, One time cost
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment | 84200
Design and Construction | 89900
Taxes | 28900
Development & Financing | 79200
Profit | 53400
Operating Cost (per year)
Equipment O&M | 7689.12 |  | Removed replacement costs
Insurance | 1006.8
Technology Fees | 1200
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 4027.2
Maintenance Costs ($/kW/y) | 92.2694
EOL replacement costs (% of initial) | 2.7% |  | Lifetime Inverter Replacement Cost

## 21
#21 -PSE Customer-Sited Solar+Storage Offering
Nameplate Capacity (AC) | MW | 0.0058333 |  | ILR | 1.2
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.76
Degradation | %/year | 0.05%
First Year Available |  | 2022 |  | 48.2857
Economic Life | Years | 10
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 0.005
Operating Range (e) | % | 50%
R/T Efficiency | % | 90%
Discharge at Nominal Power | Hours | 3
Maximum Storage | MWh | 0.014
Economic Life | Years | 10 |  | Storage Degradation | 5%
Yield | 1200 | kWh/kW
Production | 7000 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.9349 | 0.87191 | 0.83104 | 0.79228 | 0.76747 | 0.75155 | 0.73575 | 0.72007 | 0.7045 | 0.68469
[17 empty] | BESS |  |  |  |  | SOLAR
Cost Estimate | $ Per System (2020$) | [10 empty] | $ | kW | $/kW | kWh | $/kWh | $ | kW | $/kW | kWh | $/kWh | $ | kW | $/kW | kWh | $/kWh
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Program Costs (per Year)
Marketing | 243
Administration | 810
Incentives | 8100 |  | Solar Incentive (WA), BESS Incentive (CA), One time cost
PPA / Recurring Payment | 225 |  | Estimated $225/year for DR participation
Non-Utility Costs
Installed Cost
Equipment | 15045
Design and Construction | 9545
Taxes | 2984
Development & Financing | 6490
Profit | 5540
Operating Cost (per year)
Equipment O&M | 290 |  | Removed replacement costs
Insurance | 118.812
Technology Fees | 55
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 6789.2571
Maintenance Costs ($/kW/y) | 49.7143
EOL replacement costs (% of initial) | 1.1% |  | Lifetime Inverter Replacement Cost (10 years in line with battery)

## 22
#22 - Residential Roof-top Solar Leasing
Nameplate Capacity (AC) | MW | 0.0058333 |  | ILR | 1.2
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.76
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 30
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 7000 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Installation Cost (% of 2020 cost) | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632 | 0.83632 | 0.82632 | 0.81632 | 0.80632 | 0.79632 | 0.78632 | 0.77632 | 0.76632 | 0.75632 | 0.74632 | 0.73632 | 0.72632 | 0.71632 | 0.70632 | 0.69632
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 5894
Design and Construction | 3493
Taxes | 2023
Development & Financing | 5544
Profit | 3738
Operating Cost (per year)
Equipment O&M | 157.5 |  | Removed replacement costs
Insurance | 16.94
Technology Fees | 55
Land / Lease Costs | 720 |  | Calculated to be cost competitive with solar lease
Program Costs (per Year)
Marketing | 28.8
Administration | 242 |  | Assume SGA = 12% of revenue - estimated on residential solar lease per site
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 0
Maintenance Costs ($/kW/y) | 0
EOL replacement costs (% of initial) | 7.1% |  | Lifetime Inverter Replacement Cost

## 23
#22 - Low Income Residential Roof-top Solar Leasing
Nameplate Capacity (AC) | MW | 0.0058333 |  | ILR | 1.2
Capacity Factor | % | 13.7%
Land Area | acres/MW | 2.76
Degradation | %/year | 0.05%
First Year Available |  | 2022
Economic Life | Years | 30
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW
Operating Range (e) | %
R/T Efficiency | %
Discharge at Nominal Power | Hours
Maximum Storage | MWh
Economic Life | Years
Yield | 1200 | kWh/kW
Production | 7000 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.96 | 0.92 | 0.92 | 0.92 | 0.92 | 0.90526 | 0.89053 | 0.87579 | 0.86105 | 0.84632
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment | 5894
Design and Construction | 8693
Taxes | 2023
Development & Financing | 5544
Profit | 3738
Operating Cost (per year)
Equipment O&M | 157.5 |  | Removed replacement costs
Insurance | 16.94
Technology Fees | 55
Land / Lease Costs | 960 |  | 33% higher than market offering
Program Costs (per Year)
Marketing | 28.8
Administration | 242 |  | Assume SGA = 12% of revenue - estimated on residential solar lease per site
Incentives
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kW) | 0
Maintenance Costs ($/kW/y) | 0
EOL replacement costs (% of initial) | 7.1% |  | Lifetime Inverter Replacement Cost

## 24
#24 - C&I BYO Battery
Nameplate Capacity | MW
Capacity Factor | %
Land Area | acres/MW
Degradation | %/year | 5%
First Year Available |  | 2022
Economic Life | Years
Greenfield Dev. & Const. Leadtime | Years | 1
Storage
Nameplate Capacity | MW | 0.2
Operating Range (e) | % | 50%
R/T Efficiency | % | 88%
Discharge at Nominal Power | Hours | 2
Maximum Storage | MWh | 0.4
Economic Life | Years | 10
Yield | 1200 | kWh/kW
Production | 0 | kWh/y
Installation Cost Over Time (2020$)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Installation Cost (% of 2020 cost) | 1 | 0.90979 | 0.82382 | 0.74207 | 0.66456 | 0.61494 | 0.59783 | 0.58097 | 0.56434 | 0.54795 | 0.52307
Cost Estimate | $ Per System (2020$)
Utility Cost
Installed Cost
Equipment
Design and Construction
Taxes
Development & Financing
Profit
Operating Cost (per year)
Equipment O&M
Insurance
Technology Fees
Land / Lease Costs
Program Costs (per Year)
Marketing | 248.28
Administration | 1241.4
Incentives | 12414 |  | CA - PGE CBP, One time cost
PPA / Recurring Payment
Non-Utility Costs
Installed Cost
Equipment | 342555
Design and Construction | 155793
Taxes | 35968
Development & Financing | 30723
Profit | 49424
Operating Cost (per year)
Equipment O&M | 2575
Insurance | 1843.389
Technology Fees | 240
Land / Lease Costs
Developer SG&A
Subscription Costs
Participant | Customer
Turnkey design and Implementation ($/kWh) | 1536.1575
Maintenance Costs ($/kW/y) | 12.875
EOL replacement costs (% of initial)