## Slide 1: Avista 2011 Integrated Resource Plan Presentation to WUTC October 10, 2011
Clint Kalich
Manager, Resource Planning & Power Supply Analyses
clint.kalich@avistacorp.com
509.495.4532

## Slide 2: 2011 IRP Summary
Lower Market Prices
Slower Load Growth
Adequate Supply Through 2018
Continued Gas Reliance
40% Less Wind
Higher Conservation and Budgets ($1.4B over 20 years)
$1.7 Billion Investment in Generation Portfolio
Notes: Load Forecast Update -- load growth projection from 1.6% AARG to 1.3% AARG, before new conservation measures, from 1.4% to 1.1% after new conservation
DSM spending triples from $20MM to $60MM/yr. between now and 2018, with a 17% AARG 2011-2020, and 9% AARG 2011-31
Conservation meets ~50% of Avista load growth
25% of gas is peaking instead of 100% CCCT
40% less wind, result of lower growth and more expected hydro upgrades

## Slide 3: 2011 Integrated Resource Plan Modeling Process
Preferred Resource Strategy
AURORA
“Wholesale Electric Market”
300 Simulations
PRiSM
“Avista Portfolio”
Efficient Frontier
Fuel Prices
Fuel Availability
Resource Availability
Demand
Emission Pricing
Existing Resources
Resource Options
Transmission
Resource & Portfolio Margins
Conservation Trends
Existing Resources
Avista Load Forecast
Energy,
Capacity,
& RPS Balances
New Resource Options & Costs
Cost Effective T&D
Projects/Costs
Cost Effective Conservation Measures/Costs
Mid-Columbia Prices
Stochastic Inputs
Deterministic Inputs
Capacity Value
Avoided Costs

## Slide 4: Major Planning Issues of 2011 IRP
Renewable Portfolio Standards (I-937)
  State and federal
Greenhouse Gas Regulations
  State, regional, and federal
  Emissions performance standards and reporting
Energy Efficiency Requirements (I-937)
Reliability Planning (adoption of NPCC reserves method)
Variable Resource Integration
Smart Grid

## Slide 5: Historical Load Forecast Comparisons
28

## Slide 6: Load Forecast Statistics
21
Low 0.95%, High 2.13% by ratio method based
on NPCC 6th Power Plan
Residential Use/Customer
Commercial Use/Customer

## Slide 7: Key Capacity Planning Assumptions
  Methodology Relies on Northwest Power Council
    24% winter and 23% summer planning margin
      compares to 15% assumption in 2009 IRP
      ~10% higher than 2009 IRP (15% + ~6% operating reserves)
    Based on 18-hour sustained capacity methodology
  Market Reliance on “Modified” NWPP L&R Balance
    Ignores regional conservation assumption, use Wood-Mac 0.9% forecast
    No capacity contribution for wind (-250 MW)
    Add 10% wind capacity reserves, (-500 MW, no on-peak wind interruptions)
  5.5% of Regional Surplus is Available to Avista
    Linear phased-out over 10 years

## Slide 9: Avista Energy Position

## Slide 10: Avista Winter Capacity Positions

## Slide 11: Avista Summer Capacity Positions

## Slide 12: Avista I-937 (Renewable Energy) Position

## Slide 13
RECENT AVISTA TRANSMISSION UPGRADES
Benewah Station:
  230 / 115 kV Station with a Single 125 MVA Transformer.
  230 kV Connections between the North and South Avista Load Centers.
  230 kV Double Breaker / Double Bus Configuration for increased reliability.
Benewah – Shawnee 230 kV line:
  Completes transmission required for both load service and the West of Hatwai transfer requirements.
  Allows for resource integration in the center and south areas of the Avista system.

## Slide 14: Examples of Future Construction Required to Meet NERC / WECC Reliability Standards
Moscow Station:
  230 / 115 kV Station, single 250 MVA transformer.
  Increases capacity to the Moscow / Pullman area and relieves loading on the Shawnee transformer.
Westside Station:
  230 / 115 kV Station, two 250 MVA transformers.
  Increases capacity and security to the West Plains area of Spokane County, and relieves heavy loading on large transformers in the central Spokane area.
Irvin 115 kV and Associated 115 kV Reconductoring:
  115 kV Switching Station and other upgrades to meet additional load growth in the Spokane Valley.

## Slide 16: Natural Gas Price Forecast (Henry Hub)
$7.30
$8.87
$5.93
Nominal Levelized Costs

## Slide 17: Greenhouse Gas (CO2) Price Trajectories
$59.36
2015-2031 Levelized Price per Short Ton
$28.02
$46.48
$00.00
$40.20

## Slide 18: Mid-Columbia Electric Price Forecast
$77.94
$70.50
$57.01
$52.86
Levelized
Cost

## Slide 19: Conservation Consistency with Sixth Plan
End-use model — bottom-up approach to understanding savings
  Measure life
  Stock accounting
  Measure saturation and applicability
Accounts for
  Naturally occurring conservation
  Codes and standards
Measures include those in Sixth Plan (other measures also)
Considers both lost opportunity and non-lost opportunity
Economic potential, based on Total Resource Cost (TRC) test
Achievable potential considers realistic rate at which technologies can be deployed
Maximum potential in 20 years is 85% of economic potential

## Slide 20: End-Use Segmentation Example

## Slide 21: Conservation Avoided Cost = $104.39/MWh *
{(E + PC + R) * (1 + P)} * (1 + L) + DC * (1 + L)
Where:
E = market energy price (calculated by Aurora, including forecasted CO2 mitigation)
PC = new resource capacity savings (calculated by PRISM)
R = Risk premium to account for RPS and rate volatility reduction (calculated by PRISM)
P = Power Act preference premium (10% assumption)
DC = distribution capacity savings (~$10/kW-year based on Heritage Project calculation)
L = transmission and distribution losses (6.1% assumption based on Avista’s system average losses)
Item | $/MWh
Energy Price | 70.50
Generation Capacity | 10.51
Risk Premium | 7.38
10% Preference | 8.84
Distribution Capacity | 1.14
T&D losses | 6.02
Total | 104.39
* Assumes flat delivery measure; those with more on-peak shape get a higher price

## Slide 22: Summary of EE results $1.4 Billion over 20 years
Summary of Energy Savings from Energy Efficiency
Savings by housing type, 2022

## Slide 23: BPC Target Update (MWh)
 | 2012 | 2013 | Biennium Total | 2012-2021 Total
6th Power Plan Calc | 71,983 | 77,982 | 149,965 | 950,784
Busbar to Site Adj. | 64,785 | 70,184 | 134,969 | 855,706
Less: Distribution Eff. | (4,129) | (5,221) | (9,350) | (88,656)
Revised 6th Plan Target | 60,656 | 64,963 | 125,618 | 767,050
RAP w/o Nat. Occurring | 34,424 | 42,832 | 77,256 | 600,553
Less: Fuel Conversions | (383) | (671) | (1,054) | (71,439)
Adj. RAP | 34,041 | 42,161 | 76,202 | 529,114
MAP w/o Nat. Occurring | 59,044 | 86,219 | 145,263 | 1,278,697
Less: Fuel Conversions | (2,460) | (5,393) | (7,853) | (199,352)
Adj. MAP | 56,584 | 80,826 | 137,410 | 1,079,345

## Slide 24: Thermal Resource Options
Resource Type | First Year | Size (MW) | Levelized Overnight Costs (2012 $/MWh)* | Overnight Capital Cost (Nominal 2012)
SCCT (aero) | 2014 | 46 | $106 | $1,033/kW
SCCT (frame) | 2014 | 83 | $114 | $591/kW
Hybrid SCCT | 2014 | 94 | $103 | $1,107/kW
CCCT (air) | 2016 | 270 | $88 | $1,105/kW
CCCT (water) | 2016 | 275 | $85 | $1,053/kW
Small Cogeneration | 2015 | 5 | $112 | $3,472/kW
Recip. Engines | 2014 | 99 | $111 | $1,139 /kW
Coal (Ultra-critical) | 2018 | 300 | $123 | $3,250/kW
Coal (IGCC) | 2014 | 300 | $138 | $3,252/kW
Coal (IGCC w/seq.) | 2018 | 250 | $156 | $4,722/kW
Nuclear | 2021 | 500 | $150 | $5,802/kW
* Prices are based on a preliminary gas price forecast

## Slide 25: Thermal Upgrade Options
Resource Type | Winter (MW) | Summer (MW)
Rathdrum CT to CCCT | 77 | 91
Rathdrum Inlet Fogging | <5 | 18
Coyote Springs 2 (CS2) Inlet Chiller | 0 | 30
CS2 Cold Day Performance Software | 18 | 1
CS2 Hot Gas Path Hardware Upgrade | 9 | 7
CS2 Cooling Optimization Hardware | 3 | 2
Kettle Falls Wood Fuel Gasification | 0 | 0

## Slide 26: Renewable Resource Options
Resource Type | First Year | Size (MW) | Levelized Overnight Costs (2012 $/MWh)* | Overnight Capital Cost (Nominal 2012)
Wind | 2016 | 50 | $106 | $1,951/kW
Geothermal | 2017 | 15 | $110 | $4,463/kW
Wood Biomass | 2015 | 25 | $166 | $3,710/kW
Landfill Gas | 2014 | 3.2 | $60 | $2,023/kW
Manure Digester | 2013 | 0.85 | $111 | $4,304/kW
Waste Water Treatment | 2014 | 0.85 | $114 | $4,304/kW
Solar Photovoltaic | 2014 | 5 | $429 | $7,140/kW
Solar Thermal | 2016 | 25 | $195 | $4,751/kW

## Slide 27: Hydro Upgrade Options
Resource Type | Year | Size (MW)
Little Falls 1 Upgrade | 2014 | 1.0
Little Falls 2 Upgrade | 2015 | 1.0
Little Falls 3 Upgrade | 2016 | 1.0
Little Falls 4 Upgrade | 2017 | 1.0
Post Falls New Powerhouse | TBD | TBD
Upper Falls Upgrade | 2019 | 2.0
Long Lake 2nd Powerhouse / Pumped Storage | 2020 | 60
Long Lake 2nd Powerhouse | 2020 | 50 – 60
Monroe Street Unit 2 | TBD | 37.5
Cabinet Gorge Unit 5 | 2015 | 50

## Slide 28: 2011 IRP Scenario Analysis
Scenarios Test Differing Planning Assumptions
Avista’s Current Load and Resource Portfolio
Preferred Resource Strategy
Wholesale Electric Market
Different Resource Options
Scenarios Performed for 2011 IRP
  Deterministic scenarios
  Stochastic market scenarios
  Portfolio scenarios

## Slide 29: 2011 IRP Deterministic/Stochastic Scenarios
  Deterministic Scenarios
    Low and High Gas Scenarios
    High Wind Penetration Scenarios
    Carbon Scenarios
    Western Coal Plant Phase Out Scenario
  Stochastic Scenarios
    Expected Case
    average hydro, load, gas, wind, emissions and outages
    Volatile Fuel Scenario
    higher gas price volatility
    Unconstrained Carbon Scenario
    determines financial impacts of carbon price assumptions
    Mandatory Coal Retirement Scenario
    western coal plants retired after 40 service years
Notes:   Deterministic scenarios test the Preferred Resource Strategy (PRS) across several different futures
  Low and High Gas – consultant 1 vs. consultant 2
  High Wind Penetration – regional study, price changes, in 2016 (no wind, current wind, and double wind)
  Carbon scenarios – emissions reduced to the weighted average of the four greenhouse gas emissions cases
  Western Coal Plant Phase Out

## Slide 30: 2011 IRP Portfolio Scenarios (a sampling)
  Market Reliance Only
  Capacity Only
  All CCCT and Wind
  All SCCT and Wind
  GHG Credit Allocations
  2025 Nuclear Availability
  2009 PRS
  National Renewable Energy Standard
  Simple-Cycle CT Versus Combined-Cycle CT Tipping Point
  Wind Versus Solar Tipping Point
  Carbon Sequestration

## Slide 31: PRiSM Objective Function
Linear program solving for the optimal resource strategy to meet resource deficits over planning horizon.
Model selects its resources to reduce cost, risk, or both.
Minimize: Total Power Supply Cost on NPV basis (2012-2052 with emphasis on first 11 years of the plan)
Subject to:
Risk Level
Capacity Need +/- deviation
Energy Need +/- deviation
Renewable Portfolio Standards
Resource Limitations and Timing

## Slide 32: Efficient Frontier
Demonstrates the Trade Offs Between Cost and Risk
Avoided Cost Calculation
Risk
Least Cost Portfolio
Least Risk Portfolio
Find least cost portfolio at a given level of risk
Short-Term Market
Market
+ Capacity
+ RPS
= Avoided Cost
Capacity Need
+ Risk
Cost

## Slide 33: Actual Efficient Frontier Results

## Slide 34: 2011 Preferred Resource Strategy $3.1 Billion over 20 years
($1.7 billion over 20 years)
($1.4 billion over 20 years)
($1.7 billion over 20 years)

## Slide 35: Preferred Resource Strategy IRP Nameplate Comparison
2009 IRP
1,110 MW
2011 IRP
1,024 MW

## Slide 36: Avista Greenhouse Gas Emissions

## Slide 37: Power Supply Cost/MWh Index
4.1% + Inflation
3.8% + Inflation
2.6% + Inflation

## Slide 38: Portfolio Resource Scenarios (MW)

## Slide 39: Capital Expenditures (Alternative Portfolios)

## Slide 40: Greenhouse Gas and Costs of Carbon Mitigation Scenarios
Market Scenario | Change to GHG Emissions From 2012 by 2031 | Added Levelized Cost per Year (Billions)
Unconstrained GHG Gas Case | 14% | 0.0
Expected Case | -18% | 3.5
Coal Mandatory Retirement | -22% | 8.1
National Cap & Trade | -29% | 4.9

## Slide 41: Impact of Carbon on Efficient Frontier

## Slide 42: Resource Cost Tipping Point Analysis
 | Target Capital Cost ($/kW) | Required Capital Cost ($/kW) | Percent Reduction
CCCT Replaces SCCT | $1,609 | $1,255 | -22%
Wind Replaces Solar | $4,371 | $2,052 | -53%

## Slide 43: 2011 IRP Summary
Lower Market Prices
Slower Load Growth
Adequate Supply Through 2018
Continued Gas Reliance
40% Less Wind
Higher Conservation and Budgets ($1.4B over 20 years)
$1.7 Billion Investment in Generation Portfolio
Notes: Load Forecast Update -- load growth projection from 1.6% AARG to 1.3% AARG, before new conservation measures, from 1.4% to 1.1% after new conservation
DSM spending triples from $20MM to $60MM/yr. between now and 2018, with a 17% AARG 2011-2020, and 9% AARG 2011-31
Conservation meets ~50% of Avista load growth
25% of gas is peaking instead of 100% CCCT
40% less wind, result of lower growth and more expected hydro upgrades

## Slide 44: High Wind Penetration Scenarios: Change to Monthly Average Mid-C Prices
Notes: Understand impact to the power system with more than forecasted amount of wind generation
Uses IRP Expected Case for 2015
Adjust model to allow for negative pricing using -$40/MWh for Northwest hydro projects and -$10 to -$30/MWh for wind projects
Run 100 iterations for each of these scenarios
    Add 2,000 MW of wind
    Add 5,000 MW of wind
    Add 10,000 MW of wind

## Slide 45: High Wind Penetration Scenarios: Hours of 2015 Negative Prices

## Slide 46: High Wind Penetration Scenarios: Change to Avista Plant Operating Margins

## Slide 47: Palouse Wind Summary
RFP Process
  Issued Feb-11, contract executed Jun-11
  20-yr. cap of $62/MWh
  ~40% lower prices than late-09
Contract highlights
  ~104 MW, 39 aMW
  Online late 2012
  30-year term with buy-out option after year 10
  Winter peaking resource
  “Apprentice labor”

## Slide 48
Thank You