## Readme
This workbook provides a summary of cost assumptions and details on cost adjustments applied to the Generic Resources PSE will consider in the 2023 Electric Progress Report portfolio planning process. The majority of cost assumptions are sourced from the 2022 National Renewable Energy Laboratory (NREL) Annual Technology Baseline (ATB) cost report.
Objective
The objective of this document is to 1) provide updates PSE is making to Generic Resource operating assumptions; and 2) provide a detailed look at the captial costs breakdown and cost adjustments PSE has performed based on internal information. Costs provided may differ from the actual costs modeled in the 2023 Electric Progress Report as new information is available and assumptions are updated. The information contained in this document supercedes informpation presented in the document, "2023_ElectricProgressReport_GenericResourcesCostAdjustments.xlsx" posted to PSE's 2023 Electric Progress Report website on March 22, 2022.
Definitions
| Capital Cost | This document presents the CAPEX or total capital expenditure required to achieve commerical operation of the generation plant, as published in the 2022 NREL ATB. The 2022 NREL ATB does not provide an in-depth review of the numerous components which compose the total capital cost of a generating resource. Therefore, PSE has reviewed the source materials cited in the NREL ATB to get an understanding of the components of each technology's capital cost, for example: equipment costs, balance of plant costs and financing costs. Often times, the total capital costs of the source materials differed from the costs presented in the NREL ATB. In these cases, PSE used the ratio of the total capital cost of the source materials to the total capital cost of the NREL ATB to scale component costs to gain an understanding of the contribution of each component to the NREL ATB cost. In cases, where PSE deemed it necessary to make an adjustment to the capital cost of a resource, the cost is applied to the specific component which required an adjustment.
| Fixed O&M | Fixed operation and maintenance (O&M) costs are defined in alignment with the 2022 ATB. Fixed O&M includes administrative fees and labor, insurance, land lease payments, legal fees operating labor, property taxes, site security, taxes, project management, and general, scheduled, and unscheduled maintenance. Different technologies may include additinal items (NREL 2022).
| Variable O&M | Variable O&M costs are defined in alignment with the 2022 ATB. Variable cost components include consumables, such as water, chemicals, and catalysts; waste disposal, transformer maintenance, and an annualized present value of large componenet replacement over the technical life of the technology (including batteries; NREL 2022).
Other Notes:
Dollar values are in 2020 US Dollars, unless otherwise noted.
Production Tax Credits (PTCs) and Investment Tax Credits (ITCs) are not included in this workbook. The tax credits will be accounted for in a later step for modeling.
Reference:
BC Hydro (British Columbia Hydro and Power Authority). 2015. Pennask and Shinnish Creek Wind Farm Interconnection System Impact Re-Study. Report No: T&S Planning 2015-050. October 2015. Availalbe at: https://app.bchydro.com/content/dam/BCHydro/customer-portal/documents/accounts-billing/electrical-connections/Pennask-Shinnish-Wind-SIS-ReStudy-redacted.pdf
CAISO (California Independent System Operator). 2020. Variable Operations and Maintenance Cost Review, Final Proposal. October 22, 2022. Available at: https://stakeholdercenter.caiso.com/StakeholderInitiatives/Variable-operations-maintenance-cost-review.
EIA (U.S. Energy Information Administration). 2019. Annual Energy Outlook 2019. January 24, 2019. Available at: https://www.eia.gov/outlooks/archive/aeo19/ .
EIA. 2020. Capital Cost and Performance Characteric Estimates for Utility Scale Electric Power Generating Technolgies. Prepared by Sargent & Lundy. February 2020. Available at: https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2020.pdf.
EIA. 2022. Annual Energy Outlook 2022. March 3, 2022. Available at: https://www.eia.gov/outlooks/aeo/.
HDR. 2019. Generic Resource Costs for Integrated Resource Planning. Conducted on behalf of Puget Sound Energy. January 23, 2019. Revision 4. Available at: https://www.pse.com/IRP/Get-involved.
Mongrid, K., V. Viswanathan, J. Alam, C. Vartanian, V. Sprenkle. 2020. 2020 Grid energy storage technology cost and performance assessment. Pacific Northwest National Laboratory. Tech Reprot Pub. No. DOE/PA-0204. December 2020.
NREL (National Renewable Energy Laboratory). 2022. 2022 Annual Technology Baseline. Available at: https://atb.nrel.gov/electricity/2022/data.
PSE (Puget Sound Energy). 2021a. 2021 PSE Integrated Resource Plan. April 1, 2021. Available at: https://www.pse.com/IRP/Past-IRPs/2021-IRP.
PSE. 2021b. 2021 All-Source RFP for Renewable and Peak Capacity Resources. June 30, 2021. Available at: https://www.pse.com/en/pages/energy-supply/acquiring-energy.
S&P Global (S&P Global IQ Pro Platform). 2022. Availabel at: https://www.capitaliq.spglobal.com/web/client?auth=inherit#news/home. Accessed on May 19, 2022.
Severy, M., D. Overhus, L. Tugade, A. Copping. 2022. Preliminary data aggregation and analysis of the effects on fish, marine mammals, and other marine organisms, and the habitats that support them, from a proposed offshore wind farm off the coast of Grays Harbor, Washington. PNNL. January 2022.
Please refer to companion workbook on NREL ATB Cost Breakdown for complete listing of data sources.
Feldman, David, Vignesh Ramasamy, Ran Fu, Ashwin Ramdas, Jal Desai, and Robert Margolis. “U.S. Solar Photovoltaic System and Energy Storage Cost Benchmark: Q1 2020.” National Renewable Energy Lab. (NREL), Golden, CO (United States), January 27, 2021. https://doi.org/10.2172/1764908.

## Operating Life Assumptions
Operating Life by Resource
Generic resource operating assumptions for the 2023 Electric Progress Report
Technology | Capital Recovery Period (Years)1
Offshore Wind, WA | 30
Wind, BC | 30
Wind, WA | 30
Wind, MT | 30
Wind, ID/WY | 30
Solar, WA | 30
Solar, ID/WY | 30
Solar, DER (Residential) | 30
Biomass | 30
PHES, WA/OR2 | 40
PHES, MT2 | 40
Battery (2hr, Li-Ion) | 30
Battery (4hr, Li-Ion) | 30
Battery (6hr, Li-Ion) | 30
Battery, DER (Residential) | 30
Wind + Battery, WA | 30
Solar + Battery, WA | 30
Wind + Solar + Battery, WA | 30
Frame Peaker | 30
CCCT | 30
Recip Peaker | 30
Small Modular Nuclear | 30
Notes
1: Source: NREL 2022.
2: Though the NREL 2022 ATB assumes a 100 year operating life, PSE assumes the operating life will be the length of the FERC permitting cycle, at 40 years.

## O&M Costs Assumptions
O&M Costs by Resource - Comparison of Several Sources
Source: "R:\ResourcePlanning\2023 IRP\Generic Resource Costs\O&M_Costs\2023_IRP_O&M_Comparison_20220622.xlsx"
Fixed O&M
2023 Vintage, | Fixed Operating and Maintenance | Comparison of Sources
2020 U.S. Dollars | ($/kW-yr) | ($/kW-yr)
| 2023 Progress Report (NREL 2021; S&P Global 2022) | 2019 HDR Report (HDR 2019) | 2021 IRP Operating Assumptions (PSE 2021a) | 2022 ATB1 (NREL 2022) | FERC Form 1s2 (S&P Global 2022) | CAISO Defaults Values (CAISO 2020)
Offshore Wind, WA | 70.7845 | 142.6423 | 118.5491 | 70.7845 | -- | --
Wind, BC | 41.785 | 43.9814 | -- | 41.785 | -- | --
Wind, WA | 41.785 | 43.9814 | 43.7259 | 41.785 | -- | --
Wind, MT | 41.785 | 43.9814 | -- | 41.785 | -- | --
Wind, ID/WY | 41.785 | 43.9814 | -- | 41.785 | -- | --
Solar, WA | 19.3544 | 25.212 | 23.9366 | 19.3544 | -- | --
Solar, ID/WY | 19.3544 | 25.212 | -- | 19.3544 | -- | --
Solar, DER (Residential) | 25.482 | 32.3204 | -- | 25.482 | -- | --
Biomass | 151 | 410.3343 | 222.92 | 151 | -- | --
PHES, WA/OR | 17.82 | 20.6831 | 17.2302 | 17.82 | -- | --
PHES, MT | 17.82 | 20.6831 | 17.2302 | 17.82 | -- | --
Battery (2hr, Li-Ion) | 20.1009 | 24.4156 | 25.2939 | 20.1228 | -- | --
Battery (4hr, Li-Ion) | 32.8427 | 38.2281 | 34.3877 | 32.7612 | -- | --
Battery (6hr, Li-Ion) | 45.5845 | -- | -- | 45.4851 | -- | --
Battery, DER (Residential) | 98.0643 | -- | -- | 98.0643 | -- | --
Wind + Battery, WA3 | -- | -- | 69.0199 | -- | -- | --
Solar + Battery, WA3 | -- | -- | 49.2305 | 32.2377 | -- | --
Wind + Solar + Battery, WA3 | -- | -- | -- | -- | -- | --
Frame Peaker | 9.5187 | 4.6715 | 8.267 | 28 | 9.5187 | --
CCCT | 22.6725 | 16.8318 | 13.8569 | 21 | 22.6725 | --
Recip Peaker | 14.5301 | 4.4457 | 6.8963 | -- | 14.5301 | --
Small Modular Nuclear | 114 | -- | 10.7689 | 114 | -- | --
Notes
1: FOM for wind, solar, battery storage, and hybrid resources are presented in the 2022 ATB as a curve. Vintage year 2023 only is presented in this table for comparison with other FOM costs.
2: From the S&P Global IQ screener tool, averaged the "fixed production expence," for PSE existing resources in 2021. The Port Westward 2 "fixed production expense" from 2021 was adopted as the recipricating peaker fixed O&M.
3: Weighted averages (using nameplate capacities for hybrid configurations) are used to calculate the FOM for hybrid resources. Because FOM for the generating resource is a curve, the FOM for hybrid resources are also a curve.
Variable O&M
2023 Vintage, | Variable Operating and Maintenance | Comparison of Sources
2020 U.S. Dollars | ($/MWh) | ($/MWh)
| 2023 Progress Report (NREL 2021; CAISO 2020) | 2019 HDR Report (HDR 2019) | 2021 IRP Operating Assumptions (PSE 2021a) | 2022 ATB (NREL 2022) | FERC Form 1s1 (S&P Global 2022) | CAISO Defaults Values (CAISO 2020)
Offshore Wind, WA | 0 | 0 | 0 | 0 | -- | --
Wind, BC | 0 | 0 | -- | 0 | -- | --
Wind, WA | 0 | 0 | 0 | 0 | -- | --
Wind, MT | 0 | 0 | 0 | 0 | -- | --
Wind, ID/WY | 0 | 0 | 0 | 0 | -- | --
Solar, WA | 0 | 0 | 0 | 0 | -- | --
Solar, ID/WY | 0 | 0 | 0 | 0 | -- | --
Solar, DER (Residential) | 0 | 0 | 0 | 0 | -- | --
Biomass | 5.8 | 7.8453 | 6.6746 | 5.8 | -- | --
PHES, WA/OR | 0.5125 | 1.783 | 0 | 0.5125 | -- | --
PHES, MT | 0.5125 | 1.783 | 0 | 0.5125 | -- | --
Battery (2hr, Li-Ion) | 0 | 0 | 0 | 0 | -- | --
Battery (4hr, Li-Ion) | 0 | 0 | 0 | 0 | -- | --
Battery (6hr, Li-Ion) | 0 | 0 | 0 | 0 | -- | --
Battery, DER (Residential) | 0 | -- | 0 | 0 | -- | --
Wind + PHES, MT | 0 | -- | 0 | -- | -- | --
Wind + Battery, WA | 0 | -- | 0 | -- | -- | --
Solar + Battery, WA | 0 | -- | 0 | 0 | -- | --
Wind + Solar + Battery, WA | 0 | -- | -- | -- | -- | --
Frame Peaker2 | 1.0191 | 7.7978 | 8.4694 | 2 | 48.833 | 1.0191
CCCT3 | 6.1595 | 2.9955 | 3.58 | 5 | 4.1184 | 6.1595
Recip Peaker | 1.1557 | 6.3 | 7.5882 | -- | 4.4539 | 1.1557
Small Modular Nuclear | 2.84 | -- | 7.5382 | 2.84 | 0 | --
Notes
1: From the S&P Global IQ screener tool, averaged the "fixed production expence," for PSE existing resources in 2021. The Port Westward 2 "fixed production expense" from 2021 was adopted as the recipricating peaker fixed O&M.
2: CAISO default values calculated by dividing the default minimum load adder of $1.74/run-hour/MW by PSE's 20-year forecasted capacity factor for CCCTs of 33% (PSE 2021 IRP), then adding the energy O&M adder of $0.59/MWh.
3: The CAISO default value appears low; however, CAISO also provides a startup O&M adder of $52.13/start/MW, which will be applied to generic frame peakers in the 2023 Electric Progress Report.

## FOM Cost Curves
FOM cost curves across all available resources, all listings in 2020 dollars per kiloWatt-year
Source of FOM cost curves: 2022 NREL ATB, unless otherwise noted.
R:\ResourcePlanning\2023 IRP\Generic Resource Costs\2022 NREL ATB\2022 v1 Annual Technology Baseline Workbook Original 6-14-2022.xlsx
FOM ($/kW-yr)
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Offshore Wind | 70.7845 | 69.0358 | 67.521 | 66.1848 | 64.9896 | 63.9083 | 62.9213 | 62.0132 | 61.1725 | 60.3898 | 59.6577 | 58.9699 | 58.3215 | 57.7082 | 57.1263 | 56.5728 | 56.045 | 55.5408 | 55.058 | 54.5949 | 54.1499 | 53.7218 | 53.3092 | 52.9111 | 52.5265 | 52.1546 | 51.7944 | 51.4453
Wind, BC | 41.785 | 41.38 | 40.975 | 40.57 | 40.165 | 39.76 | 39.355 | 38.95 | 38.6579 | 38.3658 | 38.0736 | 37.7815 | 37.4894 | 37.1973 | 36.9051 | 36.613 | 36.3209 | 36.0288 | 35.7366 | 35.4445 | 35.1524 | 34.8603 | 34.5681 | 34.276 | 33.9839 | 33.6917 | 33.3996 | 33.1075
Wind, WA | 41.785 | 41.38 | 40.975 | 40.57 | 40.165 | 39.76 | 39.355 | 38.95 | 38.6579 | 38.3658 | 38.0736 | 37.7815 | 37.4894 | 37.1973 | 36.9051 | 36.613 | 36.3209 | 36.0288 | 35.7366 | 35.4445 | 35.1524 | 34.8603 | 34.5681 | 34.276 | 33.9839 | 33.6917 | 33.3996 | 33.1075
Wind, MT | 41.785 | 41.38 | 40.975 | 40.57 | 40.165 | 39.76 | 39.355 | 38.95 | 38.6579 | 38.3658 | 38.0736 | 37.7815 | 37.4894 | 37.1973 | 36.9051 | 36.613 | 36.3209 | 36.0288 | 35.7366 | 35.4445 | 35.1524 | 34.8603 | 34.5681 | 34.276 | 33.9839 | 33.6917 | 33.3996 | 33.1075
Wind, ID/WY | 41.785 | 41.38 | 40.975 | 40.57 | 40.165 | 39.76 | 39.355 | 38.95 | 38.6579 | 38.3658 | 38.0736 | 37.7815 | 37.4894 | 37.1973 | 36.9051 | 36.613 | 36.3209 | 36.0288 | 35.7366 | 35.4445 | 35.1524 | 34.8603 | 34.5681 | 34.276 | 33.9839 | 33.6917 | 33.3996 | 33.1075
Solar, WA | 19.3544 | 18.759 | 18.1654 | 17.5734 | 16.9831 | 16.3945 | 15.8073 | 15.2216 | 15.1209 | 15.0204 | 14.9202 | 14.8203 | 14.7206 | 14.6212 | 14.522 | 14.423 | 14.3242 | 14.2257 | 14.1274 | 14.0294 | 13.9315 | 13.8339 | 13.7364 | 13.6392 | 13.5422 | 13.4454 | 13.3488 | 13.2523
Solar, ID/WY | 19.3544 | 18.759 | 18.1654 | 17.5734 | 16.9831 | 16.3945 | 15.8073 | 15.2216 | 15.1209 | 15.0204 | 14.9202 | 14.8203 | 14.7206 | 14.6212 | 14.522 | 14.423 | 14.3242 | 14.2257 | 14.1274 | 14.0294 | 13.9315 | 13.8339 | 13.7364 | 13.6392 | 13.5422 | 13.4454 | 13.3488 | 13.2523
Solar, DER (Residential) | 25.482 | 23.7361 | 21.9903 | 20.2444 | 18.4986 | 16.7527 | 15.0068 | 13.261 | 13.1526 | 13.0442 | 12.9359 | 12.8275 | 12.7191 | 12.6107 | 12.5023 | 12.394 | 12.2856 | 12.1772 | 12.0688 | 11.9605 | 11.8521 | 11.7437 | 11.6353 | 11.5269 | 11.4186 | 11.3102 | 11.2018 | 11.0934
Biomass | 151 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
PHES, WA/OR | 17.82 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
PHES, MT | 17.82 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Battery, LI 2hr1 | 20.1009 | 19.0671 | 18.1093 | 17.5743 | 17.0755 | 16.4357 | 16.0779 | 15.6152 | 15.4294 | 15.2342 | 15.039 | 14.8438 | 14.6486 | 14.4534 | 14.2582 | 14.0631 | 13.8679 | 13.6727 | 13.4775 | 13.2823 | 13.0871 | 12.8919 | 12.6967 | 12.5015 | 12.3063 | 12.1112 | 11.916 | 11.7234
Battery, LI 4hr1 | 32.8427 | 30.5163 | 28.8742 | 27.6426 | 26.5479 | 25.3163 | 24.3583 | 23.4004 | 23.1196 | 22.827 | 22.5345 | 22.242 | 21.9495 | 21.657 | 21.3645 | 21.072 | 20.7795 | 20.487 | 20.1945 | 19.902 | 19.6095 | 19.317 | 19.0245 | 18.732 | 18.4395 | 18.147 | 17.8545 | 17.562
Battery, LI 6hr1 | 45.5845 | 41.9818 | 39.6574 | 37.7382 | 36.0547 | 34.236 | 32.6875 | 31.2395 | 30.863 | 30.4725 | 30.082 | 29.6915 | 29.301 | 28.9105 | 28.5201 | 28.1296 | 27.7391 | 27.3486 | 26.9581 | 26.5676 | 26.1771 | 25.7866 | 25.3961 | 25.0056 | 24.6151 | 24.2246 | 23.8341 | 23.4411
Battery, DER (Residential)1 | 98.0643 | 91.0356 | 84.3659 | 80.9541 | 77.9261 | 75.3263 | 72.8388 | 70.5872 | 69.7239 | 68.8416 | 67.9593 | 67.0769 | 66.1946 | 65.3123 | 64.43 | 63.5476 | 62.6653 | 61.783 | 60.9006 | 60.0183 | 59.136 | 58.2536 | 57.3713 | 56.489 | 55.6067 | 54.7243 | 53.842 | 52.9404
Wind + Battery, WA3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Solar + Battery, WA3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Wind + Solar + Battery, WA3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Frame Peaker2 | 9.5187 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
CCCT2 | 22.6725 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Reciprocating Peaker2 | 14.5301 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Small Modular Nuclear | 114 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Notes
1: Following the 2022 NREL ATB, the FOM for Li-ion batteries is 2.5% of the capital cost.
2: From 2021 Form 1s (scaled to vintage 2023).
3: Each element of the hybrid resource is modeled seperatly in AURORA. FOM for these elements are input into the model seperatly.

## Spur Line Assumptions
Proposed spur line lengths and costs for the 2023 Electric Progress Report generic resources
Resource | 2023 Proposed Tie Line Length10 | Tie Line Length Source | Capacity | Spur Line Size | Spur Line Cost | Total Spur Line Cost9 | Total Spur Line Cost
|  |  | (MW) | (kV) | ($M) | ($) | $/kW
Offshore Wind1 | 20 | Severy et. Al (2022) | 100 | 115 | 2.8 | 59000000 | 590
Wind, BC4 | 14 | BC Hydro (2015) | 100 | 115 | 2.8 | 42200000 | 422
Wind, WA2 | 4.5 | PSE 2021 All Source RFP Bids | 100 | 115 | 2.8 | 15600000 | 156
Wind, MT3 | 40.5 | PSE 2021 All Source RFP Bids | 100 | 115 | 2.8 | 116400000 | 1164
Wind, ID/WY3 | 40.5 | PSE 2021 All Source RFP Bids | 400 | 230 | 4.5 | 185250000 | 463.125
Solar, WA2 | 4.5 | PSE 2021 All Source RFP Bids | 100 | 115 | 2.8 | 15600000 | 156
Solar, ID/WY3 | 40.5 | PSE 2021 All Source RFP Bids | 400 | 230 | 4.5 | 185250000 | 463.125
Solar, DER (Residential) | -- | -- | 300 | -- | -- | --
Biomass5 | 2 | GIS Calculation | 15 | 115 | 2.8 | 8600000 | 573.3333
PHES, WA/OR6 | 17 | GIS Calculation | 100 | 115 | 2.8 | 50600000 | 506
PHES, MT6 | 6 | GIS Calculation | 100 | 115 | 2.8 | 19800000 | 198
Battery (2hr, Li-Ion)7 | 1 | PSE 2021 All Source RFP Bids | 100 | 115 | 2.8 | 5800000 | 58
Battery (4hr, Li-Ion)7 | 1 | PSE 2021 All Source RFP Bids | 100 | 115 | 2.8 | 5800000 | 58
Battery (6hr, Li-Ion)7 | 1 | PSE 2021 All Source RFP Bids | 100 | 115 | 2.8 | 5800000 | 58
Battery, DER (Residential) | -- | -- | NA | -- | -- | --
Wind + Battery, WA2 | 4.5 | PSE 2021 All Source RFP Bids | 150 | 115 | 2.8 | 15600000 | 104
Solar + Battery, WA2 | 4.5 | PSE 2021 All Source RFP Bids | 150 | 115 | 2.8 | 15600000 | 104
Wind + Solar + Battery, WA2 | 4.5 | PSE 2021 All Source RFP Bids | 250 | 115 | 2.8 | 15600000 | 62.4
Frame Peaker8 | 1 | PSE 2021 All Source RFP Bids | 225 | 115 | 2.8 | 5800000 | 25.7778
CCCT8 | 1 | PSE 2021 All Source RFP Bids | 336 | 230 | 4.5 | 7500000 | 22.3214
Recip Peaker8 | 1 | PSE 2021 All Source RFP Bids | 219 | 115 | 2.8 | 5800000 | 26.484
Small Modular Nuclear8 | 1 | PSE 2021 All Source RFP Bids | 600 | 230 | 4.5 | 7500000 | 12.5
Notes
1: Assumptions based upon the Grays Harbor Wind Project, which is proposed to make landfall approximatly 20 miles from Aberdeen, WA
2: OR/WA wind, solar, and hybrid resoruces from the 2021 RFP were combined to create this overall average.
3: ID, MT, and WY wind, solar, and hybrid resources spur line lengths from projects submitted to PSE's 2021 RFP process were combined to create this overall average.
4: This is the average inerconnection distance estimated for Shinish Creek and Pennask Wind Farms, located in south central BC.
5: Existing biomass plant interconnection distances were caluclated using GIS for plants located in ID, MT, Northern OR, and WA.
6: PHES spur line lengths were determined using data provided by PHES projects in development: WA/OR used an average of Swan Lake and Goldendale data; MT use Gordon Butte spur line length.
7: The average interconnection length for all batteries proposed in the 2021 RFP process, with outliers removed. Acutual value is 0.7.
8: Assumed to be have a similar interconnection length to the 2021 RFP batteries because the resource would be similarly sited.
9: Includes a $3M substation hook-up addition.
10: Miles are rounded to the nearest 0.5 mile.

## Capital Cost Curves
Cost curves across all available resources, all listings in 2020 dollars per kiloWatt
Capital Cost Curves
| Year | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Offshore Wind |  |  |  | 4728.1642 | 4599.8596 | 4495.027 | 4415.1774 | 4346.8899 | 4287.4173 | 4234.8859 | 4187.9604 | 4137.4299 | 4090.9462 | 4047.9091 | 4007.8425 | 3970.3628 | 3935.1559 | 3901.962 | 3870.5633 | 3840.7755 | 3812.4413 | 3785.4255 | 3759.6108 | 3734.8949 | 3711.1881 | 3688.4113 | 3666.4942 | 3645.3742 | 3624.9954 | 3605.3076 | 3586.2654
| Wind, BC |  |  |  | 1730.4 | 1662.6864 | 1594.9728 | 1529.1599 | 1463.1796 | 1397.0319 | 1330.7165 | 1264.2332 | 1251.5909 | 1238.9485 | 1226.3062 | 1213.6639 | 1201.0215 | 1188.3792 | 1175.7369 | 1163.0945 | 1150.4522 | 1137.8099 | 1125.1675 | 1112.5252 | 1099.8829 | 1087.2405 | 1074.5982 | 1061.9559 | 1049.3136 | 1036.6712 | 1024.0289 | 1011.3866
| Wind, WA |  |  |  | 1464.4 | 1407.0954 | 1349.7909 | 1294.0949 | 1238.2572 | 1182.2778 | 1126.1565 | 1069.8931 | 1059.1942 | 1048.4953 | 1037.7963 | 1027.0974 | 1016.3985 | 1005.6996 | 995.0006 | 984.3017 | 973.6028 | 962.9038 | 952.2049 | 941.506 | 930.807 | 920.1081 | 909.4092 | 898.7102 | 888.0113 | 877.3124 | 866.6134 | 855.9145
| Wind, MT |  |  |  | 2472.4 | 2375.6506 | 2278.9013 | 2184.8676 | 2090.5949 | 1996.0828 | 1901.3311 | 1806.3397 | 1788.2763 | 1770.2129 | 1752.1495 | 1734.0861 | 1716.0227 | 1697.9593 | 1679.8959 | 1661.8325 | 1643.7691 | 1625.7057 | 1607.6423 | 1589.5789 | 1571.5155 | 1553.4521 | 1535.3887 | 1517.3253 | 1499.2619 | 1481.1985 | 1463.1351 | 1445.0717
| Wind, ID/WY |  |  |  | 1771.525 | 1702.2021 | 1632.8792 | 1565.5022 | 1497.9538 | 1430.234 | 1362.3425 | 1294.2792 | 1281.3364 | 1268.3936 | 1255.4508 | 1242.508 | 1229.5652 | 1216.6224 | 1203.6796 | 1190.7369 | 1177.7941 | 1164.8513 | 1151.9085 | 1138.9657 | 1126.0229 | 1113.0801 | 1100.1373 | 1087.1945 | 1074.2517 | 1061.3089 | 1048.3661 | 1035.4234
| Solar, WA |  |  |  | 1229.784 | 1177.0573 | 1124.3306 | 1072.4269 | 1020.4415 | 968.3744 | 916.2258 | 863.9958 | 856.2969 | 848.5979 | 840.899 | 833.2 | 825.5011 | 817.8022 | 810.1032 | 802.4043 | 794.7053 | 787.0064 | 779.3074 | 771.6085 | 763.9096 | 756.2106 | 748.5117 | 740.8127 | 733.1138 | 725.4148 | 717.7159 | 710.017
| Solar, ID/WY |  |  |  | 1536.909 | 1471.0144 | 1405.1198 | 1340.2537 | 1275.2854 | 1210.2152 | 1145.0431 | 1079.7692 | 1070.1476 | 1060.5259 | 1050.9042 | 1041.2826 | 1031.6609 | 1022.0392 | 1012.4175 | 1002.7959 | 993.1742 | 983.5525 | 973.9309 | 964.3092 | 954.6875 | 945.0659 | 935.4442 | 925.8225 | 916.2009 | 906.5792 | 896.9575 | 887.3359
| Solar, DER (Residential) |  |  |  | 2286.9841 | 2105.4762 | 1923.9683 | 1742.4603 | 1560.9524 | 1379.4445 | 1197.9365 | 1016.4286 | 1005.1612 | 993.8937 | 982.6262 | 971.3588 | 960.0913 | 948.8238 | 937.5564 | 926.2889 | 915.0214 | 903.754 | 892.4865 | 881.219 | 869.9516 | 858.6841 | 847.4166 | 836.1492 | 824.8817 | 813.6143 | 802.3468 | 791.0793
| Biomass |  |  |  | 4905.5466 | 4874.1812 | 4842.1302 | 4821.9069 | 4801.5619 | 4781.0984 | 4760.513 | 4739.8064 | 4708.083 | 4676.3598 | 4644.6398 | 4612.9139 | 4581.1922 | 4549.4697 | 4517.7498 | 4486.0271 | 4454.3052 | 4422.584 | 4390.8583 | 4359.1361 | 4327.4137 | 4295.6921 | 4263.9734 | 4232.2507 | 4200.5279 | 4168.8037 | 4137.0817 | 4105.3596
| PHES, WA/OR |  |  |  | 3910.0622 | 3910.0622 | 3910.0622 | 3914.9135 | 3919.768 | 3924.6258 | 3929.4868 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351
| PHES, MT |  |  |  | 3602.0622 | 3602.0622 | 3602.0622 | 3606.5314 | 3611.0035 | 3615.4786 | 3619.9567 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377
| Battery, LI 2hr |  |  |  | 804.0367 | 762.6859 | 724.3709 | 702.9727 | 683.0202 | 657.4288 | 643.1152 | 624.6084 | 617.1753 | 609.3677 | 601.5601 | 593.7525 | 585.9449 | 578.1373 | 570.3297 | 562.5221 | 554.7145 | 546.9069 | 539.0993 | 531.2917 | 523.4841 | 515.6764 | 507.8688 | 500.0612 | 492.2536 | 484.446 | 476.6384 | 468.9356
| Battery, LI 4hr |  |  |  | 1313.7082 | 1220.6539 | 1154.9685 | 1105.7044 | 1061.9142 | 1012.6501 | 974.3336 | 936.0171 | 924.7822 | 913.082 | 901.3817 | 889.6815 | 877.9813 | 866.2811 | 854.5809 | 842.8807 | 831.1805 | 819.4802 | 807.78 | 796.0798 | 784.3796 | 772.6794 | 760.9792 | 749.279 | 737.5788 | 725.8785 | 714.1783 | 702.4781
| Battery, LI 6hr |  |  |  | 1823.3798 | 1679.2718 | 1586.2945 | 1509.5292 | 1442.1864 | 1369.4396 | 1307.5009 | 1249.5805 | 1234.5206 | 1218.9008 | 1203.2811 | 1187.6613 | 1172.0416 | 1156.4218 | 1140.802 | 1125.1823 | 1109.5625 | 1093.9428 | 1078.323 | 1062.7033 | 1047.0835 | 1031.4637 | 1015.844 | 1000.2242 | 984.6045 | 968.9847 | 953.365 | 937.6447
| Battery, DER (Residential) |  |  |  | 3922.573 | 3641.4242 | 3374.6375 | 3238.1631 | 3117.0424 | 3013.052 | 2913.5515 | 2823.4879 | 2788.9573 | 2753.6641 | 2718.3709 | 2683.0778 | 2647.7846 | 2612.4914 | 2577.1982 | 2541.905 | 2506.6118 | 2471.3187 | 2436.0255 | 2400.7323 | 2365.4391 | 2330.1459 | 2294.8527 | 2259.5595 | 2224.2664 | 2188.9732 | 2153.68 | 2117.6159
| Wind + Battery, WA1 |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Solar + Battery, WA1 |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Wind + Solar + Battery, WA1 |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Frame Peaker |  |  |  | 943.7155 | 921.8815 | 904.8995 | 895.1954 | 883.0654 | 875.7874 | 868.5094 | 863.6574 | 857.5924 | 852.7404 | 847.8884 | 844.2494 | 839.3974 | 834.5453 | 829.6933 | 826.0543 | 821.2023 | 816.3503 | 811.4983 | 807.8593 | 803.0073 | 798.1553 | 793.3033 | 789.6643 | 784.8123 | 781.1733 | 779.9603 | 777.5343
| CCCT |  |  |  | 987.0888 | 973.5978 | 964.6039 | 957.8584 | 949.9887 | 944.3674 | 938.7462 | 935.3734 | 929.7522 | 926.3795 | 921.8825 | 918.5097 | 914.0128 | 910.64 | 906.143 | 902.7703 | 898.2733 | 894.9006 | 891.5278 | 887.0308 | 883.6581 | 879.1611 | 875.7884 | 871.2914 | 867.9186 | 863.4216 | 861.1731 | 858.9247
| Reciprocating Peaker |  |  |  | 2045.246 | 2017.6825 | 2001.3624 | 1982.8689 | 1958.4339 | 1932.7306 | 1908.0154 | 1889.1544 | 1872.3999 | 1855.715 | 1839.7399 | 1826.3146 | 1811.82 | 1799.7024 | 1791.8774 | 1784.4688 | 1777.0703 | 1769.2044 | 1760.0334 | 1750.5578 | 1740.6259 | 1729.9755 | 1719.346 | 1709.6765 | 1699.5918 | 1690.4241 | 1682.4881 | 1673.695
| Small Modular Nuclear |  |  |  | 10930.3353 | 10860.709 | 10791.0906 | 10769.8712 | 10748.2791 | 10726.32 | 10703.9822 | 10681.2647 | 10610.0521 | 10538.8426 | 10467.639 | 10396.4217 | 10325.2147 | 10254.0052 | 10182.8016 | 10111.5917 | 10040.3835 | 9969.1778 | 9897.9616 | 9826.753 | 9755.544 | 9684.335 | 9613.1349 | 9541.9249 | 9470.7163 | 9399.5025 | 9328.294 | 9257.0856
| Hybrid Wind2 |  |  |  | 1334.6666 | 1282.4387 | 1230.2109 | 1179.4491 | 1128.5581 | 1077.538 | 1026.3886 | 975.1097 | 965.3586 | 955.6075 | 945.8564 | 936.1053 | 926.3542 | 916.6031 | 906.852 | 897.1009 | 887.3498 | 877.5987 | 867.8476 | 858.0965 | 848.3454 | 838.5943 | 828.8432 | 819.0921 | 809.341 | 799.59 | 789.8389 | 780.0878
| Hybrid Solar2 |  |  |  | 1088.7108 | 1042.0325 | 995.3543 | 949.4047 | 903.3827 | 857.2884 | 811.122 | 764.8835 | 758.0677 | 751.252 | 744.4362 | 737.6204 | 730.8047 | 723.9889 | 717.1731 | 710.3574 | 703.5416 | 696.7258 | 689.9101 | 683.0943 | 676.2785 | 669.4628 | 662.647 | 655.8312 | 649.0155 | 642.1997 | 635.3839 | 628.5682
| Hybrid Battery2 |  |  |  | 1262.1588 | 1172.7559 | 1109.6479 | 1062.317 | 1020.245 | 972.9141 | 936.1011 | 899.2881 | 888.4941 | 877.253 | 866.0119 | 854.7708 | 843.5297 | 832.2886 | 821.0474 | 809.8063 | 798.5652 | 787.3241 | 776.083 | 764.8419 | 753.6008 | 742.3597 | 731.1186 | 719.8775 | 708.6364 | 697.3953 | 686.1542 | 674.9131
| Hybrid - Triple Wind2 |  |  |  | 1291.4493 | 1240.9126 | 1190.3759 | 1141.2578 | 1092.0147 | 1042.6467 | 993.1535 | 943.535 | 934.0997 | 924.6643 | 915.229 | 905.7936 | 896.3583 | 886.9229 | 877.4876 | 868.0522 | 858.6169 | 849.1815 | 839.7462 | 830.3108 | 820.8755 | 811.4401 | 802.0048 | 792.5694 | 783.1341 | 773.6987 | 764.2634 | 754.828
| Hybrid-Triple Solar2 |  |  |  | 1057.3371 | 1012.004 | 966.6709 | 922.0454 | 877.3497 | 832.5837 | 787.7477 | 742.8417 | 736.2223 | 729.603 | 722.9836 | 716.3642 | 709.7449 | 703.1255 | 696.5062 | 689.8868 | 683.2675 | 676.6481 | 670.0288 | 663.4094 | 656.7901 | 650.1707 | 643.5513 | 636.932 | 630.3126 | 623.6933 | 617.0739 | 610.4546
| Hybrid-Triple Battery2 |  |  |  | 1251.0078 | 1162.3948 | 1099.8444 | 1052.9316 | 1011.2313 | 964.3185 | 927.8308 | 891.3431 | 880.6444 | 869.5026 | 858.3608 | 847.219 | 836.0772 | 824.9354 | 813.7936 | 802.6518 | 791.5101 | 780.3683 | 769.2265 | 758.0847 | 746.9429 | 735.8011 | 724.6593 | 713.5175 | 702.3757 | 691.234 | 680.0922 | 668.9504
Notes
1: Placeholder rows for PSE internal use: see rows 27-32 for hybrid component capital costs.
2: Each element of the hybrid resource is modeled seperatly in AURORA. Capital costs for these elements are input into the model seperatly.
Percent change per year (2022 ATB)
| Year | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Offshore Wind |  |  |  |  | -2.714% | -2.279% | -1.776% | -1.547% | -1.368% | -1.225% | -1.108% | -1.207% | -1.123% | -1.052% | -0.9898% | -0.9352% | -0.8867% | -0.8435% | -0.8047% | -0.7696% | -0.7377% | -0.7086% | -0.6819% | -0.6574% | -0.6347% | -0.6137% | -0.5942% | -0.576% | -0.559% | -0.5431% | -0.5282%
| Wind, BC |  |  |  |  | -3.913% | -4.073% | -4.126% | -4.315% | -4.521% | -4.747% | -4.996% | -1% | -1.01% | -1.02% | -1.031% | -1.042% | -1.053% | -1.064% | -1.075% | -1.087% | -1.099% | -1.111% | -1.124% | -1.136% | -1.149% | -1.163% | -1.176% | -1.19% | -1.205% | -1.22% | -1.235%
| Wind, WA |  |  |  |  | -3.913% | -4.073% | -4.126% | -4.315% | -4.521% | -4.747% | -4.996% | -1% | -1.01% | -1.02% | -1.031% | -1.042% | -1.053% | -1.064% | -1.075% | -1.087% | -1.099% | -1.111% | -1.124% | -1.136% | -1.149% | -1.163% | -1.176% | -1.19% | -1.205% | -1.22% | -1.235%
| Wind, MT |  |  |  |  | -3.913% | -4.073% | -4.126% | -4.315% | -4.521% | -4.747% | -4.996% | -1% | -1.01% | -1.02% | -1.031% | -1.042% | -1.053% | -1.064% | -1.075% | -1.087% | -1.099% | -1.111% | -1.124% | -1.136% | -1.149% | -1.163% | -1.176% | -1.19% | -1.205% | -1.22% | -1.235%
| Wind, ID/WY |  |  |  |  | -3.913% | -4.073% | -4.126% | -4.315% | -4.521% | -4.747% | -4.996% | -1% | -1.01% | -1.02% | -1.031% | -1.042% | -1.053% | -1.064% | -1.075% | -1.087% | -1.099% | -1.111% | -1.124% | -1.136% | -1.149% | -1.163% | -1.176% | -1.19% | -1.205% | -1.22% | -1.235%
| Solar, WA |  |  |  |  | -4.287% | -4.48% | -4.616% | -4.847% | -5.102% | -5.385% | -5.701% | -0.8911% | -0.8991% | -0.9073% | -0.9156% | -0.924% | -0.9326% | -0.9414% | -0.9504% | -0.9595% | -0.9688% | -0.9783% | -0.9879% | -0.9978% | -1.008% | -1.018% | -1.029% | -1.039% | -1.05% | -1.061% | -1.073%
| Solar, ID/WY |  |  |  |  | -4.287% | -4.48% | -4.616% | -4.847% | -5.102% | -5.385% | -5.701% | -0.8911% | -0.8991% | -0.9073% | -0.9156% | -0.924% | -0.9326% | -0.9414% | -0.9504% | -0.9595% | -0.9688% | -0.9783% | -0.9879% | -0.9978% | -1.008% | -1.018% | -1.029% | -1.039% | -1.05% | -1.061% | -1.073%
| Solar, DER (Residential) |  |  |  |  | -7.937% | -8.621% | -9.434% | -10.42% | -11.63% | -13.16% | -15.15% | -1.109% | -1.121% | -1.134% | -1.147% | -1.16% | -1.174% | -1.188% | -1.202% | -1.216% | -1.231% | -1.247% | -1.262% | -1.279% | -1.295% | -1.312% | -1.33% | -1.348% | -1.366% | -1.385% | -1.404%
| Biomass |  |  |  |  | -0.6394% | -0.6576% | -0.4177% | -0.4219% | -0.4262% | -0.4306% | -0.435% | -0.6693% | -0.6738% | -0.6783% | -0.6831% | -0.6877% | -0.6925% | -0.6972% | -0.7022% | -0.7071% | -0.7121% | -0.7174% | -0.7225% | -0.7277% | -0.733% | -0.7384% | -0.744% | -0.7495% | -0.7552% | -0.7609% | -0.7668%
| PHES, WA/OR |  |  |  |  | 0% | 0% | 0.1241% | 0.124% | 0.1239% | 0.1239% | 0.1238% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| PHES, MT |  |  |  |  | 0% | 0% | 0.1241% | 0.124% | 0.1239% | 0.1239% | 0.1238% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Battery, LI 2hr |  |  |  |  | -5.143% | -5.024% | -2.954% | -2.838% | -3.747% | -2.177% | -2.878% | -1.19% | -1.265% | -1.281% | -1.298% | -1.315% | -1.332% | -1.35% | -1.369% | -1.388% | -1.407% | -1.428% | -1.448% | -1.47% | -1.491% | -1.514% | -1.537% | -1.561% | -1.586% | -1.612% | -1.616%
| Battery, LI 4hr |  |  |  |  | -7.083% | -5.381% | -4.265% | -3.96% | -4.639% | -3.784% | -3.933% | -1.2% | -1.265% | -1.281% | -1.298% | -1.315% | -1.333% | -1.351% | -1.369% | -1.388% | -1.408% | -1.428% | -1.448% | -1.47% | -1.492% | -1.514% | -1.538% | -1.562% | -1.586% | -1.612% | -1.638%
| Battery, LI 6hr |  |  |  |  | -7.903% | -5.537% | -4.839% | -4.461% | -5.044% | -4.523% | -4.43% | -1.205% | -1.265% | -1.281% | -1.298% | -1.315% | -1.333% | -1.351% | -1.369% | -1.388% | -1.408% | -1.428% | -1.449% | -1.47% | -1.492% | -1.514% | -1.538% | -1.562% | -1.586% | -1.612% | -1.649%
| Battery, DER (Residential) |  |  |  |  | -7.167% | -7.326% | -4.044% | -3.74% | -3.336% | -3.302% | -3.091% | -1.223% | -1.265% | -1.282% | -1.298% | -1.315% | -1.333% | -1.351% | -1.369% | -1.388% | -1.408% | -1.428% | -1.449% | -1.47% | -1.492% | -1.515% | -1.538% | -1.562% | -1.587% | -1.612% | -1.675%
| Wind + Battery, WA |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Solar + Battery, WA |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Wind + Solar + Battery, WA |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Frame Peaker |  |  |  |  | -2.314% | -1.842% | -1.072% | -1.355% | -0.8242% | -0.831% | -0.5587% | -0.7022% | -0.5658% | -0.569% | -0.4292% | -0.5747% | -0.578% | -0.5814% | -0.4386% | -0.5874% | -0.5908% | -0.5944% | -0.4484% | -0.6006% | -0.6042% | -0.6079% | -0.4587% | -0.6144% | -0.4637% | -0.1553% | -0.311%
| CCCT |  |  |  |  | -1.367% | -0.9238% | -0.6993% | -0.8216% | -0.5917% | -0.5952% | -0.3593% | -0.601% | -0.3628% | -0.4854% | -0.3659% | -0.4896% | -0.369% | -0.4938% | -0.3722% | -0.4981% | -0.3755% | -0.3769% | -0.5044% | -0.3802% | -0.5089% | -0.3836% | -0.5135% | -0.3871% | -0.5181% | -0.2604% | -0.2611%
| Reciprocating Peaker3 |  |  |  |  | -1.348% | -0.8089% | -0.924% | -1.232% | -1.312% | -1.279% | -0.9885% | -0.8869% | -0.8911% | -0.8609% | -0.7297% | -0.7937% | -0.6688% | -0.4348% | -0.4135% | -0.4146% | -0.4426% | -0.5184% | -0.5384% | -0.5674% | -0.6119% | -0.6144% | -0.5624% | -0.5899% | -0.5394% | -0.4695% | -0.5226%
| Small Modular Nuclear |  |  |  |  | -0.637% | -0.641% | -0.1966% | -0.2005% | -0.2043% | -0.2083% | -0.2122% | -0.6667% | -0.6712% | -0.6756% | -0.6804% | -0.6849% | -0.6897% | -0.6944% | -0.6993% | -0.7042% | -0.7092% | -0.7144% | -0.7194% | -0.7246% | -0.7299% | -0.7352% | -0.7408% | -0.7463% | -0.7519% | -0.7576% | -0.7634%
| Hybrid Wind |  |  |  |  | -3.913% | -4.073% | -4.126% | -4.315% | -4.521% | -4.747% | -4.996% | -1% | -1.01% | -1.02% | -1.031% | -1.042% | -1.053% | -1.064% | -1.075% | -1.087% | -1.099% | -1.111% | -1.124% | -1.136% | -1.149% | -1.163% | -1.176% | -1.19% | -1.205% | -1.22% | -1.235%
| Hybrid Solar |  |  |  |  | -4.287% | -4.48% | -4.616% | -4.847% | -5.102% | -5.385% | -5.701% | -0.8911% | -0.8991% | -0.9073% | -0.9156% | -0.924% | -0.9326% | -0.9414% | -0.9504% | -0.9595% | -0.9688% | -0.9783% | -0.9879% | -0.9978% | -1.008% | -1.018% | -1.029% | -1.039% | -1.05% | -1.061% | -1.073%
| Hybrid Battery |  |  |  |  | -7.083% | -5.381% | -4.265% | -3.96% | -4.639% | -3.784% | -3.933% | -1.2% | -1.265% | -1.281% | -1.298% | -1.315% | -1.333% | -1.351% | -1.369% | -1.388% | -1.408% | -1.428% | -1.448% | -1.47% | -1.492% | -1.514% | -1.538% | -1.562% | -1.586% | -1.612% | -1.638%
| Hybrid - Triple Wind |  |  |  |  | -3.913% | -4.073% | -4.126% | -4.315% | -4.521% | -4.747% | -4.996% | -1% | -1.01% | -1.02% | -1.031% | -1.042% | -1.053% | -1.064% | -1.075% | -1.087% | -1.099% | -1.111% | -1.124% | -1.136% | -1.149% | -1.163% | -1.176% | -1.19% | -1.205% | -1.22% | -1.235%
| Hybrid-Triple Solar |  |  |  |  | -4.287% | -4.48% | -4.616% | -4.847% | -5.102% | -5.385% | -5.701% | -0.8911% | -0.8991% | -0.9073% | -0.9156% | -0.924% | -0.9326% | -0.9414% | -0.9504% | -0.9595% | -0.9688% | -0.9783% | -0.9879% | -0.9978% | -1.008% | -1.018% | -1.029% | -1.039% | -1.05% | -1.061% | -1.073%
| Hybrid-Triple Battery |  |  |  |  | -7.083% | -5.381% | -4.265% | -3.96% | -4.639% | -3.784% | -3.933% | -1.2% | -1.265% | -1.281% | -1.298% | -1.315% | -1.333% | -1.351% | -1.369% | -1.388% | -1.408% | -1.428% | -1.448% | -1.47% | -1.492% | -1.514% | -1.538% | -1.562% | -1.586% | -1.612% | -1.638%
Notes
3: Recipricating peaker technology was not included in the 2022 ATB. This capital cost curve was sourced from the 2022 EIA AEO (EIA 2022).

## Capital Cost Comparisons
2023 Vintage, 2020$ |  | 2021 IRP | 2023 PR, 2021 ATB | 2023 PR, 2022 ATB
| Offshore Wind | 5658.1001 | 4807.7765 | 4728.1642
| Wind, BC | -- | 1660.8194 | 1730.4
| Wind, WA | 1867.6881 | 1427.5558 | 1464.4
| Wind, MT | 1864.3261 | 1801.1283 | 1890.4
| Wind, ID/WY | 1864.3261 | 1696.8832 | 1771.525
| Solar, WA | 1727.3344 | 1360.4149 | 1229.784
| Solar, ID/WY | 1727.3344 | 1624.5323 | 1536.909
| Solar, DER (Residential) | 3771.7947 | 2253.2786 | 2286.9841
| Biomass | 7396.1727 | 4948.7418 | 4905.5466
| PHES, WA/OR | 2790.6197 | -- | 3910.0622
| PHES, MT | 2790.6197 | -- | 3602.0622
| Battery, LI 2hr | 1148.5186 | 787.2661 | 804.9102
| Battery, LI 4hr | 2032.2211 | 1287.3478 | 1310.4488
| Battery, LI 6hr | -- | 1790.7555 | 1819.4037
| Battery, DER (Residential) | -- | 3631.6263 | 3922.573
| Wind + Battery, WA | 2714.586 | 1285.4151 | 1309.4354
| Solar + Battery, WA | 2588.2677 | 1225.7472 | 1145.4648
| Wind + Solar + Battery, WA | -- | 1572.5154 | 1189.0802
| Frame Peaker | 1002.6813 | 1005.0059 | 943.7155
| CCCT | 1308.6116 | 1079.1537 | 987.0888
| Reciprocating Peaker | 1768.5436 | -- | 2045.246
| Small Modular Nuclear | -- | -- | 10930.3353
| Battery (4hr, Flow) | 2682.3088 | -- | --
| Battery (6hr, Flow) | 3713.8926 | -- | --

## Offshore Wind
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 1005
Capital Cost Component | $/kW | % of Total | $/kW | Adder | $/kW | $/kW
Turbine capital costs
SUB TOTAL | 1301 | 24.42% | 1010.2743 | 0 | 1010.2743 | 1010.2743
Balance of System |  |  |  |  | 0
Development | 165 | 3.097% | 128.1286 | 0 | 128.1286 | 128.1286
Engineering & Mgmt | 85 | 1.595% | 66.0056 | 0 | 66.0056 | 66.0056
Substructure & foundation | 1438 | 26.99% | 1116.6598 | 0 | 1116.6598 | 1116.6598
Port & staging,logistics,transport | 44 | 0.8258% | 34.1676 | 0 | 34.1676 | 34.1676
electrical infrastructure | 979 | 18.37% | 760.2294 | 590 | 1350.2294 | 1350.2294
Assembly & installation | 439 | 8.239% | 340.8996 | 0 | 340.8996 | 340.8996
Lease price | 88 | 1.652% | 68.3352 | 0 | 68.3352 | 68.3352
SUB TOTAL | 3237 | 60.75% | 2513.6494 | 0 | 3104.4259 | 3104.4259
Soft Costs |  |  |  |  | 0
Insurance during construction | 52 | 0.976% | 40.3799 | 0 | 40.3799 | 40.3799
Decommissioning bond | 76 | 1.426% | 59.0168 | 0 | 59.0168 | 59.0168
construction financing | 221 | 4.148% | 171.6146 | 0 | 171.6146 | 171.6146
contingency | 389 | 7.301% | 302.0728 | 0 | 302.0728 | 302.0728
Plant commissioning | 52 | 0.976% | 40.3799 | 0 | 40.3799 | 40.3799
SUB TOTAL | 790 | 14.83% | 613.464 | 0 | 613.464 | 613.464
Total CAPEX | 5328 | 100% | 4137.3876 | 0 | 4728.1642 | 4728.1642
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB, Moderate Class 8 | 4137.3876 | 4025.1145 | 3933.3806 | 3863.5081 | 3803.753 | 3751.7114 | 3705.7437 | 3664.6815 | 3620.4646 | 3579.7891 | 3542.1294 | 3507.069 | 3474.2723 | 3443.4645 | 3414.4181 | 3386.9426 | 3360.8767 | 3336.0829 | 3312.4426 | 3289.8534 | 3268.2258 | 3247.4811 | 3227.5502 | 3208.3716 | 3189.8905 | 3172.0581 | 3154.8302 | 3138.1673
% change on year | -- | 0.027136 | 0.02279 | 0.017764 | 0.015467 | 0.013682 | 0.012252 | 0.011081 | 0.012066 | 0.011235 | 0.01052 | 0.0098981 | 0.0093516 | 0.0088674 | 0.0084352 | 0.0080469 | 0.007696 | 0.0073772 | 0.0070862 | 0.0068195 | 0.006574 | 0.0063474 | 0.0061373 | 0.0059422 | 0.0057603 | 0.0055903 | 0.0054311 | 0.0052817
After PSE Adjustments | 4728.1642 | 4599.8596 | 4495.027 | 4415.1774 | 4346.8899 | 4287.4173 | 4234.8859 | 4187.9604 | 4137.4299 | 4090.9462 | 4047.9091 | 4007.8425 | 3970.3628 | 3935.1559 | 3901.962 | 3870.5633 | 3840.7755 | 3812.4413 | 3785.4255 | 3759.6108 | 3734.8949 | 3711.1881 | 3688.4113 | 3666.4942 | 3645.3742 | 3624.9954 | 3605.3076 | 3586.2654

## Wind BC
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 200
Capital Cost Component | $/kW | % of Total | $/kW | Adder | $/kW | $/kW
Turbine capital cost
Rotor module | 287 | 19.99% | 261.4978 | 0 | 261.4978 | 261.4978
Nacelle module | 488 | 33.98% | 444.6373 | 0 | 444.6373 | 444.6373
Tower module | 215 | 14.97% | 195.8955 | 0 | 195.8955 | 195.8955
total | 991 | 69.01% | 902.9418 | 0 | 902.0306 | 902.0306
Balance of System |  |  |  |  | 0
Dev cost | 16 | 1.114% | 14.5783 | 0 | 14.5783 | 14.5783
Engineering & Mgmt | 18 | 1.253% | 16.4006 | 0 | 16.4006 | 16.4006
Foundation | 59 | 4.109% | 53.7574 | 0 | 53.7574 | 53.7574
Site access & staging | 44 | 3.064% | 40.0903 | 0 | 40.0903 | 40.0903
Assembly & installation | 44 | 3.064% | 40.0903 | 0 | 40.0903 | 40.0903
electrical infrastructure | 145 | 10.1% | 132.1156 | 422 | 554.1156 | 554.1156
Total | 326 | 22.7% | 297.0323 | 0 | 719.0323 | 719.0323
financial costs
Construction financing | 34 | 2.368% | 30.9788 | 0 | 30.9788 | 30.9788
Contingency fund | 86 | 5.989% | 78.3582 | 0 | 78.3582 | 78.3582
Total | 120 | 8.357% | 109.337 | 0 | 109.337 | 109.337
Total CAPEX | 1436 | 100% | 1308.4 | 0 | 1730.4 | 1730.4
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB, Class 4 | 1308.4 | 1257.2 | 1206 | 1156.2372 | 1106.3478 | 1056.3318 | 1006.189 | 955.9193 | 946.3601 | 936.8009 | 927.2417 | 917.6825 | 908.1233 | 898.5641 | 889.0049 | 879.4457 | 869.8865 | 860.3273 | 850.7682 | 841.209 | 831.6498 | 822.0906 | 812.5314 | 802.9722 | 793.413 | 783.8538 | 774.2946 | 764.7354
% change on year | -- | 0.039132 | 0.040725 | 0.041263 | 0.043148 | 0.045208 | 0.047469 | 0.049961 | 0.01 | 0.010101 | 0.010204 | 0.010309 | 0.010417 | 0.010526 | 0.010638 | 0.010753 | 0.01087 | 0.010989 | 0.011111 | 0.011236 | 0.011364 | 0.011494 | 0.011628 | 0.011765 | 0.011905 | 0.012048 | 0.012195 | 0.012346
After PSE Adjustments | 1730.4 | 1662.6864 | 1594.9728 | 1529.1599 | 1463.1796 | 1397.0319 | 1330.7165 | 1264.2332 | 1251.5909 | 1238.9485 | 1226.3062 | 1213.6639 | 1201.0215 | 1188.3792 | 1175.7369 | 1163.0945 | 1150.4522 | 1137.8099 | 1125.1675 | 1112.5252 | 1099.8829 | 1087.2405 | 1074.5982 | 1061.9559 | 1049.3136 | 1036.6712 | 1024.0289 | 1011.3866

## Wind WA
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 200
Capital Cost Component | $/kW | % of Total | $/kW | Adder | $/kW | $/kW
Turbine capital cost
Rotor module | 287 | 19.99% | 261.4978 | 0 | 261.4978 | 261.4978
Nacelle module | 488 | 33.98% | 444.6373 | 0 | 444.6373 | 444.6373
Tower module | 215 | 14.97% | 195.8955 | 0 | 195.8955 | 195.8955
total | 991 | 69.01% | 902.9418 | 0 | 902.0306 | 902.0306
Balance of System
Dev cost | 16 | 1.114% | 14.5783 | 0 | 14.5783 | 14.5783
Engineering & Mgmt | 18 | 1.253% | 16.4006 | 0 | 16.4006 | 16.4006
Foundation | 59 | 4.109% | 53.7574 | 0 | 53.7574 | 53.7574
Site access & staging | 44 | 3.064% | 40.0903 | 0 | 40.0903 | 40.0903
Assembly & installation | 44 | 3.064% | 40.0903 | 0 | 40.0903 | 40.0903
electrical infrastructure | 145 | 10.1% | 132.1156 | 156 | 288.1156 | 288.1156
Total | 326 | 22.7% | 297.0323 | 0 | 453.0323 | 453.0323
financial costs
Construction financing | 34 | 2.368% | 30.9788 | 0 | 30.9788 | 30.9788
Contingency fund | 86 | 5.989% | 78.3582 | 0 | 78.3582 | 78.3582
Total | 120 | 8.357% | 109.337 | 0 | 109.337 | 109.337
Total CAPEX | 1436 | 100% | 1308.4 | 0 | 1464.4 | 1464.4
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB, Class 4 | 1308.4 | 1257.2 | 1206 | 1156.2372 | 1106.3478 | 1056.3318 | 1006.189 | 955.9193 | 946.3601 | 936.8009 | 927.2417 | 917.6825 | 908.1233 | 898.5641 | 889.0049 | 879.4457 | 869.8865 | 860.3273 | 850.7682 | 841.209 | 831.6498 | 822.0906 | 812.5314 | 802.9722 | 793.413 | 783.8538 | 774.2946 | 764.7354
% change on year | -- | 0.039132 | 0.040725 | 0.041263 | 0.043148 | 0.045208 | 0.047469 | 0.049961 | 0.01 | 0.010101 | 0.010204 | 0.010309 | 0.010417 | 0.010526 | 0.010638 | 0.010753 | 0.01087 | 0.010989 | 0.011111 | 0.011236 | 0.011364 | 0.011494 | 0.011628 | 0.011765 | 0.011905 | 0.012048 | 0.012195 | 0.012346
After PSE Adjustments | 1464.4 | 1407.0954 | 1349.7909 | 1294.0949 | 1238.2572 | 1182.2778 | 1126.1565 | 1069.8931 | 1059.1942 | 1048.4953 | 1037.7963 | 1027.0974 | 1016.3985 | 1005.6996 | 995.0006 | 984.3017 | 973.6028 | 962.9038 | 952.2049 | 941.506 | 930.807 | 920.1081 | 909.4092 | 898.7102 | 888.0113 | 877.3124 | 866.6134 | 855.9145

## Wind MT
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 200
Capital Cost Component | $/kW | % of Total | $/kW | Adder | $/kW | $/kW
Turbine capital cost
Rotor module | 287 | 19.99% | 261.4978 | 0 | 261.4978 | 261.4978
Nacelle module | 488 | 33.98% | 444.6373 | 0 | 444.6373 | 444.6373
Tower module | 215 | 14.97% | 195.8955 | 0 | 195.8955 | 195.8955
total | 991 | 69.01% | 902.9418 | 0 | 902.0306 | 902.0306
Balance of System
Dev cost | 16 | 1.114% | 14.5783 | 0 | 14.5783 | 14.5783
Engineering & Mgmt | 18 | 1.253% | 16.4006 | 0 | 16.4006 | 16.4006
Foundation | 59 | 4.109% | 53.7574 | 0 | 53.7574 | 53.7574
Site access & staging | 44 | 3.064% | 40.0903 | 0 | 40.0903 | 40.0903
Assembly & installation | 44 | 3.064% | 40.0903 | 0 | 40.0903 | 40.0903
electrical infrastructure | 145 | 10.1% | 132.1156 | 1164 | 1296.1156 | 1296.1156
Total | 326 | 22.7% | 297.0323 | 0 | 1461.0323 | 1461.0323
financial costs
Construction financing | 34 | 2.368% | 30.9788 | 0 | 30.9788 | 30.9788
Contingency fund | 86 | 5.989% | 78.3582 | 0 | 78.3582 | 78.3582
Total | 120 | 8.357% | 109.337 | 0 | 109.337 | 109.337
Total CAPEX | 1436 | 100% | 1308.4 | 0 | 2472.4 | 2472.4
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB, Class 4 | 1308.4 | 1257.2 | 1206 | 1156.2372 | 1106.3478 | 1056.3318 | 1006.189 | 955.9193 | 946.3601 | 936.8009 | 927.2417 | 917.6825 | 908.1233 | 898.5641 | 889.0049 | 879.4457 | 869.8865 | 860.3273 | 850.7682 | 841.209 | 831.6498 | 822.0906 | 812.5314 | 802.9722 | 793.413 | 783.8538 | 774.2946 | 764.7354
% change on year | -- | 0.039132 | 0.040725 | 0.041263 | 0.043148 | 0.045208 | 0.047469 | 0.049961 | 0.01 | 0.010101 | 0.010204 | 0.010309 | 0.010417 | 0.010526 | 0.010638 | 0.010753 | 0.01087 | 0.010989 | 0.011111 | 0.011236 | 0.011364 | 0.011494 | 0.011628 | 0.011765 | 0.011905 | 0.012048 | 0.012195 | 0.012346
After PSE Adjustments | 2472.4 | 2375.6506 | 2278.9013 | 2184.8676 | 2090.5949 | 1996.0828 | 1901.3311 | 1806.3397 | 1788.2763 | 1770.2129 | 1752.1495 | 1734.0861 | 1716.0227 | 1697.9593 | 1679.8959 | 1661.8325 | 1643.7691 | 1625.7057 | 1607.6423 | 1589.5789 | 1571.5155 | 1553.4521 | 1535.3887 | 1517.3253 | 1499.2619 | 1481.1985 | 1463.1351 | 1445.0717

## Wind ID WY
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 200
Capital Cost Component | $/kW | % of Total | $/kW | Adder | $/kW | $/kW
Turbine capital cost
Rotor module | 287 | 19.99% | 261.4978 | 0 | 261.4978 | 261.4978
Nacelle module | 488 | 33.98% | 444.6373 | 0 | 444.6373 | 444.6373
Tower module | 215 | 14.97% | 195.8955 | 0 | 195.8955 | 195.8955
total | 991 | 69.01% | 902.9418 | 0 | 902.0306 | 902.0306
Balance of System
Dev cost | 16 | 1.114% | 14.5783 | 0 | 14.5783 | 14.5783
Engineering & Mgmt | 18 | 1.253% | 16.4006 | 0 | 16.4006 | 16.4006
Foundation | 59 | 4.109% | 53.7574 | 0 | 53.7574 | 53.7574
Site access & staging | 44 | 3.064% | 40.0903 | 0 | 40.0903 | 40.0903
Assembly & installation | 44 | 3.064% | 40.0903 | 0 | 40.0903 | 40.0903
electrical infrastructure | 145 | 10.1% | 132.1156 | 463.125 | 595.2406 | 595.2406
Total | 326 | 22.7% | 297.0323 | 0 | 760.1573 | 760.1573
financial costs
Construction financing | 34 | 2.368% | 30.9788 | 0 | 30.9788 | 30.9788
Contingency fund | 86 | 5.989% | 78.3582 | 0 | 78.3582 | 78.3582
Total | 120 | 8.357% | 109.337 | 0 | 109.337 | 109.337
Total CAPEX | 1436 | 100% | 1308.4 | 0 | 1771.525 | 1771.525
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB, Class 4 | 1308.4 | 1257.2 | 1206 | 1156.2372 | 1106.3478 | 1056.3318 | 1006.189 | 955.9193 | 946.3601 | 936.8009 | 927.2417 | 917.6825 | 908.1233 | 898.5641 | 889.0049 | 879.4457 | 869.8865 | 860.3273 | 850.7682 | 841.209 | 831.6498 | 822.0906 | 812.5314 | 802.9722 | 793.413 | 783.8538 | 774.2946 | 764.7354
% change on year | -- | 0.039132 | 0.040725 | 0.041263 | 0.043148 | 0.045208 | 0.047469 | 0.049961 | 0.01 | 0.010101 | 0.010204 | 0.010309 | 0.010417 | 0.010526 | 0.010638 | 0.010753 | 0.01087 | 0.010989 | 0.011111 | 0.011236 | 0.011364 | 0.011494 | 0.011628 | 0.011765 | 0.011905 | 0.012048 | 0.012195 | 0.012346
After PSE Adjustments | 1771.525 | 1702.2021 | 1632.8792 | 1565.5022 | 1497.9538 | 1430.234 | 1362.3425 | 1294.2792 | 1281.3364 | 1268.3936 | 1255.4508 | 1242.508 | 1229.5652 | 1216.6224 | 1203.6796 | 1190.7369 | 1177.7941 | 1164.8513 | 1151.9085 | 1138.9657 | 1126.0229 | 1113.0801 | 1100.1373 | 1087.1945 | 1074.2517 | 1061.3089 | 1048.3661 | 1035.4234

## Solar WA
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 134 | % of Total | $/kW | adder | $/kW | $/kW
Module component | Cost in $, rough
Module | 41000000 | 40.59% | 435.8925 | 0 | 435.8925 | 435.8925
Inverter | 5000000 | 4.95% | 53.1576 | 0 | 53.1576 | 53.1576
Structural BOS | 12000000 | 11.88% | 127.5783 | 0 | 127.5783 | 127.5783
Electrical BOS | 7000000 | 6.931% | 74.4207 | 0 | 74.4207 | 74.4207
Total BOS | 19000000 | 18.81% | 201.999 | 0 | 201.999 | 201.999
Install labor & equipment | 11000000 | 10.89% | 116.9468 | 0 | 116.9468 | 116.9468
EPC overhead | 6000000 | 5.941% | 63.7892 | 0 | 63.7892 | 63.7892
Sales tax | 4000000 | 3.96% | 42.5261 | 0 | 42.5261 | 42.5261
Total EPC | 86000000 | 85.15% | 914.3112 | 0 | 914.3112 | 914.3112
Land
Permitting fee
Interconnection fee | 3000000 | 2.97% | 31.8946 | 0 | 31.8946 | 31.8946
Transmission line | 2000000 | 1.98% | 21.2631 | 156 | 177.2631 | 177.2631
Developer overhead | 2000000 | 1.98% | 21.2631 | 0 | 21.2631 | 21.2631
Contingency | 3000000 | 2.97% | 31.8946 | 0 | 31.8946 | 31.8946
EPC/developer profit | 5000000 | 4.95% | 53.1576 | 0 | 53.1576 | 53.1576
Developer cost | 15000000 | 14.85% | 159.4729 | 0 | 315.4729 | 315.4729
Total | 101000000 | 100% | 1073.784 | 0 | 1229.784 | 1229.784
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB Listing | 1073.784 | 1027.7458 | 981.7076 | 936.3879 | 890.9969 | 845.5346 | 800.0011 | 754.3966 | 747.6743 | 740.952 | 734.2296 | 727.5073 | 720.785 | 714.0627 | 707.3404 | 700.618 | 693.8957 | 687.1734 | 680.4511 | 673.7288 | 667.0065 | 660.2841 | 653.5618 | 646.8395 | 640.1172 | 633.3949 | 626.6725 | 619.9502
% change on year | -- | 0.042875 | 0.044795 | 0.046164 | 0.048475 | 0.051024 | 0.053852 | 0.057006 | 0.0089109 | 0.008991 | 0.0090725 | 0.0091556 | 0.0092402 | 0.0093264 | 0.0094142 | 0.0095037 | 0.0095948 | 0.0096878 | 0.0097826 | 0.0098792 | 0.0099778 | 0.010078 | 0.010181 | 0.010286 | 0.010393 | 0.010502 | 0.010613 | 0.010727
After PSE Adjustments | 1229.784 | 1177.0573 | 1124.3306 | 1072.4269 | 1020.4415 | 968.3744 | 916.2258 | 863.9958 | 856.2969 | 848.5979 | 840.899 | 833.2 | 825.5011 | 817.8022 | 810.1032 | 802.4043 | 794.7053 | 787.0064 | 779.3074 | 771.6085 | 763.9096 | 756.2106 | 748.5117 | 740.8127 | 733.1138 | 725.4148 | 717.7159 | 710.017

## Solar ID WY
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 134 | % of Total | $/kW | adder | $/kW | $/kW
Module component | Cost in $, rough
Module | 41000000 | 40.59% | 435.8925 | 0 | 435.8925 | 435.8925
Inverter | 5000000 | 4.95% | 53.1576 | 0 | 53.1576 | 53.1576
Structural BOS | 12000000 | 11.88% | 127.5783 | 0 | 127.5783 | 127.5783
Electrical BOS | 7000000 | 6.931% | 74.4207 | 0 | 74.4207 | 74.4207
Total BOS | 19000000 | 18.81% | 201.999 | 0 | 201.999 | 201.999
Install labor & equipment | 11000000 | 10.89% | 116.9468 | 0 | 116.9468 | 116.9468
EPC overhead | 6000000 | 5.941% | 63.7892 | 0 | 63.7892 | 63.7892
Sales tax | 4000000 | 3.96% | 42.5261 | 0 | 42.5261 | 42.5261
Total EPC | 86000000 | 85.15% | 914.3112 | 0 | 914.3112 | 914.3112
Land
Permitting fee
Interconnection fee | 3000000 | 2.97% | 31.8946 | 0 | 31.8946 | 31.8946
Transmission line | 2000000 | 1.98% | 21.2631 | 463.125 | 484.3881 | 484.3881
Developer overhead | 2000000 | 1.98% | 21.2631 | 0 | 21.2631 | 21.2631
Contingency | 3000000 | 2.97% | 31.8946 | 0 | 31.8946 | 31.8946
EPC/developer profit | 5000000 | 4.95% | 53.1576 | 0 | 53.1576 | 53.1576
Developer cost | 15000000 | 14.85% | 159.4729 | 0 | 622.5979 | 622.5979
Total | 101000000 | 100% | 1073.784 | 0 | 1536.909 | 1536.909
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB Listing | 1073.784 | 1027.7458 | 981.7076 | 936.3879 | 890.9969 | 845.5346 | 800.0011 | 754.3966 | 747.6743 | 740.952 | 734.2296 | 727.5073 | 720.785 | 714.0627 | 707.3404 | 700.618 | 693.8957 | 687.1734 | 680.4511 | 673.7288 | 667.0065 | 660.2841 | 653.5618 | 646.8395 | 640.1172 | 633.3949 | 626.6725 | 619.9502
% change on year | -- | 0.042875 | 0.044795 | 0.046164 | 0.048475 | 0.051024 | 0.053852 | 0.057006 | 0.0089109 | 0.008991 | 0.0090725 | 0.0091556 | 0.0092402 | 0.0093264 | 0.0094142 | 0.0095037 | 0.0095948 | 0.0096878 | 0.0097826 | 0.0098792 | 0.0099778 | 0.010078 | 0.010181 | 0.010286 | 0.010393 | 0.010502 | 0.010613 | 0.010727
After PSE Adjustments | 1536.909 | 1471.0144 | 1405.1198 | 1340.2537 | 1275.2854 | 1210.2152 | 1145.0431 | 1079.7692 | 1070.1476 | 1060.5259 | 1050.9042 | 1041.2826 | 1031.6609 | 1022.0392 | 1012.4175 | 1002.7959 | 993.1742 | 983.5525 | 973.9309 | 964.3092 | 954.6875 | 945.0659 | 935.4442 | 925.8225 | 916.2009 | 906.5792 | 896.9575 | 887.3359

## Solar DER
Source material
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 134 | % of Total | $/kW | $/kW
Module component | Cost in $, rough
PV modules | 2844 | 16.66% | 381.03 | 381.03
Lithium-ion battery | 0 | 0% | 0 | 0
PV inverter | 1754 | 10.28% | 234.9953 | 234.9953
Battery inverter | 0 | 0% | 0 | 0
Structural BOS | 589 | 3.45% | 78.9123 | 78.9123
Electrical BOS | 1600 | 9.373% | 214.3629 | 214.3629
Supply chain costs | 1825 | 10.69% | 244.5077 | 244.5077
Sales tax | 440 | 2.578% | 58.9498 | 58.9498
Installed Labor & equipment | 1309 | 7.668% | 175.3756 | 175.3756
Permitting, inspection, interconnection | 1668 | 9.772% | 223.4733 | 223.4733
Sales & Marketing | 2996 | 17.55% | 401.3945 | 401.3945
Net profit | 2045 | 11.98% | 273.9826 | 273.9826
Total | 17070 | 100% | 2286.9841 | 2286.9841
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB Listing | 2286.9841 | 2105.4762 | 1923.9683 | 1742.4603 | 1560.9524 | 1379.4445 | 1197.9365 | 1016.4286 | 1005.1612 | 993.8937 | 982.6262 | 971.3588 | 960.0913 | 948.8238 | 937.5564 | 926.2889 | 915.0214 | 903.754 | 892.4865 | 881.219 | 869.9516 | 858.6841 | 847.4166 | 836.1492 | 824.8817 | 813.6143 | 802.3468 | 791.0793
% change on year | -- | 0.079366 | 0.086208 | 0.09434 | 0.10417 | 0.11628 | 0.13158 | 0.15152 | 0.011085 | 0.01121 | 0.011337 | 0.011467 | 0.0116 | 0.011736 | 0.011875 | 0.012018 | 0.012164 | 0.012314 | 0.012467 | 0.012625 | 0.012786 | 0.012952 | 0.013122 | 0.013296 | 0.013475 | 0.013659 | 0.013849 | 0.014043
After PSE Adjustments | 2286.9841 | 2105.4762 | 1923.9683 | 1742.4603 | 1560.9524 | 1379.4445 | 1197.9365 | 1016.4286 | 1005.1612 | 993.8937 | 982.6262 | 971.3588 | 960.0913 | 948.8238 | 937.5564 | 926.2889 | 915.0214 | 903.754 | 892.4865 | 881.219 | 869.9516 | 858.6841 | 847.4166 | 836.1492 | 824.8817 | 813.6143 | 802.3468 | 791.0793

## Biomass
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: Add 5 Mile Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 50
Cost component | $ | % of Total | $/kW | Adder | $/kW | $/kW
civil/structural/architectural | 22266000 | 10.87% | 470.8656 | 0 | 470.8656 | 470.8656
Mechanical | 88818000 | 43.36% | 1878.2602 | 0 | 1878.2602 | 1878.2602
Electrical | 26608000 | 12.99% | 562.6872 | 0 | 562.6872 | 562.6872
Project indirects | 15418000 | 7.526% | 326.049 | 0 | 326.049 | 326.049
EPC fee | 15311000 | 7.474% | 323.7862 | 0 | 323.7862 | 323.7862
EPC subtotal | 168421000 | 82.21% | 3561.6482 | 0 | 3561.6482 | 3561.6482
Owners costs
Owner's services | 11789000 | 5.755% | 249.3054 | 0 | 249.3054 | 249.3054
Land | 1500000 | 0.7322% | 31.7209 | 0 | 31.7209 | 31.7209
Electrical Interconnection* | 1200000 | 0.5858% | 25.3768 | 573.3333 | 598.7101 | 598.7101
Owners cost subtotal | 14489000 | 7.073% | 306.4031 | 0 | 879.7365 | 879.7365
Contingency | 21949000 | 10.71% | 464.1619 | 0 | 464.1619 | 464.1619
Total CAPEX | 204859000 | 100% | 4332.2132 | 0 | 4905.5466 | 4905.5466
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB Listing ($/kW) | 4332.2132 | 4304.5137 | 4276.2086 | 4258.3489 | 4240.3818 | 4222.3099 | 4204.1304 | 4185.8438 | 4157.8281 | 4129.8125 | 4101.7999 | 4073.7819 | 4045.7676 | 4017.7526 | 3989.74 | 3961.7249 | 3933.7105 | 3905.6967 | 3877.6789 | 3849.6642 | 3821.6493 | 3793.6352 | 3765.6236 | 3737.6085 | 3709.5933 | 3681.5768 | 3653.5623 | 3625.5477
% change on year | -- | 0.0063939 | 0.0065757 | 0.0041765 | 0.0042193 | 0.0042618 | 0.0043056 | 0.0043497 | 0.006693 | 0.006738 | 0.006783 | 0.0068307 | 0.0068767 | 0.0069245 | 0.0069722 | 0.0070218 | 0.0070713 | 0.0071215 | 0.0071736 | 0.0072246 | 0.0072772 | 0.0073304 | 0.0073838 | 0.0074397 | 0.0074955 | 0.0075524 | 0.0076094 | 0.0076677
After PSE Adjustments ($/kW) | 4905.5466 | 4874.1812 | 4842.1302 | 4821.9069 | 4801.5619 | 4781.0984 | 4760.513 | 4739.8064 | 4708.083 | 4676.3598 | 4644.6398 | 4612.9139 | 4581.1922 | 4549.4697 | 4517.7498 | 4486.0271 | 4454.3052 | 4422.584 | 4390.8583 | 4359.1361 | 4327.4137 | 4295.6921 | 4263.9734 | 4232.2507 | 4200.5279 | 4168.8037 | 4137.0817 | 4105.3596

## PHES WA OR
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
Mongrid et al. 2020 (PNNL) | 500
Hours | 10
Cost component | $/kW | % of Total | $/kW | Adder | $/kW | $/kW
Upper + lower reservoir | 1016 | 31.69% | 1078.7671 | -- | 1078.7671 | 1078.7671
Tunnels | 163 | 5.084% | 173.0699 | -- | 173.0699 | 173.0699
Powerhouse excavation | 97 | 3.026% | 102.9925 | -- | 102.9925 | 102.9925
Powerhouse structure, equip. BOP | 1010 | 31.5% | 1072.3964 | 506 | 1578.3964 | 1578.3964
Total direct costs | 2286 | 71.3% | 2427.2259 | -- | 2933.2259 | 2933.2259
EPC management services inc. contingency | 472 | 14.72% | 501.1595 | -- | 501.1595 | 501.1595
Owner's cost | 448 | 13.97% | 475.6768 | -- | 475.6768 | 475.6768
Proj mgmt & design engineering | 103 | 3.213% | 109.3632 | -- | 109.3632 | 109.3632
Construction mgmt & startup support | 103 | 3.213% | 109.3632 | -- | 109.3632 | 109.3632
contingency | 308 | 9.607% | 327.0278 | -- | 327.0278 | 327.0278
Total indirect cost | 920 | 28.7% | 976.8363 | -- | 976.8363 | 976.8363
Total installed cost | 3206 | 100% | 3404.0622 | -- | 3910.0622 | 3910.0622
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB Listing | 3404.0622 | 3404.0622 | 3404.0622 | 3408.2857 | 3412.512 | 3416.7411 | 3420.973 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078
% change on year | -- | 0 | 0 | -0.0012407 | -0.00124 | -0.0012393 | -0.0012386 | -0.0012379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
After PSE Adjustments | 3910.0622 | 3910.0622 | 3910.0622 | 3914.9135 | 3919.768 | 3924.6258 | 3929.4868 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351 | 3934.351

## PHES MT
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
Mongrid et al. 2020 (PNNL) | 500
Hours | 10
Cost component | $/kW | % of Total | $/kW | Adder | $/kW | $/kW
Upper + lower reservoir | 1016 | 31.69% | 1078.7671 | -- | 1078.7671 | 1078.7671
Tunnels | 163 | 5.084% | 173.0699 | -- | 173.0699 | 173.0699
Powerhouse excavation | 97 | 3.026% | 102.9925 | -- | 102.9925 | 102.9925
Powerhouse structure, equip. BOP | 1010 | 31.5% | 1072.3964 | 198 | 1270.3964 | 1270.3964
Total direct costs | 2286 | 71.3% | 2427.2259 | -- | 2625.2259 | 2625.2259
EPC management services inc. contingency | 472 | 14.72% | 501.1595 | -- | 501.1595 | 501.1595
Owner's cost | 448 | 13.97% | 475.6768 | -- | 475.6768 | 475.6768
Proj mgmt & design engineering | 103 | 3.213% | 109.3632 | -- | 109.3632 | 109.3632
Construction mgmt & startup support | 103 | 3.213% | 109.3632 | -- | 109.3632 | 109.3632
contingency | 308 | 9.607% | 327.0278 | -- | 327.0278 | 327.0278
Total indirect cost | 920 | 28.7% | 976.8363 | -- | 976.8363 | 976.8363
Total installed cost | 3206 | 100% | 3404.0622 | -- | 3602.0622 | 3602.0622
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB Listing | 3404.0622 | 3404.0622 | 3404.0622 | 3408.2857 | 3412.512 | 3416.7411 | 3420.973 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078 | 3425.2078
% change on year | -- | 0 | 0 | -0.0012407 | -0.00124 | -0.0012393 | -0.0012386 | -0.0012379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
After PSE Adjustments | 3602.0622 | 3602.0622 | 3602.0622 | 3606.5314 | 3611.0035 | 3615.4786 | 3619.9567 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377 | 3624.4377

## Battery Utility
Source material, 2 hr |  |  |  | Adjustments | [5 empty] | Source material, 4 hr |  |  |  |  | Adjustments | [5 empty] | Source material, 6 hr |  |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: Overbuild Storage Block | PSE Adjustment 1 Total | PSE Adjustment 2: add Spur line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST | Notes |  |  | Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: Overbuild Storage Block | PSE Adjustment 1 Total | PSE Adjustment 2: add Spur line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST | Notes |  |  | Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: Overbuild Storage Block | PSE Adjustment 1 Total | PSE Adjustment 2: add Spur line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST | Notes
NREL ATB Nameplate (MW) | 60 | [8 empty] | NREL ATB Nameplate (MW) |  | 60 | [8 empty] | NREL ATB Nameplate (MW) |  | 60
Duration (Hours) | 2 | [8 empty] | Duration (Hours) |  | 4 | [8 empty] | Duration (Hours) |  | 6
Lithium Ion Batteries | [9 empty] | Lithium Ion Batteries | [10 empty] | Lithium Ion Batteries
Duration | [9 empty] | Duration | [10 empty] | Duration
Module Component | $/kW | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW |  | Module Component |  | $/kW | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW |  | Module Component |  | $/kW | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW
Storage Block | 336 | 39.3% | 293.1793 |  | 293.1793 | 0 | 293.1793 | 293.1793 |  | Storage Block |  | 660 | 42.94% | 539.2111 |  | 539.2111 | 0 | 539.2111 | 539.2111 |  | Storage Block |  | 984 | 44.42% | 784.259 |  | 784.259 | 0 | 784.259 | 784.259
Storage balance of system | 82 | 9.591% | 71.5497 | -- | 71.5497 | 0 | 71.5497 | 71.5497 |  | Storage balance of system |  | 152 | 9.889% | 124.1819 | -- | 124.1819 | 0 | 124.1819 | 124.1819 |  | Storage balance of system |  | 222 | 10.02% | 176.9365 | -- | 176.9365 | 0 | 176.9365 | 176.9365
Power Equipment | 63 | 7.368% | 54.9711 | -- | 54.9711 | 0 | 54.9711 | 54.9711 |  | Power Equipment |  | 63 | 4.099% | 51.4701 | -- | 51.4701 | 0 | 51.4701 | 51.4701 |  | Power Equipment |  | 63 | 2.844% | 50.2117 | -- | 50.2117 | 0 | 50.2117 | 50.2117
Controls & communication | 2 | 0.2339% | 1.7451 | -- | 1.7451 | 0 | 1.7451 | 1.7451 |  | Controls & communication |  | 2 | 0.1301% | 1.634 | -- | 1.634 | 0 | 1.634 | 1.634 |  | Controls & communication |  | 2 | 0.09029% | 1.594 | -- | 1.594 | 0 | 1.594 | 1.594
System integration | 96 | 11.23% | 83.7655 | -- | 83.7655 | 0 | 83.7655 | 83.7655 |  | System integration |  | 176 | 11.45% | 143.7896 | -- | 143.7896 | 0 | 143.7896 | 143.7896 |  | System integration |  | 252 | 11.38% | 200.8468 | -- | 200.8468 | 0 | 200.8468 | 200.8468
Eng., procurement, construction | 116 | 13.57% | 101.2167 | -- | 101.2167 | 0 | 101.2167 | 101.2167 |  | Eng., procurement, construction |  | 212 | 13.79% | 173.2011 | -- | 173.2011 | 0 | 173.2011 | 173.2011 |  | Eng., procurement, construction |  | 306 | 13.81% | 243.8854 | -- | 243.8854 | 0 | 243.8854 | 243.8854
Project Dev | 140 | 16.37% | 122.1581 | -- | 122.1581 | 0 | 122.1581 | 122.1581 |  | Project Dev |  | 252 | 16.4% | 205.8806 | -- | 205.8806 | 0 | 205.8806 | 205.8806 |  | Project Dev |  | 366 | 16.52% | 291.7061 | -- | 291.7061 | 0 | 291.7061 | 291.7061
Grid integration | 20 | 2.339% | 17.4512 | -- | 17.4512 | 58 | 75.4512 | 75.4512 |  | Grid integration |  | 20 | 1.301% | 16.3397 | -- | 16.3397 | 58 | 74.3397 | 74.3397 |  | Grid integration |  | 20 | 0.9029% | 15.9402 | -- | 15.9402 | 58 | 73.9402 | 73.9402
Total ESS intalled cost | 855 | 100% | 746.0367 | -- | 746.0367 | 0 | 804.0367 | 804.0367 |  | Total ESS intalled cost |  | 1537 | 100% | 1255.7082 | -- | 1255.7082 | 0 | 1313.7082 | 1313.7082 |  | Total ESS intalled cost |  | 2215 | 100% | 1765.3798 | -- | 1765.3798 | 0 | 1823.3798 | 1823.3798
↓ COST CURVES ↓
2hr LI
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 746.0367 | 707.6688 | 672.1177 | 652.263 | 633.7498 | 610.0045 | 596.7234 | 579.5517 | 572.6548 | 565.4104 | 558.166 | 550.9216 | 543.6772 | 536.4328 | 529.1884 | 521.944 | 514.6996 | 507.4552 | 500.2108 | 492.9664 | 485.722 | 478.4776 | 471.2332 | 463.9888 | 456.7444 | 449.5 | 442.2556 | 435.1085
% change on year | -- | 0.051429 | 0.050237 | 0.029541 | 0.028383 | 0.037468 | 0.021772 | 0.028777 | 0.0119 | 0.012651 | 0.012813 | 0.012979 | 0.01315 | 0.013325 | 0.013505 | 0.01369 | 0.01388 | 0.014075 | 0.014276 | 0.014483 | 0.014696 | 0.014915 | 0.015141 | 0.015373 | 0.015613 | 0.015861 | 0.016117 | 0.016161
After PSE Adjustments | 804.0367 | 762.6859 | 724.3709 | 702.9727 | 683.0202 | 657.4288 | 643.1152 | 624.6084 | 617.1753 | 609.3677 | 601.5601 | 593.7525 | 585.9449 | 578.1373 | 570.3297 | 562.5221 | 554.7145 | 546.9069 | 539.0993 | 531.2917 | 523.4841 | 515.6764 | 507.8688 | 500.0612 | 492.2536 | 484.446 | 476.6384 | 468.9356
4hr LI
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 1255.7082 | 1166.7622 | 1103.9768 | 1056.8878 | 1015.0308 | 967.9418 | 931.3169 | 894.6921 | 883.9532 | 872.7695 | 861.5859 | 850.4022 | 839.2186 | 828.0349 | 816.8513 | 805.6676 | 794.484 | 783.3003 | 772.1167 | 760.933 | 749.7494 | 738.5657 | 727.3821 | 716.1984 | 705.0148 | 693.8311 | 682.6475 | 671.4638
% change on year | -- | 0.070833 | 0.053812 | 0.042654 | 0.039604 | 0.046392 | 0.037838 | 0.039326 | 0.012003 | 0.012652 | 0.012814 | 0.01298 | 0.013151 | 0.013326 | 0.013506 | 0.013691 | 0.013881 | 0.014077 | 0.014278 | 0.014484 | 0.014697 | 0.014917 | 0.015142 | 0.015375 | 0.015615 | 0.015863 | 0.016119 | 0.016383
After PSE Adjustments | 1313.7082 | 1220.6539 | 1154.9685 | 1105.7044 | 1061.9142 | 1012.6501 | 974.3336 | 936.0171 | 924.7822 | 913.082 | 901.3817 | 889.6815 | 877.9813 | 866.2811 | 854.5809 | 842.8807 | 831.1805 | 819.4802 | 807.78 | 796.0798 | 784.3796 | 772.6794 | 760.9792 | 749.279 | 737.5788 | 725.8785 | 714.1783 | 702.4781
6hr LI
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 1765.3798 | 1625.8557 | 1535.8359 | 1461.5125 | 1396.3118 | 1325.879 | 1265.9105 | 1209.8326 | 1195.2516 | 1180.1287 | 1165.0058 | 1149.8829 | 1134.76 | 1119.6371 | 1104.5142 | 1089.3913 | 1074.2684 | 1059.1455 | 1044.0226 | 1028.8997 | 1013.7768 | 998.6538 | 983.5309 | 968.408 | 953.2851 | 938.1622 | 923.0393 | 907.8191
% change on year | -- | 0.079033 | 0.055368 | 0.048393 | 0.044612 | 0.050442 | 0.045229 | 0.044299 | 0.012052 | 0.012652 | 0.012815 | 0.012981 | 0.013152 | 0.013327 | 0.013507 | 0.013692 | 0.013882 | 0.014077 | 0.014278 | 0.014485 | 0.014698 | 0.014917 | 0.015143 | 0.015376 | 0.015616 | 0.015864 | 0.01612 | 0.016489
After PSE Adjustments | 1823.3798 | 1679.2718 | 1586.2945 | 1509.5292 | 1442.1864 | 1369.4396 | 1307.5009 | 1249.5805 | 1234.5206 | 1218.9008 | 1203.2811 | 1187.6613 | 1172.0416 | 1156.4218 | 1140.802 | 1125.1823 | 1109.5625 | 1093.9428 | 1078.323 | 1062.7033 | 1047.0835 | 1031.4637 | 1015.844 | 1000.2242 | 984.6045 | 968.9847 | 953.365 | 937.6447
Note on E8: Karpoff, Alexandra: Overbuild storage capacity adder removed because 2022 ATB accounts for overbuild in CAPEX costs. 7/7/2022

## Battery DER
Source material
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 5 kW, 14.5 kWh | % of Total | $/kW | $/kW
Module component | $
Lithium Ion Battery | 3479 | 18.56% | 728.1699 | 728.1699
Battery Inverter | 2393 | 12.77% | 500.8653 | 500.8653
Electrical BOS | 1507 | 8.041% | 315.4217 | 315.4217
Suuply Chain Costs | 369 | 1.969% | 77.2333 | 77.2333
Sales Tax | 535 | 2.855% | 111.9778 | 111.9778
Install Labor and Equipment | 1560 | 8.324% | 326.5148 | 326.5148
Permitting, Inspection, Interconnection | 1209 | 6.451% | 253.049 | 253.049
Overhead | 1940 | 10.35% | 406.0505 | 406.0505
Sales and Marketing | 3829 | 20.43% | 801.4264 | 801.4264
Net Profit | 1920 | 10.24% | 401.8644 | 401.8644
TOTAL | 18741 | 100% | 3922.573 | 3922.573
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 3922.573 | 3641.4242 | 3374.6375 | 3238.1631 | 3117.0424 | 3013.052 | 2913.5515 | 2823.4879 | 2788.9573 | 2753.6641 | 2718.3709 | 2683.0778 | 2647.7846 | 2612.4914 | 2577.1982 | 2541.905 | 2506.6118 | 2471.3187 | 2436.0255 | 2400.7323 | 2365.4391 | 2330.1459 | 2294.8527 | 2259.5595 | 2224.2664 | 2188.9732 | 2153.68 | 2117.6159
% change on year | -- | 0.071675 | 0.073264 | 0.040441 | 0.037404 | 0.033362 | 0.033023 | 0.030912 | 0.01223 | 0.012655 | 0.012817 | 0.012983 | 0.013154 | 0.013329 | 0.013509 | 0.013694 | 0.013885 | 0.01408 | 0.014281 | 0.014488 | 0.014701 | 0.01492 | 0.015146 | 0.015379 | 0.015619 | 0.015867 | 0.016123 | 0.016745
After PSE Adjustments | 3922.573 | 3641.4242 | 3374.6375 | 3238.1631 | 3117.0424 | 3013.052 | 2913.5515 | 2823.4879 | 2788.9573 | 2753.6641 | 2718.3709 | 2683.0778 | 2647.7846 | 2612.4914 | 2577.1982 | 2541.905 | 2506.6118 | 2471.3187 | 2436.0255 | 2400.7323 | 2365.4391 | 2330.1459 | 2294.8527 | 2259.5595 | 2224.2664 | 2188.9732 | 2153.68 | 2117.6159

## Hybrid
Solar + Battery |  | Benefit | 7.573% |  |  | Wind + Battery |  | Benefit | 6.525% |  |  | Wind + Solar + Battery |  | Benefit | 10.18% | [5 empty] | Rationale for Hybrid Discount Assumptions:
[21 empty] | Source: | \\spestfile01v01\REACQ\ResourcePlanning\2023 IRP\Generic Resource Costs\Hybrid_Resources\Hybrid_resource_discount_factor.xlsx
Battery Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW |  |  | Battery Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW |  |  | Battery Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW | [5 empty] | Based on savings from Solar + Strorage for AC-Coupled System
Storage Block | 539.2111 | 0 | 539.2111 |  |  | Storage Block | 539.2111 | 0 | 539.2111 |  |  | Storage Block | 539.2111 | 0 | 539.2111 | [5 empty] | Discounts applied on a component-by-component basis on the following schedule:
Storage balance of system | 124.1819 | 0 | 124.1819 |  |  | Storage balance of system | 124.1819 | 0 | 124.1819 |  |  | Storage balance of system | 124.1819 | 0 | 124.1819 | [5 empty] | Component costs varied resource to resource, used best judgement in applying discount factors.
Power Equipment | 51.4701 | 0 | 51.4701 |  |  | Power Equipment | 51.4701 | 0 | 51.4701 |  |  | Power Equipment | 51.4701 | 0 | 51.4701
Controls & communication | 1.634 | 0.15 | 1.3889 |  |  | Controls & communication | 1.634 | 0.15 | 1.3889 |  |  | Controls & communication | 1.634 | 0.15 | 1.3889
System integration | 143.7896 | 0.15 | 122.2212 |  |  | System integration | 143.7896 | 0.15 | 122.2212 |  |  | System integration | 143.7896 | 0.15 | 122.2212 | [5 empty] | Component | Discount Factor | Related Items
Eng., procurement, construction | 173.2011 | 0 | 173.2011 |  |  | Eng., procurement, construction | 173.2011 | 0 | 173.2011 |  |  | Eng., procurement, construction | 173.2011 | 0 | 173.2011 | [5 empty] | Equipment | 0 | power plant equipment
Project Dev | 205.8806 | 0 | 205.8806 |  |  | Project Dev | 205.8806 | 0 | 205.8806 |  |  | Project Dev | 205.8806 | 0 | 205.8806 | [5 empty] | Balance of System | 0.15 | controls, BOS/BOP, Buildings
Grid integration | 74.3397 | 0.4 | 44.6038 |  |  | Grid integration | 74.3397 | 0.4 | 44.6038 |  |  | Grid integration | 74.3397 | 0.55 | 33.4529 | [5 empty] | Installation | 0.15 | Installation, Labor, Engineering, Management
Total | 1313.7082 |  | 1262.1588 |  |  | Total | 1313.7082 |  | 1262.1588 |  |  | Total | 1313.7082 |  | 1251.0078 | [5 empty] | Grid Connection Costs (2 projects) | 0.4 | Interconnection, permits, fees, spur line
[21 empty] | Grid Connection Costs (3 projects) | 0.55 | Interconnection, permits, fees, spur line
[21 empty] | Owner's Costs | 0 | Financing, Development, Contingency
Solar Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW |  |  | Wind Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW |  |  | Solar Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW
Module | 435.8925 | 0 | 435.8925 |  |  | Rotor module | 261.4978 | 0 | 261.4978 |  |  | Module | 435.8925 | 0 | 435.8925
Inverter | 53.1576 | 0 | 53.1576 |  |  | Nacelle module | 444.6373 | 0 | 444.6373 |  |  | Inverter | 53.1576 | 0 | 53.1576
Structural BOS | 127.5783 | 0.15 | 108.4416 |  |  | Tower module | 195.8955 | 0 | 195.8955 |  |  | Structural BOS | 127.5783 | 0.15 | 108.4416
Electrical BOS | 74.4207 | 0.15 | 63.2576 |  |  | Dev cost | 14.5783 | 0 | 14.5783 |  |  | Electrical BOS | 74.4207 | 0.15 | 63.2576
Install labor & equipment | 116.9468 | 0.15 | 99.4048 |  |  | Engineering & Mgmt | 16.4006 | 0.15 | 13.9405 |  |  | Install labor & equipment | 116.9468 | 0.15 | 99.4048
EPC overhead | 63.7892 | 0.15 | 54.2208 |  |  | Foundation | 53.7574 | 0 | 53.7574 |  |  | EPC overhead | 63.7892 | 0.15 | 54.2208
Sales tax | 42.5261 | 0 | 42.5261 |  |  | Site access & staging | 40.0903 | 0.15 | 34.0767 |  |  | Sales tax | 42.5261 | 0 | 42.5261
Land | 0 | 0 | 0 |  |  | Assembly & installation | 40.0903 | 0.15 | 34.0767 |  |  | Land | 0 | 0 | 0
Permitting fee | 0 | 0 | 0 |  |  | electrical infrastructure | 288.1156 | 0.4 | 172.8694 |  |  | Permitting fee | 0 | 0.55 | 0
Interconnection fee | 31.8946 | 0.4 | 19.1367 |  |  | Construction financing | 30.9788 | 0 | 30.9788 |  |  | Interconnection fee | 31.8946 | 0.55 | 14.3526
Transmission line | 177.2631 | 0.4 | 106.3578 |  |  | Contingency fund | 78.3582 | 0 | 78.3582 |  |  | Transmission line | 177.2631 | 0.55 | 79.7684
Developer overhead | 21.2631 | 0 | 21.2631 |  |  | Total | 1464.4 |  | 1334.6666 |  |  | Developer overhead | 21.2631 | 0 | 21.2631
Contingency | 31.8946 | 0 | 31.8946 | [8 empty] | Contingency | 31.8946 | 0 | 31.8946
EPC/developer profit | 53.1576 | 0 | 53.1576 | [8 empty] | EPC/developer profit | 53.1576 | 0 | 53.1576
Total | 1229.784 |  | 1088.7108 | [8 empty] | Total | 1229.784 |  | 1057.3371
[13 empty] | Wind Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW
[13 empty] | Rotor module | 261.4978 | 0 | 261.4978
[13 empty] | Nacelle module | 444.6373 | 0 | 444.6373
[13 empty] | Tower module | 195.8955 | 0 | 195.8955
[13 empty] | Dev cost | 14.5783 | 0 | 14.5783
[13 empty] | Engineering & Mgmt | 16.4006 | 0.15 | 13.9405
[13 empty] | Foundation | 53.7574 | 0 | 53.7574
[13 empty] | Site access & staging | 40.0903 | 0.15 | 34.0767
[13 empty] | Assembly & installation | 40.0903 | 0.15 | 34.0767
[13 empty] | electrical infrastructure | 288.1156 | 0.55 | 129.652
[13 empty] | Construction financing | 30.9788 | 0 | 30.9788
[13 empty] | Contingency fund | 78.3582 | 0 | 78.3582
[13 empty] | Total | 1464.4 |  | 1291.4493
↓ COST CURVE ↓
WA Solar + Battery/WA Wind + Battery | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Solar - NREL ATB | 1073.784 | 1027.7458 | 981.7076 | 936.3879 | 890.9969 | 845.5346 | 800.0011 | 754.3966 | 747.6743 | 740.952 | 734.2296 | 727.5073 | 720.785 | 714.0627 | 707.3404 | 700.618 | 693.8957 | 687.1734 | 680.4511 | 673.7288 | 667.0065 | 660.2841 | 653.5618 | 646.8395 | 640.1172 | 633.3949 | 626.6725 | 619.9502
Solar - % change on year |  | 4.287% | 4.48% | 4.616% | 4.847% | 5.102% | 5.385% | 5.701% | 0.8911% | 0.8991% | 0.9073% | 0.9156% | 0.924% | 0.9326% | 0.9414% | 0.9504% | 0.9595% | 0.9688% | 0.9783% | 0.9879% | 0.9978% | 1.008% | 1.018% | 1.029% | 1.039% | 1.05% | 1.061% | 1.073%
Solar - PSE | 1088.7108 | 1042.0325 | 995.3543 | 949.4047 | 903.3827 | 857.2884 | 811.122 | 764.8835 | 758.0677 | 751.252 | 744.4362 | 737.6204 | 730.8047 | 723.9889 | 717.1731 | 710.3574 | 703.5416 | 696.7258 | 689.9101 | 683.0943 | 676.2785 | 669.4628 | 662.647 | 655.8312 | 649.0155 | 642.1997 | 635.3839 | 628.5682
Battery - NREL ATB | 1255.7082 | 1166.7622 | 1103.9768 | 1056.8878 | 1015.0308 | 967.9418 | 931.3169 | 894.6921 | 883.9532 | 872.7695 | 861.5859 | 850.4022 | 839.2186 | 828.0349 | 816.8513 | 805.6676 | 794.484 | 783.3003 | 772.1167 | 760.933 | 749.7494 | 738.5657 | 727.3821 | 716.1984 | 705.0148 | 693.8311 | 682.6475 | 671.4638
Battery - % change on year | -- | 0.070833 | 0.053812 | 0.042654 | 0.039604 | 0.046392 | 0.037838 | 0.039326 | 0.012003 | 0.012652 | 0.012814 | 0.01298 | 0.013151 | 0.013326 | 0.013506 | 0.013691 | 0.013881 | 0.014077 | 0.014278 | 0.014484 | 0.014697 | 0.014917 | 0.015142 | 0.015375 | 0.015615 | 0.015863 | 0.016119 | 0.016383
Battery - PSE | 1262.1588 | 1172.7559 | 1109.6479 | 1062.317 | 1020.245 | 972.9141 | 936.1011 | 899.2881 | 888.4941 | 877.253 | 866.0119 | 854.7708 | 843.5297 | 832.2886 | 821.0474 | 809.8063 | 798.5652 | 787.3241 | 776.083 | 764.8419 | 753.6008 | 742.3597 | 731.1186 | 719.8775 | 708.6364 | 697.3953 | 686.1542 | 674.9131
WA Wind - NREL ATB | 1308.4 | 1257.2 | 1206 | 1156.2372 | 1106.3478 | 1056.3318 | 1006.189 | 955.9193 | 946.3601 | 936.8009 | 927.2417 | 917.6825 | 908.1233 | 898.5641 | 889.0049 | 879.4457 | 869.8865 | 860.3273 | 850.7682 | 841.209 | 831.6498 | 822.0906 | 812.5314 | 802.9722 | 793.413 | 783.8538 | 774.2946 | 764.7354
WA Wind - % change on year | -- | 0.039132 | 0.040725 | 0.041263 | 0.043148 | 0.045208 | 0.047469 | 0.049961 | 0.01 | 0.010101 | 0.010204 | 0.010309 | 0.010417 | 0.010526 | 0.010638 | 0.010753 | 0.01087 | 0.010989 | 0.011111 | 0.011236 | 0.011364 | 0.011494 | 0.011628 | 0.011765 | 0.011905 | 0.012048 | 0.012195 | 0.012346
WA Wind - PSE | 1334.6666 | 1282.4387 | 1230.2109 | 1179.4491 | 1128.5581 | 1077.538 | 1026.3886 | 975.1097 | 965.3586 | 955.6075 | 945.8564 | 936.1053 | 926.3542 | 916.6031 | 906.852 | 897.1009 | 887.3498 | 877.5987 | 867.8476 | 858.0965 | 848.3454 | 838.5943 | 828.8432 | 819.0921 | 809.341 | 799.59 | 789.8389 | 780.0878
100 MW WA Solar + 50 MW Battery | 1146.5268 | 1085.607 | 1033.4522 | 987.0421 | 942.3368 | 895.8303 | 852.7817 | 809.6851 | 801.5432 | 793.2523 | 784.9614 | 776.6705 | 768.3797 | 760.0888 | 751.7979 | 743.507 | 735.2161 | 726.9253 | 718.6344 | 710.3435 | 702.0526 | 693.7618 | 685.4709 | 677.18 | 668.8891 | 660.5982 | 652.3074 | 644.0165
100 MW WA Wind + 50 MW Battery | 1310.4973 | 1245.8778 | 1190.0232 | 1140.405 | 1092.4538 | 1042.6634 | 996.2928 | 949.8358 | 939.7371 | 929.4893 | 919.2416 | 908.9938 | 898.746 | 888.4983 | 878.2505 | 868.0027 | 857.755 | 847.5072 | 837.2594 | 827.0117 | 816.7639 | 806.5161 | 796.2684 | 786.0206 | 775.7728 | 765.5251 | 755.2773 | 745.0295
O&M Scratch | 36.9293 | 36.2703 | 35.6113 | 34.9584 | 34.3049 | 33.6507 | 32.996 | 32.3407 | 32.0891 | 31.8376 | 31.5861 | 31.3345 | 31.083 | 30.8314 | 30.5799 | 30.3283 | 30.0768 | 29.8252 | 29.5737 | 29.3221 | 29.0706 | 28.819 | 28.5675 | 28.3159 | 28.0644 | 27.8128 | 27.5613 | 27.3097
WA Solar + Wind + Battery | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Solar - NREL ATB | 1073.784 | 1027.7458 | 981.7076 | 936.3879 | 890.9969 | 845.5346 | 800.0011 | 754.3966 | 747.6743 | 740.952 | 734.2296 | 727.5073 | 720.785 | 714.0627 | 707.3404 | 700.618 | 693.8957 | 687.1734 | 680.4511 | 673.7288 | 667.0065 | 660.2841 | 653.5618 | 646.8395 | 640.1172 | 633.3949 | 626.6725 | 619.9502
Solar - % change on year | -- | 0.042875 | 0.044795 | 0.046164 | 0.048475 | 0.051024 | 0.053852 | 0.057006 | 0.0089109 | 0.008991 | 0.0090725 | 0.0091556 | 0.0092402 | 0.0093264 | 0.0094142 | 0.0095037 | 0.0095948 | 0.0096878 | 0.0097826 | 0.0098792 | 0.0099778 | 0.010078 | 0.010181 | 0.010286 | 0.010393 | 0.010502 | 0.010613 | 0.010727
Solar - PSE | 1057.3371 | 1012.004 | 966.6709 | 922.0454 | 877.3497 | 832.5837 | 787.7477 | 742.8417 | 736.2223 | 729.603 | 722.9836 | 716.3642 | 709.7449 | 703.1255 | 696.5062 | 689.8868 | 683.2675 | 676.6481 | 670.0288 | 663.4094 | 656.7901 | 650.1707 | 643.5513 | 636.932 | 630.3126 | 623.6933 | 617.0739 | 610.4546
WA Wind - NREL ATB | 1308.4 | 1257.2 | 1206 | 1156.2372 | 1106.3478 | 1056.3318 | 1006.189 | 955.9193 | 946.3601 | 936.8009 | 927.2417 | 917.6825 | 908.1233 | 898.5641 | 889.0049 | 879.4457 | 869.8865 | 860.3273 | 850.7682 | 841.209 | 831.6498 | 822.0906 | 812.5314 | 802.9722 | 793.413 | 783.8538 | 774.2946 | 764.7354
WA Wind - % change on year | -- | 0.039132 | 0.040725 | 0.041263 | 0.043148 | 0.045208 | 0.047469 | 0.049961 | 0.01 | 0.010101 | 0.010204 | 0.010309 | 0.010417 | 0.010526 | 0.010638 | 0.010753 | 0.01087 | 0.010989 | 0.011111 | 0.011236 | 0.011364 | 0.011494 | 0.011628 | 0.011765 | 0.011905 | 0.012048 | 0.012195 | 0.012346
WA Wind - PSE | 1291.4493 | 1240.9126 | 1190.3759 | 1141.2578 | 1092.0147 | 1042.6467 | 993.1535 | 943.535 | 934.0997 | 924.6643 | 915.229 | 905.7936 | 896.3583 | 886.9229 | 877.4876 | 868.0522 | 858.6169 | 849.1815 | 839.7462 | 830.3108 | 820.8755 | 811.4401 | 802.0048 | 792.5694 | 783.1341 | 773.6987 | 764.2634 | 754.828
Battery - NREL ATB | 1255.7082 | 1166.7622 | 1103.9768 | 1056.8878 | 1015.0308 | 967.9418 | 931.3169 | 894.6921 | 883.9532 | 872.7695 | 861.5859 | 850.4022 | 839.2186 | 828.0349 | 816.8513 | 805.6676 | 794.484 | 783.3003 | 772.1167 | 760.933 | 749.7494 | 738.5657 | 727.3821 | 716.1984 | 705.0148 | 693.8311 | 682.6475 | 671.4638
Battery - % change on year | -- | 0.070833 | 0.053812 | 0.042654 | 0.039604 | 0.046392 | 0.037838 | 0.039326 | 0.012003 | 0.012652 | 0.012814 | 0.01298 | 0.013151 | 0.013326 | 0.013506 | 0.013691 | 0.013881 | 0.014077 | 0.014278 | 0.014484 | 0.014697 | 0.014917 | 0.015142 | 0.015375 | 0.015615 | 0.015863 | 0.016119 | 0.016383
Battery - PSE | 1251.0078 | 1162.3948 | 1099.8444 | 1052.9316 | 1011.2313 | 964.3185 | 927.8308 | 891.3431 | 880.6444 | 869.5026 | 858.3608 | 847.219 | 836.0772 | 824.9354 | 813.7936 | 802.6518 | 791.5101 | 780.3683 | 769.2265 | 758.0847 | 746.9429 | 735.8011 | 724.6593 | 713.5175 | 702.3757 | 691.234 | 680.0922 | 668.9504
100 MW WA Wind + 100 MW WA/OR Solar + 50 MW Battery | 1189.7161 | 1133.6456 | 1082.7876 | 1035.9076 | 989.992 | 942.9559 | 897.9266 | 852.8193 | 844.2577 | 835.6074 | 826.9572 | 818.307 | 809.6567 | 801.0065 | 792.3562 | 783.706 | 775.0558 | 766.4055 | 757.7553 | 749.105 | 740.4548 | 731.8046 | 723.1543 | 714.5041 | 705.8538 | 697.2036 | 688.5534 | 679.9031

## Frame Peaker
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: Add Fuel Storage Tank | PSE Adjustment 1 Total | PSE Adjustment 2: Add Spur Line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST | Notes
NREL ATB Nameplate (MW) | 233
Cost Components | $, thousands | % of Total | $/kW | Adder | $/kW | Adder | $/kW | $/kW
Civil/structural/architectural subtotal | 12300 | 7.419% | 63.2877 | -- | 63.2877 | -- | 63.2877 | 63.2877
Mech. Major equipment | 54000 | 32.57% | 277.8482 | -- | 277.8482 | -- | 277.8482 | 277.8482
Mech. BOP | 17200 | 10.37% | 88.4998 | 64.3777 | 152.8775 | -- | 152.8775 | 152.8775 | add fuel oil (distillate or biodiesel) storage tank, assumed $15,000,000 for 24hrs of capacit
Mechanical subtotal | 71200 | 42.95% | 366.348 | -- | 366.348 | -- | 366.348 | 366.348
Electrical subtotal | 20200 | 12.18% | 103.9358 | -- | 103.9358 | -- | 103.9358 | 103.9358
Project indirects | 1900 | 1.146% | 9.7761 | -- | 9.7761 | -- | 9.7761 | 9.7761
EPC fee | 12270 | 7.401% | 63.1333 | -- | 63.1333 | -- | 63.1333 | 63.1333
EPC subtotal | 134970 | 81.41% | 694.4662 | -- | 1037.2067 | -- | 759.3584 | 759.3584
Owner's services | 9448 | 5.699% | 48.6131 | -- | 48.6131 | -- | 48.6131 | 48.6131
Land | 600 | 0.3619% | 3.0872 | -- | 3.0872 | -- | 3.0872 | 3.0872
Electrical Interconnection | 1200 | 0.7238% | 6.1744 | -- | 6.1744 | 25.7778 | 31.9522 | 31.9522
Gas interconnection | 4500 | 2.714% | 23.154 | -- | 23.154 | -- | 23.154 | 23.154
Owner's cost subtotal | 15748 | 9.499% | 81.0288 | -- | 81.0288 | -- | 106.8066 | 106.8066
Project contingency | 15072 | 9.091% | 77.5505 | -- | 77.5505 | -- | 77.5505 | 77.5505
Total CAPEX | 165790 | 100% | 853.0455 | -- | 1195.786 | -- | 943.7155 | 943.7155
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 853.0455 | 833.3093 | 817.9588 | 809.1871 | 798.2225 | 791.6438 | 785.065 | 780.6792 | 775.1969 | 770.8111 | 766.4252 | 763.1358 | 758.75 | 754.3642 | 749.9783 | 746.6889 | 742.3031 | 737.9173 | 733.5314 | 730.2421 | 725.8562 | 721.4704 | 717.0845 | 713.7952 | 709.4093 | 706.1199 | 705.0235 | 702.8306
% change on year | -- | 0.023136 | 0.018421 | 0.010724 | 0.01355 | 0.0082418 | 0.0083102 | 0.0055866 | 0.0070225 | 0.0056577 | 0.0056899 | 0.0042918 | 0.0057471 | 0.0057803 | 0.005814 | 0.004386 | 0.0058737 | 0.0059084 | 0.0059435 | 0.0044843 | 0.006006 | 0.0060423 | 0.006079 | 0.0045872 | 0.0061444 | 0.0046368 | 0.0015528 | 0.0031104
After PSE Adjustments | 943.7155 | 921.8815 | 904.8995 | 895.1954 | 883.0654 | 875.7874 | 868.5094 | 863.6574 | 857.5924 | 852.7404 | 847.8884 | 844.2494 | 839.3974 | 834.5453 | 829.6933 | 826.0543 | 821.2023 | 816.3503 | 811.4983 | 807.8593 | 803.0073 | 798.1553 | 793.3033 | 789.6643 | 784.8123 | 781.1733 | 779.9603 | 777.5343

## CCCT
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 727
Description | $/kW | % of Total | $/kW | Adder | $/kW | $/kW
Feedwater & Misc. BOP Systems | 129.5406 | 12.46% | 119.9293 | 0 | 119.9293 | 119.9293
CT & Accessories | 156.4801 | 15.05% | 144.87 | 0 | 144.87 | 144.87
HRSG, Ductwork & Stack | 158.5832 | 15.25% | 146.8171 | 0 | 146.8171 | 146.8171
Steam Turbine & Accessories | 132.8377 | 12.77% | 122.9818 | 0 | 122.9818 | 122.9818
Cooling Water System | 53.6561 | 5.16% | 49.6751 | 0 | 49.6751 | 49.6751
Accessory Electric Plant | 56.8542 | 5.468% | 52.6359 | 0 | 52.6359 | 52.6359
Instrumentation & Control | 26.8955 | 2.586% | 24.8999 | 0 | 24.8999 | 24.8999
Improvements to Site | 38.2916 | 3.682% | 35.4506 | 0 | 35.4506 | 35.4506
Building & Structure | 26.74 | 2.572% | 24.756 | 22.3214 | 47.0775 | 47.0775
Total | 779.879 | 75% | 722.0156 | 0 | 744.337 | 744.337
Owners Cost
Pre-Production Costs | 27.5598 | 2.65% | 25.515 | 0 | 25.515 | 25.515
Inventory Capital | 4.3109 | 0.4146% | 3.991 | 0 | 3.991 | 3.991
Initial Cost for Catalyst & Chemicals | 1.1651 | 0.112% | 1.0786 | 0 | 1.0786 | 1.0786
Land | 0.41265 | 0.03968% | 0.38204 | 0 | 0.38204 | 0.38204
Other Owner's Costs | 116.9821 | 11.25% | 108.3026 | 0 | 108.3026 | 108.3026
Financing Costs | 21.0564 | 2.025% | 19.4941 | 0 | 19.4941 | 19.4941
Total Overnight Costs | 951.3659 | 91.49% | 880.779 | 0 | 903.1005 | 903.1005
TASC Multiplier (IOU, 33 year) | 1.093 | 1.093 | 1052.2218 | 1.093 | 1.093 | 1.093
Total As-Spent Cost | 1039.8429 | 100% | 962.6915 | 0 | 987.0888 | 987.0888
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 962.6915 | 949.534 | 940.7623 | 934.1835 | 926.5083 | 921.026 | 915.5437 | 912.2543 | 906.772 | 903.4827 | 899.0968 | 895.8074 | 891.4216 | 888.1322 | 883.7464 | 880.457 | 876.0712 | 872.7818 | 869.4924 | 865.1066 | 861.8172 | 857.4314 | 854.142 | 849.7561 | 846.4668 | 842.0809 | 839.888 | 837.6951 | 842.0809 | 839.888 | 837.6951
% change on year | -- | 0.013667 | 0.0092379 | 0.006993 | 0.008216 | 0.0059172 | 0.0059524 | 0.0035928 | 0.0060096 | 0.0036276 | 0.0048544 | 0.0036585 | 0.004896 | 0.00369 | 0.0049383 | 0.0037221 | 0.0049813 | 0.0037547 | 0.0037688 | 0.0050441 | 0.0038023 | 0.0050891 | 0.0038363 | 0.0051348 | 0.003871 | 0.0051813 | 0.0026042 | 0.002611 | -0.0052356 | 0.0026042 | 0.002611
After PSE Adjustments | 987.0888 | 973.5978 | 964.6039 | 957.8584 | 949.9887 | 944.3674 | 938.7462 | 935.3734 | 929.7522 | 926.3795 | 921.8825 | 918.5097 | 914.0128 | 910.64 | 906.143 | 902.7703 | 898.2733 | 894.9006 | 891.5278 | 887.0308 | 883.6581 | 879.1611 | 875.7884 | 871.2914 | 867.9186 | 863.4216 | 861.1731 | 858.9247 | 863.4216 | 861.1731 | 858.9247

## Recip Peaker
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: Add Spur Line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST | Notes
2022 EIA AEO (MW) | 21.4
Cost Components | $, thousands | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW
Civil/structural/architectural subtotal | 6861 | 17.72% | 348.9272 | 2.5% | 357.6504 | -- | 357.6504 | 357.6504
Engines | 11974 | 30.92% | 608.957 | 2.5% | 624.181 | -- | 624.181 | 624.181
Mechanical BOP | 5521 | 14.26% | 280.7793 | 2.5% | 287.7988 | -- | 287.7988 | 287.7988
Mechanical subtotal | 17495 | 45.18% | 889.7364 | 2.5% | 911.9798 | -- | 911.9798 | 911.9798
Electrical subtotal | 6668 | 17.22% | 339.1119 | 2.5% | 347.5897 | -- | 347.5897 | 347.5897
Project indirects | 180 | 0.4648% | 9.1542 | 2.5% | 9.383 | -- | 9.383 | 9.383
EPC fee | 1923 | 4.966% | 97.7973 | 2.5% | 100.2422 | -- | 100.2422 | 100.2422
EPC subtotal | 33127 | 85.54% | 1684.7269 | 2.5% | 1726.8451 | -- | 1726.8451 | 1726.8451
Owner's services | 1586 | 4.095% | 80.6586 | 2.5% | 82.675 | -- | 82.675 | 82.675
Land | 300 | 0.7747% | 15.257 | 2.5% | 15.6384 | -- | 15.6384 | 15.6384
Owner's fuirnished equipment |  |  | 0
Electrical Interconnection | 720 | 1.859% | 36.6168 | 2.5% | 37.5322 | 26.484 | 64.0162 | 64.0162
Gas interconnection | 125 | 0.3228% | 6.3571 | 2.5% | 6.516 | -- | 6.516 | 6.516
Owner's cost subtotal | 14705 | 37.97% | 747.8464 | 2.5% | 766.5426 | -- | 766.5426 | 766.5426
Project contingency | 2869 | 7.408% | 145.9076 | 2.5% | 149.5553 | -- | 149.5553 | 149.5553
Total CAPEX | 38727 | 100% | 1969.5239 | 2.5% | 2018.762 | -- | 2045.246 | 2045.246
↓ COST CURVE ↓
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 EIA AEO | 1969.5239 | 1942.9808 | 1927.265 | 1909.4562 | 1885.9259 | 1861.1742 | 1837.374 | 1819.2113 | 1803.0771 | 1787.01 | 1771.6263 | 1758.6981 | 1744.7401 | 1733.0712 | 1725.5359 | 1718.4016 | 1711.277 | 1703.7023 | 1694.8709 | 1685.7461 | 1676.1819 | 1665.9258 | 1655.6898 | 1646.3783 | 1636.667 | 1627.8387 | 1620.1965 | 1611.729
% change on year | -- | 0.013477 | 0.0080885 | 0.0092405 | 0.012323 | 0.013124 | 0.012788 | 0.0098852 | 0.0088688 | 0.008911 | 0.0086086 | 0.0072974 | 0.0079366 | 0.0066881 | 0.0043479 | 0.0041345 | 0.0041461 | 0.0044263 | 0.0051837 | 0.0053837 | 0.0056736 | 0.0061187 | 0.0061443 | 0.005624 | 0.0058986 | 0.005394 | 0.0046947 | 0.0052262
After PSE Adjustments | 2045.246 | 2017.6825 | 2001.3624 | 1982.8689 | 1958.4339 | 1932.7306 | 1908.0154 | 1889.1544 | 1872.3999 | 1855.715 | 1839.7399 | 1826.3146 | 1811.82 | 1799.7024 | 1791.8774 | 1784.4688 | 1777.0703 | 1769.2044 | 1760.0334 | 1750.5578 | 1740.6259 | 1729.9755 | 1719.346 | 1709.6765 | 1699.5918 | 1690.4241 | 1682.4881 | 1673.695

## Small Modular Nuclear
Source material |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2022 NREL 2020 vintage, 2020 $ | PSE Adjustment 1: Add 5 Mile Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 600 |  | $/kW | Adder | $/kW | $/kW
Civil/structural/architectural subtotal | 583524 | 15.71% | 1231.4669 | -- | 1231.4669 | 1231.4669
Nuclear island | 648360 | 17.45% | 1368.2966 | -- | 1368.2966 | 1368.2966
Conventional island | 421434 | 11.35% | 889.3928 | -- | 889.3928 | 889.3928
Balance of Plant | 389016 | 10.47% | 820.9779 | -- | 820.9779 | 820.9779
Mechanical subtotal | 1458810 | 39.27% | 3078.6673 | -- | 3078.6673 | 3078.6673
Electrical subtotal | 259344 | 6.982% | 547.3186 | -- | 547.3186 | 547.3186
Project indirects | 551000 | 14.83% | 1162.8284 |  | 1162.8284 | 1162.8284
EPC fee | 285267.8 | 7.68% | 602.0281 | -- | 602.0281 | 602.0281
EPC subtotal | 3137945.8 | 84.48% | 6622.3093 | -- | 6622.3093 | 6622.3093
Owner's services | 235346 | 6.336% | 496.6733 |  | 496.6733 | 496.6733
Land | 1050 | 0.02827% | 2.2159 | -- | 2.2159 | 2.2159
Electrical Interconnection | 2520 | 0.06784% | 5.3182 | 12.5 | 17.8182 | 17.8182
Owner's cost subtotal | 238916 | 6.432% | 504.2075 | -- | 516.7075 | 516.7075
Project contingency | 337686 | 9.091% | 712.6513 |  | 712.6513 | 712.6513
Total CAPEX | 3714547.8 | 100% | 10917.8353 |  | 10930.3353 | 10930.3353
Not enough information available to generate reliable cost curve at present
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2022 NREL ATB | 7839.1681 | 7789.2325 | 7739.3026 | 7724.0842 | 7708.5985 | 7692.8495 | 7676.829 | 7660.5361 | 7609.463 | 7558.392 | 7507.3251 | 7456.2486 | 7405.1793 | 7354.1083 | 7303.0415 | 7251.9702 | 7200.9002 | 7149.8319 | 7098.7561 | 7047.6857 | 6996.6151 | 6945.5444 | 6894.4801 | 6843.4088 | 6792.3384 | 6741.2643 | 6690.194 | 6639.1239
% change on year | -- | 0.00637 | 0.0064101 | 0.0019664 | 0.0020049 | 0.002043 | 0.0020825 | 0.0021223 | 0.0066671 | 0.0067115 | 0.0067563 | 0.0068036 | 0.0068492 | 0.0068967 | 0.006944 | 0.0069932 | 0.0070422 | 0.0070919 | 0.0071436 | 0.0071943 | 0.0072464 | 0.0072993 | 0.0073521 | 0.0074076 | 0.0074627 | 0.0075194 | 0.0075758 | 0.0076336
After PSE Adjustments ($/kW) | 10930.3353 | 10860.709 | 10791.0906 | 10769.8712 | 10748.2791 | 10726.32 | 10703.9822 | 10681.2647 | 10610.0521 | 10538.8426 | 10467.639 | 10396.4217 | 10325.2147 | 10254.0052 | 10182.8016 | 10111.5917 | 10040.3835 | 9969.1778 | 9897.9616 | 9826.753 | 9755.544 | 9684.335 | 9613.1349 | 9541.9249 | 9470.7163 | 9399.5025 | 9328.294 | 9257.0856

## Inflation
Average Annual Inflation: | 2.5%