0099

1   BEFORE THE WASHINGTON UTILITIES AND TRANSPORTATION

2                         COMMISSION

3   WASHINGTON UTILITIES AND      )

TRANSPORTATION COMMISSION,    )

4                                 )

Complainant,   )

5                                 )

vs.                 )    DOCKET NO. PG-041624

6                                 )    Volume VII

PUGET SOUND ENERGY, INC.,     )    Pages 99 - 135

7                                 )

Respondent.    )

8   ---------------------------------

9

10             A settlement conference in the above matter

11   was held on September 28, 2005, at 2:00 p.m., at 1300

12   South Evergreen Park Drive Southwest, Olympia,

13   Washington, before Administrative Law Judge THEODORA

14   MACE, Chairman MARK SIDRAN, Commissioner PATRICK J.

15   OSHIE, Commissioner PHILIP B. JONES.

16

The parties were present as follows:

17

WASHINGTON UTILITIES AND TRANSPORTATION

18   COMMISSION, by DONALD T. TROTTER, Assistant Attorney

General, 1400 South Evergreen Park Drive Southwest,

19   Post Office Box 40128, Olympia, Washington  98504;

telephone, (360) 664-1189.

20

PUGET SOUND ENERGY, INC., by JAMES F.

21   WILLIAMS and AMANDA BEANE, Attorneys at Law, Perkins

Coie, LLP, 1201 Third Avenue, Suite 4800, Seattle,

22   Washington  98101; telephone, (206) 359-3543.

23             CITY OF BELLEVUE, by CHERYL A. ZAKRZEWSKI,

Attorney at Law, City Attorney's Office, Post Office

24   Box 90012, Bellevue, Washington  98009; telephone,

(425) 452-6829.

25

Kathryn T. Wilson, CCR, Court Reporter

0100

1   _____________________________________________________

2                      INDEX OF EXHIBITS

3   _____________________________________________________

4   EXHIBIT:            MARKED:   OFFERED:  ADMITTED:

5      1                103       109       109

6      2                103       109       109

7   All prefiled exhibits admitted on Page 109.  See

8   attached list.

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

0101

1                    P R O C E E D I N G S

2             JUDGE MACE:  Let's be on the record in

3   Docket No. PG-041624.  This is a complaint of the

4   Washington Utilities and Transportation Commission

5   against Puget Sound Energy.  We are convened today,

6   September 28th, 2005, at the offices of the Washington

7   Utilities and Transportation Commission in Olympia,

8   Washington for a hearing to review a settlement

9   agreement filed by the parties to this case in revised

10   form on September 22nd, 2005.

11             My name is Theodora Mace.  I'm the

12   administrative law judge assigned to this case.  With

13   me on the Bench are Commission Chairman Mark Sidran to

14   my right, and Commissioners Patrick Oshie and Philip

15   Jones.

16             At this point, I would like to take the oral

17   appearances of the parties, and I'll begin with the

18   Company.

19             MR. WILLIAMS:  This is James Williams, and

20   here with me is Amanda Beane on behalf of Puget Sound

21   Energy.

22             JUDGE MACE:  Ms. Zakrzewski?

23             MS. ZAKRZEWSKI:  This is Cheryl Zakrzewski.

24   I'm here on behalf of the City of Bellevue.

25             MR. TROTTER:  Donald T. Trotter, assistant

0102

1   attorney general for Commission staff.

2             JUDGE MACE:  Are there any appearances from

3   the conference bridge?  Let the record show I hear

4   none.

5             This case was initiated by the Commission to

6   investigate a natural gas explosion that occurred in

7   the Spirit Ridge neighborhood of the City of Bellevue

8   on September 2nd, 2004.  As a result of this explosion

9   at the residence of Mrs. Francis Schmitz, Mrs. Schmitz

10   subsequently died.

11             The parties to the case, Commission staff,

12   Puget Sound Energy and the City of Bellevue, have

13   engaged in an intensive investigation of the explosion

14   and its possible causes.  Both the Commission staff and

15   Puget Sound Energy filed direct testimony in the case,

16   including the testimony of leading experts on corrosion

17   and natural gas pipes and on the system of cathodic

18   protection for those pipes.  Ultimately, the parties

19   reached a settlement, which in its revised form is what

20   we have before us today.

21             At this point, I'm just going to go briefly

22   through our agenda for the proceeding.  I'm going to

23   ask counsel to describe and present the settlement

24   agreement and the narrative supporting the settlement

25   agreement.  After the settlement is presented, I'm

0103

1   going to swear the witnesses in, and I understand that

2   there will be two witnesses, Mr. Secrist for Puget

3   Sound Energy; is that right?

4             MR. WILLIAMS:  That's correct.  Mr. Secrist

5   and Mr. Henderson.

6             JUDGE MACE:  And Mr. Rathbun from Commission

7   staff, and Mr. Rathbun will be appearing via conference

8   bridge.  I will ask the witnesses to make their

9   statements about the settlement agreement, particularly

10   addressing the public interest related to the

11   settlement agreement, and then we will open it to the

12   commissioners for questions with regard to the

13   settlement agreement.

14             So that's the procedure that we are going to

15   follow today, and I would like to begin at this point

16   indicating to counsel that --

17             CHAIRMAN SIDRAN:  Judge, excuse me.  Sorry to

18   interrupt you, but I would like to inquire as to

19   whether there is anyone from the Schmitz family or

20   anyone representing Mrs. Schmitz here or on the bridge

21   line?  Thank you.

22             JUDGE MACE:  So to get back to the agenda,

23   let me hear first from counsel about the settlement

24   agreement, present the settlement agreement.  I have

25   marked the settlement agreement Exhibit No. 1 and the

0104

1   narrative in support as Exhibit No. 2.  Mr. Trotter.

2             MR. TROTTER:  I would be happy to introduce

3   these two documents if there is no objection from other

4   counsel.  Hearing none, I will proceed.

5             Your Honor, I will give a brief overview of

6   both documents.  I believe Mr. Rathbun will be giving a

7   statement in support of the settlement that will go

8   into some of the details, but as the Commission is

9   aware, on September 2nd of 2004, there was a tragic gas

10   explosion in Bellevue, Washington.  Mrs. Schmitz was

11   killed as a result of that explosion.  She died several

12   days after the event of burns.

13             A very comprehensive investigation took

14   place, but shortly after the explosion on September

15   13th, the Commission issued a complaint.  In that

16   complaint, it alleged that the explosion was due to

17   corrosion.  It also alleged there was a cross-wired

18   rectifier in the vicinity.  It alleged several specific

19   violations related to the cross-wired rectifier, and

20   then it had some general allegations.

21             Shortly after that, the parties brought to

22   the Commission in the context of an emergency

23   adjudication an action plan to promptly assess the

24   nature of the plant in the area and to take whatever

25   steps were necessary to assure this type of incident

0105

1   would not be repeated.  That included 30-day gas leak

2   inspections and so on when the normal interval for a

3   residential area is five years, so it was a very

4   aggressive program, and as the testimony of Staff

5   states, PSE complied with that order.

6             Before you now is a proposal to settle this

7   case.  As you know, the Staff and the Company have

8   filed testimony.  Staff has not filed any rebuttal

9   testimony, but that is the stage where we are right

10   now.  You have the direct cases of both parties.  The

11   City of Bellevue did not file direct testimony.

12             The settlement, if accepted, would resolve

13   all issues in the docket.  It's in Exhibit No. 1.  I'll

14   provide some background information.  The agreement

15   does recite the basic findings of the results of the

16   investigations of Staff, experts, and the experts for

17   PSE.  Alan Rathbun will give you some more information

18   on that.

19             It does recite that the specific violations

20   alleged in the Complaint have been cured, and those

21   relate to the cross-wired rectifier and the violations

22   of the Company's failure to maintain proper levels of

23   cathodic protection as a result of that cross-wired

24   configuration.  Those violations have been cured, and

25   by that, I mean the cross-wired rectifier has been

0106

1   wired correctly, and as you see in the Agreement, there

2   have been some provisions for addressing similar-type

3   problems in other parts of the system, potential

4   problems.  None have been found.

5             A key part of the Agreement starts in

6   Paragraph 14, which is the risk assessment and

7   mitigation program.  Whereas you read in Staff's

8   expert's testimony, there was concern that similar-type

9   vintage systems in PSE's service territory may have

10   similar problems.  We don't know if they do.  We don't

11   know if they do not.

12             This program is designed, first of all, to

13   gather information on the characteristics of various

14   parts of the system and prioritize an assessment and

15   mitigation plan if any problems are found in those

16   parts of PSE's system that are ranked according to the

17   need to look at it and examine whether similar problems

18   might exist.

19             There is procedures for bringing issues to

20   the Commission if they arise, but we don't believe any

21   other company is doing this sort of assessment in the

22   State of Washington.  We think it's an important

23   program and will have value for the Company and the

24   Commission and the ratepayers.

25             Starting on Paragraph 20, the Commission

0107

1   staff through the testimony of Mr. Kuan-Shi Chu made

2   some specific recommendations regarding securing

3   rectifiers, changes to the Company's procedural manual

4   on the way they take cathodic protection readings and

5   certain protocols in those regards, and the Company has

6   changed its policies accordingly in compliance with

7   those recommendations, and that's what Paragraphs 20

8   through 22 are all about.

9             Paragraphs 23 and 24 address what to do about

10   the conditions in Order No. 1, because that order was

11   not time limited, and one of the things that will be

12   changed is the monthly leak surveys will cease.  We

13   will have one more leak survey between June 20th, 2006,

14   and September 20th, 2006, and then that system will go

15   on a different track.  So we had to do something to

16   determine what should happen to the conditions in Order

17   No. 1, and Paragraphs 23 and 24 address that.

18             Regarding other matters in the Agreement, it

19   calls for a $90,000 cash penalty.  According to the

20   Agreement, it recites Staff's calculation of $125,000

21   maximum penalty for the specific violations.  Staff

22   testified to six mitigating factors that are listed in

23   the Agreement, brought that to $90,000 based on

24   consideration of those factors.  The remainder of the

25   agreement, I think, is fairly standard in terms of

0108

1   procedures and integrative agreement and so on.

2             With regard to Exhibit 2, the revised

3   narrative supporting settlement, by and large, that

4   recites what the Agreement does, and hopefully, it's

5   consistent with what I've told you today and with

6   Exhibit 1, and then it contains the statements of each

7   party in support of the narrative, and I think it

8   pretty much speaks for itself, but if you wish to have

9   some highlighting on that, perhaps Mr. Rathbun is the

10   best one to provide that.  I have nothing further to

11   offer.  I would be happy to respond to any questions.

12             JUDGE MACE:  Mr. Williams?

13             MR. WILLIAMS:  Just one point of

14   clarification.  I agree with everything that counsel

15   has said, but from the Company's perspective, one thing

16   we think is important to note is that we are confident

17   that there are no other anomalous situations like the

18   one that was created at the Schmitz house, but in an

19   abundance of caution, we agree we should take a look at

20   those other homes that are of a similar vintage.

21             JUDGE MACE:  Ms. Zakrzewski, did you have

22   anything to add?

23             MS. ZAKRZEWSKI:  No.

24             JUDGE MACE:  Do the parties offer the

25   Settlement Agreement and the narrative in support into

0109

1   evidence?

2             MR. TROTTER:  Yes, Your Honor.

3             JUDGE MACE:  I'll admit those documents at

4   this time as Exhibits No. 1 and 2.  Under the terms of

5   the settlement agreement, the parties also stipulate to

6   the entry of all the prefiled exhibits.  I have marked

7   those and provided a copy of the exhibit list to the

8   court reporter, to counsel, and also to the

9   commissioners, and in view of the stipulation for entry

10   of the exhibits into evidence, I will admit them at

11   this time.

12             At this point, I'm ready to have the

13   witnesses in the hearing room stand and raise their

14   right hands, and Mr. Rathbun, are you on the conference

15   bridge?

16             MR. RATHBUN:  Yes, I am, Judge Mace.

17             JUDGE MACE:  I'm going to administer the oath

18   at this time, and I will ask you to say "I do" at the

19   end.

20             (Witnesses sworn.)

21             JUDGE MACE:  Mr. Secrist and Mr. Henderson

22   from Puget Sound Energy, gentlemen, also the same

23   advice for you.  You need to have that button popped

24   up.  I understand, Mr. Rathbun, that you have a

25   statement with regard to the Agreement.  I would like

0110

1   to have Mr. Rathbun speak first, unless the parties

2   have another agreement about that, and then have

3   Mr. Secrist and Mr. Henderson address the settlement

4   agreement if they desire to do so.  Mr. Rathbun?

5             MR. RATHBUN:  Good afternoon, Judge Mace,

6   Chairman Sidran, Commissioners Oshie and Jones.  Can

7   you hear me okay?

8             JUDGE MACE:  Yes.  And Mr. Rathbun and

9   Mr. Secrist and Mr. Henderson, we need to have you

10   state your names, employers, and positions before you

11   begin to speak.  Go ahead, Mr. Rathbun.

12             MR. RATHBUN:  Thank you.  Again, my name is

13   Alan Rathbun.  I'm the pipeline safety director to the

14   Washington Utilities and Transportation Commission.  I

15   thank you for the opportunity to testify this afternoon

16   relative to the settlement that is before you.

17             I would like to very briefly give a summary

18   of the events that's before you today and then describe

19   in a little bit more detail some of the elements of

20   that settlement and how we arrived at those.

21             On September 2nd, 2004, Staff reacted

22   immediately to this tragic incident by sending two

23   investigators to the scene and commencing an

24   investigation.  PSE on September 3rd, the following

25   day, discovered that the rectifier was cross-wired and

0111

1   immediately did notify Staff.

2             Given the serious ultimate fatal injury, the

3   extent of damage, and the unknown impact of the

4   cross-wired rectifier, sought emergency action.  The

5   Commission initiated an emergency adjudicative

6   proceeding.  Staff and PSE submitted and agreed upon a

7   nine-step action plan designed to, one, provide for

8   public communication; two, conducting of a thorough and

9   orderly investigation, and three, taking other

10   operational precautions to assure the safety of the

11   community during the investigation.  The Commission

12   entered this order on September 17th of 2004.

13             Staff's goal in this investigation was to,

14   one, find the cause of the leak that led to this house

15   explosion and loss of life, which at the time was

16   assumed to be external corrosion, and to investigate

17   the integrity of PSE's surrounding gas distribution

18   system.

19             The Commission hired a recognized expert,

20   Dr. Graham Bell.  Two staff members along with this

21   consultant did a thorough analysis of PSE's records,

22   interviewed PSE personnel, and monitored PSE's

23   investigation and analysis of the failed service pipe.

24   Further, Staff participated in the community outreach

25   efforts in the Spirit Ridge neighborhood and the City

0112

1   of Bellevue as a whole.

2             At the same time, PSE on its own initiative

3   completed a replacement of all coated steel service

4   pipes that they believe were potentially impacted by

5   the cross-wired rectifier.  This construction was

6   consistently under the observation of Commission staff.

7             Based on the testimony and the experts and

8   the exhibits in the record, it is clear that each of

9   the experts retained by all parties agree that the

10   cause of the service pipe failure was due to external

11   corrosion that occurred over a period that long

12   preceded the cross-wiring of the rectifier.  Likely, a

13   majority of this corrosion occurred during the period

14   between the service's installation in 1963 and the

15   application of an impressed current cathodic protection

16   system in 1982.

17             Federal pipeline safety regulations did not

18   require such cathodic protection systems until 1971,

19   and this regulation in 1971 was not retroactive to

20   systems constructed earlier.  Other than the Company's

21   failure to maintain adequate cathodic protection during

22   the period of the cross-wired rectifier, Staff did not

23   find any violation of Commission rule or federal

24   regulation.

25             In addition, staff's expert could not find

0113

1   any causal connection between the probable rule

2   violation and the leak that led to the explosion.

3   Dr. Bell's testimony concludes the leak began many

4   months to perhaps years prior to the cross-wiring.

5   However, we did find some concerns that were not

6   currently addressed by regulation, the resolution of

7   which became the focus of our recommendations and were

8   involved in our settlement negotiations.

9             Based on Staff's review of the evidence, our

10   primary recommendation in this case was for PSE to

11   assess its coated steel pipe with similar

12   circumstances.  Again, that pipe that was installed at

13   least five years prior to application of the proper

14   cathodic protection system through a comprehensive

15   analysis of existing data.  This analysis is aimed at

16   those pipes at the greatest risk to public safety, the

17   services that bring gas to residences and other

18   inhabited structures.

19             Higher risk or problematic areas identified

20   in this analysis will be subject to further

21   investigation and possible replacement or other

22   acceptable remediation.  This sort of analysis and

23   remediation is beyond any requirement of federal or

24   state pipeline safety rules.  Further, Staff

25   recommended changes to PSE's operating standards and

0114

1   practices regarding the monitoring of cathodic

2   protection and reaction to rare occurrences like the

3   cross-wired rectifier.  Also, none of these

4   requirements are in existing state or federal rules.

5             We also recommended the maximum penalty that

6   we believe we were allowed to assess under state law.

7   The Agreement before you today addresses each of

8   Staff's five recommendations included in my prefiled

9   testimony.  By adopting these recommendations, this

10   agreement institutes what's learned from this tragic

11   experience and holds the Company to a standard not

12   currently covered by federal and state regulations.

13             The $90,000 recommended penalty was based on

14   Staff's calculation of the maximum possible penalty of

15   $125,000 with the six mitigating factors applied that

16   Mr. Trotter spoke of.  Thank you very much for your

17   time, and I'm available to answer any questions you may

18   have.

19             JUDGE MACE:  Thank you, Mr. Rathbun.  I'll

20   first turn to the PSE witnesses and ask them for their

21   statements and then open it to questions.  Gentlemen,

22   would you introduce yourselves and then proceed?

23             MR. HENDERSON:  My name is Duane Henderson.

24   I'm PSE's director of safety and operations services.

25             MR. SECRIST:  My name is Steve Secrist,

0115

1   employee of Puget Sound Energy, assisting general

2   counsel.

3             JUDGE MACE:  Go ahead, Mr. Henderson.

4             MR. HENDERSON:  Thank you, Judge Mace,

5   Chairman, Commissioners.  Briefly, I just want to echo

6   the comments of Mr. Rathbun.  I want to recognize the

7   thoroughness with which the investigation, both by

8   Staff, the outside experts, and the Company, went into

9   reaching this settlement, and just in support of the

10   statement that Mr. Rathbun has shared with us already.

11             JUDGE MACE:  Mr. Secrist, anything further.

12             MR. SECRIST:  Nothing further.

13             JUDGE MACE:  I would like to open it up to

14   questions.  Chairman Sidran?

15             CHAIRMAN SIDRAN:  Thank you.  A couple of

16   questions about the PSE system.  I wonder, and I

17   suppose perhaps, Mr. Henderson, this is addressed to

18   you, can you give me some sense of how much comparable

19   pipe, so to speak, is out there?  In other words, we've

20   heard from Mr. Rathbun the description of the nature of

21   the pipe itself and the date of installation, which I

22   think he said preceded 1971 when this regulation

23   requiring cathodic protection came into effect.  Can

24   you give me some idea in terms of feet or in terms of

25   the percentage of your system that you think falls in

0116

1   this category?

2             MR. HENDERSON:  As part of this whole risk

3   assessment, the first piece is to conduct an inventory

4   to come up with a better number, but right now, we are

5   looking at something in the neighborhood of 70- to

6   100,000 services, and again, this is out of a total of

7   680,000 service lines in our service territory.

8             CHAIRMAN SIDRAN:  And Mr. Rathbun, perhaps

9   this is for you.  Have Staff examined the possible

10   extension of what's being required here as part of this

11   settlement in terms of examination of comparable pipe

12   to other companies?  Understanding that there is no

13   rule or regulation, I take your point, but is Staff

14   looking at that issue in whether there might be similar

15   circumstances among other companies?

16             MR. RATHBUN:  Chairman Sidran, yes, we did,

17   and in my prefiled testimony, in fact, we did recognize

18   that this sort of assessment, we recommend, should be

19   considered for potential rule-making.

20             CHAIRMAN SIDRAN:  Thank you.

21             JUDGE MACE:  Commissioner Oshie?

22             COMMISSIONER OSHIE:  Let's go back to the

23   question that was raised by the Chair, a corollary to

24   this, is how long a process is anticipated by both

25   Staff and PSE to complete the actions that are

0117

1   contemplated in Paragraph 14, going to look at the 70-

2   to 100,000 service lines of similar vintage, and there

3   is a series of data points that you are going to be

4   gathering.  I'm assuming that some of that has already

5   been done.  This occurred roughly a year ago, and I

6   would be surprised to find out you haven't done

7   anything to this point, so you must already have

8   started your part of the process.  You are looking at

9   your service lines.

10             So how long from this point is it going to

11   take to complete the tasks that are called for in

12   Paragraph 14, and I would like to hear from Staff's

13   view of this as well as the Company's.

14             MR. HENDERSON:  I'll offer up first.

15   Throughout the negotiations, that very question came

16   up, and we are anticipating that by this time next year

17   that we will have the assessment complete, and built

18   into the process are periodic checkpoints with Staff to

19   apprise them of both the progress and the findings that

20   we've had throughout that, but we believe the entire

21   scope can be completed by this time next year.

22             JUDGE MACE:  Mr. Rathbun, did you want to

23   address that?

24             MR. RATHBUN:  Yes, we concur.  I believe we

25   did put a date in the proposed agreement which called

0118

1   for a date of September for completion, and Staff is

2   committed to providing the resources for collaboration

3   through the entire process.

4             JUDGE MACE:  I see in Paragraph 29 a date of

5   September 1st, 2006.  Is that the date that you are

6   referring to?

7             MR. RATHBUN:  Yes, Judge Mace, that is the

8   date I'm referring to.

9             JUDGE MACE:  Commissioner Oshie?

10             COMMISSIONER OSHIE:  Not at this time, thank

11   you.

12             JUDGE MACE:  Commissioner Jones?

13             COMMISSIONER JONES:  Just a follow-up on that

14   question.  Could you give us more details on the

15   assessment?  We all realize there is no perfect energy

16   supply system in the word.  There are always risks

17   associated with it, so the assessment system and the

18   prioritization of how you do this is very important.

19   What system do you use?  How do you prioritize, and how

20   long will the assessment take before you get to

21   decisions on remediation?

22             MR. HENDERSON:  Maybe if I could describe

23   just a little bit the process that we are undertaking

24   right now.  First of all, there is the inventory, and

25   as they've described, the services of interest are

0119

1   those that have been in the ground for some period,

2   five years prior to the application of cathodic

3   protection.  That is not easily determined based on any

4   of our databases that we currently have, so there is a

5   lot of manual searching through records just to

6   understand not only when the service was installed,

7   which is fairly easy to determine, but to figure out

8   when cathodic protection was applied, so that will be

9   step one in the inventory.

10             Once we've identified the population to

11   consider, we will then be turning our attention to all

12   of the current information that we collect through our

13   normal routine, maintenance, and operation activities,

14   and this includes leakage information in geographic

15   areas and for specific services themselves.  We will be

16   looking at pipe condition reports.  Every time a piece

17   of pipe is exposed, we fill out pipe condition reports,

18   so that's another data point.

19             We will be looking at soils reports and

20   things like that.  This is a data collection effort,

21   and once we've collected that data, we will stack it up

22   and see if there are any trends or areas of concern

23   that start to come out, and this is where we will be

24   working closely with Commission staff to see that we

25   are all in agreement as to the criteria to surface

0120

1   those areas of concern.

2             COMMISSIONER JONES:  Will all this work be

3   done internally, or will you be using the same outside

4   consultants?

5             MR. HENDERSON:  It's anticipated we will

6   perform all of this work internally.

7             COMMISSIONER JONES:  You mentioned 70,000 to

8   100,000 services will be the inventory.  How many miles

9   or kilometers of pipe is that?

10             MR. HENDERSON:  70,000, roughly 100 feet per

11   service.  I don't have a calculator here, but that's a

12   rough order of the magnitude.

13             COMMISSIONER JONES:  Mr. Rathbun, in this

14   case, isn't it correct there was a 19-year interval

15   between the installation of the service line to the

16   Schmitz house and the application of cathodic

17   protection?

18             MR. RATHBUN:  Yes, that's correct,

19   approximately 19 years.

20             COMMISSIONER JONES:  Would that 19-year

21   interval -- do you as staff have any idea about -- is

22   that interval common?  Is that what we are going to

23   find out, or we just don't know at this point?  Because

24   I would think a 19-year interval is fairly significant.

25   Do you have any idea what the interval would be on the

0121

1   70,000 to 100,000 services, or are we just going to

2   wait to see what PSE comes up with in its inventory?

3             MR. RATHBUN:  Again, we really don't have

4   that information available right now.  The information

5   that we do have is from PSE's annual reports, which

6   talked about, as I recall, about 167,000 coated steel

7   services, the ones for which there likely may have been

8   a cathodic protection, similar type of pipes.

9             What we don't have is that inventory which

10   says how many of those were put in the ground when.

11   The five-year interval that we are using to inventory

12   is based on our expert's analysis of how long something

13   should be in the ground without cathodic protection

14   still allowing for the factors of safety in doing this

15   sort of analysis.

16             It was not a consideration that anything in

17   the ground without cathodic protection for more than

18   five years necessarily caused a risk, but it was

19   something that we used as a criteria, again, including

20   safety factors.  So I think that this sort of analysis,

21   again, not required in regulation, is the leading edge,

22   as far as distribution systems, that I'm aware of in

23   the United States.

24             MR. HENDERSON:  If I could, I want to

25   reiterate a point that Mr. Williams made a little

0122

1   earlier.  Throughout our operation, we are continually

2   evaluating our system as it ages to look for trends.

3   Not maybe to the depth that we are contemplating in

4   this assessment, but there is nothing to indicate that

5   services of this vintage are of a problem throughout

6   our system.  In fact, throughout the country, there is

7   systems that are much older and still providing very

8   serviceable use to the utility.

9             COMMISSIONER JONES:  Just on that point,

10   Mr. Rathbun, I have read Mr. Bell's testimony in some

11   detail, and I think he does make several points that

12   raise uncertainties in my mind.  One of the points is

13   that while the Company alleges that the circumstances

14   in this case are unique, Mr. Bell made a pretty strong

15   argument, did he not, that the circumstances in his

16   view are not unique; that the relationship between

17   cathodic protection and these sorts of perforations of

18   pipe externally or internally could happen under a

19   variety of circumstances, and wasn't one of his strong

20   recommendations was to conduct a very thorough

21   inventory of similar vintage pipe as quickly as

22   possible?  Am I misreading his analysis in the

23   testimony?

24             MR. RATHBUN:  Commissioner Jones, I would

25   agree that you are reading his testimony specifically.

0123

1   I do believe that while in a majority of cases, the

2   experts agreed, I think that there may have been some

3   disagreement from PSE's expert in this particular

4   regard.

5             COMMISSIONER JONES:  A question on Spirit

6   Ridge.  Has all of the pipe under the control of the

7   Vasa Park rectifier been replaced, mains and service

8   lines and everything, or are there still some lines

9   that haven't been replaced?

10             JUDGE MACE:  Mr. Henderson, are you going to

11   address that?

12             MR. HENDERSON:  Yes.  All of the lines that

13   were connected to the rectifier while it was

14   experiencing the cross-wiring impact have been

15   replaced, mains and services.  There is pipe outside of

16   that area that at the time of the incident were

17   disconnected from the rectifier for other maintenance

18   reasons we did not include in the replacement effort.

19             COMMISSIONER JONES:  And all of that pipe has

20   been plastic pipe?

21             MR. HENDERSON:  That's correct.

22             COMMISSIONER JONES:  So it's not directly

23   related to polarity reversal and all the issues

24   associated with a rectifier, if you will.

25             MR. HENDERSON:  That's correct.

0124

1             COMMISSIONER JONES:  Just one last question

2   for Mr. Rathbun.  Just one other thing that concerned

3   me was Mr. Bell's testimony when he talked about leak

4   surveys in the Spirit Ridge neighborhood, and perhaps

5   you could address this as well, Mr. Henderson.  It's

6   dated something like 10 years prior to the explosion at

7   the Schmitz residence, the Company had detected three

8   leaks, and in the nine months from September through

9   June, I think, September '04 through June '05, 23 leaks

10   were detected; is that correct?

11             MR. HENDERSON:  I believe that's an accurate

12   representation of what was found out there.  I would

13   like to point out that distribution systems do leak.

14   They are built into the regulations, the fact that they

15   do, and we are allowed an opportunity to find these, to

16   grade these, and repair them at some frequency.

17             One of the things we found with Spirit Ridge,

18   we've never inspected a system as thoroughly as we did

19   in Spirit Ridge.  A leakage survey cycle of every 30

20   days is bound to find things that have been long

21   existing that on an annual basis or a five-year basis

22   may not surface.  So I think a lot of what we found

23   there was simply due to the fact of the frequency of

24   the surveys.  The majority of the leaks that we did

25   find were very low grade, very small leaks that may not

0125

1   be detectable on a day due to certain ground

2   conditions, atmospheric conditions, whatnot.

3             COMMISSIONER JONES:  In fairness, I should

4   state for the record that Dr. Bell's recommendation --

5   I think I'm stating this correctly -- was that when the

6   inventory is taken and when a remediation program is

7   instituted that leak surveys be conducted for pipe of

8   similar vintage once per year.  I don't know if that's

9   the plan of the Company going forward or if that

10   depends on the assessment and the inventory and the

11   prioritization that you are going to enter into

12   hereafter.

13             MR. HENDERSON:  That's part of the mitigation

14   side of this whole assessment is that once we've

15   identified areas of concern, that may be one of the

16   mitigation steps that we take is an increased leakage

17   survey cycle or up to and including replacement of the

18   services.

19             COMMISSIONER JONES:  That's all I have for

20   now.

21             MR. RATHBUN:  May I add one more thing?  Just

22   to highlight that the one other element relative to

23   Spirit Ridge that's in the Settlement that's before

24   you, and that relates to the remainder of the Spirit

25   Ridge area that is the nonreplaced pipe, in other

0126

1   words, the steel services and main that remains, that

2   there is a requirement for one additional leak survey

3   in September or June or September time frame of 2006,

4   again, to provide that added protection, and then the

5   rest of Spirit Ridge will be factored into the same

6   analysis as everything else within PSE's operating

7   system.

8             COMMISSIONER JONES:  Mr. Rathbun, again, what

9   is the current WAC requirement for leak surveys of this

10   vintage?

11             MR. RATHBUN:  Again, this is a five-year

12   return interval.

13             COMMISSIONER JONES:  Okay.

14             JUDGE MACE:  Commissioner Oshie?

15             COMMISSIONER OSHIE:  One of the questions

16   that Commissioner Jones actually got involved in, I

17   guess you could say, but Mr. Rathbun, why is it in the

18   public interest in this situation to wait for at least

19   a year until the completion of the surveys of the

20   territories that are of similar vintage, is the term

21   used in the Settlement Agreement, or am I just reading

22   that strictly in the Agreement, or are there certain

23   conditions that would cause Staff to require the

24   Company to take action prior to the one-year period

25   terminated?

0127

1             MR. RATHBUN:  Commissioner Oshie, first of

2   all, I think that we were asking for integration of all

3   available data that PSE has, and that was really

4   necessary to be able to make these decisions, but I

5   would think that PSE would agree that if the

6   circumstances presented itself, given trends in what we

7   find, that remediation would be taken if something that

8   was troubling a surface drain was indicated on

9   analysis.

10             COMMISSIONER OSHIE:  So the one year is just

11   an estimate to complete the whole job, and if something

12   comes up in the meantime, PSE will attend to it.  Is

13   that Staff's understanding?

14             MR. RATHBUN:  That is Staff's understanding.

15             COMMISSIONER OSHIE:  The status report that's

16   called for in the Agreement, what are we to anticipate

17   from that as Commission?

18             MR. RATHBUN:  As I recall, the Agreement

19   talks for basically quarterly updates.  I think that

20   one of the things we will do is develop a more detailed

21   plan, and of particular interest, we'll be able to

22   bring before the Commission protocol to be considered

23   in the analysis, what we find.  I view this as kind of

24   a big analyses of all available data, and then trying

25   to assess if we see any trends, in what circumstance or

0128

1   what sort of trends might trigger a more detailed

2   analysis.

3             PSE did do some relatively detailed

4   technological analysis in the Spirit Ridge neighborhood

5   that was required under the action plan.  Those are

6   elements that are referenced in the Agreement that

7   might be used if we find those sort of trends that

8   trigger further analysis.

9             COMMISSIONER OSHIE:  One more question for

10   the Company.  How is the Company going to prioritize

11   the service territories in which you are going to be

12   conducting this examination, or is there any plan for

13   prioritization?

14             MR. HENDERSON:  There really isn't a plan for

15   prioritization other than the assessment is to identify

16   where they are located, and based on that, and again,

17   one of the data points will be a geographical look at

18   the system in looking for concentrations of these areas

19   that we may hone in on first to evaluate.

20             And again, as Alan said, this is kind of a

21   continuous improvement-type process whereas more data

22   is brought in, it may direct us in different ways, and

23   we don't want to presuppose right now where that might

24   be until we see what the data suggests.

25             CHAIRMAN SIDRAN:  Thank you.  A couple of

0129

1   questions I think to the Company; although Mr. Rathbun,

2   you are free to respond as well if you wish.

3             It's clear from the record that at the

4   Schmitz home, there were a couple of aspects that may

5   or may not have been contributing factors.  One was a

6   plumbing drain from a sink of some kind in the basement

7   that came out of the foundation wall, I believe, and

8   drained near or above the service pipe, and second,

9   either as a result of that drain or perhaps there was

10   some other reason, there was a hole in the foundation

11   wall, again in proximity to the service line.

12             So I assume without asking you to speculate

13   about what, if any, contributing cause those two

14   factors may have played here, would it be fair to say

15   that water drainage above a gas service line

16   contributes to the risk of corrosion, or is that

17   inaccurate?

18             MR. HENDERSON:  Well certainly, a moist

19   condition such as you are suggesting provides an

20   environment for corrosion to occur, but that's why we

21   put the coatings on and why we have cathodic protection

22   to mitigate that fact.  So just the fact alone that you

23   have wet conditions there does not necessarily

24   presuppose that it was more likely to cause the

25   corrosion on that service line.

0130

1             CHAIRMAN SIDRAN:  The second question related

2   to -- I assume that holes in foundation walls also

3   create risks in the event of a leak, that the leak will

4   migrate into the building.

5             MR. HENDERSON:  That's correct.  It provides

6   a path of least resistance, if you will.

7             CHAIRMAN SIDRAN:  Does the Company do

8   anything by way of -- I know that you provide

9   information to your customers.  Do you do anything with

10   respect to these two issues to try to educate consumers

11   that placements of drainage downspouts, for example, or

12   drains should generally try to avoid placement on top

13   of their gas service lines and that holes in foundation

14   walls in proximity to their service lines are risky and

15   to be avoided?

16             MR. HENDERSON:  We do not address some of

17   those specific things.  We rely on the local building

18   codes and plumbing codes to address those particular

19   situations.  However, the third-party damage is a major

20   risk to our system, and we work very closely with a

21   number of agencies to get the word out about any kind

22   of construction around our facilities to make sure that

23   people are careful and in using the one-call system to

24   make sure our facilities can be located and damage

25   prevented that way.

0131

1             CHAIRMAN SIDRAN:  I would encourage the

2   Company to think about, given the particulars of this

3   case, ways they might inform the public that corrosion

4   is a risk and the Company does what it can to reduce

5   that risk through coatings and through cathodic

6   protection, but that homeowner's, for example, can also

7   take measures to reduce risk by thinking about drainage

8   and thinking about the integrity of their foundation

9   walls.

10             The second question has to do with what

11   similarities or distinctions you would draw between the

12   corrosion cathodic protection issues in this case and

13   those that arose in the prior complaint, which was

14   PG-030080, which was a very large case involving

15   multiple issues and alleged violations, which I note

16   was filed June 26th of 2004, so it was pending at the

17   time that this tragedy occurred, and I understand there

18   are differences; that that case, if I understand it,

19   involved steel pipe, uncoated pipe, compared to this

20   pipe, but in that case, which involved a substantial,

21   as I'm sure you recall, a substantial settlement and

22   penalty in the range of, I believe, $700,000 with part

23   of that suspended, could you just explain to me how

24   that case and the issues of corrosion and cathodic

25   protection that were at issue there compares or

0132

1   contrasts with the issues that we are talking about

2   this afternoon?  Mr. Rathbun, go ahead.

3             (Pause in the proceedings.)

4             MR. RATHBUN:  It was simply because of the

5   silence, I guess, I didn't catch what was happening, so

6   it was just unclear to me as to whom the question was

7   directed to.

8             CHAIRMAN SIDRAN:  The question was addressed

9   to Mr. Henderson, and we paused for the reporter, and I

10   believe he's about to answer, but you are welcome to

11   respond as well, if you wish.

12             JUDGE MACE:  Do you want to respond?

13             MR. RATHBUN:  I'll let Mr. Henderson address

14   it.  I may have some follow-up.

15             JUDGE MACE:  Go ahead, Mr. Henderson.

16             MR. HENDERSON:  I think the situation around

17   the previous settlement or complaint that was filed was

18   more around some of our maintenance activities or

19   inspection activities and the timing of that.  It

20   wasn't really related to actual corrosion or the

21   condition of the system, and that's what prompted the

22   agreement to the bare steel replacement as well as a

23   lot of the penalty was associated with missing dates

24   for actual inspections.

25             Whereas in this case, I think it's a

0133

1   condition that while the cross-wiring existed, our

2   normal inspection procedures well within the

3   requirements of the regulations had not surfaced it

4   yet, and once it was identified, prompt action was

5   taken and our activities were well within the

6   regulation.  So I think that is the distinction that I

7   see there between the two cases.

8             CHAIRMAN SIDRAN:  Mr. Rathbun, would you

9   respond to that same question?

10             MR. RATHBUN:  Chairman Sidran, I would tend

11   to agree that the 03 case to which you referred and

12   settlement was agreed to last year in large part dealt

13   with -- of course, it was an audit of Pierce and King

14   County -- it did find a lot of circumstances in which

15   inspection activities, timing of events by PSE were

16   found to be not according to regulation, but we also

17   looked upon it a little bit further from a standpoint

18   of formalizing some ongoing problematic changes for

19   Puget Sound Energy.  One was the bare steel replacement

20   program, and also, a check the system line that they

21   had already commenced about the isolated services,

22   isolated facilities.  Those elements were also added to

23   that settlement, but I would agree with Mr. Henderson

24   that in large part, a lot of the issues related to

25   timing of their activities was out of compliance with

0134

1   state and federal regulations.

2             CHAIRMAN SIDRAN:  Thank you.

3             JUDGE MACE:  Do you or any of the

4   commissioners have any further questions?  All right,

5   sir.  Thank you.  At this point, the witnesses are

6   excused.

7             I want to ask again on the conference bridge,

8   because I've heard what may be several people coming

9   onto the bridge, is there anyone on the bridge who is

10   from Mrs. Schmitz's family or anyone representing

11   Mrs. Schmitz's team?  Thank you.  I hear no response.

12             Is there anyone else who wants to address the

13   Settlement Agreement at this time; any counsel seek to

14   address the settlement agreement?  All right.  Barring

15   unforeseen events, the Commission will be deliberating

16   and will be entering an order within a short period of

17   time.  I want to express appreciation to the parties

18   for their cooperation in working out the Settlement and

19   revised Settlement, and at this point, unless there is

20   anything further...

21             CHAIRMAN SIDRAN:  Yes.  I would like to

22   commend the parties and the Company, because I realize

23   that this was -- first I want to commend the Company

24   for responding constructively and promptly to this

25   issue.  I know that it was difficult.  At the same

0135

1   time, I also want to express, I think, the Commission's

2   sympathies to the Schmitz family.  Although they are

3   not literally represented here at the moment, it was a

4   tragic loss of life.

5             I also want to commend the parties, including

6   the Staff and counsel, for their constructive approach

7   to the Settlement in arriving at what I think is a

8   constructive resolution of this particular case, so

9   thank you for your hard work.

10             JUDGE MACE:  Thank you.  The record is

11   closed.

12              (Hearing concluded at 2:55 p.m.)

13

14

15

16

17

18

19

20

21

22

23

24

25