## Sheet1
ANNUAL HEAT LOSS FOR INSULATED PIPE
1 1/2" THICK INSULATION, 150F PIPE WALL TEMP
1.5-inch polyisocyanurate insulation
Pipe Dia, in | Length of Uninsulated Pipe, ft | Annual Operating Hours | Heatloss Btu/ft-hr (bare) | Heatloss Btu/ft-hr (Ins at 1.5") | Total Energy Savings , Btu/hour/ft | Fuel Savings Thm per year per foot
1 | 1 | 4000 | 77.1263 | 7.0321 | 70.0941 | 3.5047
1.25 | 1 | 4000 | 88.3125 | 7.6156 | 80.6969 | 4.0348
1.5 | 1 | 4000 | 103.0312 | 8.3209 | 94.7104 | 4.7355
2 | 1 | 4000 | 139.8281 | 9.8661 | 129.962 | 6.4981
3 | 1 | 4000 | 206.0625 | 12.1868 | 193.8757 | 9.6938
4 | 1 | 4000 | 264.9375 | 13.9752 | 250.9623 | 12.5481
5 | 1 | 4000 | 327.345 | 15.705 | 311.64 | 15.582
6 | 1 | 4000 | 390.0469 | 17.3271 | 372.7197 | 18.636
[5 empty] | 0 | 0
Sched 40 Steel Pipe Properties
[8 empty] | Nom D | Actual D | Radius | Bare Area/LF | Ins Area/LF
[8 empty] | in | in | in | sq ft | sq ft
(1.5"ins thick)
[8 empty] | 1 | 1.31 | 0.655 | 0.34278 | 1.1278
[8 empty] | 1.25 | 1.5 | 0.75 | 0.3925 | 1.1775
[8 empty] | 1.5 | 1.75 | 0.875 | 0.45792 | 1.2429
[8 empty] | 2 | 2.375 | 1.1875 | 0.62146 | 1.4065
[8 empty] | 3 | 3.5 | 1.75 | 0.91583 | 1.7008
[8 empty] | 4 | 4.5 | 2.25 | 1.1775 | 1.9625
| Assumptions: | [6 empty] | 5 | 5.56 | 2.78 | 1.4549 | 2.2399
[8 empty] | 6 | 6.625 | 3.3125 | 1.7335 | 2.5185
| Heating system thermal efficiency |  |  |  |  | 80%
| Pipe wall temp |  |  |  |  | 150
| Delta T |  |  |  |  | 90 | F
| Thermal conductivity of product k = .18 btu-in/hr-sq ft-F |  |  |  |  | 0.18 | btu-in/hr-sq ft-F
| Overall heat transfer coefficient h = 2.5 Btu/hr-sq ft-F |  |  |  |  | 2.5 | Btu/hr-sq ft-F
| Heat transfer equation - |  | Q/A =( Tin-Tambient)/ ((R Ins pipe x ln (R ins pipe /R pipe)/k + 1/h)
For bare pipe D = 2" for example, R pipe = R insulation, ln (1.1875/1.1875) =0, therefore Q/A=( Tin-Tambient)/ ( 1/h)
Area of pipe per lineal foot of pipe = (pi x D) = 3.14 x 2.375 /12 = .62 sq ft/lf of pipe
Q/LF bare 2" pipe = 90/(1/2.5) x .62 sq ft/lf= 400 Btu/hr x .62 = 140 Btu/hr-LF of bare pipe
Q/LF insulated 2" pipe with 1.5" insulation = 90/ ( (2.687 x ln (2.687/1.187)/.18 + 1/2.5) x 1.41= 6.5 Btu/hr-LF of insulated pipe