## Figure Data
Figure F.1 - Base Schedule Ramping Adjustment |  |  | Figure F.2 - Probability of Exceeding Allowed Deviation
Time (Interval Ending) | Base Schedule | Adjusted Base Schedule | ACE Shortfall (MW) | Exceedance Probability (PACE) | Exceedance Probability (PACW)
4:45 | 2325 | 2325 | 0 | 0% | 0%
4:46 | 2325 | 2325 | 1 | 9.819e-34% | 5.089e-08%
4:47 | 2325 | 2325 | 2 | 3.111e-33% | 1.167e-07%
4:48 | 2325 | 2325 | 3 | 7.71e-33% | 2.018e-07%
4:49 | 2325 | 2325 | 4 | 1.761e-32% | 3.115e-07%
4:50 | 2325 | 2325 | 5 | 3.882e-32% | 4.526e-07%
4:50 | 2325 | 2350 | 6 | 8.409e-32% | 6.338e-07%
4:51 | 2325 | 2350 | 7 | 1.804e-31% | 8.66e-07%
4:52 | 2325 | 2350 | 8 | 3.843e-31% | 1.163e-06%
4:53 | 2325 | 2350 | 9 | 8.147e-31% | 1.542e-06%
4:54 | 2325 | 2350 | 10 | 1.719e-30% | 2.026e-06%
4:55 | 2325 | 2350 | 11 | 3.612e-30% | 2.641e-06%
4:55 | 2325 | 2375 | 12 | 7.561e-30% | 3.421e-06%
4:56 | 2325 | 2375 | 13 | 1.576e-29% | 4.41e-06%
4:57 | 2325 | 2375 | 14 | 3.273e-29% | 5.66e-06%
4:58 | 2325 | 2375 | 15 | 6.77e-29% | 7.238e-06%
4:59 | 2325 | 2375 | 16 | 1.395e-28% | 9.226e-06%
5:00 | 2325 | 2375 | 17 | 2.863e-28% | 1.172e-05%
5:00 | 2450 | 2400 | 18 | 5.853e-28% | 1.486e-05%
5:01 | 2450 | 2400 | 19 | 1.192e-27% | 1.879e-05%
5:02 | 2450 | 2400 | 20 | 2.418e-27% | 2.37e-05%
5:03 | 2450 | 2400 | 21 | 4.886e-27% | 2.982e-05%
5:04 | 2450 | 2400 | 22 | 9.836e-27% | 3.745e-05%
5:05 | 2450 | 2400 | 23 | 1.972e-26% | 4.692e-05%
5:05 | 2450 | 2425 | 24 | 3.939e-26% | 5.868e-05%
5:06 | 2450 | 2425 | 25 | 7.838e-26% | 7.323e-05%
5:07 | 2450 | 2425 | 26 | 1.553e-25% | 9.121e-05%
5:08 | 2450 | 2425 | 27 | 3.067e-25% | 0.0001134%
5:09 | 2450 | 2425 | 28 | 6.031e-25% | 0.0001407%
5:10 | 2450 | 2425 | 29 | 1.181e-24% | 0.0001742%
5:10 | 2450 | 2450 | 30 | 2.305e-24% | 0.0002153%
5:11 | 2450 | 2450 | 31 | 4.481e-24% | 0.0002656%
5:12 | 2450 | 2450 | 32 | 8.676e-24% | 0.000327%
5:13 | 2450 | 2450 | 33 | 1.673e-23% | 0.0004019%
5:14 | 2450 | 2450 | 34 | 3.215e-23% | 0.000493%
5:15 | 2450 | 2450 | 35 | 6.153e-23% | 0.0006036%
5:16 | 2450 | 2450 | 36 | 1.173e-22% | 0.0007377%
5:17 | 2450 | 2450 | 37 | 2.228e-22% | 0.0008999%
5:18 | 2450 | 2450 | 38 | 4.214e-22% | 0.001096%
5:19 | 2450 | 2450 | 39 | 7.94e-22% | 0.001332%
5:20 | 2450 | 2450 | 40 | 1.49e-21% | 0.001615%
5:21 | 2450 | 2450 | 41 | 2.787e-21% | 0.001956%
5:22 | 2450 | 2450 | 42 | 5.191e-21% | 0.002364%
5:23 | 2450 | 2450 | 43 | 9.63e-21% | 0.002852%
5:24 | 2450 | 2450 | 44 | 1.78e-20% | 0.003434%
5:25 | 2450 | 2450 | 45 | 3.277e-20% | 0.004127%
5:26 | 2450 | 2450 | 46 | 6.009e-20% | 0.004952%
5:27 | 2450 | 2450 | 47 | 1.098e-19% | 0.00593%
5:28 | 2450 | 2450 | 48 | 1.998e-19% | 0.007088%
5:29 | 2450 | 2450 | 49 | 3.621e-19% | 0.008457%
5:30 | 2450 | 2450 | 50 | 6.539e-19% | 0.01007%
5:31 | 2450 | 2450 | 51 | 1.176e-18% | 0.01197%
5:32 | 2450 | 2450 | 52 | 2.107e-18% | 0.01421%
5:33 | 2450 | 2450 | 53 | 3.761e-18% | 0.01683%
5:34 | 2450 | 2450 | 54 | 6.687e-18% | 0.01989%
5:35 | 2450 | 2450 | 55 | 1.184e-17% | 0.02348%
5:36 | 2450 | 2450 | 56 | 2.09e-17% | 0.02766%
5:37 | 2450 | 2450 | 57 | 3.672e-17% | 0.03252%
5:38 | 2450 | 2450 | 58 | 6.429e-17% | 0.03817%
5:39 | 2450 | 2450 | 59 | 1.121e-16% | 0.04472%
5:40 | 2450 | 2450 | 60 | 1.947e-16% | 0.0523%
5:41 | 2450 | 2450 | 61 | 3.37e-16% | 0.06105%
5:42 | 2450 | 2450 | 62 | 5.809e-16% | 0.07114%
5:43 | 2450 | 2450 | 63 | 9.974e-16% | 0.08274%
5:44 | 2450 | 2450 | 64 | 1.706e-15% | 0.09607%
5:45 | 2450 | 2450 | 65 | 2.907e-15% | 0.1113%
5:46 | 2450 | 2450 | 66 | 4.934e-15% | 0.1288%
5:47 | 2450 | 2450 | 67 | 8.342e-15% | 0.1487%
5:48 | 2450 | 2450 | 68 | 1.405e-14% | 0.1715%
5:49 | 2450 | 2450 | 69 | 2.357e-14% | 0.1973%
5:50 | 2450 | 2450 | 70 | 3.94e-14% | 0.2266%
5:50 | 2450 | 2505 | 71 | 6.559e-14% | 0.2598%
5:51 | 2450 | 2505 | 72 | 1.088e-13% | 0.2974%
5:52 | 2450 | 2505 | 73 | 1.797e-13% | 0.3398%
5:53 | 2450 | 2505 | 74 | 2.957e-13% | 0.3875%
5:54 | 2450 | 2505 | 75 | 4.848e-13% | 0.4411%
5:55 | 2450 | 2505 | 76 | 7.917e-13% | 0.5013%
5:55 | 2450 | 2560 | 77 | 1.288e-12% | 0.5687%
5:56 | 2450 | 2560 | 78 | 2.087e-12% | 0.644%
5:57 | 2450 | 2560 | 79 | 3.369e-12% | 0.728%
5:58 | 2450 | 2560 | 80 | 5.418e-12% | 0.8216%
5:59 | 2450 | 2560 | 81 | 8.679e-12% | 0.9255%
6:00 | 2450 | 2560 | 82 | 1.385e-11% | 1.041%
6:00 | 2725 | 2615 | 83 | 2.201e-11% | 1.168%
6:01 | 2725 | 2615 | 84 | 3.486e-11% | 1.309%
6:02 | 2725 | 2615 | 85 | 5.498e-11% | 1.465%
6:03 | 2725 | 2615 | 86 | 8.64e-11% | 1.636%
6:04 | 2725 | 2615 | 87 | 1.352e-10% | 1.824%
6:05 | 2725 | 2615 | 88 | 2.109e-10% | 2.029%
6:05 | 2725 | 2670 | 89 | 3.276e-10% | 2.255%
6:06 | 2725 | 2670 | 90 | 5.069e-10% | 2.501%
6:07 | 2725 | 2670 | 91 | 7.813e-10% | 2.769%
6:08 | 2725 | 2670 | 92 | 1.2e-09% | 3.061%
6:09 | 2725 | 2670 | 93 | 1.835e-09% | 3.377%
6:10 | 2725 | 2670 | 94 | 2.796e-09% | 3.72%
6:10 | 2725 | 2725 | 95 | 4.245e-09% | 4.091%
6:11 | 2725 | 2725 | 96 | 6.419e-09% | 4.492%
6:12 | 2725 | 2725 | 97 | 9.669e-09% | 4.924%
6:13 | 2725 | 2725 | 98 | 1.451e-08% | 5.388%
6:14 | 2725 | 2725 | 99 | 2.169e-08% | 5.886%
6:15 | 2725 | 2725 | 100 | 3.23e-08% | 6.419%
6:16 | 2725 | 2725 | 101 | 4.792e-08% | 6.99%
6:17 | 2725 | 2725 | 102 | 7.081e-08% | 7.598%
6:18 | 2725 | 2725 | 103 | 1.042e-07% | 8.246%
6:19 | 2725 | 2725 | 104 | 1.529e-07% | 8.935%
6:20 | 2725 | 2725 | 105 | 2.234e-07% | 9.666%
6:21 | 2725 | 2725 | 106 | 3.251e-07% | 10.44%
6:22 | 2725 | 2725 | 107 | 4.713e-07% | 11.26%
6:23 | 2725 | 2725 | 108 | 6.807e-07% | 12.12%
6:24 | 2725 | 2725 | 109 | 9.795e-07% | 13.03%
6:25 | 2725 | 2725 | 110 | 1.404e-06% | 13.98%
6:26 | 2725 | 2725 | 111 | 2.005e-06% | 14.98%
6:27 | 2725 | 2725 | 112 | 2.852e-06% | 16.03%
6:28 | 2725 | 2725 | 113 | 4.041e-06% | 17.12%
6:29 | 2725 | 2725 | 114 | 5.705e-06% | 18.26%
6:30 | 2725 | 2725 | 115 | 8.023e-06% | 19.45%
6:31 | 2725 | 2725 | 116 | 1.124e-05% | 20.68%
6:32 | 2725 | 2725 | 117 | 1.569e-05% | 21.96%
6:33 | 2725 | 2725 | 118 | 2.181e-05% | 23.28%
6:34 | 2725 | 2725 | 119 | 3.022e-05% | 24.64%
6:35 | 2725 | 2725 | 120 | 4.17e-05% | 26.05%
6:36 | 2725 | 2725 | 121 | 5.732e-05% | 27.5%
6:37 | 2725 | 2725 | 122 | 7.851e-05% | 28.98%
6:38 | 2725 | 2725 | 123 | 0.0001071% | 30.5%
6:39 | 2725 | 2725 | 124 | 0.0001456% | 32.06%
6:40 | 2725 | 2725 | 125 | 0.0001971% | 33.65%
6:41 | 2725 | 2725 | 126 | 0.000266% | 35.26%
6:42 | 2725 | 2725 | 127 | 0.0003574% | 36.91%
6:43 | 2725 | 2725 | 128 | 0.0004786% | 38.58%
6:44 | 2725 | 2725 | 129 | 0.0006383% | 40.27%
6:45 | 2725 | 2725 | 130 | 0.0008483% | 41.98%
6:46 | 2725 | 2725 | 131 | 0.001123% | 43.7%
6:47 | 2725 | 2725 | 132 | 0.001481% | 45.44%
6:48 | 2725 | 2725 | 133 | 0.001946% | 47.18%
6:49 | 2725 | 2725 | 134 | 0.002548% | 48.93%
6:50 | 2725 | 2725 | 135 | 0.003323% | 50.69%
6:50 | 2725 | 2795 | 136 | 0.004318% | 52.44%
6:51 | 2725 | 2795 | 137 | 0.00559% | 54.18%
6:52 | 2725 | 2795 | 138 | 0.007209% | 55.92%
6:53 | 2725 | 2795 | 139 | 0.009263% | 57.65%
6:54 | 2725 | 2795 | 140 | 0.01186% | 59.36%
6:55 | 2725 | 2795 | 141 | 0.01513% | 61.06%
6:55 | 2725 | 2865 | 142 | 0.01922% | 62.73%
6:56 | 2725 | 2865 | 143 | 0.02433% | 64.38%
6:57 | 2725 | 2865 | 144 | 0.03069% | 100%
6:58 | 2725 | 2865 | 145 | 0.03857% | 100%
6:59 | 2725 | 2865 | 146 | 0.0483% | 100%
7:00 | 2725 | 2865 | 147 | 0.06025% | 100%
7:00 | 3075 | 2935 | 148 | 0.07489% | 100%
7:01 | 3075 | 2935 | 149 | 0.09274% | 100%
7:02 | 3075 | 2935 | 150 | 0.1144% | 100%
7:03 | 3075 | 2935 | 151 | 0.1407% | 100%
7:04 | 3075 | 2935 | 152 | 0.1723% | 100%
7:05 | 3075 | 2935 | 153 | 0.2103% | 100%
7:05 | 3075 | 3005 | 154 | 0.2558% | 100%
7:06 | 3075 | 3005 | 155 | 0.3099% | 100%
7:07 | 3075 | 3005 | 156 | 0.3742% | 100%
7:08 | 3075 | 3005 | 157 | 0.4502% | 100%
7:09 | 3075 | 3005 | 158 | 0.5396% | 100%
7:10 | 3075 | 3005 | 159 | 0.6445% | 100%
7:10 | 3075 | 3075 | 160 | 0.7671% | 100%
7:11 | 3075 | 3075 | 161 | 0.9098% | 100%
7:12 | 3075 | 3075 | 162 | 1.075% | 100%
7:13 | 3075 | 3075 | 163 | 1.266% | 100%
7:14 | 3075 | 3075 | 164 | 1.486% | 100%
7:15 | 3075 | 3075 | 165 | 1.737% | 100%
|  |  | 166 | 2.024% | 100%
|  |  | 167 | 2.351% | 100%
|  |  | 168 | 2.72% | 100%
|  |  | 169 | 3.137% | 100%
|  |  | 170 | 3.605% | 100%
|  |  | 171 | 4.129% | 100%
|  |  | 172 | 4.714% | 100%
|  |  | 173 | 5.362% | 100%
|  |  | 174 | 6.079% | 100%
|  |  | 175 | 6.87% | 100%
|  |  | 176 | 7.737% | 100%
|  |  | 177 | 8.685% | 100%
|  |  | 178 | 9.717% | 100%
|  |  | 179 | 10.84% | 100%
|  |  | 180 | 12.05% | 100%
|  |  | 181 | 13.35% | 100%
|  |  | 182 | 14.74% | 100%
|  |  | 183 | 16.23% | 100%
|  |  | 184 | 17.82% | 100%
|  |  | 185 | 19.5% | 100%
|  |  | 186 | 21.27% | 100%
|  |  | 187 | 23.13% | 100%
|  |  | 188 | 25.08% | 100%
|  |  | 189 | 27.11% | 100%
|  |  | 190 | 29.22% | 100%
|  |  | 191 | 31.41% | 100%
|  |  | 192 | 33.66% | 100%
|  |  | 193 | 35.97% | 100%
|  |  | 194 | 38.34% | 100%
|  |  | 195 | 40.75% | 100%
|  |  | 196 | 43.19% | 100%
|  |  | 197 | 45.66% | 100%
|  |  | 198 | 48.15% | 100%
|  |  | 199 | 50.65% | 100%
|  |  | 200 | 53.14% | 100%
|  |  | 201 | 55.62% | 100%
|  |  | 202 | 58.08% | 100%
|  |  | 203 | 100% | 100%
|  |  | 204 | 100% | 100%
|  |  | 205 | 100% | 100%
|  |  | 206 | 100% | 100%
|  |  | 207 | 100% | 100%
|  |  | 208 | 100% | 100%
|  |  | 209 | 100% | 100%
|  |  | 210 | 100% | 100%
|  |  | 211 | 100% | 100%
|  |  | 212 | 100% | 100%
|  |  | 213 | 100% | 100%
|  |  | 214 | 100% | 100%
|  |  | 215 | 100% | 100%
|  |  | 216 | 100% | 100%
|  |  | 217 | 100% | 100%
|  |  | 218 | 100% | 100%
|  |  | 219 | 100% | 100%
|  |  | 220 | 100% | 100%
|  |  | 221 | 100% | 100%
|  |  | 222 | 100% | 100%
|  |  | 223 | 100% | 100%
|  |  | 224 | 100% | 100%
|  |  | 225 | 100% | 100%

## Table F.1-F.6
Table F.1 - Portfolio Regulation Reserve Requirements
| Wind Capacity | Solar Capacity | Stand-alone Regulation Requirement | Portfolio Diversity Credit | Regulation Requirement with Diversity
Case | (MW) | MW | (MW) | (%) | (MW)
CY2017 (2019 IRP) | 2750 | 1021 | 994 | 47% | 531
2018-2019 (2021 IRP) | 2745.1632 | 1080.3226 | 1057.4174 | 48.96% | 539.6598
Table F.2 - 2023 Flexible Resource Costs as Compared to 2021 Costs, $/MWh
[7 empty] | Wind 2023 FRS | Solar 2023 FRS | Wind 2021 FRS | Solar 2021 FRS
[7 empty] | (2022$) | (2022$) | (2022$) | (2022$)
[6 empty] | Study Period | 2025-2042 | 2025-2042 | 2023-2040 | 2023-2040
[6 empty] | Flexible Resource Cost | 1.3837 | 1.5913 | 1.5832 | 1.3242
Table F.3 – Summary of Stand-alone Regulation Reserve Requirements
[12 empty] | Stand-alone Regulation | Capacity | Stand-alone Regulation
[11 empty] | Scenario | Forecast (aMW) | (MW) | Forecast (%)
[11 empty] | Non-VER | 106.2828 | 1304 | 8.151%
[11 empty] | Load | 334.4714 | 10094 | 3.314%
[11 empty] | VER - Wind | 457.1697 | 2745.1632 | 16.65%
[11 empty] | VER - Solar | 159.4935 | 1080.3226 | 14.76%
[11 empty] | Total | 1057.4174
Table F.4 - EIM Diversity Benefit Application Example
[16 empty] | a | b | c | d | e = a+b+c+d | f | g = e-f | h = g / e | i = c * h | j = c - i
[16 empty] | CAISO req't. before benefit | NEVP req't. before benefit | PACE req't. before benefit | PACW req't. before benefit | Total req't. before benefit | Total req't. after benefit | Total diversity benefit | Diversity benefit ratio | PACE benefit | PACE req't. after benefit
[15 empty] | Hour | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW)
[15 empty] | 1 | 550 | 110 | 165 | 100 | 925 | 583 | 342 | 37% | 61 | 104
[15 empty] | 2 | 600 | 110 | 165 | 100 | 975 | 636 | 339 | 34.8% | 57 | 108
[15 empty] | 3 | 650 | 110 | 165 | 110 | 1035 | 689 | 346 | 33.4% | 55 | 110
[15 empty] | 4 | 667 | 120 | 180 | 113 | 1080 | 742 | 338 | 31.3% | 56 | 124
Table F.5 – 2018-2019 Results with Portfolio Diversity and EIM Diversity Benefits
[27 empty] | Stand-alone Regulation Forecast | Stand-alone Rate | Portfolio Regulation Forecast w/EIM | Portfolio Rate | Capacity | Rate
[26 empty] | Scenario | (aMW) | (%) | (aMW) | (%) | (MW) | Determinant
[26 empty] | Non-VER | 106.2828 | 8.151% | 55.0307 | 4.22% | 1304 | Nameplate
[26 empty] | Load | 334.4714 | 3.314% | 171.5212 | 1.699% | 10094 | 12 CP
[26 empty] | VER - Wind | 457.1697 | 16.65% | 236.9319 | 8.631% | 2745.1632 | Nameplate
[26 empty] | VER - Solar | 159.4935 | 14.76% | 76.1759 | 7.051% | 1080.3226 | Nameplate
[26 empty] | Total | 1057.4174 |  | 539.6598
Table F.6: Portfolio Diversity Exponent Example
[36 empty] | Incremental Requirement w/ Diversity (MW) |  |  | Portfolio Diversity (%)
[36 empty] | By Diversity Exponent |  |  | By Diversity Exponent
[33 empty] | Stand-alone Reserve Req. (MW) | EIM Floor (MW) | Stand-alone Incremental Req. (MW) | d = c ^ 75% | e = c ^ 85% | f = c ^ 95% | g = 1 - (b + d)/a | h = 1 - (b + e)/a | i = 1 - (b + f)/a
[33 empty] | a | b | c = a - b | 75% | 85% | 95% | 75% | 85% | 95%
[33 empty] | 200 | 200 | 0 | 0 | 0 | 0 | 0% | 0% | 0%
[33 empty] | 250 | 200 | 50 | 18.803 | 27.8051 | 41.117 | 12.48% | 8.878% | 3.553%
[33 empty] | 300 | 200 | 100 | 31.6228 | 50.1187 | 79.4328 | 22.79% | 16.63% | 6.856%
[33 empty] | 350 | 200 | 150 | 42.8616 | 70.742 | 116.758 | 30.61% | 22.65% | 9.498%
[33 empty] | 400 | 200 | 200 | 53.183 | 90.339 | 153.4541 | 36.7% | 27.42% | 11.64%
[33 empty] | 450 | 200 | 250 | 62.8717 | 109.2066 | 189.6894 | 41.58% | 31.29% | 13.4%
[33 empty] | 500 | 200 | 300 | 72.0843 | 127.5126 | 225.5616 | 45.58% | 34.5% | 14.89%

## Table F.7-F.8
Average Stand-alone Requirements w/o Hourly Diversity
[5 empty] | Non-VER | Load | Wind | Solar | Total
|  |  |  | PACE | 50.2336 | 197.4101 | 328.493 | 132.1529 | 708.2896
|  |  |  | PACW | 56.0492 | 137.0613 | 128.6767 | 27.3406 | 349.1278
|  |  |  | Total | 106.2828 | 334.4714 | 457.1697 | 159.4935 | 1057.4174 | [13 empty] | Table F.7: PacifiCorp East Diversity by Portfolio Composition
[24 empty] | MW | % | (% Reduction vs. Stand-alone Requirements)
|  | LOLP (hrs/yr) |  | Combined Req w EIM Reserves |  | Capacity |  |  |  | Stand-alone Req East |  |  |  |  | East | Stand-alone Req West |  |  |  |  | West | System | East Wind Capacity | 8223.6 | 548.2% | 17.23% | 18.83% | 20.62%
StudyCount | Year | East | West | East | West | East Wind | East Solar | West Wind | West Solar | Non-VER | Load | VER - Wind | VER - Solar | Total | Portfolio Diversity | Non-VER | Load | VER - Wind | VER - Solar | Total | Portfolio Diversity | Portfolio Diversity |  | 7183.6 | 471.7% | 19.18% | 21.49% | 23.01% | 25.54% | 26.52%
1 | Actual | 0.060553 | 0.056855 | 368.3717 | 201.2127 | 1575 | 855 | 725.55 | 221.2 | 50.2336 | 197.4101 | 328.493 | 132.1529 | 708.2896 | 47.99% | 56.0492 | 137.0613 | 128.6767 | 27.3406 | 349.1278 | 42.37% | 46.13% |  | 6143.6 | 395.2% | 22.91% | 24.15% | 25.58% | 27.93% | 28.54% | 29.02%
2 | A1 | 0.0087326 | 0.056703 | 434.8557 | 206.2498 | 1575 | 1462.35 | 725.55 | 320.91 | 50.2336 | 197.4101 | 328.493 | 226.0279 | 802.1645 | 45.79% | 56.0492 | 137.0613 | 128.6767 | 39.6648 | 361.4521 | 42.94% | 44.9% |  | 5103.6 | 318.7% | 26% | 27.28% | 29.18% | 30.68% | 30.65% | 30.52% | 29.51%
3 | A2 | 0.098056 | 0.10417 | 547.5838 | 231.4969 | 1575 | 2502.35 | 725.55 | 1040.91 | 50.2336 | 197.4101 | 328.493 | 386.7753 | 962.9119 | 43.13% | 56.0492 | 137.0613 | 128.6767 | 128.6577 | 450.4449 | 48.61% | 44.88% |  | 4063.6 | 242.2% | 30.4% | 31.56% | 32.94% | 33.83% | 32.65% | 32.78% | 32.81%
4 | A3 | 0.056268 | 0.11713 | 680.1282 | 273.7539 | 1575 | 3542.35 | 725.55 | 1760.91 | 50.2336 | 197.4101 | 328.493 | 547.5227 | 1123.6593 | 39.47% | 56.0492 | 137.0613 | 128.6767 | 217.6505 | 539.4377 | 49.25% | 42.64% |  | 3023.6 | 165.7% | 35.04% | 36.2% | 38.46% | 37.1% | 37.61% | 36.18% | 33.92% | 31.92%
5 | A4 | 0.0012514 | 0.10451 | 824.7513 | 328.6573 | 1575 | 4582.35 | 725.55 | 2480.91 | 50.2336 | 197.4101 | 328.493 | 708.2701 | 1284.4067 | 35.79% | 56.0492 | 137.0613 | 128.6767 | 306.6433 | 628.4305 | 47.7% | 39.7% |  | 1575 | 100% |  | 47.99% | 45.79% | 43.13% | 39.47% | 35.79% | 32.24% | 29.41%
6 | A5 | 0.22956 | 0.10007 | 979.1646 | 386.1851 | 1575 | 5622.35 | 725.55 | 3200.91 | 50.2336 | 197.4101 | 328.493 | 869.0175 | 1445.1542 | 32.24% | 56.0492 | 137.0613 | 128.6767 | 395.6361 | 717.4233 | 46.17% | 36.86% |  | 787.5 | 50% |  |  | 46.42% | 40.35% | 36.41% | 32.96% | 30% | 27.26%
7 | A6 | 0.0009423 | 0.10559 | 1133.588 | 448.5923 | 1575 | 6662.35 | 725.55 | 3920.91 | 50.2336 | 197.4101 | 328.493 | 1029.7649 | 1605.9016 | 29.41% | 56.0492 | 137.0613 | 128.6767 | 484.6289 | 806.4161 | 44.37% | 34.41% |  |  |  | 50% | 100% | 165.7% | 329.2% | 492.8% | 656.3% | 819.9% | 983.4% | %
8 | A7 | 9.91e-07 | 0.09243 | 341.8199 | 173.1427 | 787.5 | 1462.35 | 362.775 | 320.91 | 50.2336 | 197.4101 | 164.2465 | 226.0279 | 637.918 | 46.42% | 56.0492 | 137.0613 | 64.3383 | 39.6648 | 297.1137 | 41.73% | 44.93% |  |  |  | 427.5 | 855 | 1462.35 | 2502.35 | 3542.35 | 4582.35 | 5622.35 | 6662.35 | MW
9 | A8 | 0.14689 | 0.14635 | 476.426 | 204.324 | 787.5 | 2502.35 | 362.775 | 1040.91 | 50.2336 | 197.4101 | 164.2465 | 386.7753 | 798.6654 | 40.35% | 56.0492 | 137.0613 | 64.3383 | 128.6577 | 386.1065 | 47.08% | 42.54% |  |  |  | East Solar Capacity
10 | A9 | 0.058226 | 0.22097 | 610.0636 | 238.3327 | 787.5 | 3542.35 | 362.775 | 1760.91 | 50.2336 | 197.4101 | 164.2465 | 547.5227 | 959.4128 | 36.41% | 56.0492 | 137.0613 | 64.3383 | 217.6505 | 475.0994 | 49.84% | 40.86% | [5 empty] | 2018-2019 Actual Wind and Solar Capacity
11 | A10 | 0.014249 | 0.17156 | 750.9855 | 296.4783 | 787.5 | 4582.35 | 362.775 | 2480.91 | 50.2336 | 197.4101 | 164.2465 | 708.2701 | 1120.1603 | 32.96% | 56.0492 | 137.0613 | 64.3383 | 306.6433 | 564.0922 | 47.44% | 37.81%
12 | A11 | 0.10185 | 0.11786 | 896.6259 | 359.4768 | 787.5 | 5622.35 | 362.775 | 3200.91 | 50.2336 | 197.4101 | 164.2465 | 869.0175 | 1280.9077 | 30% | 56.0492 | 137.0613 | 64.3383 | 395.6361 | 653.085 | 44.96% | 35.05% | Table F.8: PacifiCorp West Diversity by Portfolio Composition
13 | A12 | 0.20849 | 0.091042 | 1048.7094 | 421.8151 | 787.5 | 6662.35 | 362.775 | 3920.91 | 50.2336 | 197.4101 | 164.2465 | 1029.7649 | 1441.6551 | 27.26% | 56.0492 | 137.0613 | 64.3383 | 484.6289 | 742.0778 | 43.16% | 32.66% |  | MW | % | (% Reduction vs. Stand-alone Requirements)
14 | A13 | 0.054491 | 0.041742 | 644.6075 | 210.5353 | 3023.6 | 855 | 788.95 | 221.2 | 50.2336 | 197.4101 | 630.6231 | 132.1529 | 1010.4197 | 36.2% | 56.0492 | 137.0613 | 139.9207 | 27.3406 | 360.3718 | 41.58% | 37.62% | West Wind Capacity | 4388.95 | 548.2% | 21.13% | 22.36% | 22.9%
15 | A14 | 0.089639 | 0.24044 | 839.9988 | 319.6941 | 4063.6 | 855 | 1508.95 | 221.2 | 50.2336 | 197.4101 | 847.5328 | 132.1529 | 1227.3293 | 31.56% | 56.0492 | 137.0613 | 267.6131 | 27.3406 | 488.0642 | 34.5% | 32.39% |  | 3668.95 | 471.7% | 23.43% | 24.81% | 25.37% | 28.96% | 32.97%
16 | A15 | 0.018205 | 0.17429 | 1050.2202 | 427.1569 | 5103.6 | 855 | 2228.95 | 221.2 | 50.2336 | 197.4101 | 1064.4424 | 132.1529 | 1444.239 | 27.28% | 56.0492 | 137.0613 | 395.3055 | 27.3406 | 615.7566 | 30.63% | 28.28% |  | 2948.95 | 395.2% | 26.24% | 26.71% | 27.57% | 32.05% | 34.79% | 38.15%
17 | A16 | 0.083232 | 0.086515 | 1260.002 | 544.8719 | 6143.6 | 855 | 2948.95 | 221.2 | 50.2336 | 197.4101 | 1281.3521 | 132.1529 | 1661.1487 | 24.15% | 56.0492 | 137.0613 | 522.9978 | 27.3406 | 743.449 | 26.71% | 24.94% |  | 2228.95 | 318.7% | 29.61% | 30.63% | 31.38% | 36.21% | 39.48% | 42.66% | 42.73%
18 | A17 | 0.09229 | 0.099044 | 1474.452 | 655.0529 | 7183.6 | 855 | 3668.95 | 221.2 | 50.2336 | 197.4101 | 1498.2617 | 132.1529 | 1878.0583 | 21.49% | 56.0492 | 137.0613 | 650.6902 | 27.3406 | 871.1413 | 24.81% | 22.54% |  | 1508.95 | 242.2% | 33.82% | 34.5% | 36.26% | 40.8% | 45.2% | 46.15% | 43.95%
19 | A18 | 0.045514 | 0.20729 | 1700.407 | 775.521 | 8223.6 | 855 | 4388.95 | 221.2 | 50.2336 | 197.4101 | 1715.1714 | 132.1529 | 2094.968 | 18.83% | 56.0492 | 137.0613 | 778.3826 | 27.3406 | 998.8337 | 22.36% | 19.97% |  | 788.95 | 165.7% | 38.75% | 41.58% | 43.05% | 47.61% | 48.39% | 47.7% | 45% | 44.32%
20 | A19 | 0.054487 | 0.027691 | 613.447 | 212.3456 | 3023.6 | 427.5 | 788.95 | 110.6 | 50.2336 | 197.4101 | 630.6231 | 66.0765 | 944.3432 | 35.04% | 56.0492 | 137.0613 | 139.9207 | 13.6703 | 346.7015 | 38.75% | 36.04% |  | 725.55 | 100% |  | 42.37% | 42.94% | 48.61% | 49.25% | 47.7% | 46.17% | 44.37%
21 | A20 | 0.065747 | 0.14699 | 808.1932 | 313.9333 | 4063.6 | 427.5 | 1508.95 | 110.6 | 50.2336 | 197.4101 | 847.5328 | 66.0765 | 1161.2529 | 30.4% | 56.0492 | 137.0613 | 267.6131 | 13.6703 | 474.3939 | 33.82% | 31.4% |  | 362.775 | 50% |  |  | 41.73% | 47.08% | 49.84% | 47.44% | 44.96% | 43.16%
22 | A21 | 0.028464 | 0.1647 | 1019.8374 | 423.8024 | 5103.6 | 427.5 | 2228.95 | 110.6 | 50.2336 | 197.4101 | 1064.4424 | 66.0765 | 1378.1625 | 26% | 56.0492 | 137.0613 | 395.3055 | 13.6703 | 602.0863 | 29.61% | 27.1% |  |  |  | 50% | 100% | 165.7% | 329.2% | 492.8% | 656.3% | 819.9% | 983.4% | %
23 | A22 | 0.087954 | 0.056079 | 1229.648 | 538.3153 | 6143.6 | 427.5 | 2948.95 | 110.6 | 50.2336 | 197.4101 | 1281.3521 | 66.0765 | 1595.0722 | 22.91% | 56.0492 | 137.0613 | 522.9978 | 13.6703 | 729.7787 | 26.24% | 23.95% |  |  |  | 110.6 | 221.2 | 320.91 | 1040.91 | 1760.91 | 2480.91 | 3200.91 | 3920.91 | MW
24 | A23 | 0.14018 | 0.1157 | 1464.3958 | 656.5495 | 7183.6 | 427.5 | 3668.95 | 110.6 | 50.2336 | 197.4101 | 1498.2617 | 66.0765 | 1811.9819 | 19.18% | 56.0492 | 137.0613 | 650.6902 | 13.6703 | 857.471 | 23.43% | 20.55% |  |  |  | West Solar Capacity
25 | A24 | 0.031686 | 0.050551 | 1679.369 | 777.0286 | 8223.6 | 427.5 | 4388.95 | 110.6 | 50.2336 | 197.4101 | 1715.1714 | 66.0765 | 2028.8915 | 17.23% | 56.0492 | 137.0613 | 778.3826 | 13.6703 | 985.1634 | 21.13% | 18.5% | [5 empty] | 2018-2019 Actual Wind and Solar Capacity
26 | 2021 | 0.055343 | 0.048706 | 679.5952 | 212.2375 | 3023.6 | 1462.35 | 788.95 | 320.91 | 50.2336 | 197.4101 | 630.6231 | 226.0279 | 1104.2946 | 38.46% | 56.0492 | 137.0613 | 139.9207 | 39.6648 | 372.6961 | 43.05% | 39.62%
27 | 1 | 0.081706 | 0.19923 | 885.9498 | 318.9541 | 4063.6 | 1462.35 | 1508.95 | 320.91 | 50.2336 | 197.4101 | 847.5328 | 226.0279 | 1321.2043 | 32.94% | 56.0492 | 137.0613 | 267.6131 | 39.6648 | 500.3885 | 36.26% | 33.85%
28 | 2 | 0.017517 | 0.21733 | 1089.2997 | 431.0119 | 5103.6 | 1462.35 | 2228.95 | 320.91 | 50.2336 | 197.4101 | 1064.4424 | 226.0279 | 1538.1139 | 29.18% | 56.0492 | 137.0613 | 395.3055 | 39.6648 | 628.0808 | 31.38% | 29.82%
29 | 3 | 0.11769 | 0.17233 | 1306.0503 | 547.4113 | 6143.6 | 1462.35 | 2948.95 | 320.91 | 50.2336 | 197.4101 | 1281.3521 | 226.0279 | 1755.0236 | 25.58% | 56.0492 | 137.0613 | 522.9978 | 39.6648 | 755.7732 | 27.57% | 26.18%
30 | 4 | 0.085926 | 0.12539 | 1518.2033 | 659.3077 | 7183.6 | 1462.35 | 3668.95 | 320.91 | 50.2336 | 197.4101 | 1498.2617 | 226.0279 | 1971.9333 | 23.01% | 56.0492 | 137.0613 | 650.6902 | 39.6648 | 883.4656 | 25.37% | 23.74%
31 | 5 | 0.04079 | 0.083048 | 1737.5767 | 779.5523 | 8223.6 | 1462.35 | 4388.95 | 320.91 | 50.2336 | 197.4101 | 1715.1714 | 226.0279 | 2188.8429 | 20.62% | 56.0492 | 137.0613 | 778.3826 | 39.6648 | 1011.158 | 22.9% | 21.34%
32 | 6 | 0.054491 | 0.075446 | 795.6853 | 241.858 | 3023.6 | 2502.35 | 788.95 | 1040.91 | 50.2336 | 197.4101 | 630.6231 | 386.7753 | 1265.042 | 37.1% | 56.0492 | 137.0613 | 139.9207 | 128.6577 | 461.6889 | 47.61% | 39.91%
33 | 7 | 0.048292 | 0.10187 | 980.6096 | 348.9224 | 4063.6 | 2502.35 | 1508.95 | 1040.91 | 50.2336 | 197.4101 | 847.5328 | 386.7753 | 1481.9517 | 33.83% | 56.0492 | 137.0613 | 267.6131 | 128.6577 | 589.3813 | 40.8% | 35.81%
34 | 8 | 0.017614 | 0.1954 | 1177.639 | 457.3905 | 5103.6 | 2502.35 | 2228.95 | 1040.91 | 50.2336 | 197.4101 | 1064.4424 | 386.7753 | 1698.8614 | 30.68% | 56.0492 | 137.0613 | 395.3055 | 128.6577 | 717.0737 | 36.21% | 32.32%
35 | 9 | 0.093332 | 0.17399 | 1380.7169 | 573.9991 | 6143.6 | 2502.35 | 2948.95 | 1040.91 | 50.2336 | 197.4101 | 1281.3521 | 386.7753 | 1915.771 | 27.93% | 56.0492 | 137.0613 | 522.9978 | 128.6577 | 844.766 | 32.05% | 29.19%
36 | 10 | 0.084361 | 0.2458 | 1587.9783 | 690.8681 | 7183.6 | 2502.35 | 3668.95 | 1040.91 | 50.2336 | 197.4101 | 1498.2617 | 386.7753 | 2132.6807 | 25.54% | 56.0492 | 137.0613 | 650.6902 | 128.6577 | 972.4584 | 28.96% | 26.61%
37 | 11 | 0.054502 | 0.086118 | 889.5941 | 284.1815 | 3023.6 | 3542.35 | 788.95 | 1760.91 | 50.2336 | 197.4101 | 630.6231 | 547.5227 | 1425.7895 | 37.61% | 56.0492 | 137.0613 | 139.9207 | 217.6505 | 550.6817 | 48.39% | 40.61%
38 | 12 | 0.039539 | 0.14258 | 1106.35 | 371.7609 | 4063.6 | 3542.35 | 1508.95 | 1760.91 | 50.2336 | 197.4101 | 847.5328 | 547.5227 | 1642.6991 | 32.65% | 56.0492 | 137.0613 | 267.6131 | 217.6505 | 678.3741 | 45.2% | 36.32%
39 | 13 | 0.018702 | 0.1819 | 1289.5568 | 487.855 | 5103.6 | 3542.35 | 2228.95 | 1760.91 | 50.2336 | 197.4101 | 1064.4424 | 547.5227 | 1859.6088 | 30.65% | 56.0492 | 137.0613 | 395.3055 | 217.6505 | 806.0665 | 39.48% | 33.32%
40 | 14 | 0.083156 | 0.14606 | 1483.9365 | 608.929 | 6143.6 | 3542.35 | 2948.95 | 1760.91 | 50.2336 | 197.4101 | 1281.3521 | 547.5227 | 2076.5184 | 28.54% | 56.0492 | 137.0613 | 522.9978 | 217.6505 | 933.7588 | 34.79% | 30.48%
41 | 15 | 0.079226 | 0.098174 | 1012.5964 | 334.5487 | 3023.6 | 4582.35 | 788.95 | 2480.91 | 50.2336 | 197.4101 | 630.6231 | 708.2701 | 1586.5369 | 36.18% | 56.0492 | 137.0613 | 139.9207 | 306.6433 | 639.6745 | 47.7% | 39.49%
42 | 16 | 0.03956 | 0.14598 | 1212.1998 | 413.1942 | 4063.6 | 4582.35 | 1508.95 | 2480.91 | 50.2336 | 197.4101 | 847.5328 | 708.2701 | 1803.4465 | 32.78% | 56.0492 | 137.0613 | 267.6131 | 306.6433 | 767.3669 | 46.15% | 36.78%
43 | 17 | 0.018702 | 0.23112 | 1403.7834 | 513.2659 | 5103.6 | 4582.35 | 2228.95 | 2480.91 | 50.2336 | 197.4101 | 1064.4424 | 708.2701 | 2020.3562 | 30.52% | 56.0492 | 137.0613 | 395.3055 | 306.6433 | 895.0593 | 42.66% | 34.24%
44 | 18 | 0.10995 | 0.058092 | 1154.6431 | 400.7669 | 3023.6 | 5622.35 | 788.95 | 3200.91 | 50.2336 | 197.4101 | 630.6231 | 869.0175 | 1747.2843 | 33.92% | 56.0492 | 137.0613 | 139.9207 | 395.6361 | 728.6673 | 45% | 37.18%
45 | 19 | 0.039828 | 0.11268 | 1319.6876 | 480.0127 | 4063.6 | 5622.35 | 1508.95 | 3200.91 | 50.2336 | 197.4101 | 847.5328 | 869.0175 | 1964.1939 | 32.81% | 56.0492 | 137.0613 | 267.6131 | 395.6361 | 856.3597 | 43.95% | 36.19%
46 | 20 | 0.054778 | 0.094232 | 1298.8992 | 455.2904 | 3023.6 | 6662.35 | 788.95 | 3920.91 | 50.2336 | 197.4101 | 630.6231 | 1029.7649 | 1908.0317 | 31.92% | 56.0492 | 137.0613 | 139.9207 | 484.6289 | 817.6602 | 44.32% | 35.64%
47 | X1 | 0.084285 | 0.14387 | 1685.1114 | 711.5189 | 7183.6 | 3542.35 | 3668.95 | 1760.91 | 50.2336 | 197.4101 | 1498.2617 | 547.5227 | 2293.4281 | 26.52% | 56.0492 | 137.0613 | 650.6902 | 217.6505 | 1061.4512 | 32.97% | 28.56%
48 | X2 | 0.083156 | 0.19751 | 1588.0457 | 632.6079 | 6143.6 | 4582.35 | 2948.95 | 2480.91 | 50.2336 | 197.4101 | 1281.3521 | 708.2701 | 2237.2658 | 29.02% | 56.0492 | 137.0613 | 522.9978 | 306.6433 | 1022.7517 | 38.15% | 31.88%
49 | X3 | 0.019967 | 0.22697 | 1537.5346 | 563.5865 | 5103.6 | 5622.35 | 2228.95 | 3200.91 | 50.2336 | 197.4101 | 1064.4424 | 869.0175 | 2181.1036 | 29.51% | 56.0492 | 137.0613 | 395.3055 | 395.6361 | 984.0521 | 42.73% | 33.62%
| X4 | 0.020961 | 0.13265 | 1997.7177 | 924.556 | 8183.6 | 4542.35 | 4668.95 | 2760.91 | 50.2336 | 197.4101 | 1706.8287 | 702.0875 | 2656.5599 | 24.8% | 56.0492 | 137.0613 | 828.0407 | 341.2516 | 1362.4029 | 32.14% | 27.29%
| X5 | 0.066918 | 0.19119 | 1893.0117 | 847.3582 | 7143.6 | 5582.35 | 3948.95 | 3480.91 | 50.2336 | 197.4101 | 1489.9191 | 862.8349 | 2600.3976 | 27.2% | 56.0492 | 137.0613 | 700.3484 | 430.2444 | 1323.7033 | 35.99% | 30.17%
| X6 | 0.10705 | 0.1338 | 1825.973 | 790.8813 | 6103.6 | 6622.35 | 3228.95 | 4200.91 | 50.2336 | 197.4101 | 1273.0094 | 1023.5823 | 2544.2354 | 28.23% | 56.0492 | 137.0613 | 572.656 | 519.2372 | 1285.0038 | 38.45% | 31.66%
| X7 | 0.067112 | 0.084436 | 2278.5679 | 1133.5159 | 9183.6 | 5542.35 | 5668.95 | 3760.91 | 50.2336 | 197.4101 | 1915.3957 | 856.6523 | 3019.6917 | 24.54% | 56.0492 | 137.0613 | 1005.3913 | 464.8527 | 1663.3545 | 31.85% | 27.14%
| X8 | 0.015336 | 0.10758 | 2208.6914 | 1060.2796 | 8143.6 | 6582.35 | 4948.95 | 4480.91 | 50.2336 | 197.4101 | 1698.486 | 1017.3997 | 2963.5294 | 25.47% | 56.0492 | 137.0613 | 877.6989 | 553.8455 | 1624.655 | 34.74% | 28.75%
| X9 | 0.053419 | 0.1099 | 2135.976 | 1024.7153 | 7103.6 | 7622.35 | 4228.95 | 5200.91 | 50.2336 | 197.4101 | 1481.5764 | 1178.1472 | 2907.3672 | 26.53% | 56.0492 | 137.0613 | 750.0065 | 642.8384 | 1585.9554 | 35.39% | 29.66%
| X10 | 0.03387 | 0.020552 | 2590.2587 | 1353.9915 | 10183.6 | 6542.35 | 6668.95 | 4760.91 | 50.2336 | 197.4101 | 2123.9627 | 1011.2172 | 3382.8235 | 23.43% | 56.0492 | 137.0613 | 1182.7418 | 588.4539 | 1964.3062 | 31.07% | 26.24%
| X11 | 0.060562 | 0.13131 | 2485.5951 | 1309.3226 | 9143.6 | 7582.35 | 5948.95 | 5480.91 | 50.2336 | 197.4101 | 1907.053 | 1171.9646 | 3326.6612 | 25.28% | 56.0492 | 137.0613 | 1055.0494 | 677.4467 | 1925.6066 | 32% | 27.75%
| X12 | 0.011186 | 0.027081 | 2449.3974 | 1255.6203 | 8103.6 | 8622.35 | 5228.95 | 6200.91 | 50.2336 | 197.4101 | 1690.1434 | 1332.712 | 3270.499 | 25.11% | 56.0492 | 137.0613 | 927.357 | 766.4395 | 1886.9071 | 33.46% | 28.16%
| X13 | 0.081596 | 0.041125 | 4061.1165 | 2559.9018 | 15183.6 | 11542.35 | 11668.95 | 9760.91 | 50.2336 | 197.4101 | 3166.7976 | 1784.0413 | 5198.4825 | 21.88% | 56.0492 | 137.0613 | 2069.4944 | 1206.4595 | 3469.0645 | 26.21% | 23.61%
| X14 | 0.018123 | 0.024331 | 3983.9357 | 2500.2214 | 14143.6 | 12582.35 | 10948.95 | 10480.91 | 50.2336 | 197.4101 | 2949.8879 | 1944.7887 | 5142.3202 | 22.53% | 56.0492 | 137.0613 | 1941.8021 | 1295.4523 | 3430.3649 | 27.12% | 24.36%
| X15 | 0.0044017 | 0.029682 | 3924.3704 | 2456.1414 | 13103.6 | 13622.35 | 10228.95 | 11200.91 | 50.2336 | 197.4101 | 2732.9782 | 2105.5361 | 5086.158 | 22.84% | 56.0492 | 137.0613 | 1814.1097 | 1384.4451 | 3391.6654 | 27.58% | 24.74%
[6 empty] | #N/A |  | #N/A
[6 empty] | #N/A |  | #N/A
[6 empty] | #N/A |  | #N/A
[6 empty] | #N/A |  | #N/A
[6 empty] | #N/A |  | #N/A
[6 empty] | #N/A |  | #N/A
[6 empty] | #N/A |  | #N/A
[6 empty] | #N/A |  | #N/A
[6 empty] | #N/A |  | #N/A
[6 empty] | #N/A |  | #N/A

## References
In total, the FRS study period includes an average of 2,745 megawatts of wind
and 1,080 megawatts of solar
In total, the FRS includes 2,202 megawatts of Non-VERs
|  | 1035.5 | approximately 1,000 five-minute intervals,
|  | 0.4938% | or 0.5% of the data was removed due to data errors
|  |  | 210216 | five-minute intervals evaluated
|  |  | 209182 | PACW
|  |  | 1034 | PACW Errors
|  |  | 0.4919% | PACW Rate
|  |  | 209179 | PACE
|  |  | 1037 | PACE Errors
|  |  | 0.4957% | PACE Rate
|  | 1.041% | For instance, a 82 MW ACE shortfall in PACW has a one percent chance of exceeding the Balancing Authority ACE Limit.
PACE | PACW
0.0021903 | 5.8688e-05 |  | In 2018-2019, PacifiCorp’s deviations and Balancing Authority ACE Limits were uncorrelated, which indicates that PacifiCorp’s contribution to WECC-wide frequency is small.
433.3062 | 245.2942 | 678.6004 | Total Requirement after Portfolio Diversity (MW)
|  | 378.817 | Portfolio Diversity Benefit (MW)
|  | 35.82% | Portfolio Diversity Benefit (%)
|  | 140.1697 | In the historical period, EIM diversity benefits used in the FRS would have reduced regulation reserve requirements by approximately 140 MW.
|  | 17.9887 | the average requirement of 540 MW would require ramping capability of at least 17.7 MW per minute
1.6663 | 0.8024 |  | At the 97.5th percentile, fast ramping requirements for PACE and PACW are 1.7 MW/minute and 0.8 MW/minute higher than the Requirement 2 ramp rate, respectively;
|  | -0.60548 | however, if dynamic transfers between the BAAs are available, the 97.5th percentile for system as a whole is 0.6 MW / minute lower than the Requirement 2 value
Table F.1 - Portfolio Regulation Reserve Requirements
Table F.2 - 2023 Flexible Resource Costs as Compared to 2021 Costs, $/MWh
Table F.3 – Summary of Stand-alone Regulation Reserve Requirements
Table F.4 - EIM Diversity Benefit Application Example
Table F.5 – 2018-2019 Results with Portfolio Diversity and EIM Diversity Benefits