## Sheet1
ANNUAL HEAT LOSS FOR INSULATED PIPE
2 1/2" THICK INSULATION, 225F PIPE WALL TEMP
|  |  |  | 1.5-inch polyisocyanurate insulation |  |  |  | 2.5-inch polyisocyanurate insulation
Pipe Dia, in | Length of Uninsulated Pipe, ft | Annual Operating Hours | Heatloss Btu/ft-hr (bare) | Heatloss Btu/ft-hr (Ins at 1.5") | Total Energy Savings , Btu/hour/ft | Fuel Savings Thm per year per foot |  | Heatloss Btu/ft-hr (Ins at 2.5") | Total Energy Savings , Btu/hour/ft | Fuel Savings Thm per year per foot
1 | 1 | 4000 | 141.3981 | 12.8922 | 128.5059 | 6.4253 |  | 8.7468 | 132.6514 | 6.6326
1.25 | 1 | 4000 | 161.9062 | 13.9619 | 147.9443 | 7.3972 |  | 9.7528 | 152.1534 | 7.6077
1.5 | 1 | 4000 | 188.8906 | 15.2549 | 173.6357 | 8.6818 |  | 11.0117 | 177.8789 | 8.8939
2 | 1 | 4000 | 256.3516 | 18.0879 | 238.2637 | 11.9132 |  | 13.8972 | 242.4544 | 12.1227
3 | 1 | 4000 | 377.7812 | 22.3425 | 355.4388 | 17.7719 |  | 18.4213 | 359.36 | 17.968
4 | 1 | 4000 | 485.7188 | 25.6212 | 460.0976 | 23.0049 |  | 21.9637 | 463.755 | 23.1878
5 | 1 | 4000 | 600.1325 | 28.7926 | 571.3399 | 28.567 |  | 25.39 | 574.7425 | 28.7371
6 | 1 | 4000 | 715.0859 | 31.7664 | 683.3195 | 34.166 |  | 28.5869 | 686.4991 | 34.325
[5 empty] | 0 | 0
Sched 40 Steel Pipe Properties
[11 empty] | Nom D | Actual D | Radius | Bare Area/LF | Ins Area/LF | Ins Area/LF
[11 empty] | in | in | in | sq ft | sq ft | sq ft
[15 empty] | (1.5"ins thick) | (2.5"ins thick)
[11 empty] | 1 | 1.31 | 0.655 | 0.34278 | 1.1278 | 1.6511
[11 empty] | 1.25 | 1.5 | 0.75 | 0.3925 | 1.1775 | 1.7008
[11 empty] | 1.5 | 1.75 | 0.875 | 0.45792 | 1.2429 | 1.7663
[11 empty] | 2 | 2.375 | 1.1875 | 0.62146 | 1.4065 | 1.9298
[11 empty] | 3 | 3.5 | 1.75 | 0.91583 | 1.7008 | 2.2242
[11 empty] | 4 | 4.5 | 2.25 | 1.1775 | 1.9625 | 2.4858
| Assumptions: | [9 empty] | 5 | 5.56 | 2.78 | 1.4549 | 2.2399 | 2.7632
[11 empty] | 6 | 6.625 | 3.3125 | 1.7335 | 2.5185 | 3.0419
| Pipe wall temp |  |  |  |  | 225
| Delta T |  |  |  |  | 165 | F
| Thermal conductivity of product k = .18 btu-in/hr-sq ft-F |  |  |  |  | 0.18 | btu-in/hr-sq ft-F
| Overall heat transfer coefficient h = 2.5 Btu/hr-sq ft-F |  |  |  |  | 2.5 | Btu/hr-sq ft-F
| Heat transfer equation - |  | Q/A =( Tin-Tambient)/ ((R Ins pipe x ln (R ins pipe /R pipe)/k + 1/h)
For bare pipe D = 2" for example, R pipe = R insulation, ln (1.1875/1.1875) =0, therefore Q/A=( Tin-Tambient)/ ( 1/h)
Area of pipe per lineal foot of pipe = (pi x D) = 3.14 x 2.375 /12 = .62 sq ft/lf of pipe
Q/LF bare 2" pipe = 165/(1/2.5) x .62 sq ft/lf= 412 Btu/hr x .62 = 256 Btu/hr-LF of bare pipe
Q/LF insulated 2" pipe with 1.5" insulation = 165/ ( (2.687 x ln (2.687/1.187)/.18 + 1/2.5) x 1.41= 18 Btu/hr-LF of insulated pipe