## Slide 1: San Juan Island fiber-based transport system inspection results - Coriant 7100 Backbone - FW7420 Backbone
November 17, 2016

## Slide 2: San Juan Island fiber results
This inspection documents signal strength between the Coriant 7100 optical electronics located at Lopez Island and at La Conner Washington
  Fiber loss was calculated as the difference between the transmit (Tx) level and the receive (Rx) levels.
  These levels were observed on the optical service channels of the 7100 AMP Modules.

## Slide 3: San Juan Island fiber results
Tx = -0.2db
LOPZWAXXO02010025
LACNWAAXKRC01CUST06B-A
Tx = +2.0db
Rx = -12.6db
Overall fiber loss: -12.4db
Overall fiber loss: -15.1db
La Conner to Lopez Island
The Reconfigurable Optical Add/Drop Multiplexer (ROADM ) system supports up to 26db span loss
Rx = -13.1db
Rx = -13.2db
Tx = +2.8db
Rx = -15.7db
Overall fiber loss: -18.4db
Overall fiber loss: -16.0db
Tx = +2.7db
Degree A
Degree B
LACNWAAXKRC01CUST06A-A

## Slide 4: San Juan Island fiber results
This inspection documents signal strength between the Fujitsu FW7420 optical electronics located at Lopez Island and at Friday Harbor Washington
  Fiber loss is calculated as the difference between the Tx level and the Rx levels.
  These levels were observed on the optical service channels of the FW7420.

## Slide 5: San Juan Island fiber results
Tx = +1.7db
Rx = -18.4db
FRHRWAXAO02
Mod 1-3
SC-1-3-NE
LOPZWAXXO01
Mod 1-7
CH-1-7-NW F2488
Tx = +2.5db
Rx = -15.8db
Overall fiber loss: -18.5db
Overall fiber loss: -18.5db
The Friday Harbor to Lopez Island system supports up to 26db span loss

## Slide 6
At the Pear Point landing site on San Juan Island, inspection revealed that the outer protective sheath of the cable had been abraded, but the cable’s integrity and its optical communication paths had not been compromised. A section of cable will be replaced. The permit approvals necessary to complete the work are pending. In the unlikely event of a submarine cable failure, CenturyLink's radio-based transport systems have the capacity to support E911, FAA, and telephony service.
A site survey was conducted at the first location where submarine cable appears on land and is accessible. The survey involved visual examination of the fiber optic cable, condition of the vault or pedestal, and changes in the surrounding environment.
San Juan Island fiber results