## Slide 1: Utility Reliability Performance Objectives: Theoretical and Practical Considerations
Joseph H. Eto
jheto@lbl.gov
September 19, 2017
Washington Utilities and Transportation Commission
Olympia, Washington

## Slide 2: LBNL Reliability Research
Reliability Performance Data and Metrics
Review of reliability data reported to PUCs (2008)
Review of reliability data reported to NERC/EIA (2012)
Support for EIA collection of reliability data (2013, 2016)
Analysis of Major Event definitions (2016)
Analysis of Distribution vs. Bulk Power System Reliability (submitted for publication)
GMLC task 1.1 – develop new bulk power system metric for NERC State of Reliability report (in progress)
Reliability Analysis
Econometric analysis of trends in reliability (2012, 2014, update in progress)
Customer adoption of stand-by generation/UPS (2016)
Review of reliability information posted in real-time by utilities (in progress)
The Economic Value of Reliability
Interruption Cost Estimate (ICE) Calculator (2005, 2010, 2015)
Review of regional economic modeling to estimate cost of long-duration, widespread interruptions (2016)
Insurance industry perspectives (2016)
Value-based Reliability Planning
National cost of power interruptions (2004, submitted for publication)
Utility case studies (2015)
PUC experiences with utility filings (2016)
GMLC task 1.1 - incorporate ICE Calculator into APPA web portal (in progress)
https://emp.lbl.gov/research-areas/electricity-reliability

## Slide 3
The pace of electricity grid modernization efforts will be determined by decisions made by electric utilities, their customers, and local communities/states to adopt new technologies and practices
An important motivation for these actions will be maintaining or improving the reliability and resiliency of electric service
From an economic perspective, the justification for these actions will therefore, depend, at least in part, on:
  The cost of the actions under consideration (including who pays for them);
  The impact they are expected to have on reliability or resilience; and
  The value these impacts have to the utility, its customers, and the community/state
Better information will enable, but does not guarantee, better decisions …and we will never have perfect information
Opening Remarks

## Slide 4
Value-Based Reliability Planning (VBRP) takes into account the cost of interruptions in guiding reliability decisions

## Slide 5
DOE/LBNL developed the Interruption Cost Estimate (ICE) Calculator to support VBRP applications
http://icecalculator.com

## Slide 6
From Distribution Automation at EPB Chattanooga:
Customers Impacted: 174,000 customers (entire territory)
Investment: 1,200 automated circuit switches and sensors on 171 circuits
Reliability Improvement Achieved between 2010 and 2015:
  SAIDI 45%
  from 112 to 61.8 minutes / year
  SAIFI 51%
  from 1.42 to 0.69 interruptions / year
Chart: 
| Benefits | Investment Costs
Utility | 5.5691
Avoided customer outage costs | 26.8
Annual Costs and Benefits
Avoided Cost of Severe Storm
VBRP Example: Electric Power Board of Chattanooga

## Slide 7: SAIDI and SAIFI aggregate/mask information on the types of customers affected by power interruptions, as well as information on how long and when their lights are out
System Average Interruption Duration Index (SAIDI)
System Average Interruption Frequency Index (SAIFI)
Electric utility industry reliability metrics, by themselves, are not well-suited for supporting VBRP

## Slide 8: The economic cost of power interruptions
Varies by type of customer and depends on when and for how long their lights are out

## Slide 9
IEEE Standard 1366 | Investor Owned | Cooperative | Municipal
Number of utilities reporting | 137 | 296 | 117
% of U.S. sales by type of utility | 51% | 47% | 43%
SAIDI with Major Events | 237 | 302 | 115
SAIDI without Major Events | 136 | 159 | 50
SAIFI with Major Events | 1.4 | 2.8 | 0.9
SAIFI without Major Events | 1.2 | 2.1 | 0.7
Reliability data collected by the US Energy Information Administration for calendar year 2015

## Slide 10: LBNL finds that reliability is getting worse due to increased severity/frequency of major events
Source: Larsen, P. K LaCommare, J. Eto, J. Sweeney. Recent Trends in Power System Reliability and Implications for Evaluating Future Investments in Resiliency. Energy 117 (2016) 29-46. http://dx.doi.org/10.1016/j.energy.2016.10.063
Notes: If major events are not included (see Figure ES-1), we find the following statistically significant relationships:
A 5% increase in annual average wind speed is correlated with a 5% increase in SAIDI; yet a 10% increase in annual average wind speed is correlated with a 2% decrease in SAIDI; and
Independent of these factors, each successive year over the analysis period is correlated with a slightly larger than 1% increase in the SAIDI.
If major events are included (see Figure ES-2), we find the following statistically significant relationships:
A 10% increase in annual precipitation—above the long-term (generally, 13-year) average—is correlated with a 10% increase in SAIDI;
A 10% increase in the number of cooling degree-days (i.e., warmer weather)—above the long-term (generally,13-year) average—is correlated with a 8% decrease in SAIDI;
A 5% increase in annual average wind speed is correlated with a 56% increase SAIDI; a 10% increase in annual average wind speed is correlated with a 75% increase in SAIDI;
A 10% increase in the percentage share of underground line miles is correlated with a 14% decrease in SAIDI; and
Independent of the above factors, each successive year over the analysis period is also correlated with a nearly 10% increase in SAIDI.
We believe that this apparently counterintuitive result is explained by recognizing that utilities categorize higher average wind speed events (i.e., major storms) into the dataset that includes major events.

## Slide 11
Chart: Back-up Generation (BUG) share of total installed capacity
| New England | Mid-Atlantic | East North Central | West North Central | South Atlantic | West South Central | East South Central | Mountain | Pacific
Residential | 0.0088729 | 0.19202 | 0.017891 | 0.0063645 | 0.11416 | 0.014158 | 0.014158 | 0.0080024 | 0.027739
Commercial | 0.13821 | 0.22599 | 0.14211 | 0.86077 | 0.19485 | 0.06897 | 0.06897 | 0.039187 | 0.18246
Industrial | 0.13606 | 0.52399 | 0.11356 | 0.11916 | 0.10168 | 0.17964 | 0.17964 | 0.15033 | 0.21878
Source: Frost and Sullivan. 2015. “Analysis of the US Power Quality Equipment Market.” Berkeley California: Lawrence Berkeley National Laboratory. LBNL-1003990. August. Accessible at: http://eetd.lbl.gov/sites/all/files/lbnl-1003990.pdf
Customers are augmenting utility-provided reliability by purchasing back-up generation

## Slide 12
“What's measured improves” ― Peter F. Drucker
“Delegating your accountabilities is abdication” ― Michael E. Gerber
“Not everything that can be counted counts, and not everything that counts can be counted” ― Albert Einstein
Some themes to keep in mind