ATTACHMENT A

Investigation Report

CenturyTel of Inter Island d/b/a CenturyLink

UT-132234

Staff Investigation

Consumer Protection

Regulatory Services

August 2014

TABLE OF CONTENTS

#### Purpose, Scope, and Authority	3
Executive Summary	4

Background	7

Investigation – Network Description, Outage, and Restoral	8

Investigation – Communication During the Outage	15

Recommendations	22

Appendices	26

# PURPOSE, SCOPE, AND AUTHORITY

Purpose

The purpose of this investigation is to determine whether CenturyTel of Inter Island d/b/a CenturyLink (CenturyLink) complied with Utilities and Transportation Commission (commission) laws and rules during a ten day service outage that began Nov. 5, 2013, when an underwater fiber failure caused toll and data outages in San Juan County, and whether commission staff should recommend penalties for any violations of laws or rules.

Scope

The scope of this investigation focuses on CenturyLink’s business practices prior to, during, and immediately following the outage.

Authority

Staff undertakes this investigation pursuant to Revised Code of Washington (RCW) 80.01.040 and 80.04.070, which grant the commission authority to conduct such an investigation, as well as RCW 80.04.380, which authorizes the commission to penalize public service companies for violations of commission rules and other requirements.

Note: this report presents the findings of a commission staff investigation and staff’s recommendations for action by the three-member commission in a subsequent proceeding. This report has not been reviewed formally by the commissioners. Conclusions and recommendations contained in this report are those of commission staff, and not the commissioners.

Staff

Rayne Pearson, Consumer Protection

(360) 664-1136

rpearson@utc.wa.gov

Robert Williamson, Regulatory Services 
(360) 664-1288
bwilliam@utc.wa.gov

# EXECUTIVE SUMMARY

Beginning early on the morning of Nov. 5, 2013, CenturyLink experienced a voice and data outage in the San Juan Islands when an underwater fiber segment of the company’s system was severed, which isolated the host switch in Friday Harbor from the remainder of the network.

The outage resulted in a loss of toll calls, data communications, and local calls on San Juan, Lopez, Orcas, Blakely, Decatur, and Shaw Islands, and between those islands and the mainland. Approximately 5,800 access lines on San Juan Island retained intra-island calling ability.  Following considerable efforts and incremental restoration, CenturyLink fully restored service on Nov. 15, 2013. The outage affected a total of 15,921 regulated access lines.

Commission staff initiated an investigation on Dec. 6, 2013. On Dec. 9, the commission held a public hearing in Friday Harbor to hear from the Company, as well as from local customers and government agencies. Representatives from the San Juan County Department of Emergency Management, San Juan Fire Service, Orcas Power and Light Cooperative (OPALCO), San Juan Chamber of Commerce, and local businesses expressed dissatisfaction with CenturyLink’s infrastructure, equipment, and service; communication during and immediately following the outage; and the service restoral timeframe.

Subsequent to the hearing, commission staff undertook further investigation to:

- Determine what caused the outage;

- Evaluate CenturyLink’s restoration efforts;

- Evaluate CenturyLink’s communications with affected customers during the outage; and

- Determine the extent to which CenturyLink’s facilities in the San Juan Islands were adequate to provide service as required by state law.

Staff worked with an outside consultant, Robert Munoz, Undersea Cable Consultants, LLC, to assist in the investigation of the cause of the outage and evaluate the company’s restoration efforts. Mr. Munoz’s full report is attached as Appendix J.

As a result of this investigation, staff concluded that CenturyLink violated the following laws and commission rules:

- WAC 480-120-412(2), Major Outages – Notification to the commission

- WAC 480-120-412(3), Major Outages – Notification to county E911 coordinator

- WAC 480-120-412(5), Major Outages – Dissemination of information to the public

Staff also concluded that, given the circumstances, CenturyLink was fortunate to have restored service in just 10 days.  Finally, after investigating the national standards in the telecommunications industry for providing service to island communities, staff was unable to conclude that CenturyLink’s facilities were inadequate compared to similar facilities around the country.

Following the outage, CenturyLink replaced the severed undersea cable and committed to installing a microwave system to ensure backup service in the event of future disruptions. That installation is currently underway.

Penalty Recommendation

Staff recommends the commission issue a formal complaint against the company and assess a penalty of up to $173,210 for 15,935 violations of commission laws and rules, as follows:

- Up to $3,000 for three violations of WAC 480-120-412(2) for failing to promptly notify the commission of the outage.

- Up to $10,000 for ten violations of WAC 480-120-412(3) for failing to immediately notify the county E911 coordinator of the outage and provide periodic updates.

- Up to $1,000 for one violation of WAC 480-120-412(5) for failing to implement procedures specific to this outage to disseminate information to the public and public officials.

- $10 for each of 15,921 violations of WAC 480-120-412(5) for failing to disseminate information to the public, for a total penalty of $159,210.

Technical Recommendations

To limit the impact of future outages, staff recommends the commission require CenturyLink to do each of the following:

- Notify the commission when each microwave system’s spectrum has been approved by both the Federal Communications Commission and Canadian authorities.

- Notify the commission when both microwave systems are suitable for providing service.

- Submit an annual maintenance plan to the commission specifying, at a minimum, the microwave facilities to be inspected and the frequency and manner in which inspections are conducted.

- Report annually to the commission that both San Juan microwave systems are able to provide redundant capacity to island customers.

- Report annually to the commission any routine maintenance performed during the preceding year for both the underwater fiber cable and microwave systems.

- Require the company to petition the commission for approval of any company plans to modify or eliminate redundant service between the islands and from the islands to the mainland.

- By Nov. 30 each year, submit proposed annual inspection plans for the subsequent calendar year for all underwater facilities in Washington owned by CenturyLink that connect a community to the public switched network. The plans should, at a minimum, specify the location of the facility to be inspected and the frequency and manner in which inspections are conducted.

- By March 31 each year, submit an annual report to the commission describing the actual inspections conducted in the preceding calendar year.

Report Format
This investigation report is divided into four sections. The first section provides background information about the company and the investigation. The second section describes the network and discusses findings related to the cause and restoral of the outage. The third section discusses findings related to CenturyLink’s communications with commission staff, local government, and affected customers during the outage. Staff’s recommendations appear in the last section.

BACKGROUND

Company Information
CenturyTel of Inter Island d/b/a CenturyLink is an incumbent Local Exchange Carrier (LEC) in the San Juan Islands, incorporated in the state of Washington and owned by CenturyTel of the Northwest. CenturyTel of the Northwest is owned by CenturyLink Holdings, which is in turn owned by CenturyLink, Inc. On March 14, 2011, the commission issued Final Order 14 in Docket UT-100820, approving and adopting, subject to conditions, a multiparty settlement agreement authorizing CenturyLink, Inc. to acquire indirect control of Qwest Corporation, Qwest LD Corp. and Qwest Communications Company LLC. 

Investigation
Following CenturyLink’s November 2013 voice and data outage in the San Juan Islands, commission staff initiated this investigation to determine whether the company complied with commission laws and rules. On Dec. 6, 2013, Regulatory Services staff sent a series of data requests to CenturyLink inquiring about the make and manufacturer of the severed fiber optic cable, placement of the cable, pre-existing or past damage to the cable, maintenance of the cable, metrics for measuring network reliability, and information about whether CenturyLink had or has service agreements with OPALCO for assistance in the event of a network outage. Staff issued follow up data requests on Jan. 8, 2014, and Feb. 28, 2014.

On Jan. 6, 2014, Consumer Protection staff requested the following information from CenturyLink related to the service outage:

- The number of affected customers, identified by island, customer type (commercial or residential), and CenturyLink services affected.

- A chronology of all internal communications related to the outages, including summaries of phone calls and copies of any emails or other written correspondence.

- A chronology of all communications with stakeholders related to the outages (such as commission staff, other federal, state, county, and local governments), including summaries of phone calls and copies of any emails or other written correspondence.

- A chronology of service restoral by location, number of customers, and service type.

- Information about whether CenturyLink had a communication plan in place.

- Information regarding plans for communicating with stakeholders during future outages.

- CenturyLink’s plans to provide bill credits to the customers who the missed service during the outage.

On Jan. 21, CenturyLink provided responsive information to all but item 2, above. On March 4, CenturyLink produced the remaining responsive documents and information.

INVESTIGATION – NETWORK DESCRIPTION, OUTAGE, AND RESTORAL

Network Description

CenturyLink provides voice services in the San Juan Islands through one central office host switch (located in Friday Harbor on San Juan Island) and a number of remote line switches connected by underground and submarine fiber optic links. The map below, prepared by CenturyLink and modified by staff, illustrates the network that provides voice, E911, and data services to the San Juan Islands.

Long distance calling and E911 services require a connection between the central office host switch in Friday Harbor (located on San Juan Island) and the remote line switches located on the other islands. The two fuchsia flags identified as “single route” on the chart above represent the two connections that, if severed, would isolate the central office host switch in Friday Harbor.

The submarine fiber optic cables have been installed over time, as follows:

- The link from Anacortes through Decatur Island to Lopez Island was installed in 1984.

- The link from Shaw Island to Lopez Island was installed in 1985.

- The link from Orcas Island to Shaw Island was installed in 1986.

- The link from Blakely Island to Orcas Island was installed in 1986.

- The link from Decatur Island is also linked to Blakely Island, and was installed in 1988.

- The link from Lopez Island to San Juan Island was installed in 1999 and replaced in 2013.

The original CenturyLink “MF48” submarine cable replaced an analog microwave route from the islands to the mainland. It was built by Pirelli Jacobsen, an underwater fiber contractor, in 1999. Harbor Offshore, Inc., laid the last fiber link from Anacortes to Decatur Island in 2004, completing the company’s fiber route for its San Juan Islands customers to the mainland. The Pirelli single-armored submarine cable consists of 48 glass optical fibers embedded within a hermetically sealed copper tube. Inside the tube, the 48 fibers are contained in a helical slotted plastic rod extruded around a high strength steel wire. The copper tube is covered by a polyethylene sheath. Outside the polyethylene sheath, there is a layer of galvanized steel wires that provide mechanical protection.  The wires are then wrapped with a thick layer of polypropylene yarn, and subsequently wrapped with jute. The Pirelli submarine cable is similar to other non-repeated optical submarine cables in use around the world today for shallow water applications, and it meets international standards.

Network Outage

On Nov. 5, 2013, CenturyLink experienced a voice and data outage in the San Juan Islands when a fiber segment of the company’s system connecting Lopez Island to the main switch on San Juan Island was severed.

During the failure, CenturyLink customers on Orcas, Decatur, and Lopez Islands had access to local intra-island service, but were unable to contact other islands until Nov. 7, 2013. Because of the loss of connectivity to the Friday Harbor central office host switch on San Juan Island, customers on those islands had no access to long distance calling and could not reach 911 for emergency services. Before basic 911 service was restored on Nov. 7, CenturyLink issued a press release instructing its customers to call their local fire department in the event of an emergency. CenturyLink customers on San Juan Island could make basic 911 calls, but had no access to inter-island calling or long-distance service. Limited Internet service was available on all islands except San Juan. The outage partially impacted cellular service provided by unaffiliated carriers.

The fiber link connection where the failure occurred follows a corridor specified by the Washington State Department of Natural Resources (DNR) between Lopez and San Juan Islands. A power cable owned by OPALCO also lies within the DNR cable crossing corridor, which is clearly marked on marine charts as a cable crossing. The company’s contractor, Harbor Offshore, used a remotely operated underwater vehicle to inspect the CenturyLink fiber optic cable and found that it had been moved or dragged north from its original position and pulled tight up against a rock feature.

On Nov. 4, 2013, at 8:05 p.m., the ebb current ran south at 4.02 knots; it changed to a strong flood with a north-running current at 4.53 knots on Nov. 5 at 2:46 a.m., about one hour before the network failure was noticed at 3:45 a.m. It is possible that the cable suffered earlier damage and the subsequent tidal movement severed the cable. When staff and consultant Mr. Munoz later viewed the failed section at the company warehouse in Gig Harbor, it appeared that the cable had been severed, rather than abraded, from tidal movement.

CenturyLink personnel contacted the U.S. Coast Guard and the Washington Department of Fish and Wildlife requesting any information they had concerning vessels in the area on Nov. 5. Neither entity was aware of any vessels in the area. Mr. Munoz also performed a search of historical vessel data at the time of the failure and found that a research vessel, the R/V Centennial, owned and operated by the University of Washington, passed over the cable on its regular schedule on Oct. 9, 15, 22, and 29, 2013.  Staff requested from the university information concerning the vessel’s activities at that time, and copies of the vessel’s sailing log. The university provided a copy of the log on June 11, 2014. While the log only provided information on the vessel’s departure and arrival times at its dock at Friday Harbor, the cover letter explained that any research equipment the vessel drags through the water is delicate, and would break if it touched the bottom. Mr. Munoz could not identify any other definitive ship traffic in that area. Further discussions of other possible factors that may have contributed to the fiber break are contained in Mr. Munoz’s report.

Restoral

CenturyLink contracted with Harbor Offshore, Inc. to repair the failed fiber link. The contractor’s dive team arrived at the San Juan Island site on Nov. 6, 2013, to begin making repairs. According to Mr. Munoz,

“The cable service was restored in less than 10 days after the break, which is somewhat unusual for shallow water repairs. Shallow water repairs require specialized equipment such as a barge, navigation tools, cable chute, a powered cable reel and experienced repair personnel. A ROV (Remote Operated underwater Vehicle) was also on site to assist with locating the cable break and performing the repair. For all of these tools and resources to be available on such short notice is an achievement worth noting. It usually takes up to a month or more to mobilize the necessary tools and resources for a shallow water repair.”

CenturyLink located a sufficient amount of spare submarine fiber cable at a company warehouse in Kent and purchased the appropriate splicing equipment from Waveguide, Inc. in Seattle. CenturyLink has since restocked spare cable and supplies.

According to Mr. Munoz, even with the right equipment and crew in place, finding and fixing the cable was difficult. The month of November was stormy, and high winds in the San Juan Islands made it difficult to use the ROV and barge. Additionally, in the San Juan Channel at Griffin Bay between San Juan and Lopez Islands, the tidal current— which changes every six hours mostly running north and south— sometimes runs above four knots. The company reported that current and wind made it very difficult to keep the barge on station so that the ROV could “swim” the cable to find the fault. Also, when an “armored” submarine splits, it recoils from the tensile pressure of the metal armor moving the ends from the original position, and the ends of the severed cable may be moved even farther by the current. Once Harbor Offshore found the ends of the failed cable it needed tractor tugs to “hold station” within a three-foot window to bring one end of the existing cable to the surface, splice it to a new section of cable, and lower the repaired cable to the seabed.

Mr. Munoz stated,

“Cable repair operations commenced with the recovery of the parted western end of the cable. Once sufficient cable had been recovered beyond any damaged cable and water ingress, the Western end of the cable was cut and prepared for splicing. The western end of the cable was spliced to a section of spare cable, and once the splice was completed, the repair barge began laying spare cable eastward towards Fishermen Bay landing. The cable repair was completed with a new shore landing at Fishermen Bay.”

When the new 6,100 foot cable was spliced to the undamaged portion of the remaining cable, the repaired cable was lowered to the seabed and anchored to the bottom using large heavy portions of chain to restrict potential tidal movement. The cable was rerouted away from an existing rock pinnacle, which may have been a factor in the failure.

Service was fully restored on Nov. 15, 2013. Both Mr. Munoz and CenturyLink’s repair contractor stated that the repair of the fiber cable was accomplished in a short period of time because of the availability of the necessary equipment and qualified personnel. They also agreed it is not unusual for an underwater repair to take longer than 30 days.

Service Restoral Timeline
The following table, submitted by CenturyLink in response to staff’s data requests, details the service restoration chronology.

| Date | Time | Voice Service Impact |
| --- | --- | --- |
| 11/05/13 | 0345 | Voice monitoring systems detect loss of connection to Friday Harbor switch. Approximately 11,000 voice customers are impacted. About 5,800 on have intra-island calling capability on San Juan Island. The remaining 5,200 on other islands have no voice calling capability over the CenturyLink network – some cellular service is still working. |
| 11/05/13 | 0815 | 911 service re-routed to local law enforcement on San Juan Island. (Approximately 5800 voice connections). |
| 11/05/13 | 0926 | 911 service re-routed to local law enforcement on Orcas Island. (Approximately 4200 voice connections). |
| 11/05/13 | 1555 | It becomes clear that the cause of the trouble is under water. |
| 11/06/13 | 1340 | Dive team arrives on location. Weather and unexpectedly strong currents would hamper search for cable damage over the next several days. |
| 11/06/13 | 1750 | CenturyLink and OPALCO complete a fiber connection in preparation for partial restoration of service over radio. Minimal change in service impact. |
| 11/07/13 | 1301 | CenturyLink authorizes Verizon to use space on its Radio tower to partially restore Verizon cellular service. |
| 11/07/13 | 2359 | Inter-island calling restored on Lopez and Orcas islands. 911 re-routed to San Juan County Sherriff’s office on San Juan Island. ANI/ALI service not yet available for 911. Almost all voice customers now have intra and inter-island calling capability. |
| 11/08/13 | 2022 | Toll service (outside the islands) calling partially restored. All voice customers have the capability to call outside the islands, but capacity is limited. |
| 11/09/13 | 0925 | Some special service circuits for cellular carriers and other large business customers are restored. |
| 11/09/13 | 2108 | 911 ANI/ALI enabled – 911 operations normal. |
| 11/11/13 | 1729 | Fiber damage located with Remotely Operated Vehicle. |
| 11/11/13 | 1739 | Confirmed all FAA service restored. Voicemail restored. |
| 11/12/13- 11/14/13 |  | Isolated outages with relatively short durations occur as CenturyLink works to add additional capacity. |
| 11/15/13 | 0930 | Service is 100% restored. |

On the date of the failure, the San Juan Islands had a single connection to the outside world from the Friday Harbor central office host switch. The lack of multiple physical routes between the main switch at Friday Harbor and the rest of the islands’ networks, coupled with the main switch’s lack of multiple physical routes to the mainland, contributed to the company’s inability to offer uninterrupted service.

Following the repair of the severed undersea cable, two portions of the network without multiple routes remain, and the loss of either would result in the same situation experienced during the outage on Nov. 5. The single route links are as follows:

- The submarine fiber optic link between Anacortes and Lopez Islands (via Decatur Island) compose the single connection to the mainland, and its loss would isolate the islands. This link crosses Rosario Strait, an extremely busy shipping lane. Any repair in this location would be complicated by restrictions for working in the middle of that shipping lane.

- The submarine fiber optic link between Lopez Island and San Juan Island isolates the host Friday Harbor central office switch from the outside world and the other inter-island remotes.

In order to provide continuous voice and 911 service among the San Juan Islands and between the San Juan Islands and the rest of the national network, CenturyLink has committed to installing two digital microwave systems. The first supports voice and 911 service between the islands, and the second establishes a connection from Friday Harbor to Bellingham via Mt. Constitution, which, pending completion, will support commission-regulated services such as E911 and voice calling between the San Juan islands and the rest of the national network in the event the undersea cables fail.  These microwave systems are estimated to cost about $500,000, not including ongoing maintenance and tower leasing costs.

In addition to the construction of the microwave networks, CenturyLink is also actively seeking an agreement for capacity sharing with another fiber provider in the San Juan Islands. This agreement would provide redundancy for 100 percent of its voice and data traffic – both regulated and non-regulated services – to its San Juan Island customers.

State Network Requirements

Washington law requires telecommunications companies to provide services “in a prompt, expeditious and efficient manner … and … service shall be modern, adequate, sufficient and efficient.” Neither the law nor Commission rules define what constitutes “modern, adequate, sufficient and efficient” service. More specifically, Commission rules do not currently require telecommunications companies to provide multiple physical routes between a company’s switching centers, or to the broader national telecommunications network.

In this case, whether service is “modern, adequate, sufficient and efficient” can be determined by looking at the common practices throughout the telecommunications industry. Accordingly, staff sought information from other jurisdictions in North America with island communities to determine whether those jurisdictions have laws or rules requiring multiple physical routes between switching centers, or to the broader national telecommunications network.

At staff’s request, the National Association of Regulatory Utility Commissions (NARUC) distributed a survey to members of its telecommunications committee. It received responses from New York, Georgia, Arkansas, New Mexico, Iowa, Wisconsin, Michigan, Pennsylvania, and Texas.  None of these states have rules requiring telecommunications companies to provide multiple physical routes between a company’s switching centers or to the broader national network.  In addition to the NARUC survey, staff independently contacted Maine, North Carolina, South Carolina, Georgia, Florida, California, Oregon, Alaska, and the Canadian provinces of Nova Scotia and British Columbia.  Like those states that responded to the NARUC survey, none of these jurisdictions require multiple physical routes between switching centers or to the broader network.

Major Outages

Staff reviewed CenturyLink’s recovery effort to determine whether the company complied with WAC 480-120-412(1), Major Outages, which provides as follows:

All companies must make reasonable provisions to minimize the effects of major outages, including those caused by force majeure, and inform and train pertinent employees to prevent or minimize interruption or impairment of service.

Today’s telecommunications companies provide an array of voice and data services, and outages potentially affect businesses, banking, medical services, and other essential activities. While a normal landline cable repair can be completed in hours, not days, the repair of an underwater fiber cable is extremely complex and time consuming.

Staff’s investigation determined the company had sufficient materials on hand to repair the fiber, and its employees were adequately trained to locate the break and engage qualified contractors to repair the cable. Staff believes the company took the necessary steps to comply with the Major Outages rule; repairing an underwater cable damaged at a depth of approximately 280 feet on a seabed floor could have taken substantially longer to repair given the complex environment.

Staff supports the company’s efforts to install redundant systems, and believes CenturyLink should additionally seek a capacity sharing agreement with OPALCO to ensure each company has redundant routes to the mainland. This option would give CenturyLink a third redundant route, allowing the company to transport all of its voice and data traffic to the mainland in the event of an outage.

INVESTIGATION – COMMUNICATION DURING THE OUTAGE

Public Hearing
As part of this investigation, the commission held a public hearing on Dec. 9, 2013, in Friday Harbor. A number of local government officials and business owners spoke about the outage and provided feedback related to CenturyLink’s responsiveness and restoration efforts. Consumers also expressed concerns about the company’s infrastructure and lack of redundancy.

The following themes emerged during the public comment hearing:

- The serious financial consequences the outage had on local businesses;

- CenturyLink’s failure to communicate adequately with affected customers; and

- The company’s lack of redundancy and reliable infrastructure.

External Communication during the Outage
The following table, submitted by CenturyLink in response to staff’s data request, contains a chronology of the company’s communications with external stakeholders during the outage.

| Date | Time | Topic | Reach |
| --- | --- | --- | --- |
| 11/05/13 | Not provided | “A fiber optic cable has been cut underwater between Lopez and San Juan Islands impacting CenturyLink Services, including 911 services, throughout the islands; 911 services on San Juan Island have been rerouted to the local 911 center.” | Local and Regional media |
| 11/05/13 | Not provided | - Outage notifications sent to the commission. - Coast Guard from operations department inquiring about vessel traffic in the area at the time of the breakage; no traffic was identified during that time period by the Coast Guard, but they did not rule out the possibility of private fishing vessels with no GPS equipment. - Multiple communications with OPALCO. | N/A |
| 11/06/13 | Not provided | “CenturyLink is working with Orcas Power & Light Cooperative (OPALCO) to provide a temporary solution that would restore local voice and 911 services for customers on San Juan, Orcas, and Lopez Islands.” | Local and Regional media |
| 11/06/13 | Not provided | - Coast Guard to CenturyLink operations reporting lack of vessel activity in the area of the cable breakage on Nov. 5. - OPALCO to CenturyLink Construction Engineering re: emergency circuit configuration. - OPALCO to network planners re: emergency workload logistics. - CenturyLink Network Operations to Verizon requesting any available radio/microwave capabilities to assist in restoral. | N/A |
| 11/07/13 | Not provided | “CenturyLink crews restored 911 and local phone service between Lopez and San Juan Island last night at 11:59 p.m. 911 has been rerouted to the San Juan County Sheriff’s office in Friday Harbor.” | Local and Regional media |
| 11/07/13 | Not provided | - E911 IT Program/Operations Manager to commission and CenturyLink Public Policy describing short and long term effects of restoration project. CenturyLink Public Policy to government officials forwarding the short and long term efforts on the restoration project. - Commission staff forwarding an email from E911 Operations to CenturyLink Public Policy and Legal informing that dial tone has been restored. - Commission staff to CenturyLink Public Policy informing that staff received notification from the Washington Military Department regarding the CenturyLink San Juan Island outage. | N/A |
| Date | Time | Topic | Reach |
| 11/08/13 | Not provided | “CenturyLink crews restored 911 and local phone service between Lopez and San Juan Islands Wednesday, Nov. 6, at 11:59 p.m. 911 has been rerouted to the San Juan County Sheriff’s office in Friday Harbor.” | Local and Regional media |
| 11/08/13 | Not provided | - OPALCO to CenturyLink Operations explaining that OPALCO will seek to recover damages from CenturyLink should any damages to OPALCO services result from CenturyLink recovery efforts. - CenturyLink Public Policy to commission providing a detailed update on the San Juan outage and restoration efforts. FCC Operations at Homeland Security to CenturyLink Engineering granting the Special Temporary Authority. Commission staff to CenturyLink Operations and Public Policy requesting an understanding of how the network is configured in the San Juans. - Seattle Times to CenturyLink Marketing requesting information to report on the cable break. - OPALCO to CenturyLink Engineering giving summary of week’s progress. - Commission to CenturyLink Operations and Public Policy requesting information on how the network is configured in the San Juans. - Emails among commission staff, 911 Operations Manager and restoration team discussing status of 911 on the islands. | N/A |
| 11/09/13 | Not provided | “Overnight, CenturyLink crews restored long distance service throughout San Juan County. CenturyLink and OPALCO continued to work through the night to restore internet service to San Juan island.” | Local and Regional media |
| 11/09/13 | Not provided | Harbor Offshore to CenturyLink confirming 5 cables sighted; described as damaged cable, bird caged armor, with football shaped weights. CenturyLink network to ADTRAN discussing the order of products necessary for repairs. | N/A |
| 11/10/13 | 11:36 a.m. | “Services have been temporarily restored to the San Juan Islands.” | Local and Regional media |
| 11/10/13 | 10:38 p.m. | “CenturyLink is working around the clock to restore communications.” | Local and Regional media |
| 11/11/13 | Midnight | “CenturyLink is working around the clock to restore communications.” | Statewide media via newswire; local distribution and CL social media |
| 11/11/13 | 6:26 p.m. | “CenturyLink severed fiber located: company continues massive effort to repair cable, restore service.” | Statewide media via newswire and local distribution and CenturyLink social media |
| 11/12/13 | 9:35 a.m. | “CenturyLink restoration efforts on the barge are temporarily suspended due to inclement weather and 40 knot winds.” | Local and Regional media |
| 11/12/13 | 11:27 a.m. | “Currently, CenturyLink is experiencing an outage on Orcas Island that is impacting 911 and voice services.” | Local and Regional media |

| Date | Time | Topic | Reach |
| --- | --- | --- | --- |
| 11/12/13 | Not provided | - Commission staff to CenturyLink Public Policy, Legal, and additional commission staff forwarding a complaint email from Rock Island Technology Solutions. Commission Staff to CenturyLink Public Policy requesting that Public Policy contact San Juan County Emergency Management re: outage update, media questions. - Commission staff to CenturyLink Public Policy forwarding email from San Juan County Emergency Management exploring alternative solutions for additional bandwidth. | N/A |
| 11/13/13 | 10:22 a.m. | “The outage that was reported on Orcas Island on 11/12 was caused by call volumes exceeding capacity.” | Local and Regional media |
| 11/13/13 | 4:42 p.m. | “CenturyLink is experiencing an outage impacting voice communication services on the islands starting at approx. 3:59 p.m. on Wednesday, 11/13. This outage is not due to capacity, but adding additional equipment to augment the network.” | Local and Regional media |
| 11/13/13 | 8:24 p.m. | “As previously messaged, CenturyLink experienced voice communication outages earlier this afternoon, services were restored for the majority of residents at 5:10 p.m. CenturyLink continued to monitor issues with a small number of customers until 8 p.m. this evening on Lopez and Orcas Islands.” | Local and Regional media |
| 11/13/13 | Not provided | “Orcas Island, Wash. – CenturyLink will be hosting a public forum to address any concerns from customers regarding the underwater fiber cut.” |  |
| 11/13/13 | Not provided | - San Juan County Emergency Management to CenturyLink, State and Federal elected officials, and local government facilitating a conference call to update the public on restoration efforts. - CenturyLink Public Policy and Marketing from San Juan County Emergency Management proposing new agenda for daily update calls. - Commission staff to CenturyLink Public Policy inquiring how much the outage will cost CenturyLink. - CenturyLink Public Policy to Senator Ranker informing him of the FCC request for Special Temporary Authority for a microwave radio pass in the 11 GHz band. - Commission staff to CenturyLink Public Policy and additional commission staff attaching emergency declaration. - CenturyLink Public Policy to commission staff discussing general estimate of projected costs to CenturyLink on the outage. - San Juan Journal to CenturyLink Marketing and Operations asking for clarification of cable replacement and backup system. - Construction Engineering to OPALCO concerning possible issues with fiber on the OPALCO-CTL cross connect. |  |
| 11/14/13 | 11:34 a.m. | “CenturyLink services may experience intermittent disruptions throughout the day in voice, 911, and data services as we continue with the restoration effort.” | Local and Regional media |
| 11/14/13 | Not provided | - San Juan County Department of Emergency Management to elected officials and local government providing contact information for CenturyLink. - CenturyLink marketing to parties affected by outage, including department of emergency management and local government officials. - Updates from CenturyLink Construction Management regarding submarine cable repair work. | N/A |
| 11/15/13 | Not provided | “CenturyLink crews restored services, including all voice and high-speed internet, to the San Juan Islands this morning. Crews worked overnight in the rain to connect the new fiber that was laid yesterday.” | Statewide media via newswire and local distribution and CenturyLink social media |
| Date | Time | Topic | Reach |
| 11/15/13 | 11:01 a.m. | “Lopez Island, Wash. – CenturyLink will be hosting a public forum to update residents on the progress of the underwater fiber restoration.” | Local and Regional media |
| 11/15/13 | Not provided | - San Juan County Emergency Department to CenturyLink thanking CenturyLink for restoration efforts and concerns going forward. - CenturyLink operations and marketing updating a reporter at the San Juan Journal. - OPALCO legal to CenturyLink team requesting review and signatures on master service agreement. | N/A |
| 11/20/13 | 5:17 p.m. | “Because of the recent outage caused by the undersea fiber optic cable cut, CenturyLink is actively working on a solution for out of service adjustments.” | Local and Regional media |

Communication with Commission Staff
CenturyLink’s chronology notes that it provided an outage report to commission staff on Nov. 5, 2013. The report, received by staff at 3:47 a.m., described the outage as follows: “5831 lines impacted due to toll isolation. Possible maintenance activity.” The notice gave an estimated restoral time of 8 a.m. that same morning. Subsequent to the company’s report, the Military Department’s State Emergency Operations Officer notified Staff that the outage was far more extensive and was likely due to a severed fiber cable. The Military Department invited Regulatory Services staff to participate in conference calls with CenturyLink on Nov. 6 at 10:30 a.m. and Nov. 7 at 10 a.m. CenturyLink’s first official communication with Staff about the nature and extent of the outage came on Friday, Nov. 8, 2013, in an email from Mark Reynolds, NW Regional Vice President. In his email, Mr. Reynolds explained the company’s lack of communication as follows:

“Notice was made to the WUTC via our standard notice process on 11/5. Rebecca 	[Beaton, Regulatory Services] and I agree that with such a major event, the WUTC 	needs to be linked into all information dissemination. I assumed that the notification of 	subsequent meetings of the emergency management agencies included the WUTC.  	Obviously that was not a good assumption and I take full responsibility for not reaching  	out to WUTC to ensure it was in the loop. I apologize for the inconvenience and commit  	to making immediate contact when future events arise.”

WAC 480-120-412(2), Major Outages, provides that: “When a company receives notice of or detects a major outage, it must notify the commission and any PSAP serving the affected area as soon as possible.” The outage report submitted by CenturyLink on the morning of Nov. 5 did not describe a major outage; it described a toll restriction due to “possible maintenance” that was expected to be restored within hours.  CenturyLink’s first official communication with commission staff about the nature and extent of the outage came from the aforementioned email from Mr. Reynolds.

CenturyLink’s failure to comply with WAC 480-120-412(2) and notify the commission directly of a major outage violates the rule for each day the company failed to act. Because the Company identified the cause of the outage on the afternoon of Nov. 5, staff finds three violations of WAC 480-120-412(2) for Nov. 5, 6, and 7. 

Communication with the PSAP and E911
Brendan Cowan, Director of San Juan County Department of Emergency Management, spoke at the Dec. 9 public hearing in Friday Harbor, where he expressed concern that his department was not directly notified of the outage until nearly 12 hours after it had occurred, and then only in response to an email Mr. Cowan sent to the company. For the San Juan Islands, the Department of Emergency Management serves as both the PSAP and the E911 coordinator. Mr. Cowan reported that at 3:03 p.m. on Nov. 5, 2013, “our office reached out to the mainland CenturyLink contacts, asking for information about a possible submarine cable break – that was news to us.” Because CenturyLink failed to communicate with the Department of Emergency Management, Mr. Cowan relied on unconfirmed reports in the local media and “an amateur radio volunteer who reported overhearing radio traffic indicating that the outage was due to a submarine cable break.”

Mr. Cowan sent the following email to CenturyLink on Nov. 5 at 3:03 p.m.:

“As I assume you’re aware, we’re in the midst of a serious comms/911 outage in San 	Juan County. Initial reports were that it was an underground fiber line that was dug up 	and it would be repaired by 2pm, but now we’re hearing rumors (not from 	CenturyLink) that it was actually an underwater cable and might be much longer, 	possibly days.

So far, the information coming from CenturyLink about this has been non-existent 	or minimal. Calls and emails to Debbie Martinez, our local CenturyLink contact, have 	been unreturned. I understand that you’re busy, but would really benefit from better 	information flow from your organization.

We’ve long had an effective system in place where updates were emailed by 	CenturyLink to outage@sanjuandem.net and this automatically updated our key 	Emergency Response 	organizations. Since the personnel transition following the 	retirement of Bill Henikman, this has not happened.”

On Nov. 5, 2014, At 3:13 p.m., both the Department of Emergency Management and State 911 were first officially notified by CenturyLink that, “We’ve had splicers working on the fiber cut since 1:30 p.m. today and hope to resolve this soon.”

In addition to violating WAC 480-120-412(2) as it relates to notifying PSAPs “as soon as possible,” CenturyLink’s failure to immediately notify the San Juan County Department of Emergency Management violated WAC 480-120-412(3), which provides, “When a major outage affects any emergency response facility, a company must notify immediately the county E911 coordinator and the state emergency management authorities, and provide periodic updates on the status of the outage.”

According to Mr. Cowan, “we never had clear information, it was always complicated.” And according to Mr. Duncan, the Friday Harbor Town Administrator, “The information that was being passed down the line that we could pass on to our citizens was muddled at best.” Staff believes the evidence provided by Mr. Cowan and Mr. Duncan supports a finding that CenturyLink violated WAC 480-120-412(3) by failing to provide meaningful periodic updates on the status of the outage for its duration.  Each day of the outage constitutes a separate and distinct violation; between Nov. 5 and Nov. 15, CenturyLink violated the rule ten times.

Communication with Customers
WAC 480-120-412(5) provides that, in the event of a major outage, “all companies must implement procedures to disseminate information to the public, public officials, and news media. All companies must provide a statement about the major outage that includes the time, the cause, the general location and approximate number of affected access lines, and the anticipated duration.”

At the commission’s public hearing on Dec. 9, 2013, several consumers and public officials commented about the company’s lack of communication during the outage. Bob Jarman, a San Juan County Council member, stated that, “The main issue we had with CenturyLink was communication, failure to get information out.”

Duncan Wilson, Friday Harbor Town Administrator, commented that, “Somebody knew where the ships were, somebody knew where the divers were, somebody knew what was going on, and that information was not making it back to this island.”

Paul Kamin, Manager, Eastsound Water Users Association, submitted a written comment, noting that, “CenturyLink was slow in releasing information about the outage and was completely dependent on media outlets to distribute their press releases …The lack of information added to the stress of the situation. I encourage the UTC to examine the timeline of this service outage in conjunction with the announcements that CenturyLink provided. San Juan County has no radio stations in the County, and there is no daily print media.”

Sandra Green, from the Four Winds Camp, submitted the following written comments: “We need an emergency communication plan. What do we do, how do we find out what’s going on – besides the jungle drums, which are not always accurate …The people in the islands understand about underwater cables and we know that equipment mainly breaks; just give us the information without the spin.”

Connie Jones, of Canoe Island French Camp, submitted the following written comment: “My biggest complaint about CenturyLink and the phone/internet outage was the lack of communication with their clients. As a client of both internet and phone in Washington and Oregon, I was quite amazed that I never received an email or phone call from CenturyLink during or after the hiatus in service.”

Rick McCoy, from Lopez Island Pharmacy, submitted the following written comments: “…when off-island health care providers tried to call us we later found out that they were told that the numbers were disconnected. First this cost us revenue and second some of those calling thought we were out of business, a perception that someone who calls us infrequently still might have … a more specific automated answer needs to be implemented, something that outlines the problem to the caller in exact terms … [and] a more widespread notice to local broadcast media and others on the problem, as well as blast email at least to CenturyLink subscribers.”

Roger Sherman, of Microsoft, submitted the following written comment: “In my opinion, CenturyLink should be severely penalized for its failure to provide basic communications services to this county. There is no excuse for lack of a backup. Failures like this are totally predictable except for the date of their occurrence. The response to this failure was also totally botched for lack of adequate planning.”

Although CenturyLink issued daily news releases for the duration of the outage, the company failed to post information at its local Friday Harbor office or other physical locations throughout the islands, such as fire stations, schools, or grocery stores until “about the third day.”  At that point, CenturyLink posted its news releases “on the door of the central office located at 50 Second Street, Friday Harbor, and at Kings Market, the Post Office and Market Street Grocery.” Each of those locations is in Friday Harbor; nothing was posted at any location on the other affected islands.

In response to staff’s data request for any existing communications plan, CenturyLink submitted a document entitled “Local Outage Procedures – Market Development Managers & Corporate Communications” that describes, in general terms, which personnel are authorized to speak with the media, what information should be collected, and external messaging. The document describes generic procedures that are not at all specific to Washington or this outage. Staff therefore finds that CenturyLink failed to implement procedures specific to this outage to disseminate information to the public and public officials, as required by WAC 480-120-412(5). Additionally, CenturyLink’s failure to communicate adequately with its customers during the outage constitutes 15,921 violations of WAC 480-120-412(5), one for each regulated access line affected by the outage.

Commission-Referred Consumer Complaints and Inquiries	
Consumer protection staff received two complaints and two inquiries related to the outage. Two customers requested and received credits.

RECOMMENDATIONS

Enforcement Authority and Policy
Staff typically recommends a “per violation” penalty against a regulated company where the violations result in serious consumer harm; for repeat violations of a rule after the company receives technical assistance; or for intentional violations of commission laws or rules. The commission has the authority to assess penalties of $100 per violation, per day against a regulated company without providing the opportunity for a hearing. The commission also has the authority to assess penalties of up to $1,000 per violation, per day following a formal complaint and hearing.

In this investigation, staff documented 15,935 violations of commission laws and rules, and recommends a penalty of up to $173,210. While the company restored service as soon as possible, staff believes the foreseeability of the outage – coupled with the company’s lack of planning and poor communication with regulators, customers, and stakeholders during the outage – warrants a penalty of this size. While staff could recommend penalties of up to $1,000 per violation, to do so would be unduly punitive. Staff considered the following factors to determine the recommended penalty amount:

- How serious or harmful the violation is to the public.

CenturyLink’s equipment failure caused serious financial harm to customers and, because of 911 outages, could have resulted in fatalities. Business owners described significant revenue losses due to an inability to communicate with suppliers and customers; pharmacies were unable to communicate with doctors’ offices to obtain necessary medication for patients; and residents could not communicate with 	family members off-island. The financial impact was significant, and could have been avoided if the company had installed redundancy or coordinated other backup planning in advance.

- Whether the violation is intentional.

Although the outage itself was unintentional, the evidence supports a finding that it was foreseeable. CenturyLink’s lack of redundancy ensured that, in the event of a cable break, services would be lost indefinitely.

Staff also believes the evidence supports a finding that while CenturyLink’s poor communication with commission staff, E911, and its customers was unintentional, it was avoidable. Without a redundant system in place, the company knew or should have known that such an outage was inevitable, and therefore should have had procedures in place for notifying regulators and other stakeholders about the nature and extent of the outage, as well as the expected restoral timeframe.

- Whether the company self-reported the violation.

The company failed to report the outage to the commission until three days after it occurred, which violates commission rules.

- Whether the company was cooperative and responsive.

Responses to Consumer Protection staff’s data requests were delayed and incomplete. Otherwise, the company was cooperative and responsive during the investigation.

- Whether the company promptly corrected the violations and remedied the impacts.

Given the circumstances, the company was fortunate to be able to restore service in a relatively short time, and has provided credits totaling $271,487.86 to affected customers.

- The number of violations and the number of customers affected.

The outage affected 15,921 regulated access lines, and staff found a total of 15,935 violations.

- The likelihood of recurrence.

Absent a redundant network, the likelihood of recurrence is very high. With redundancy, however, the likelihood of recurrence with respect the company’s communication during an outage is contingent upon the company’s plans and strategy going forward.

- The company’s past performance regarding compliance, violations and penalties.

In August 2008, staff reviewed 212 commission-referred consumer complaints filed against CenturyLink’s predecessor company Qwest between Jan. 1 and June 30, 2008, to determine Qwest’s compliance with rules and laws enforced by the commission. Staff found that Qwest violated 11 consumer protection laws and rules. Staff provided Qwest with a copy of the investigation report and met with company representatives to discuss the findings and provide technical assistance.

Staff performed a follow-up investigation in March 2010, using 102 consumer complaints filed against Qwest between March 1 and June 30, 2009. Despite the company’s assurance of future compliance and the ongoing technical assistance provided through the commission’s consumer complaint process, staff found violations of ten statutes and rules. Staff recommended the commission issue a formal complaint against Qwest for 69 violations of laws and rules enforced by the commission, and recommended a penalty of $69,000.

In March 2014, staff performed a subsequent follow-up investigation using 144 consumer complaints filed against Qwest and CenturyLink from Sept. 1, 2011, to Aug. 31, 2012. Staff found several repeat violations, and recommended the commission issue a formal complaint against the company and impose penalties of up to $313,000.

- The company’s existing compliance program.

Staff is not aware of any existing compliance program.

- The size of the company.

The company reported total Washington intrastate operating revenues of $476,017,729 in 2013.

Penalty Recommendation
Staff recommends the commission issue a formal complaint against the company and assess a penalty of $173,210 for 15,935 violations of commission laws and rules, as follows:

- Up to $3,000 for three violations of WAC 480-120-412(2) for failing to promptly notify the commission of the outage.

- Up to $10,000 for ten violations of WAC 480-120-412(3) for failing to immediately notify the county E911 coordinator of the outage and provide periodic updates.

- Up to $1,000 for one violation of WAC 480-120-412(5) for failing to implement procedures specific to this outage to disseminate information to the public and public officials.

- $10 for each of 15,921 violations of WAC 480-120-412(5) for failing to disseminate information to the public, for a total penalty of $159,210.

Additionally, Staff recommends that CenturyLink closely review this report and the violations cited herein, which constitute technical assistance. Future violations will result in additional enforcement action, including penalties.

Technical Recommendations

To limit the impact of future outages, staff recommends the commission order CenturyLink to do each of the following:

- Notify the commission when each microwave system’s spectrum has been approved by both the Federal Communications Commission and Canadian authorities.

- Notify the commission when both microwave systems are suitable for providing service.

- Submit an annual maintenance plan to the commission specifying, at a minimum, the microwave facilities to be inspected and the frequency and manner in which inspections are conducted.

- Report annually to the commission that both San Juan microwave systems are able to provide redundant capacity to island customers.

- Report annually to the commission any routine maintenance performed during the preceding year for both the underwater fiber cable and microwave systems.

- Require the company to petition the commission for approval of any company plans to modify or eliminate redundant service between the islands and from the islands to the mainland.

- By Nov. 30 each year, submit proposed annual inspection plans for the subsequent calendar year for all underwater facilities in Washington owned by CenturyLink that connect a community to the public switched network. The plans should, at a minimum, specify the location of the facility to be inspected and the frequency and manner in which inspections are conducted.

- By March 31 each year, submit an annual report to the commission describing the actual inspections conducted in the preceding calendar year.

APPENDIX A

APPENDIX B

APPENDIX C

APPENDIX D

APPENDIX E

APPENDIX F

APPENDIX G

APPENDIX H

APPENDIX I

APPENDIX J

Expert Report San Juan Island Lopez Island

Century Link Cable Break

June 20, 2014

Undersea Cable Consultants, LLC. Tel: (551)404-5440

rmunoz.ucc@gmail.com

Because of its proximity to the U.S.-Canadian border, both the FCC and Canadian authorities must approve the Mount Constitution to Bellingham route.

See Appendix A for a copy of the Dec. 6, 2013, data request.

See Appendix B for a copy of the Jan. 8, 2014, data request, and Appendix C for a copy of the Feb. 28, 2014, data request.

A remote line switch aggregates calls for the customers it serves. The switch is capable of processing local calls between customers connected to the switch. Other types of calls such as long distance, E911, or customers not connected to the remote line concentrator will be sent to the host switch (Friday Harbor) for processing.

Decatur, Blakely, Orcas, Shaw, and Lopez Islands are connected via a self-healing fiber ring. A self-healing ring has the ability to automatically reroute the calls if there is a disruption in service on the primary route (e.g., the primary route for Blakely Island would send calls north to Orcas Island). For example, if this fiber link was severed, those calls would automatically reroute to Orcas in the other direction on the ring (through Decatur).

Fiber Optic repeaters are generally required for fiber optic facilities that are longer than 28 miles. None of the fiber links in the San Juan are long enough to require the signal to be repeated.

International Telecommunications Union (ITU) Recommendation G.973 and Optical Fibres, Cables and Systems Manual (ITU T Manual 2009.)

Appendix J, page 5, paragraph 2, through page 6.

Appendix J, page 15, paragraph 8.

Appendix J, page 19, paragraph 8.3, through page 21.

Appendix J, page 14, paragraph 8, through page 19.

Appendix J, page 10, paragraph 2.

Appendix J, page 7, paragraph 2.

Appendix J, page 26, paragraph 11.

Although the Commission does not have direct authority over CenturyLink’s provision of broadband (internet) services, staff understands that the microwave system will also be used for backup or redundancy purposes in support of some of the company’s broadband service offerings traveling via microwave to Bellingham.

RCW 80.36.080

Harbor Offshore is the Marine contractor that located and replaced the broken cable.

ADTRAN is a telecommunications vendor.

See Appendix D for a copy of the Nov. 5, 2013, outage notification email sent to commission staff.

See Appendix E for a copy of the Nov. 8, 2013, email from Mark Reynolds to commission staff.

A recording of the public hearing is available at http://www.avcaptureall.com/Sessions.aspx#session.f778517c-bfd9-41d6-8ffd-e15c25d9f6d8.

See Appendix F for a copy of the Nov. 5, 2013, email from Brendan Cowan to Markus Volke at CenturyLink.

See Appendix G for a copy of Mr. Volke’s Nov. 5, 2013, reply to Mr. Cowan.

See Appendix H for a copy of the May 6, 2014, email exchange between staff and CenturyLink.

See Appendix I for a copy of the non-confidential version of the document entitled, “Local Outage Procedures – Market Development Managers & Corporate Communications.”

RCW 80.04.405 allows the commission to assess an administrative penalty for any violation by a regulated company of a statute, rule, the company’s own tariff, or commission order.

RCW 80.04.380 allows the commission to assess a penalty of up to $1,000 for each violation following a hearing.

Docket A-120061, Enforcement Policy for the Washington Utilities and Transportation Commission (January 7, 2013).