BEFORE THE WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION

| In the Matter of the Petition of CASCADE NATURAL GAS CORPORATION, Request for authorization to operate a facility with a Maximum Allowable Operating Pressure between 251 psig and 499 psig within 100 feet of a proscribed area WAC 480-93-030 | DOCKET NO. UG-020663 ORDER GRANTING REQUEST |
| --- | --- |

BACKGROUND

- On April 25, 2002, Cascade Natural Gas (CNG), a Washington corporation, filed an application to receive written authorization allowing the installation of a natural gas facility having a maximum allowable operating pressure (MAOP), of 380 pounds per square inch gauge (psig).  WAC 480-93-030 prohibits the operation of a facility having a MAOP between 251 psig and 499 psig within 100 feet of a proscribed area, unless written authorization has been given by the Commission.

- The homeowner located at 4686 Aldrich Road in Bellingham, is requesting natural gas service from CNG to serve a single family dwelling.  The main was there prior to the house being built.  The new service would tap into the existing 8-inch high-pressure gas pipeline, located on Waldron Road and operated by CNG with a MAOP of 380 psig within 100 feet of the building requesting natural gas service.  Only a 10 foot portion of the proposed gas service, (which is located 85 feet from the home)  is located within the Waldron Road right-of-way, will operate at a  MAOP of 380 psig.  This request will not have a detrimental impact on public safety.  Pressure regulation installed at the property line will reduce the MAOP from 380 psig to 60 psig.

- The request for approval to operate at 380 psig in accordance with WAC 480-93-030 is reasonable and consistent with the public interest and the Commission should grant CNG’s request.

FINDINGS OF FACT

- CNG, a Washington corporation, is a public service company subject to the jurisdiction of the Commission under the provisions of RCW 80.01.040; Chapter 80.04 RCW; Chapter 80.28 RCW and WAC 480-93.

- This matter was brought before the Commission at its regularly scheduled open meeting on June 14, 2002.  The Commissioners, having determined this order to be consistent with the public interest, directed the Secretary to enter the following order and related provisions.

CONCLUSIONS OF LAW

- The Washington Utilities and Transportation Commission has jurisdiction over CNG, and subject matter of this proceeding.  RCW 80.01.040; Chapter 80.04 RCW; Chapter 80.28 RCW and WAC 480-93.

- It is consistent with the public interest that the Commission grant CNG’s request for authorization to operate the proposed service pressure not exceeding 380 psig.

O R D E R

- THE COMMISSION GRANTS the petition of Cascade Natural Gas Corporation for authorization to operate at 380 psig in accordance with WAC 480-93-030.

DATED at Olympia, Washington, and effective this 14th day of June, .

WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION

CAROLE J. WASHBURN, Secretary