# Report to the Washington Utilities and Transportation Commission

## Electric Service Reliability - Major Event Report

# Date:				September 5-6, 2013

Date Submitted:				October 8, 2013

Primary Operating Area(s) Affected:		Walla Walla

Exclude from Reporting Status: 				Yes

Report Prepared by:				Diane DeNuccio

Report Approved by:				Heide Caswell

Event Description:

The Pacific Power Emergency Action Center was activated as of 11:56 a.m. on Friday, September 6, due to a severe thunderstorm that swept through the Company’s Washington service territory on Thursday night, September 5, causing significant interruptions beginning at approximately 5:30 p.m. due to heavy rains and wind gusts of 60 miles per hour.  Lightning and vegetation into facilities caused loss of supply due to downed wire, broken poles and blown fuses in all areas but primarily and most significantly in Walla Walla.

Customers Out Sustained:  11,821

Total Customer Minutes Lost:  5,223,698

Sustained Interruptions:  136

PacifiCorp is requesting this event and the consequences thereof to be classified a “Major Event” because it exceeded the design limits of the system and the Company’s current annual IEEE 1366-2003 threshold of 1,430,667 customer minutes lost in a 24-hour period in Washington.

Restoration Description:

Additional company crews from Hood River, Madras, Bend, Pendleton, Portland and Astoria, along with contract and vegetation crews, helped local crews fix downed lines, damaged poles and other storm-related damage.

SAIDI, SAIFI, MAIFI Report:  Attached

Customers Out Over Time Chart: