## Slide 1: Pacific Northwest Resource Adequacy
Washington Utilities and Transportation Commission July 24, 2023
Dor Hirsh Bar Gai

## Slide 2: Agenda
2021 Power Plan Recommendation
2027 Adequacy Assessment
A New Multi-Metric Approach
Market Dynamics Matter
Vision for the Near Future

## Slide 3: 2021 Power Plan Recommendations
In the next six years the region needs to add:
Between 750 – 1,000 aMW of energy efficiency
At least 3,500 MW of renewable resources
Estimated 720 MW of demand response that can be used regularly to shift loads to support daily ramping and renewable integration (e.g., 520 MW of DVR and 200 MW of TOU)
At least 3,100 MW of additional reserves (on top of existing 2,900 MW, for a total of 6,000 MW)

## Slide 4: 2027 Adequacy Assessment Calls for Regional Action
In order to maintain resource adequacy, the region needs to:
Follow the Council’s 2021 Power Plan resource strategy
Includes adding 3,100 MW of additional reserves (double the current amount)
Doing nothing will put the region at great risk.
Futures with increased electrification require
additional renewable buildouts and energy efficiency
as identified in the 2021 Power Plan

## Slide 5: The Strategy Will Help Secure Regional Adequacy
Ensures that on average no more than 1 year in 20 will have a significant event
Nearly eliminates issues in the summer
Mitigates the need for emergency resources in the winter through less frequent and smaller events
Protects against long shortfall events
Reference with Resource Strategy (RS Ref)
Reference without Resource Strategy (No RS)
Heatmaps of Maximum Capacity Shortfall (MW) by Month-Hour (2027 Adequacy Assessment)

## Slide 6: Reminder of Studies for Potential Futures
  Resource Strategy baseline (RS Ref)
  No Resource Strategy (No RS)
  Minimum Resource Strategy (Min RS)
  Limited Markets (RS Ref)
  High WECC Demand (RS Ref, +200 aMW EE)
  Global Instability (RS Ref)
  Early Coal Retirement without Replacement (RS Ref)
  No WECC Buildout (RS Ref)
  SW Drought (RS Ref)
  Pipeline Freeze (RS Ref)
  Wildfire (RS Ref)
WECC Stress
Market Conditions
Plan Resource Strategy

## Slide 7
A New Multi-Metric Approach

## Slide 8: Need to Assess Multiple Areas of Risk
The Council is shifting to a new, more sophisticated, multi-dimensional approach, to measure
adequacy

## Slide 9: Proposed Metrics
LOLEV – Prevent overly frequent use of emergency measures
  Expected number of shortfall events/year, counting all shortfall events
  Adequacy Limit = Provisional threshold of 0.1 or 0.2 shortfall events/year
Duration VaR97.5 – Limit the risk of long shortfall events to 1/40 years
  Longest shortfall event for the 97.5th worst simulation year
  Adequacy Limit = Provisional threshold of 8 to 12 hours
Peak VaR97.5 – Limit the risk of big capacity shortfalls to 1/40 years
  Highest single-hour shortfall for the 97.5th worst simulation year
  Adequacy Limit = Provisional threshold of 2,000 to 3,000 MW
  Limit set to aggregate emergency capacity or acceptable amount of single-hour demand at risk
Energy VaR97.5 – Limit the risk of big energy shortfalls to 1/40 years
  Total annual shortfall energy for the 97.5th worst simulation year
  Adequacy Limit = Provisional threshold of 4,000 to 8,000 MWh
  Limit set to aggregate emergency energy or acceptable amount of annual energy demand at risk
Frequency
metric
Duration
metric
Magnitude
metrics
97.5% = 39/40
2.5% = 1/40

## Slide 10: Rephrasing the Adequacy Perspective
LOLEV:
  Every time we have a shortfall event, an emergency measure will be used, let’s not do it too often
Duration VaR97.5:
  39 out of 40 years, let’s make sure the shortfalls don’t last too long
Peak & Energy VaR97.5:
  39 out of 40 years, let’s make sure the shortfalls are not too big

## Slide 11: Multi-Metric Overview
Provisional Limit | <5% | 0.1-0.2 Event-year | 8-12 Hours | 2,000-3,000 MW | 4,000-8,000 MWh
Study | LOLP | LOLEV | VaR Duration | VaR Peak | Var Energy
RS Ref | 4.4 | 0.067 | 2 | 357 | 590
No RS | 46.1 | 0.933 | 6 | 2922 | 12504
Min RS | 4.4 | 0.061 | 2 | 837 | 1666
Limited Markets | 7.8 | 0.144 | 2 | 1450 | 3147
High WECC Demand | 17.2 | 0.589 | 5 | 4792 | 36617
Global Instability | 7.2 | 0.144 | 3.5 | 2041 | 5969
Early Coal | 13.9 | 0.233 | 2.5 | 1895 | 3807
No WECC Buildout | 8.3 | 0.172 | 3.5 | 2015 | 6410
SW Drought | 5 | 0.083 | 2 | 744 | 1421
Pipeline Freeze | 5 | 0.072 | 1.5 | 505 | 710
Wildfire | 4.4 | 0.067 | 2 | 357 | 590
Adequate with resources tested
Not adequate with resources tested
Borderline with resources tested

## Slide 12
Market Dynamics Matter

## Slide 13: Current Market Reliance Limit Offers Effective Risk Mitigation
Out-of-region market supply uncertainties have a minimal effect on regional adequacy, assuming the Council’s current market reliance limits:
  Drought
  Gas supply issues
  Wildfire
However, under certain future scenarios results show regional adequacy levels to become borderline or unacceptable:
  High gas prices coupled with continued supply chain challenges
  Lower than expected west-wide renewable generation acquisition
  Increased WECC demand, without increased regional investment in resources

## Slide 14: Future Buildouts in WECC May Pose Market Dynamic Risks that Influence Adequacy
Requires appropriate market signals, either from a regional reserve pooling effort or from an enhanced market structure
Closely related to question of (up) reserves in the region to mitigate generation forecast error of large renewable buildouts
Morning and evening ramps show reduced market availability and increased prices
This provides an opportunity for the Northwest to export to other regions in the west but also means that those are the times of most market risk for the Northwest.
Hourly pattern of renewable generation does not always coincide with the hourly pattern of greatest energy need.
Certain periods of the day may have very inexpensive market supply due to renewable surplus (mostly solar).
Renewable acquisition will change market supply and demand dynamics
Under increased supply and lower prices, NW expected to consistently import more
Substantial intra-day variation in supply and prices
Flexibility of hydro and thermal needed to ramp in response to changing market dynamics

## Slide 15: Example of Daily California Summer Import/Export Behavior
Positive = PNW import from California | Negative = PNW export to California
This example highlights the impact of High WECC Demand on a summer day (Aug):
Substantially less import during the morning ramp (A)
Earlier start to exporting during mid-day (B)
Less export in the evening ramp and night (C)
Less mid-day import (D)

## Slide 16
Vision for the Near Future

## Slide 17: Philosophical Approach to Thresholds
Emergency Capabilities
Available emergency capabilities for the region is the main driver for the initial provisional limits
Risk Tolerance
What level of risk is the aggregate emergency capabilities of the region able to protect?
Collaborate with regional utilities and stakeholders to evaluate and determine precise and appropriate regional adequacy thresholds.

## Slide 18: Planning for Uncertainty
Load uncertainty
How much energy will we need at any given time?
Policy uncertainty
Where are policies going, how to meet them and how might that impact the energy needs or choices?
Supply uncertainty
Will the energy supply be there when we need it?
Transmission uncertainty
How will the transmission system accommodate the growing renewable expansion?

## Slide 19
The Uncertainties are Growing Too

## Slide 20: Collaboration is Key
Facilitate regional conversations
Broaden discussion about reserves
Unified approach

## Slide 21: Questions
Dor Hirsh Bar Gai
dhirshbargai@nwcouncil.org

## Slide 22: Appendix

## Slide 23: Limited Markets
Removed planning reserve margins
  All other inputs the same as the baseline

## Slide 24: High WECC Demand
High electrification Pacific NW, California, BC and Alberta
  High demand only in those areas, baseline forecast elsewhere
All other inputs the same as the baseline, except updating policy targets (in MWhs)
This Photo by Unknown Author is licensed under CC BY-ND

## Slide 25: Persistent Global Instability
Higher fuel costs and delayed renewable deployment.
  Implemented by changing maximum annual new additions on short duration storage, solar and wind generation until 2030.
  Other resource ramps unchanged due to online date or previous restrictions
  All other inputs the same as the baseline
This Photo by Unknown Author is licensed under CC BY-SA-NC
This Photo by Unknown Author is licensed under CC BY
This Photo by Unknown Author is licensed under CC BY

## Slide 26: Early Coal Retirement
Removal of Colstrip 3 and 4 from the adequacy analysis without replacement
Colstrip Power Plant

## Slide 27: No WECC Buildout
Only existing resources across the WECC, except the NW
Reference resource strategy included for the PNW
As/Is

## Slide 28: Pipeline Freeze-off
Arizona
Loss of 5,000 MW natural gas from Arizona
November – February

## Slide 29: SW Drought
Glen Canyon – 1,312 MW
  Removal of 923 MW (Arizona)
Hoover – 2,078 MW
  Removal of 730 MW (Arizona)
  Removal of 316 MW (Nevada South)
Lake Oroville – 645 MW
  Removal of 542 MW (No_Cal)
Lake Shasta – 714 MW
  Removal of 315 MW (No_Cal)
On average, 2,826 MW of SW hydro is removed

## Slide 30: Wildfire
BPA_OR <-> PACW: 5,800 MW
BPA_OR <-> IP: 2,000 MW
BPA_OR <-> BPA_WA: 7,500 MW
Wildfire dates:
  July 16-23
  Derating:
    50-90% of lines