## Avoided Costs Reference
The avoided cost calculation to the left is from a 2013 TAC presentation. The table bottom left labeled Table 8.8 is from the 2013 IRP. As noted earlier, it is important to stay consistent with these values. The assumption is that the demand response is reliable (dispatchable) so that you would not need to build capacity with traditional generating resources.
Note: DR assets and associated costs would be included in the Avista Supply Resource Stack
Both tables have similar total levelized costs of approximately $68 with the Risk Premium showing the largest delta.

## Summary by Year
|  | CVR | [5 empty] | Key Benefit Assumptions:
| <300 amps |  |  | >300 amps |  |  |  | Load Factor | 0.38
[8 empty] | Avoided Cost of Energy ($/MWh) | 68
X&R Settings | [7 empty] | CVR Factor (if not known) | 0.87
1.25% savings prior to Grid Mod | [6 empty] | Grid Mod IVVC/CVR | Project Life (years) | 20.75
.75% after grid mod |  |  | AMI Augmentation |  |  |  | 2 volt drop after implementation | X&R Volt Drop | 1.25
|  |  | 2 volt drop possible |  |  |  |  | AMI Volt Drop | 2
.026% mitigation for low voltage
| Benefits |  |  | Costs
Year | X&R Savings | AMI Augmentation | Future Grid Mod | Grid Mod Cost | CVR/AMI Cost Other (Capital) | Mitigation (Capital) | CVR/AMI Cost Other (O&M)
1 | 914973.6092 | 2212474.6061 | 920665.092 | 0 | 599028.48 | 580000
2 | 953402.5008 | 2305398.5396 | 952799.0488 | 0 | 0 | 100000 | 239611.392 | Key Grid Mod Cost Assumptions (2016 Basis):
3 | 993445.4058 | 2402225.2782 | 1110048.2354 | 0 | 0 | 100000 | 246799.7338 | Viper Per Unit Cost | 75000
4 | 1035170.1129 | 2503118.7399 | 1033386.2864 | 0 | 0 | 100000 | 254203.7258 | Cap Bank Cost | 25000
5 | 1078647.2576 | 2608249.727 | 1080068.9639 | 0 | 0 | 100000 | 261829.8375 | Substation Costs | 50000
6 | 1123950.4424 | 2717796.2155 | 1129225.2828 | 0 | 0 | 100000 | 269684.7327 | Communications - FAN | 20000
7 | 1171156.361 | 2831943.6566 | 1180494.4564 | 0 | 0 | 100000 | 277775.2747 | Communications - Cell | 3600
8 | 1220344.9282 | 2950885.2902 | 1233442.3889 | 0 | 0 | 100000 | 286108.5329 | Vipers per Feeder - Rural | 1
9 | 1271599.4151 | 3074822.4723 | 1289673.1478 | 0 | 0 | 100000 | 294691.7889 | Vipers per Feeder - Urban | 2
10 | 1325006.5906 | 3203965.0162 | 1349584.7965 | 0 | 0 | 100000 | 303532.5425 | Cap Banks per Feeder Rural | 1
11 | 1380656.8674 | 3338531.5469 | 1412343.9939 | 0 | 0 | 100000 | 312638.5188 | Cap Banks per Feeder Urban | 2
12 | 1438644.4558 | 3478749.8718 | 1478819.0838 | 0 | 0 | 100000 | 322017.6744
13 | 1499067.523 | 3624857.3665 | 1550010.7596 | 0 | 0 | 100000 | 331678.2046
14 | 1562028.3589 | 3777101.3758 | 1624173.0529 | 0 | 0 | 100000 | 341628.5508 | Key Cost Assumptions Other (2016 Basis):
15 | 1627633.55 | 3935739.6336 | 1702249.1301 | 0 | 0 | 100000 | 351877.4073 | PI Dashboard Metrics | 239611.392 | (1 resource, $60/hr, 1.92 loading)
16 | 1695994.1591 | 4101040.6982 | 1783444.0467 | 0 | 0 | 100000 | 362433.7295 | X&R Relay Shop Labor | 119805.696 | (.5 resource, $60/hr, 1.92 loading)
17 | 1767225.9138 | 4273284.4076 | 1869426.0784 | 0 | 0 | 100000 | 373306.7414 | DMS Integration/Design | 239611.392 | (1 resource, $60/hr, 1.92 loading)
18 | 1841449.4022 | 4452762.3527 | 1959403.5725 | 0 | 0 | 100000 | 384505.9436 | Monitoring & Tuning | 239611.392 | (1 resource, $60/hr, 1.92 loading)
19 | 1918790.277 | 4639778.3715 | 2028615.0653 | 0 | 0 | 100000 | 396041.1219
20 | 1999379.4687 | 4834649.0631 | 2127726.485 | 0 | 0 | 100000 | 407922.3556
21 | 2083353.4064 | 5037704.3238 | 2316149.3917 | 0 | 0 | 50000 | 420160.0263
Totals | 29901920.0058 | 72305078.5531 | 31131748.3585 | 0 | 599028.48 | 2530000 | 6438447.8349
Load | 0.7% | 0.7% | 0.7% |  |  | O&M | 3%
Inflation | 3.5% | 3.5% | 3.5%
* Note Year 21 is 0.75 years | [6 empty] | labor
Note on N30: tzmj9b: Per Gibson

## Future Grid Mod
FeederName | > 6.7 MVA | DMS | SPEC | FUTURE IVVC | Rural/Urban | MVA | AmpsA | AmpsB | AmpsC | Annual GridMod Benefit | Annual R&X Benefit | Additional AMI Benefit After Grid Mod | GridMod YR | Grid Mod Cost
BEA12F1 | TRUE | N |  | Y | U | 7.9 |  | 347 |  | 34257.3057 | 21410.8161 | 12846.4897 | 2 | 220136
WAK12F2 | TRUE | N |  | Y | U | 10.3 |  | 452 |  | 44664.5885 | 27915.3678 | 16749.2207 | 2 | 170136 | 33565
LIB12F2 | TRUE | N |  | Y | U | 12.3 |  | 536 |  | 53337.3241 | 33335.8276 | 20001.4966 | 3 | 170136
MIL12F2 | TRUE | N |  | Y | U | 6.7 | 329 | 292 | 271 | 29053.6644 | 18158.5402 | 10895.1241 | 3 | 220136
INT12F1 | TRUE | N |  | Y | U | 10.9 | 470 | 475 | 418 | 47266.4092 | 29541.5057 | 17724.9034 | 4 | 220136
INT12F2 | TRUE | N |  | Y | U | 10.7 | 364 | 468 | 409 | 46399.1356 | 28999.4598 | 17399.6759 | 4 | 170136
H&W12F1 | TRUE | N | Y | Y | U | 10.6 | 459 | 463 | 466 | 45965.4989 | 28728.4368 | 17237.0621 | 5 | 220136
WAK12F1 | TRUE | N |  | Y | U | 10.4 |  | 457 |  | 45098.2253 | 28186.3908 | 16911.8345 | 5 | 220136
PDL1201 | TRUE | N |  | Y | U | 10.2 |  | 447 |  | 44230.9517 | 27644.3448 | 16586.6069 | 6 | 220136
WAK12F3 | TRUE | N |  | Y | U | 10.2 |  | 448 |  | 44230.9517 | 27644.3448 | 16586.6069 | 6 | 170136
L&R512 | TRUE | N |  | Y | U | 9.6 | 422 | 422 | 411 | 41629.131 | 26018.2069 | 15610.9241 | 7 | 220136
MEA12F2 | TRUE | N |  | Y | U | 10 | 462 | 436 | 391 | 43363.6782 | 27102.2989 | 16261.3793 | 7 | 170136
OPT12F1 | TRUE | N |  | Y | U | 9.2 |  | 401 |  | 39894.5839 | 24934.1149 | 14960.469 | 8 | 220136
SUN12F4 | TRUE | N |  | Y | U | 9.4 |  | 410 |  | 40761.8575 | 25476.1609 | 15285.6966 | 8 | 170136
COB12F1 | TRUE | N |  | Y | U | 9.1 |  | 399 |  | 39460.9471 | 24663.092 | 14797.8552 | 9 | 220136
OTH502 | TRUE | N |  | Y | U | 9.2 |  | 403 |  | 39894.5839 | 24934.1149 | 14960.469 | 9 | 220136
LIB12F4 | TRUE | N |  | Y | U | 9.1 |  | 400 |  | 39460.9471 | 24663.092 | 14797.8552 | 10 | 170136
OPT12F2 | TRUE | N |  | Y | U | 9 |  | 392 |  | 39027.3103 | 24392.069 | 14635.2414 | 10 | 170136
AIR12F1 | TRUE | N |  | Y | U | 8.7 |  | 382 |  | 37726.4 | 23579 | 14147.4 | 11 | 220136
AIR12F2 | TRUE | N |  | Y | U | 8.8 |  | 384 |  | 38160.0368 | 23850.023 | 14310.0138 | 11 | 170136
DEP12F1 | TRUE | N |  | Y | U | 8.6 | 462 | 377 | 376 | 37292.7632 | 23307.977 | 13984.7862 | 12 | 220136
SIP12F3 | TRUE | N |  | Y | U | 8.6 |  | 377 |  | 37292.7632 | 23307.977 | 13984.7862 | 12 | 220136
SIP12F5 | TRUE | N |  | Y | U | 8.6 |  | 377 |  | 37292.7632 | 23307.977 | 13984.7862 | 13 | 170136
SLK12F1 | TRUE | N |  | Y | U | 8.6 | 328 | 378 | 281 | 37292.7632 | 23307.977 | 13984.7862 | 13 | 220136
COB12F2 | TRUE | N |  | Y | U | 8.2 |  | 357 |  | 35558.2161 | 22223.8851 | 13334.331 | 14 | 170136
MEA12F1 | TRUE | N |  | Y | U | 8.3 | 390 | 365 | 370 | 35991.8529 | 22494.908 | 13496.9448 | 14 | 220136
OTH505 | TRUE | N |  | Y | U | 8.2 |  | 359 |  | 35558.2161 | 22223.8851 | 13334.331 | 15 | 170136
SUN12F2 | TRUE | N |  | Y | U | 7.9 |  | 344 |  | 34257.3057 | 21410.8161 | 12846.4897 | 15 | 220136
BEA12F6 | TRUE | N |  | Y | U | 7.7 |  | 335 |  | 33390.0322 | 20868.7701 | 12521.2621 | 16 | 170136
BKR12F1 | TRUE | N |  | Y | U | 7.7 | 364 | 335 | 281 | 33390.0322 | 20868.7701 | 12521.2621 | 16 | 220136
CLV12F4 | TRUE | N |  | Y | U | 7.7 |  | 337 |  | 33390.0322 | 20868.7701 | 12521.2621 | 17 | 220136
LIB12F3 | TRUE | N |  | Y | U | 7.5 |  | 330 |  | 32522.7586 | 20326.7241 | 12196.0345 | 17 | 170136
LIB12F1 | TRUE | N |  | Y | U | 7.4 |  | 324 |  | 32089.1218 | 20055.7011 | 12033.4207 | 18 | 220136
WAK12F4 | TRUE | N |  | Y | U | 7.3 |  | 318 |  | 31655.4851 | 19784.6782 | 11870.8069 | 18 | 170136
BKR12F2 | TRUE | N |  | Y | U | 7.2 | 364 | 317 | 252 | 31221.8483 | 19513.6552 | 11708.1931 | 19 | 170136
KET12F1 | TRUE | N | ? | Y | U | 7.2 |  | 316 |  | 31221.8483 | 19513.6552 | 11708.1931 | 19 | 220136
CHE12F3 | TRUE | N |  | Y | U | 7 |  | 307 |  | 30354.5747 | 18971.6092 | 11382.9655 | 20 | 220136
MIL12F4 | TRUE | N |  | Y | U | 6.8 | 318 | 296 | 356 | 29487.3011 | 18429.5632 | 11057.7379 | 20 | 170136
PDL1203 | TRUE | N |  | Y | U | 6.9 |  | 304 |  | 29920.9379 | 18700.5862 | 11220.3517 | 21 | 170136
|  |  |  | SUM |  | 339.7 |  |  | Annual Benefits | 1770755.3614 |  |  | Total Capital Cost | 7685304
*Note the beenfits must be cashflowed with Grid Mod Schedule

## Grid Mod AMI Augmentation
FeederName | > 6.7 MVA | DMS | SPEC | FUTURE IVVC | MVA | AmpsA | AmpsB | AmpsC | CVRf | $CVR | VDROP: | %VDROP
3HT12F1 | TRUE | Y |  | N | 8.1 | 376 | 356 | 365 | 0.81 | 37726.4 | 2 | 0.016667
3HT12F2 | FALSE | Y |  | N | 6.2 | 271 | 270 | 285 | 0.87 | 26885.4805 | 2 | 0.016667
3HT12F3 | FALSE | Y |  | N | 5.3 | 247 | 230 | 218 | 0.87 | 22982.7494 | 2 | 0.016667
3HT12F4 | TRUE | Y |  | N | 8.3 | 401 | 361 | 374 | 0.87 | 35991.8529 | 2 | 0.016667
3HT12F5 | TRUE | Y |  | N | 7.8 | 378 | 343 | 342 | 0.87 | 33823.669 | 2 | 0.016667
3HT12F6 | FALSE | Y |  | N | 5.9 | 245 | 259 | 236 | 0.87 | 25584.5701 | 2 | 0.016667
3HT12F7 | FALSE | Y |  | N | 4 | 183 | 175 | 176 | 0.87 | 17345.4713 | 2 | 0.016667
3HT12F8 | TRUE | Y |  | N | 8.7 | 367 | 380 | 373 | 0.87 | 37726.4 | 2 | 0.016667
9CE12F1 | TRUE | Y |  | N | 8.7 | 348 | 381 | 351 | 0.87 | 37726.4 | 2 | 0.016667
9CE12F2 | TRUE | Y |  | N | 7.7 |  | 336 |  | 0.87 | 33390.0322 | 2 | 0.016667
9CE12F3 | TRUE | Y |  | N | 7.6 |  | 332 |  | 0.87 | 32956.3954 | 2 | 0.016667
9CE12F4 | TRUE | Y |  | N | 8.1 | 374 | 355 | 315 | 0.75 | 40744.512 | 2 | 0.016667
BEA12F2 | TRUE | Y |  | N | 10.3 | 323 | 449 | 343 | 0.87 | 44664.5885 | 2 | 0.016667
BEA12F3 | TRUE | Y |  | N | 7.4 | 335 | 322 | 344 | 1.25 | 22334.0288 | 2 | 0.016667
BEA12F4 | TRUE | Y |  | N | 7.8 | 340 | 343 | 341 | 1.06 | 27760.9358 | 2 | 0.016667
BEA12F5 | TRUE | Y |  | N | 8.9 | 306 | 391 | 326 | 0.73 | 45995.2 | 2 | 0.016667
C&W12F1 | TRUE | Y |  | N | 7.2 | 209 | 315 | 287 | 0.87 | 31221.8483 | 2 | 0.016667
C&W12F2 | FALSE | Y |  | N | 6 | 301 | 264 | 252 | 0.87 | 26018.2069 | 2 | 0.016667
C&W12F3 | TRUE | Y |  | N | 7.4 | 349 | 324 | 339 | 0.87 | 32089.1218 | 2 | 0.016667
C&W12F4 | TRUE | Y |  | N | 8.3 | 361 | 363 | 348 | 0.87 | 35991.8529 | 2 | 0.016667
C&W12F5 | FALSE | Y |  | N | 4.3 | 243 | 187 | 267 | 0.87 | 18646.3816 | 2 | 0.016667
C&W12F6 | FALSE | Y |  | N | 6.4 | 297 | 280 | 345 | 0.87 | 27752.754 | 2 | 0.016667
F&C12F1 | TRUE | Y |  | N | 7.7 | 324 | 336 | 413 | 0.87 | 33390.0322 | 2 | 0.016667
F&C12F2 | TRUE | Y |  | N | 10.3 | 362 | 451 | 325 | 0.87 | 44664.5885 | 2 | 0.016667
F&C12F3 | TRUE | Y |  | N | 6.7 | 297 | 295 | 283 | 0.87 | 29053.6644 | 2 | 0.016667
F&C12F4 | TRUE | Y |  | N | 7.5 | 356 | 327 | 326 | 0.86 | 32900.9302 | 2 | 0.016667
F&C12F5 | FALSE | Y |  | N | 5.1 | 284 | 225 | 266 | 1.62 | 11876.8296 | 2 | 0.016667
F&C12F6 | FALSE | Y |  | N | 6.3 | 340 | 274 | 294 | 1.88 | 12642.3574 | 2 | 0.016667
FWT12F1 | FALSE | Y |  | N | 5.4 | 215 | 236 | 303 | 0.87 | 23416.3862 | 2 | 0.016667
FWT12F2 | FALSE | Y |  | N | 5.5 | 230 | 240 | 274 | 0.87 | 23850.023 | 2 | 0.016667
FWT12F3 | FALSE | Y |  | N | 5.1 | 204 | 224 | 293 | 0.87 | 22115.4759 | 2 | 0.016667
FWT12F4 | FALSE | Y |  | N | 5.8 | 268 | 254 | 295 | 0.87 | 25150.9333 | 2 | 0.016667
GLN12F1 | TRUE | Y |  | N | 8.4 | 342 | 369 | 407 | 0.73 | 43411.2 | 2 | 0.016667
GLN12F2 | TRUE | Y |  | N | 7.5 | 405 | 326 | 345 | 0.87 | 32522.7586 | 2 | 0.016667
L&S12F1 | TRUE | Y |  | N | 6.9 | 277 | 300 | 280 | 0.62 | 41985.8323 | 2 | 0.016667
L&S12F2 | TRUE | Y |  | N | 9.2 | 435 | 401 | 360 | 0.71 | 48884.9127 | 2 | 0.016667
L&S12F3 | TRUE | Y |  | N | 8.1 | 308 | 355 | 316 | 0.87 | 35124.5793 | 2 | 0.016667
L&S12F4 | TRUE | Y |  | N | 8.3 | 286 | 365 | 317 | 0.87 | 35991.8529 | 2 | 0.016667
L&S12F5 | FALSE | Y |  | N | 4.3 | 192 | 186 | 165 | 0.87 | 18646.3816 | 2 | 0.016667
NE12F1 | TRUE | Y |  | N | 7.3 | 263 | 319 | 280 | 0.87 | 31655.4851 | 2 | 0.016667
NE12F2 | FALSE | Y |  | N | 5.8 | 358 | 252 | 273 | 0.87 | 25150.9333 | 2 | 0.016667
NE12F3 | FALSE | Y |  | N | 4.6 | 144 | 201 | 250 | 0.87 | 19947.292 | 2 | 0.016667
NE12F4 | TRUE | Y |  | N | 7.2 | 332 | 315 | 313 | 0.87 | 31221.8483 | 2 | 0.016667
NE12F5 | FALSE | Y |  | N | 3 | 83 | 133 | 93 | 1.89 | 5988.3175 | 2 | 0.016667
NW12F1 | TRUE | Y |  | N | 7.2 |  | 317 |  | 0.87 | 31221.8483 | 2 | 0.016667
NW12F2 | FALSE | Y |  | N | 5 | 243 | 217 | 220 | 0.87 | 21681.8391 | 2 | 0.016667
NW12F3 | TRUE | Y |  | N | 8.2 |  | 360 |  | 0.87 | 35558.2161 | 2 | 0.016667
NW12F4 | TRUE | Y |  | N | 6.7 | 330 | 293 | 338 | 0.87 | 29053.6644 | 2 | 0.016667
PST12F1 | FALSE | Y |  | N | 5.7 | 284 | 251 | 259 | 0.87 | 24717.2966 | 2 | 0.016667
ROS12F1 | TRUE | Y |  | N | 9.7 | 497 | 423 | 395 | 0.87 | 42062.7678 | 2 | 0.016667
ROS12F2 | TRUE | Y |  | N | 9 | 386 | 394 | 360 | 0.87 | 39027.3103 | 2 | 0.016667
ROS12F3 | TRUE | Y |  | N | 7 | 295 | 307 | 330 | 0.87 | 30354.5747 | 2 | 0.016667
ROS12F4 | TRUE | Y |  | N | 8.9 | 286 | 390 | 449 | 0.87 | 38593.6736 | 2 | 0.016667
ROS12F5 | FALSE | Y |  | N | 6.2 | 283 | 273 | 337 | 0.87 | 26885.4805 | 2 | 0.016667
ROS12F6 | TRUE | Y |  | N | 7.1 | 311 | 312 | 333 | 0.87 | 30788.2115 | 2 | 0.016667
SE12F1 | TRUE | Y |  | N | 7.1 | 269 | 310 | 263 | 0.87 | 30788.2115 | 2 | 0.016667
SE12F2 | TRUE | Y |  | N | 8.7 | 453 | 382 | 508 | 0.87 | 37726.4 | 2 | 0.016667
SE12F3 | TRUE | Y |  | N | 8.7 | 322 | 379 | 270 | 0.87 | 37726.4 | 2 | 0.016667
SE12F4 | TRUE | Y |  | N | 9.3 | 364 | 406 | 428 | 0.87 | 40328.2207 | 2 | 0.016667
SE12F5 | FALSE | Y |  | N | 5.9 | 291 | 257 | 236 | 0.87 | 25584.5701 | 2 | 0.016667
SPU121 | FALSE | Y |  | N | 6.4 | 375 | 280 | 239 | 0.87 | 27752.754 | 2 | 0.016667
SPU122 | FALSE | Y |  | N | 5.7 | 249 | 249 | 252 | 0.87 | 24717.2966 | 2 | 0.016667
SPU123 | FALSE | Y |  | N | 5.8 | 333 | 253 | 276 | 0.87 | 25150.9333 | 2 | 0.016667
SPU124 | FALSE | Y |  | N | 5.5 | 246 | 241 | 238 | 0.87 | 23850.023 | 2 | 0.016667
SPU125 | TRUE | Y |  | N | 6.9 | 304 | 300 | 293 | 1.17 | 22248.9026 | 2 | 0.016667
SUN12F1 | TRUE | Y |  | N | 7.6 | 361 | 333 | 387 | 0.87 | 32956.3954 | 2 | 0.016667
SUN12F3 | TRUE | Y |  | N | 7.8 | 326 | 343 | 289 | 0.87 | 33823.669 | 2 | 0.016667
SUN12F6 | FALSE | Y |  | N | 5.5 | 314 | 241 | 166 | 0.87 | 23850.023 | 2 | 0.016667
TUR111 | FALSE | Y |  | N | 4.3 | 206 | 190 | 213 | 0.87 | 18646.3816 | 2 | 0.016667
TUR113 | TRUE | Y |  | N | 7.1 | 280 | 311 | 218 | 1.44 | 18601.2111 | 2 | 0.016667
TUR115 | FALSE | Y |  | N | 5.5 | 255 | 242 | 241 | 0.87 | 23850.023 | 2 | 0.016667
TUR116 | FALSE | Y |  | N | 5.9 | 314 | 260 | 272 | 0.87 | 25584.5701 | 2 | 0.016667
TUR117 | TRUE | Y |  | N | 9.2 | 365 | 401 | 371 | 1.7 | 20416.64 | 2 | 0.016667
TVW131 | FALSE | Y |  | N | 6.2 | 284 | 273 | 272 | 1.07 | 21860.157 | 2 | 0.016667
TVW132 | FALSE | Y |  | N | 5.1 | 210 | 221 | 194 | 0.87 | 22115.4759 | 2 | 0.016667
[9 empty] | Annual Benefit | 2212474.6061
[9 empty] | Total Benefits | 45908848.0769

## X&R Savings
FeederName | > 6.7 MVA | DMS | SPEC | FUTURE IVVC | MVA | AmpsA | AmpsB | AmpsC | CVRf | VDROP | VDROP% | $CVR
AIR12F3 | FALSE | N |  | N | 6.3 |  | 276 |  | 0.87 | 1.25 | 0.010417 | 17074.4483
ARD12F1 | FALSE | N |  | N | 3.9 | 162 | 172 | 190 | 0.87 | 1.25 | 0.010417 | 10569.8966
ARD12F2 | FALSE | N |  | N | 3.9 | 156 | 171 | 171 | 0.87 | 1.25 | 0.010417 | 10569.8966
BKR12F3 | FALSE | N |  | N | 6.4 | 353 | 282 | 285 | 0.87 | 1.25 | 0.010417 | 17345.4713
CFD1210 | FALSE | N |  | N | 5.2 | 417 | 227 | 319 | 0.87 | 1.25 | 0.010417 | 14093.1954
CFD1211 | FALSE | N |  | N | 5.3 | 221 | 234 | 208 | 0.87 | 1.25 | 0.010417 | 14364.2184
CHE12F1 | FALSE | N |  | N | 6.2 |  | 270 |  | 0.87 | 1.25 | 0.010417 | 16803.4253
CHE12F2 | FALSE | N |  | N | 5.9 |  | 260 |  | 0.87 | 1.25 | 0.010417 | 15990.3563
CHE12F4 | FALSE | N |  | N | 6.6 |  | 289 |  | 0.87 | 1.25 | 0.010417 | 17887.5172
CHW12F1 | FALSE | N |  | N | 6 | 220 | 264 | 232 | 0.87 | 1.25 | 0.010417 | 16261.3793
CHW12F2 | FALSE | N |  | N | 2.8 | 204 | 122 | 234 | 0.87 | 1.25 | 0.010417 | 7588.6437
CHW12F3 | FALSE | N |  | N | 3.1 | 129 | 134 | 147 | 0.87 | 1.25 | 0.010417 | 8401.7126
CHW12F4 | FALSE | N |  | N | 2.6 | 139 | 115 | 108 | 0.87 | 1.25 | 0.010417 | 7046.5977
CLV12F1 | FALSE | N |  | N | 3.8 |  | 166 |  | 0.87 | 1.25 | 0.010417 | 10298.8736
CLV12F2 | FALSE | N |  | N | 5.3 |  | 230 |  | 0.87 | 1.25 | 0.010417 | 14364.2184
CLV12F3 | FALSE | N |  | N | 6.4 |  | 281 |  | 0.87 | 1.25 | 0.010417 | 17345.4713
CLV34F1 | FALSE | N |  | N | 2.3 |  | 100 |  | 0.87 | 1.25 | 0.010417 | 6233.5287
DEP12F2 | FALSE | N |  | N | 4.6 | 194 | 202 | 181 | 0.87 | 1.25 | 0.010417 | 12467.0575
DIA231 | FALSE | N |  | N | 1.1 | 50 | 50 | 49 | 0.87 | 1.25 | 0.010417 | 2981.2529
DIA232 | FALSE | N |  | N | 0.9 | 47 | 41 | 48 | 0.87 | 1.25 | 0.010417 | 2439.2069
DRY1208 | FALSE | N |  | N | 5.1 | 248 | 222 | 217 | 0.87 | 1.25 | 0.010417 | 13822.1724
DRY1209 | FALSE | N |  | N | 4.2 | 196 | 182 | 171 | 0.87 | 1.25 | 0.010417 | 11382.9655
DVP12F1 | FALSE | N |  | N | 4 | 206 | 174 | 169 | 0.87 | 1.25 | 0.010417 | 10840.9195
DVP12F2 | FALSE | N |  | N | 2.2 | 71 | 98 | 103 | 0.87 | 1.25 | 0.010417 | 5962.5057
ECL221 | FALSE | N |  | N | 2.2 | 155 | 98 | 48 | 0.87 | 1.25 | 0.010417 | 5962.5057
ECL222 | FALSE | N |  | N | 6.5 | 240 | 283 | 224 | 0.87 | 1.25 | 0.010417 | 17616.4943
EFM12F1 | FALSE | N |  | N | 6.5 | 264 | 284 | 322 | 0.87 | 1.25 | 0.010417 | 17616.4943
EFM12F2 | FALSE | N |  | N | 6.1 | 312 | 266 | 284 | 0.87 | 1.25 | 0.010417 | 16532.4023
EWN241 | FALSE | N |  | N | 1.5 | 70 | 66 | 70 | 0.87 | 1.25 | 0.010417 | 4065.3448
FOR12F1 | FALSE | N |  | N | 2.1 | 63 | 94 | 83 | 0.87 | 1.25 | 0.010417 | 5691.4828
FOR2kV | FALSE | N |  | N | 0.4 | 17 | 17 | 14 | 0.87 | 1.25 | 0.010417 | 1084.092
GAR461 | FALSE | N |  | N | 4 | 113 | 175 | 170 | 0.87 | 1.25 | 0.010417 | 10840.9195
GIF34F1 | FALSE | N |  | N | 2.2 |  | 97 |  | 0.87 | 1.25 | 0.010417 | 5962.5057
GIF34F2 | FALSE | N |  | N | 1.1 |  | 47 |  | 0.87 | 1.25 | 0.010417 | 2981.2529
GRN12F1 | FALSE | N |  | N | 6.4 | 300 | 280 | 430 | 0.87 | 1.25 | 0.010417 | 17345.4713
GRN12F2 | FALSE | N |  | N | 1.8 | 100 | 80 | 90 | 0.87 | 1.25 | 0.010417 | 4878.4138
GRN12F3 | FALSE | N |  | N | 1.5 | 67 | 67 | 70 | 0.87 | 1.25 | 0.010417 | 4065.3448
H&W12F2 | FALSE | N |  | N | 4.1 | 220 | 180 | 164 | 0.87 | 1.25 | 0.010417 | 11111.9425
HAR4F1 | FALSE | N |  | N | 0 | 1 | 1 | 1 | 0.87 | 1.25 | 0.010417 | 0
HAR4F2 | FALSE | N |  | N | 0 | 1 | 1 | 1 | 0.87 | 1.25 | 0.010417 | 0
KET12F2 | FALSE | N |  | N | 0.9 |  | 41 |  | 0.87 | 1.25 | 0.010417 | 2439.2069
L&R511 | FALSE | N |  | N | 3.1 | 112 | 136 | 121 | 0.87 | 1.25 | 0.010417 | 8401.7126
LAT421 | FALSE | N |  | N | 3.9 | 143 | 172 | 141 | 0.87 | 1.25 | 0.010417 | 10569.8966
LAT422 | FALSE | N |  | N | 1.9 | 29 | 85 | 59 | 0.87 | 1.25 | 0.010417 | 5149.4368
LEO612 | FALSE | N |  | N | 2 | 96 | 87 | 130 | 0.87 | 1.25 | 0.010417 | 5420.4598
LF34F1 | FALSE | N |  | N | 2 | 88 | 86 | 98 | 0.87 | 1.25 | 0.010417 | 5420.4598
LIN711 | FALSE | N |  | N | 1.5 | 70 | 67 | 87 | 0.87 | 1.25 | 0.010417 | 4065.3448
LL12F1 | FALSE | N |  | N | 2.7 | 89 | 120 | 51 | 0.87 | 1.25 | 0.010417 | 7317.6207
LOO12F1 | FALSE | N |  | N | 4.4 | 118 | 191 | 128 | 0.87 | 1.25 | 0.010417 | 11925.0115
LOO12F2 | FALSE | N |  | N | 2.1 | 109 | 94 | 97 | 0.87 | 1.25 | 0.010417 | 5691.4828
MIL12F1 | FALSE | N |  | N | 5.8 | 290 | 254 | 218 | 0.87 | 1.25 | 0.010417 | 15719.3333
MIL12F3 | FALSE | N |  | N | 5.9 | 300 | 260 | 259 | 0.87 | 1.25 | 0.010417 | 15990.3563
MLN12F1 | FALSE | N |  | N | 3.8 | 226 | 167 | 275 | 0.87 | 1.25 | 0.010417 | 10298.8736
MLN12F2 | FALSE | N |  | N | 4.8 | 151 | 210 | 158 | 0.87 | 1.25 | 0.010417 | 13009.1034
ODS12F1 | FALSE | N |  | N | 2.9 | 124 | 126 | 129 | 0.87 | 1.25 | 0.010417 | 7859.6667
ORI12F1 | FALSE | N |  | N | 3 | 104 | 130 | 165 | 0.87 | 1.25 | 0.010417 | 8130.6897
ORI12F2 | FALSE | N |  | N | 0.8 | 65 | 33 | 36 | 0.87 | 1.25 | 0.010417 | 2168.1839
ORI12F3 | FALSE | N |  | N | 5.9 | 205 | 258 | 206 | 0.87 | 1.25 | 0.010417 | 15990.3563
OTH501 | FALSE | N |  | N | 5.4 |  | 238 |  | 0.87 | 1.25 | 0.010417 | 14635.2414
OTH503 | FALSE | N |  | N | 2.8 |  | 121 |  | 0.87 | 1.25 | 0.010417 | 7588.6437
PAL311 | FALSE | N |  | N | 3.3 | 120 | 143 | 96 | 0.87 | 1.25 | 0.010417 | 8943.7586
PAL312 | FALSE | N |  | N | 1.9 | 130 | 83 | 67 | 0.87 | 1.25 | 0.010417 | 5149.4368
PDL1202 | FALSE | N |  | N | 6.4 |  | 278 |  | 0.87 | 1.25 | 0.010417 | 17345.4713
PDL1204 | FALSE | N |  | N | 3.5 |  | 154 |  | 0.87 | 1.25 | 0.010417 | 9485.8046
PST12F2 | FALSE | N |  | N | 0 | 1 | 1 | 1 | 0.87 | 1.25 | 0.010417 | 0
RDN12F1 | FALSE | N |  | N | 3.1 | 81 | 136 | 178 | 0.87 | 1.25 | 0.010417 | 8401.7126
RDN12F2 | FALSE | N |  | N | 1.8 | 100 | 78 | 70 | 0.87 | 1.25 | 0.010417 | 4878.4138
RIT731 | FALSE | N |  | N | 2.3 | 104 | 100 | 115 | 0.87 | 1.25 | 0.010417 | 6233.5287
RIT732 | FALSE | N |  | N | 2 | 71 | 88 | 118 | 0.87 | 1.25 | 0.010417 | 5420.4598
ROK451 | FALSE | N |  | N | 1.9 | 105 | 84 | 72 | 0.87 | 1.25 | 0.010417 | 5149.4368
ROX751 | FALSE | N |  | N | 5.7 | 250 | 250 | 250 | 0.87 | 1.25 | 0.010417 | 15448.3103
RSA431 | FALSE | N |  | N | 1.8 | 108 | 79 | 139 | 0.87 | 1.25 | 0.010417 | 4878.4138
SIP12F1 | FALSE | N |  | N | 4.9 | 232 | 216 | 215 | 0.87 | 1.25 | 0.010417 | 13280.1264
SIP12F2 | FALSE | N |  | N | 5.9 |  | 256 |  | 0.87 | 1.25 | 0.010417 | 15990.3563
SIP12F4 | FALSE | N |  | N | 6.6 |  | 289 |  | 0.87 | 1.25 | 0.010417 | 17887.5172
SLK12F2 | FALSE | N |  | N | 5.3 | 222 | 234 | 242 | 0.87 | 1.25 | 0.010417 | 14364.2184
SLK12F3 | FALSE | N |  | N | 3.6 | 145 | 156 | 155 | 0.87 | 1.25 | 0.010417 | 9756.8276
SOT521 | FALSE | N |  | N | 5.1 | 207 | 222 | 189 | 0.87 | 1.25 | 0.010417 | 13822.1724
SOT522 | FALSE | N |  | N | 4.7 | 203 | 206 | 218 | 0.87 | 1.25 | 0.010417 | 12738.0805
SOT523 | FALSE | N |  | N | 5.6 | 280 | 246 | 268 | 0.87 | 1.25 | 0.010417 | 15177.2874
SPA442 | FALSE | N |  | N | 1.9 | 67 | 83 | 64 | 0.87 | 1.25 | 0.010417 | 5149.4368
SPI12F1 | FALSE | N |  | N | 3.5 | 168 | 152 | 188 | 0.87 | 1.25 | 0.010417 | 9485.8046
SPI12F2 | FALSE | N |  | N | 1.3 | 31 | 57 | 47 | 0.87 | 1.25 | 0.010417 | 3523.2989
SPR761 | FALSE | N |  | N | 1.4 | 87 | 62 | 68 | 0.87 | 1.25 | 0.010417 | 3794.3218
SUN12F5 | FALSE | N |  | N | 5.5 |  | 239 |  | 0.87 | 1.25 | 0.010417 | 14906.2644
TKO411 | FALSE | N |  | N | 3.4 | 130 | 150 | 135 | 0.87 | 1.25 | 0.010417 | 9214.7816
TKO412 | FALSE | N |  | N | 2.2 | 110 | 95 | 95 | 0.87 | 1.25 | 0.010417 | 5962.5057
TUR112 | FALSE | N |  | N | 6.6 | 303 | 289 | 307 | 0.87 | 1.25 | 0.010417 | 17887.5172
VAL12F1 | FALSE | N |  | N | 5.7 | 205 | 251 | 171 | 0.87 | 1.25 | 0.010417 | 15448.3103
VAL12F2 | FALSE | N |  | N | 1.6 | 79 | 70 | 75 | 0.87 | 1.25 | 0.010417 | 4336.3678
VAL12F3 | FALSE | N |  | N | 4 | 165 | 177 | 144 | 0.87 | 1.25 | 0.010417 | 10840.9195
WAS781 | FALSE | N |  | N | 0 |  |  |  | 0.87 | 1.25 | 0.010417 | 0
WIL12F1 | FALSE | N |  | N | 4.5 | 154 | 198 | 189 | 0.87 | 1.25 | 0.010417 | 12196.0345
WIL12F2 | FALSE | N |  | N | 4.5 | 222 | 196 | 222 | 0.87 | 1.25 | 0.010417 | 12196.0345
|  |  |  | SUM: | 337.6 | [5 empty] | Anuual Benefit | 914973.6092

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only