## 2023 Update
Decarbonization Analysis -- 2023 Update (10-04-2023)
Overview
The 2023 update leveraged four new scenarios (Full ASHP, Full CCHP, Hybrid ASHP, and Hybrid ASHP / CCHP) as a result of the decarbonization settlement. The analysis performed leveraged what was done in 2021 for consistency and at the planner-level estimate (+/- 50%). Specifically, the analysis leveraged a $ / MW average for both the short-term and long-term impacts, with a 15% increase to account for inflation in the two years based on more recent costs.
Previous Work from 2021
The following table articulates the high-level results from the 2021 system planning cost analysis:
Scenario | 2025 MW | 2025 $M | 2040 MW | 2040 $M
Carbon Out | 37.3 | $26M | 311 | $825M
Carbon Out + Add'l Electrification | 142 | $177M | 1366 | $2,583M
High Electrification | 366 | $380M | 3053 | $5,511M
Average ($/MW) | 1.0691 |  | 1.8856
2023 Average (2021 + 15%) ($/MW) | 1.2295 |  | 2.1685
New Scenarios for 2023 (high-level cost estimation)
Scenario | Description | 2030 MW | 2030 $M | 2045 MW | 2045 $M
Scenario 1 | Full ASHP | 439.1171 | $540M | 2012.5231 | $4364M
Scenario 2 | Full CCHP | 418.9622 | $515M | 1714.4402 | $3718M
Scenario 3 | Hybrid ASHP | 100.7222 | $124M | 417.3463 | $905M
Scenario 4 | Hybrid ASHP CCHP | 106.0873 | $130M | 432.4086 | $938M
New Scenarios for 2023 (detailed estimation)
Scenario | Description | 2030 MW | 2030 $M | 2045 MW | 2045 $M |  | $/MW |  | $/MW
Scenario 1 | Full ASHP | 439.1171 | 658.3544 | 2012.5231 | 4252.1462 |  | 1.4993 |  | 2.1128
Scenario 2 | Full CCHP | 418.9622 | 636.2069 | 1714.4402 | 3621.6318 |  | 1.5185 |  | 2.1124
Scenario 3 | Hybrid ASHP | 100.7222 | 165.0747 | 417.3463 | 912.4118 |  | 1.6389 |  | 2.1862
Scenario 4 | Hybrid ASHP CCHP | 106.0873 | 169.1371 | 432.4086 | 951.4094 |  | 1.5943 |  | 2.2003
[Loads pulled from "Electric - Peaks" worksheet provided by Nathan Critchfield on 9/8]
Scenario | Description | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Scenario 1 | Full ASHP | 28.827 | 66.9055 | 114.5311 | 182.4972 | 250.6186 | 336.2056 | 439.1171 | 552.1814 | 680.7842 | 786.2058 | 897.7561 | 1021.3776 | 1147.1008 | 1256.1532 | 1385.5975 | 1455.0507 | 1565.8706 | 1669.6323 | 1742.084 | 1860.596 | 1953.7445 | 2012.5231 | 2081.6709 | 2136.9105 | 2171.5961 | 2202.7142 | 2234.8174
Scenario 2 | Full CCHP | 33.213 | 96.1778 | 143.4072 | 207.5695 | 268.5381 | 336.8579 | 418.9622 | 510.0174 | 618.8635 | 705.4322 | 795.7575 | 898.4545 | 1002.5624 | 1093.0726 | 1204.7066 | 1293.4712 | 1374.111 | 1459.0181 | 1513.4472 | 1585.6011 | 1666.4907 | 1714.4402 | 1772.5295 | 1821.1489 | 1863.6939 | 1896.1352 | 1927.7406
Scenario 3 | Hybrid ASHP | 6.4817 | 14.6085 | 24.7159 | 45.6976 | 56.0237 | 76.2338 | 100.7222 | 127.7219 | 172.4698 | 194.0195 | 212.8141 | 245.1913 | 274.5131 | 301.1431 | 355.4379 | 366.1144 | 368.4759 | 383.4877 | 390.7219 | 400.0842 | 432.6214 | 417.3463 | 428.4655 | 435.5199 | 434.9663 | 441.9542 | 451.6975
Scenario 4 | Hybrid ASHP CCHP | 7.8569 | 17.7012 | 29.0416 | 51.5111 | 63.3192 | 82.0985 | 106.0873 | 131.8459 | 171.2164 | 189.0288 | 206.3445 | 236.7675 | 264.8466 | 290.5058 | 339.2575 | 352.7469 | 358.8235 | 378.0545 | 392.2919 | 406.4808 | 443.3837 | 432.4086 | 448.048 | 462.1413 | 464.8553 | 475.0434 | 488.1507
Total Cost Per Year (Cumulative)
Scenario | Description | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Scenario 1 | Full ASHP | 43.2194 | 100.3093 | 171.7128 | 273.6123 | 375.7445 | 504.0625 | 658.3544 | 1166.6728 | 1438.3905 | 1661.1297 | 1896.8181 | 2158.011 | 2423.6445 | 2654.0551 | 2927.5506 | 3074.2942 | 3308.4394 | 3527.6715 | 3680.7506 | 3931.1481 | 4127.9562 | 4252.1462 | 4398.2447 | 4514.9573 | 4588.2426 | 4653.9902 | 4721.8192
Scenario 2 | Full CCHP | 50.4349 | 146.0489 | 217.7682 | 315.2006 | 407.7833 | 511.529 | 636.2069 | 1077.3751 | 1307.3048 | 1490.175 | 1680.9807 | 1897.9207 | 2117.8411 | 2309.0373 | 2544.8562 | 2732.3652 | 2902.711 | 3082.071 | 3197.0487 | 3349.4685 | 3520.3419 | 3621.6318 | 3744.3413 | 3847.0464 | 3936.9195 | 4005.4495 | 4072.2137
Scenario 3 | Hybrid ASHP | 10.6229 | 23.942 | 40.5072 | 74.8943 | 91.818 | 124.9404 | 165.0747 | 279.2286 | 377.0573 | 424.1699 | 465.2589 | 536.0426 | 600.1468 | 658.3658 | 777.0663 | 800.4074 | 805.5704 | 838.3894 | 854.205 | 874.6731 | 945.8066 | 912.4118 | 936.7209 | 952.1433 | 950.9331 | 966.2103 | 987.5113
Scenario 4 | Hybrid ASHP CCHP | 12.5265 | 28.2214 | 46.3016 | 82.1252 | 100.9511 | 130.8912 | 169.1371 | 290.0947 | 376.7199 | 415.9117 | 454.0105 | 520.9489 | 582.7302 | 639.187 | 746.4531 | 776.1333 | 789.5034 | 831.8165 | 863.1424 | 894.3616 | 975.5573 | 951.4094 | 985.8201 | 1016.829 | 1022.8003 | 1045.2167 | 1074.0561
Total Cost Per Year (Incremental)
Scenario | Description | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Scenario 1 | Full ASHP | 43.2194 | 57.0899 | 71.4035 | 101.8995 | 102.1322 | 128.3179 | 154.2919 | 508.3184 | 271.7177 | 222.7392 | 235.6884 | 261.1929 | 265.6335 | 230.4106 | 273.4955 | 146.7437 | 234.1452 | 219.2321 | 153.0791 | 250.3975 | 196.8081 | 124.19 | 146.0984 | 116.7127 | 73.2852 | 65.7477 | 67.829
Scenario 2 | Full CCHP | 50.4349 | 95.614 | 71.7193 | 97.4324 | 92.5826 | 103.7457 | 124.6779 | 441.1682 | 229.9297 | 182.8702 | 190.8057 | 216.94 | 219.9204 | 191.1963 | 235.8188 | 187.509 | 170.3458 | 179.3601 | 114.9777 | 152.4198 | 170.8735 | 101.2899 | 122.7095 | 102.7051 | 89.8731 | 68.53 | 66.7642
Scenario 3 | Hybrid ASHP | 10.6229 | 13.3191 | 16.5651 | 34.3871 | 16.9237 | 33.1225 | 40.1343 | 114.1538 | 97.8287 | 47.1126 | 41.089 | 70.7837 | 64.1041 | 58.219 | 118.7005 | 23.3411 | 5.1629 | 32.819 | 15.8155 | 20.4681 | 71.1335 | -33.3948 | 24.3091 | 15.4224 | -1.2103 | 15.2772 | 21.3011
Scenario 4 | Hybrid ASHP CCHP | 12.5265 | 15.695 | 18.0801 | 35.8236 | 18.8259 | 29.9401 | 38.2459 | 120.9576 | 86.6251 | 39.1918 | 38.0989 | 66.9384 | 61.7812 | 56.4568 | 107.2661 | 29.6802 | 13.3701 | 42.3131 | 31.3259 | 31.2192 | 81.1957 | -24.1478 | 34.4107 | 31.0089 | 5.9713 | 22.4164 | 28.8394

## Electric - Peaks
F22 Final Electric Load Forecast - IRP Scenario
Peaks (MW) |  |  | Different values of conservation are provided to illustrate the impact of conservation. Click (+) to expand
Losses were assumed at 7.8% |  |  |  | Scenario 1 - Full Electrification w ASHP |  |  |  | Scenario 2 - Full Electrification w CCHP |  |  |  | Scenario 3 - Hybrid Heat Pump |  |  |  | Scenario 4 - HHP for existing customeres, CCHP for new customers |  |  |  | 2023 EPR Reference |  |  |  | NET Impact
|  |  | IRP Scenario - No New DSR after 2023 | Before DSR |  |  | After DSR | Before DSR |  |  | After DSR | Before DSR |  |  | After DSR | Before DSR |  |  | After DSR | Before DSR |  |  | After DSR | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4
Year | Month | Date | Normal Peak (27/28 & 94/95/96) Degrees) | Change in Peak Load | DSR | Demand Response | Total Load | Change in Peak Load | DSR | Demand Response | Total Load | Change in Peak Load | DSR | Demand Response | Total Load | Change in Peak Load | DSR | Demand Response | Total Load | Change in Peak Load | DSR | Demand Response | Total Load | Peak Delta | Peak Delta | Peak Delta | Peak Delta
2022 | DECEMBER | 2022-12-01 | 4608 | 0 | 0 | 0 | 4608 | 0 | 0 | 0 | 4608 | 0 | 0 | 0 | 4608 | 0 | 0 | 0 | 4608 | 0 | 0 | 0 | 4608 | 0 | 0 | 0 | 0
2023 |  | 2023-12-01 | 4627 | 0 | 0 | 0 | 4627 | 0 | 0 | 0 | 4627 | 0 | 0 | 0 | 4627 | 0 | 0 | 0 | 4627 | 0 | 0 | 0 | 4627 | 0 | 0 | 0 | 0
2024 |  | 2024-12-01 | 4753 | 29.386 | 27.6849 | 45.9961 | 4708.7049 | 23.7114 | 26.6526 | 49.3268 | 4700.732 | 7.0541 | 27.5003 | 50.3304 | 4682.2233 | 8.1875 | 27.5017 | 50.4035 | 4683.2823 | 0 | 26.0775 | 49.7 | 4677.2225 | 31.4825 | 23.5095 | 5.0008 | 6.0598
2025 |  | 2025-12-01 | 4803 | 70.3481 | 53.9306 | 92.768 | 4726.6495 | 79.4269 | 51.8334 | 94.7496 | 4735.8438 | 16.2817 | 53.4527 | 95.7658 | 4670.0631 | 18.9996 | 53.4584 | 96.5122 | 4672.0289 | 0 | 50.5433 | 94.55 | 4657.9067 | 68.7428 | 77.9371 | 12.1565 | 14.1222
2026 |  | 2026-12-01 | 4878 | 124.1607 | 92.4958 | 147.2964 | 4762.3685 | 122.7138 | 89.2755 | 146.5546 | 4764.8837 | 27.7882 | 91.5476 | 145.667 | 4668.5736 | 31.928 | 91.56 | 147.8379 | 4670.5301 | 0 | 86.9203 | 143.81 | 4647.2697 | 115.0988 | 117.614 | 21.3039 | 23.2604
2027 |  | 2027-12-01 | 4951 | 194.3154 | 122.6751 | 193.7698 | 4828.8706 | 179.1194 | 118.1651 | 185.138 | 4826.8162 | 43.2018 | 120.9671 | 180.3614 | 4692.8733 | 49.6249 | 120.9952 | 185.0835 | 4694.5462 | 0 | 114.5081 | 177.8 | 4658.6919 | 170.1787 | 168.1243 | 34.1814 | 35.8542
2028 |  | 2028-12-01 | 5021 | 283.2998 | 153.3603 | 241.0435 | 4909.8961 | 250.6359 | 147.2573 | 227.4119 | 4896.9667 | 62.6188 | 150.4741 | 216.511 | 4716.6337 | 71.9326 | 150.5289 | 224.7864 | 4717.6173 | 0 | 142.1022 | 213.2 | 4665.6978 | 244.1982 | 231.2689 | 50.9359 | 51.9195
2029 |  | 2029-12-01 | 5104 | 383.6575 | 209.0446 | 264.6038 | 5014.0092 | 331.6961 | 200.9362 | 247.7041 | 4987.0558 | 83.7212 | 204.4805 | 228.0233 | 4755.2174 | 94.3287 | 204.5501 | 241.3927 | 4752.3859 | 0 | 194.0164 | 224.56 | 4685.4236 | 328.5855 | 301.6321 | 69.7937 | 66.9623
2030 |  | 2030-12-01 | 5197 | 506.7163 | 246.3277 | 291.965 | 5165.4237 | 430.7683 | 235.3719 | 271.356 | 5121.0404 | 110.4731 | 239.1021 | 240.1441 | 4828.2269 | 124.44 | 239.2221 | 258.74 | 4823.4779 | 0 | 225.9313 | 236.61 | 4734.4587 | 430.965 | 386.5817 | 93.7682 | 89.0192
2031 |  | 2031-12-01 | 5296 | 645.0223 | 285.9873 | 322.4474 | 5332.5877 | 542.1233 | 271.1902 | 297.5397 | 5269.3934 | 140.5455 | 274.9808 | 251.9785 | 4909.5861 | 158.267 | 275.1694 | 277.157 | 4901.9405 | 0 | 258.4442 | 248.37 | 4789.1858 | 543.4019 | 480.2076 | 120.4003 | 112.7548
2032 |  | 2032-12-01 | 5388 | 785.1589 | 364.5081 | 355.3131 | 5453.3377 | 655.5127 | 344.7961 | 325.5931 | 5373.1235 | 169.0195 | 348.4381 | 263.0508 | 4945.5305 | 187.0835 | 348.6311 | 295.861 | 4930.5914 | 0 | 327.363 | 259.42 | 4801.217 | 652.1207 | 571.9064 | 144.3135 | 129.3744
2033 |  | 2033-12-01 | 5485 | 930.614 | 410.231 | 389.371 | 5616.012 | 773.4705 | 384.8085 | 354.4365 | 5519.2256 | 203.0333 | 388.3423 | 272.0765 | 5027.6145 | 224.1842 | 388.6106 | 314.2209 | 5006.3527 | 0 | 362.6798 | 268.51 | 4853.8102 | 762.2018 | 665.4154 | 173.8043 | 152.5426
2034 |  | 2034-12-01 | 5588 | 1088.3308 | 445.9334 | 415.928 | 5814.4694 | 901.0208 | 414.7531 | 377.4636 | 5696.8041 | 238.48 | 417.1791 | 275.5435 | 5133.7574 | 263.0034 | 417.534 | 325.3256 | 5108.1439 | 0 | 387.9014 | 272.14 | 4927.9586 | 886.5108 | 768.8455 | 205.7988 | 180.1853
2035 |  | 2035-12-01 | 5693 | 1246.2403 | 483.418 | 443.7711 | 6012.0512 | 1028.9399 | 446.0271 | 401.2896 | 5874.6231 | 274.7724 | 447.48 | 279.3418 | 5240.9506 | 302.6404 | 447.9214 | 337.7106 | 5210.0085 | 0 | 414.4792 | 276.34 | 5002.1808 | 1009.8704 | 872.4423 | 238.7698 | 207.8276
2036 |  | 2036-12-01 | 5795 | 1409.1038 | 521.5843 | 471.3904 | 6211.129 | 1160.5322 | 477.0525 | 424.3238 | 6054.1559 | 310.7904 | 477.4231 | 282.5343 | 5345.833 | 342.1133 | 477.9591 | 349.3996 | 5309.7546 | 0 | 439.8788 | 279.97 | 5075.1512 | 1135.9778 | 979.0047 | 270.6818 | 234.6034
2037 |  | 2037-12-01 | 5902 | 1557.6672 | 564.706 | 498.4405 | 6396.5207 | 1281.1947 | 512.391 | 446.8238 | 6223.9799 | 346.068 | 511.6208 | 284.6825 | 5451.7648 | 380.4782 | 512.2523 | 360.0502 | 5410.1757 | 0 | 467.7808 | 282.69 | 5151.5292 | 1244.9915 | 1072.4507 | 300.2356 | 258.6465
2038 |  | 2038-12-01 | 5995 | 1705.1878 | 608.17 | 536.1659 | 6555.8519 | 1399.8191 | 547.5388 | 475.4596 | 6371.8208 | 376.218 | 545.5859 | 288.2721 | 5537.36 | 413.7946 | 546.3144 | 376.0838 | 5486.3963 | 0 | 496.0959 | 288.26 | 5210.6441 | 1345.2079 | 1161.1767 | 326.716 | 275.7522
2039 |  | 2039-12-01 | 6096 | 1855.4516 | 651.8942 | 554.8781 | 6744.6793 | 1520.1711 | 583.031 | 497.3901 | 6535.75 | 404.9608 | 580.0207 | 288.4639 | 5632.4762 | 445.7668 | 580.8431 | 380.2037 | 5580.7199 | 0 | 525.2472 | 288.47 | 5282.2828 | 1462.3965 | 1253.4672 | 350.1934 | 298.4371
2040 |  | 2040-12-01 | 6198 | 2001.1461 | 691.5929 | 572.5859 | 6934.9673 | 1636.4126 | 616.2523 | 511.4759 | 6706.6844 | 431.4534 | 612.5449 | 288.6879 | 5728.2206 | 475.4308 | 613.4416 | 383.5068 | 5676.4824 | 0 | 553.6705 | 288.68 | 5355.6495 | 1579.3178 | 1351.0349 | 372.5711 | 320.8329
2041 |  | 2041-12-01 | 6304 | 2135.105 | 728.5929 | 588.9117 | 7121.6004 | 1742.8209 | 646.2213 | 524.3509 | 6876.2486 | 454.4773 | 641.5554 | 288.259 | 5828.6628 | 501.4851 | 642.5329 | 385.6726 | 5777.2797 | 0 | 577.7585 | 288.25 | 5437.9915 | 1683.6089 | 1438.2571 | 390.6713 | 339.2882
2042 |  | 2042-12-01 | 6407 | 2237.3922 | 771.4512 | 604.1099 | 7268.8311 | 1824.4242 | 681.8088 | 536.3701 | 7013.2453 | 473.6015 | 676.0876 | 287.7046 | 5916.8093 | 522.9399 | 677.1301 | 386.9025 | 5865.9073 | 0 | 606.4124 | 287.71 | 5512.8776 | 1755.9535 | 1500.3677 | 403.9317 | 353.0297
2043 |  | 2043-12-01 | 6509 | 2393.6821 | 826.0293 | 618.7221 | 7457.9307 | 1946.365 | 723.0431 | 547.9441 | 7184.3778 | 491.3626 | 715.9384 | 287.0986 | 5997.3256 | 544.5783 | 717.1065 | 387.6668 | 5948.805 | 0 | 639.2172 | 287.1 | 5582.6828 | 1875.2478 | 1601.695 | 414.6428 | 366.1222
2044 |  | 2044-12-01 | 6610 | 2514.4158 | 874.867 | 632.5222 | 7617.0266 | 2040.7354 | 760.2872 | 558.8705 | 7331.5777 | 507.1366 | 751.8703 | 286.3506 | 6078.9157 | 563.4594 | 753.1393 | 387.8398 | 6032.4803 | 0 | 669.2487 | 286.35 | 5654.4013 | 1962.6253 | 1677.1763 | 424.5143 | 378.0789
2045 |  | 2045-12-01 | 6717 | 2602.8933 | 913.0692 | 643.2075 | 7763.6166 | 2108.3913 | 790.2862 | 567.308 | 7467.7971 | 520.7891 | 781.2001 | 284.9335 | 6171.6555 | 580.2327 | 782.5486 | 387.3451 | 6127.339 | 0 | 695.0737 | 284.94 | 5736.9863 | 2026.6303 | 1730.8108 | 434.6693 | 390.3527
2046 |  | 2046-12-01 | 6825 | 2692.3863 | 952.7516 | 652.5082 | 7912.1265 | 2177.6485 | 822.155 | 574.9069 | 7605.5866 | 534.3742 | 812.443 | 283.3485 | 6263.5827 | 597.2182 | 813.8706 | 386.3704 | 6221.9773 | 0 | 724.2598 | 283.35 | 5817.3902 | 2094.7363 | 1788.1964 | 446.1925 | 404.5871
2047 |  | 2047-12-01 | 6931 | 2768.7371 | 988.7821 | 657.7645 | 8053.1905 | 2236.6499 | 850.3625 | 577.4749 | 7739.8125 | 546.4159 | 839.6935 | 280.1404 | 6357.582 | 612.644 | 841.2095 | 380.9619 | 6321.4726 | 0 | 748.9581 | 280.12 | 5901.9219 | 2151.2686 | 1837.8906 | 455.6601 | 419.5507
2048 |  | 2048-12-01 | 7033 | 2832.9321 | 1030.2842 | 657.7645 | 8177.8834 | 2286.5075 | 881.1783 | 577.4749 | 7860.8542 | 556.7766 | 868.9734 | 280.1404 | 6440.6629 | 626.3941 | 870.6076 | 380.9619 | 6407.8246 | 0 | 773.5128 | 280.12 | 5979.3672 | 2198.5162 | 1881.487 | 461.2956 | 428.4574
2049 |  | 2049-12-01 | 7150 | 2880.1738 | 1068.2422 | 657.7645 | 8304.1671 | 2325.7118 | 910.2116 | 577.4749 | 7988.0253 | 567.7578 | 896.5201 | 280.1404 | 6541.0973 | 640.686 | 898.2643 | 380.9619 | 6511.4598 | 0 | 797.8926 | 280.12 | 6071.9874 | 2232.1797 | 1916.0379 | 469.1099 | 439.4724
2050 |  | 2050-12-01 | 7269 | 2923.4756 | 1101.8266 | 657.7645 | 8432.8845 | 2362.0346 | 937.7231 | 577.4749 | 8115.8366 | 579.7212 | 922.8449 | 280.1404 | 6645.7359 | 656.1154 | 924.6906 | 380.9619 | 6619.4629 | 0 | 822.3676 | 280.12 | 6166.5124 | 2266.3721 | 1949.3242 | 479.2235 | 452.9505
*DSR included is codes and standards and the applicable conservation bundles.
Formulas:
Date = DATE([Losses were assumed at 7.8%], 12, 1)

## 2023 Overall Summary
2020 Numbers
Description | Unit | $/unit | 2020-2025
|  |  | Carbon Out |  | Carbon Out + Add'l Electrification |  | High Electrification |  | Average
|  | Total Load (MW) | 37.3 |  | 142 |  | 366 |  | 181.7667
115 kV Transmission (incl. substation transmission) | Miles | $4M | 0 |  | 0 |  | 0 |  | 0 |  | 4000000 | 0 | 0 | 0
230 kV Transmission | Miles | $6M | 0 |  | 0 |  | 0 |  | 0 |  | 6000000 | 0 | 0 | 0
Bulk 230/115 kV Transformers | Transformers | $8M | 0 |  | 0 |  | 0 |  | 0 |  | 8000000 | 0 | 0 | 0
Transmission Switching Stations | Switching Stations | $15M | 0 |  | 0 |  | 0 |  | 0 |  | 15000000 | 0 | 0 | 0
Distribution Substation Transformers | Transformers | $10.5M / transformer | 1 |  | 2 |  | 9 |  | 4 |  | 10500000 | 10500000 | 21000000 | 94500000
Distribution Feeder | Miles | $2M / mile | 6 |  | 12 |  | 33 |  | 17 |  | 2000000 | 12000000 | 24000000 | 66000000
Distribution Service Transformers | Transformers | $15,700 / transformer | 0 |  | 6026 |  | 9212 |  | 5079.3333 |  | 15700 | 0 | 94608200 | 144628400
[12 empty] | 22500000 | 139608200 | 305128400
Description | Unit | $/unit | 2026-2040
|  |  | Carbon Out |  | Carbon Out + Add'l Electrification |  | High Electrification |  | Average
|  | Total Load (MW) | 311 |  | 1366 |  | 3053 |  | 1576.6667
115 kV Transmission (incl. substation transmission) | Miles | $4M | 66.7 |  | 73.1 |  | 177.4 |  | 105.7333 |  | 4000000 | 266800000 | 292400000 | 709600000
230 kV Transmission | Miles | $6M | 2 |  | 3.2 |  | 4.2 |  | 3.1333 |  | 6000000 | 12000000 | 19200000 | 25200000
Bulk 230/115 kV Transformers | Transformers | $8M | 4 |  | 4.7 |  | 5.7 |  | 4.8 |  | 8000000 | 32000000 | 37600000 | 45600000
Transmission Switching Stations | Switching Stations | $15M | 3 |  | 3.25 |  | 6.25 |  | 4.1667 |  | 15000000 | 45000000 | 48750000 | 93750000
Distribution Substation Transformers | Transformers | $10.5M / transformer | 20 |  | 41 |  | 107 |  | 56 |  | 10500000 | 210000000 | 430500000 | 1123500000
Distribution Feeder | Miles | $2M / mile | 48 |  | 108 |  | 57 |  | 71 |  | 2000000 | 96000000 | 216000000 | 114000000
Distribution Service Transformers | Transformers | $15,700 / transformer | 0 |  | 55591 |  | 66714 |  | 40768.3333 |  | 15700 | 0 | 872778700 | 1047409800
[12 empty] | 661800000 | 1917228700 | 3159059800
2023 Update
15%
Description | Unit | $/unit | 2024-2030 (units / $M)
|  |  | S1: ASHP |  | S2: CCHP |  | S3: HHP |  | S4: HHP+CCHP
|  | Total Load (MW) | 439.1171 |  | 418.9622 |  | 100.7222 |  | 106.0873
115 kV Transmission (incl. substation transmission) | Miles | $4.6M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4600000 | 0 | 0 | 0 | 0
230 kV Transmission | Miles | $6.9M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6900000 | 0 | 0 | 0 | 0
Bulk 230/115 kV Transformers | Transformers | $9.2M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9200000 | 0 | 0 | 0 | 0
Transmission Switching Stations | Switching Stations | $17.2M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17250000 | 0 | 0 | 0 | 0
Distribution Substation Transformers | Transformers | $12.1M / transformer | 10 | 120.75 | 10 | 120.75 | 3 | 36.225 | 3 | 36.225 | 12075000 | 120750000 | 120750000 | 36225000 | 36225000
Distribution Feeder | Miles | $2.3M / mile | 42 | 96.6 | 40 | 92 | 10 | 23 | 10 | 23 | 2300000 | 96600000 | 92000000 | 23000000 | 23000000
Distribution Service Transformers | Transformers | $18,100 / transformer | 12271 | 221.5529 | 11708 | 211.3879 | 2815 | 50.8248 | 2965 | 53.5331 | 18055 | 221552905 | 211387940 | 50824825 | 53533075
|  | Sub-Total ($M) |  | 438.9029 |  | 424.1379 |  | 110.0498 |  | 112.7581 |  | 438902905 | 424137940 | 110049825 | 112758075
|  | Planning Estimate (+50%) |  | 658.3544 |  | 636.2069 |  | 165.0747 |  | 169.1371
Description | Unit | $/unit | 2024-2045 (units / $M)
|  |  | S1: ASHP |  | S2: CCHP |  | S3: HHP |  | S4: HHP+CCHP
|  | Total Load (MW) | 2012.5231 |  | 1714.4402 |  | 417.3463 |  | 432.4086
115 kV Transmission (incl. substation transmission) | Miles | $4.6M | 135 | 621 | 115 | 529 | 28 | 128.8 | 29 | 133.4 | 4600000 | 621000000 | 529000000 | 128800000 | 133400000
230 kV Transmission | Miles | $6.9M | 4 | 27.6 | 4 | 27.6 | 1 | 6.9 | 1 | 6.9 | 6900000 | 27600000 | 27600000 | 6900000 | 6900000
Bulk 230/115 kV Transformers | Transformers | $9.2M | 7 | 64.4 | 6 | 55.2 | 2 | 18.4 | 2 | 18.4 | 9200000 | 64400000 | 55200000 | 18400000 | 18400000
Transmission Switching Stations | Switching Stations | $17.2M | 6 | 103.5 | 5 | 86.25 | 2 | 34.5 | 2 | 34.5 | 17250000 | 103500000 | 86250000 | 34500000 | 34500000
Distribution Substation Transformers | Transformers | $12.1M / transformer | 72 | 869.4 | 61 | 736.575 | 15 | 181.125 | 16 | 193.2 | 12075000 | 869400000 | 736575000 | 181125000 | 193200000
Distribution Feeder | Miles | $2.3M / mile | 91 | 209.3 | 78 | 179.4 | 19 | 43.7 | 20 | 46 | 2300000 | 209300000 | 179400000 | 43700000 | 46000000
Distribution Service Transformers | Transformers | $18,100 / transformer | 52039 | 939.5641 | 44331 | 800.3962 | 10792 | 194.8496 | 11181 | 201.873 | 18055 | 939564145 | 800396205 | 194849560 | 201872955
|  | Sub-Total ($M) |  | 2834.7641 |  | 2414.4212 |  | 608.2746 |  | 634.273 |  | 2834764145 | 2414421205 | 608274560 | 634272955
|  | Planning Estimate (+50%) |  | 4252.1462 |  | 3621.6318 |  | 912.4118 |  | 951.4094

## Costs-Updated
Load Forecast & Incremental Load (MW) - 2025
| Winter | Summer
PSE F20 Load Forecast (Native Load) | 4595 | 3594
Transportation Load | 429 | 429
Carbon Out | 37.3 | 26.1
Carbon Out + Add'l Electrification | 142 | 26.1
High Electrification | 366 | 33
Load Forecast & Incremental Load (MW) - 2040
| Winter | Summer
F20 Load Forecast (Native Load) | 4769 | 4206
Transportation Load | 442 | 442
Carbon Out | 311 | 321
Carbon Out + Add'l Electrification | 1366 | 321
High Electrification | 3053 | 342
F20 Load Forecast numbers represent PSE native load to be served.
Transportation Load represents BPA/Network loads, 449 customers and Microsoft load. This value represents the contractual obligation to serve these customers.
Loads for the different scenarios are added on top of the load forecast value to get total load.
Incremental loads for SCL, SnoPUD, and Tacoma Power were also added to the cases to gauge regional electrification impacts on PSE's system.
Electrification costs are provded in 2020 dollars (i.e. the standard 3% per year escalation has not been applied to escalate costs to future dollars)
Costs are incremental, meaning they do not account for costs associated with normal load growth on the system, but would be added on top of the existing portfolio
Costs in the 2025 column include total incremental costs from 2020 to 2025
Costs in the 2040 column include the total incremental costs from 2026 to 2040
Costs in the Total column include 2025 costs plus 2040 costs
All costs are planning level estimates and include some contingency
Carbon Out
| 2025 | 2040 | Total | Base Cost | Contingency (%) | Planning Estimate
Transmission & Switching Stations | -- | $265M | $265M | $176.67M | 50% | $265M
Distribution Substation | $14M | $302M | $316M | $210M | 50% | $316M
Distribution Substation - T-Lines | -- | $136M | $136M | $90.67M | 50% | $136M
Distribution Feeders | $12M | $96M | $108M | $86.4M | 25% | $108M
Total | $26M | $799M | $825M
Carbon Out + Add'l Electrification
| 2025 | 2040 | Total | Base Cost | Contingency (%) | Planning Estimate
Transmission & Switching Stations | -- | $311M | $311M | $207.33M | 50% | $311M
Distribution Substation | $35M | $611M | $646M | $430.1M | 100 | $646M
Distribution Substation - T-Lines | -- | $136M | $136M | $90.67M | 50% | $136M
Distribution Feeders | $24M | $264M | $288M | $230M | 25% | $288M
Distribution - Service Transformers | $118M | $1,084M | $1,202M | $961.6M | 25% | $1,202M
Total | $177M | $2,406M | $2,583M
High Electrification
| 2025 | 2040 | Total | Base Cost | Contingency (%) | Planning Estimate
Transmission & Switching Stations | -- | $496M | $496M | $330.67M | 50% | $496M
Distribution Substation | $134M | $1,564M | $1,698M | $1131.35M | 100 | $2262.7M
Distribution Substation - T-Lines | -- | $559M | $559M | $372.67M | 50% | $559M
Distribution Feeders | $66M | $1,212M | $1,278M | $1,022M | 25% | $1,278M
Distribution - Service Transformers | $180M | $1,300M | $1,480M | $1,184M | 25% | $1,480M
Total | $380M | $5,131M | $5,511M
1. Transmission Costs include costs associated with capacity constraints under NERC credible contingency conditions.
2. Substation costs include the costs associated with the addition of distribution transformer capacity, including limited transmission modifications, substation/transformer additions, and the associated feeder getaways.
3. Substation transmission indicates the additional transmission work that would be needed to accommodate substations beyond the limited modifications included in the substation costs.
4. Distribution costs include modifications required to the existing distribution feeders to accommodate additional load. Costs associated with additional service transformers or service upgrades have been calculated separately.
5. 2040 costs are above and beyond what would be needed in 2025. The 2025 and 2040 costs need to be added to get the total cost of upgrades through the 20 year time period.
6. Costs for transmission service from BPA were not included in these totals, but transmission service would need to be obtained.
7. Transmission costs include a 50% planning level contingency, and includes typical ROW, permitting, real estate and legal costs.

## Incremental Load Growth
Load Forecast - Growth By Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Carbon Out
Winter - Residential | 1.1015 | 3.457 | 6.9394 | 11.4771 | 16.9485 | 23.2211 | 30.0853 | 37.5312 | 45.5453 | 54.1916 | 63.6325 | 74.3272 | 85.9018 | 98.33 | 111.3221 | 124.8005 | 138.3981 | 152.1645 | 166.0469 | 180.568 | 194.9168
Winter - Commercial | 0.6766 | 2.0783 | 4.1929 | 6.994 | 10.3455 | 14.1204 | 18.2911 | 22.822 | 27.6891 | 32.969 | 38.7165 | 45.0752 | 51.9227 | 59.2669 | 66.8821 | 74.7291 | 82.7069 | 90.9403 | 99.2492 | 107.7008 | 116.0449
Winter - Total | 1.7781 | 5.5353 | 11.1323 | 18.471 | 27.2939 | 37.3415 | 48.3764 | 60.3533 | 73.2344 | 87.1606 | 102.349 | 119.4024 | 137.8245 | 157.5969 | 178.2043 | 199.5296 | 221.105 | 243.1048 | 265.2961 | 288.2688 | 310.9616
Winter % Total - Overall | 0.5718% | 1.208% | 1.8% | 2.36% | 2.837% | 3.231% | 3.549% | 3.852% | 4.142% | 4.478% | 4.884% | 5.484% | 5.924% | 6.358% | 6.627% | 6.858% | 6.938% | 7.075% | 7.136% | 7.388% | 7.298%
Winer % Total - 2025 and 2040 | 4.762% | 10.06% | 14.99% | 19.65% | 23.63% | 26.91% | 4.033% | 4.377% | 4.708% | 5.09% | 5.551% | 6.233% | 6.733% | 7.226% | 7.531% | 7.794% | 7.885% | 8.04% | 8.11% | 8.396% | 8.294%
Summer | 1.2571 | 3.8906 | 7.801 | 12.9251 | 19.0856 | 26.1077 | 33.857 | 42.3051 | 51.4255 | 61.3158 | 72.1005 | 84.1537 | 97.1301 | 111.0304 | 125.5221 | 140.5922 | 156.0067 | 192.6387 | 237.7441 | 279.6846 | 321.0825
Summer % Total | 0.3915% | 0.8202% | 1.218% | 1.596% | 1.919% | 2.187% | 2.413% | 2.631% | 2.841% | 3.08% | 3.359% | 3.754% | 4.041% | 4.329% | 4.513% | 4.694% | 4.801% | 11.41% | 14.05% | 13.06% | 12.89%
Carbon Out + Add'l Electrification
Winter - Residential | 5.1421 | 15.6755 | 30.5929 | 49.6574 | 72.8011 | 99.9425 | 130.5753 | 164.9439 | 203.0762 | 244.9937 | 290.7921 | 341.7639 | 395.7048 | 452.7784 | 512.9252 | 577.9341 | 648.4448 | 725.6894 | 807.8767 | 894.5414 | 979.4128
Winter - Commercial | 2.1311 | 6.3986 | 12.6268 | 20.7541 | 30.5252 | 41.728 | 54.4098 | 68.558 | 84.1262 | 101.2602 | 119.9214 | 140.2912 | 161.8321 | 184.6628 | 208.4892 | 233.8678 | 261.2123 | 291.2208 | 322.8274 | 355.2893 | 387.0643
Winter - Total | 7.2733 | 22.0741 | 43.2197 | 70.4114 | 103.3264 | 141.6705 | 184.9851 | 233.5019 | 287.2024 | 346.254 | 410.7134 | 482.0551 | 557.5369 | 637.4412 | 721.4145 | 811.8019 | 909.657 | 1016.9102 | 1130.704 | 1249.8307 | 1366.4771
Winter % Total | 0.5323% | 1.083% | 1.547% | 1.99% | 2.409% | 2.806% | 3.17% | 3.551% | 3.93% | 4.321% | 4.717% | 5.221% | 5.524% | 5.847% | 6.145% | 6.615% | 7.161% | 7.849% | 8.328% | 8.718% | 8.536%
Winer % Total - 2025 and 2040 | 5.134% | 10.45% | 14.93% | 19.19% | 23.23% | 27.07% | 3.536% | 3.961% | 4.384% | 4.821% | 5.263% | 5.825% | 6.163% | 6.524% | 6.856% | 7.38% | 7.989% | 8.757% | 9.291% | 9.726% | 9.524%
Summer | 1.2571 | 3.8906 | 7.801 | 12.9251 | 19.0856 | 26.1077 | 33.857 | 42.3051 | 51.4255 | 61.3158 | 72.1005 | 84.1537 | 97.1301 | 111.0304 | 125.5221 | 140.5922 | 156.0067 | 192.6387 | 237.7441 | 279.6846 | 321.0825
Summer % Total | 0.3915% | 0.8202% | 1.218% | 1.596% | 1.919% | 2.187% | 2.413% | 2.631% | 2.841% | 3.08% | 3.359% | 3.754% | 4.041% | 4.329% | 4.513% | 4.694% | 4.801% | 11.41% | 14.05% | 13.06% | 12.89%
High Electrification
Winter - Residential | 15.1206 | 45.9092 | 89.2352 | 144.4322 | 211.487 | 290.3588 | 379.7329 | 480.4257 | 592.5376 | 716.0034 | 850.8222 | 991.5109 | 1131.6094 | 1271.9062 | 1412.5103 | 1558.0095 | 1708.8995 | 1867.0073 | 2027.0055 | 2187.8454 | 2334.5304
Winter - Commercial | 3.9088 | 11.6789 | 22.9349 | 37.572 | 55.1894 | 75.4707 | 98.5548 | 124.4575 | 153.1049 | 184.7273 | 219.1718 | 256.6663 | 296.1658 | 337.9246 | 381.5646 | 428.3706 | 479.3854 | 536.0081 | 596.0895 | 657.8974 | 718.3103
Winter - Total | 19.0294 | 57.5881 | 112.1702 | 182.0042 | 266.6764 | 365.8295 | 478.2877 | 604.8833 | 745.6425 | 900.7307 | 1069.994 | 1248.1772 | 1427.7752 | 1609.8307 | 1794.0749 | 1986.3802 | 2188.2849 | 2403.0154 | 2623.0951 | 2845.7428 | 3052.8406
Winter % Total | 0.6233% | 1.263% | 1.788% | 2.288% | 2.774% | 3.248% | 3.684% | 4.147% | 4.611% | 5.08% | 5.544% | 5.837% | 5.883% | 5.963% | 6.035% | 6.299% | 6.614% | 7.034% | 7.209% | 7.293% | 6.784%
Winer % Total - 2025 and 2040 | 5.202% | 10.54% | 14.92% | 19.09% | 23.15% | 27.1% | 4.185% | 4.711% | 5.239% | 5.772% | 6.299% | 6.631% | 6.684% | 6.775% | 6.857% | 7.157% | 7.514% | 7.991% | 8.191% | 8.286% | 7.707%
Summer | 1.5841 | 4.911 | 9.8381 | 16.2823 | 24.0365 | 32.8936 | 42.6628 | 53.3167 | 64.8258 | 77.3033 | 90.9135 | 105.518 | 120.6073 | 136.1518 | 151.7553 | 167.4087 | 182.8094 | 218.8467 | 262.7772 | 303.0583 | 342.2276
Summer % Total | 0.4629% | 0.9721% | 1.44% | 1.883% | 2.266% | 2.588% | 2.855% | 3.113% | 3.363% | 3.646% | 3.977% | 4.267% | 4.409% | 4.542% | 4.559% | 4.574% | 4.5% | 10.53% | 12.84% | 11.77% | 11.45%
Costs By Year
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Carbon Out | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission & Switching Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 265000000
Distribution Substations | 666648.1417 | 1408645.0981 | 2098412.2262 | 2751420.4877 | 3307851.9557 | 3767022.0905 | 12179470.9747 | 13219069.9882 | 14217162.0824 | 15370593.6549 | 16763788.9897 | 18822152.1933 | 20332826.2473 | 21823231.3757 | 22744735.9595 | 23537206.5929 | 23813237.7453 | 24281578.1711 | 24493008.7479 | 25355395.4898 | 25046541.7872 | 316000000
Distribution Substation T-Lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 136000000
Distribution Feeders | 571412.6929 | 1207410.0841 | 1798639.051 | 2358360.4181 | 2835301.6763 | 3228876.0776 | 3871619.9125 | 4202088.4731 | 4519362.7812 | 4886016.5261 | 5328886.5662 | 5983200.6972 | 6463414.966 | 6937186.1327 | 7230114.7421 | 7482025.9368 | 7569770.9389 | 7718647.3656 | 7785857.0854 | 8059993.2683 | 7961814.6078 | 108000000
Total | 1238060.8346 | 2616055.1821 | 3897051.2772 | 5109780.9058 | 6143153.6321 | 6995898.1681 | 16051090.8872 | 17421158.4613 | 18736524.8636 | 20256610.181 | 58547221.0104 | 61259898.3451 | 63250786.6679 | 65214962.963 | 66429396.1562 | 67473777.9843 | 67837554.1387 | 68454770.9913 | 68733411.2879 | 69869934.2126 | 69462901.8496 | 825000000
Running Total | 1238060.8346 | 3854116.0168 | 7751167.294 | 12860948.1998 | 19004101.8319 | 26000000 | 42051090.8872 | 59472249.3485 | 78208774.2121 | 98465384.3931 | 157012605.4035 | 218272503.7486 | 281523290.4165 | 346738253.3795 | 413167649.5356 | 480641427.5199 | 548478981.6586 | 616933752.6499 | 685667163.9378 | 755537098.1504 | 825000000 |  | Delta
Inflation (3%) | 1238060.8346 | 2694536.8376 | 4134381.7 | 5583595.5599 | 6914173.5341 | 8110163.3728 | 19165841.9357 | 21425827.497 | 23734869.1263 | 26430281.7594 | 78682569.281 | 84798026.2064 | 90180497.6933 | 95770371.7326 | 100480422.0541 | 105121947.5745 | 108859359.9391 | 113145306.1506 | 117014031.7883 | 122517352.5699 | 125457727.4233 | 1261459344.5706 | 436459344.5706
Running total with Inflation | 1238060.8346 | 3932597.6722 | 8066979.3723 | 13650574.9321 | 20564748.4662 | 28674911.8389 | 47840753.7746 | 69266581.2716 | 93001450.3979 | 119431732.1574 | 198114301.4384 | 282912327.6448 | 373092825.3381 | 468863197.0707 | 569343619.1249 | 674465566.6994 | 783324926.6385 | 896470232.7891 | 1013484264.5774 | 1136001617.1473 | 1261459344.5706
Total - Delta from Jeff | 0 | 78481.6555 | 237330.4228 | 473814.6541 | 771019.902 | 1114265.2046 | 3114751.0485 | 4004669.0357 | 4998344.2628 | 6173671.5784 | 20135348.2706 | 23538127.8613 | 26929711.0254 | 30555408.7696 | 34051025.898 | 37648169.5902 | 41021805.8004 | 44690535.1594 | 48280620.5004 | 52647418.3573 | 55994825.5737
Running Total - Delta from Jeff | 0 | 78481.6555 | 315812.0782 | 789626.7323 | 1560646.6343 | 2674911.8389 | 5789662.8874 | 9794331.9231 | 14792676.1858 | 20966347.7643 | 41101696.0349 | 64639823.8962 | 91569534.9216 | 122124943.6913 | 156175969.5892 | 193824139.1794 | 234845944.9798 | 279536480.1392 | 327817100.6396 | 380464518.9969 | 436459344.5706
Carbon Out + Add'l Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission & Switching Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 311000000
Distribution Substations | 1796873.8869 | 3656582.5612 | 5224060.2644 | 6717776.4882 | 8131701.4 | 9473005.3994 | 21607660.4228 | 24202826.4149 | 26788716.2912 | 29458129.086 | 32155886.8915 | 35589067.1312 | 37654417.0529 | 39860642.1795 | 41890402.5265 | 45090159.8629 | 48815464.2764 | 53503679.0912 | 56766566.3429 | 59426847.9508 | 58189534.4793 | 646000000
Distribution Substation T-Lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 12363636.3636 | 136000000
Distribution Feeders and Service Transformers | 7290174.0553 | 14835277.8196 | 21194758.7869 | 27254978.895 | 32991474.2514 | 38433336.1919 | 47671237.725 | 53396743.0562 | 59101783.2414 | 64991093.3027 | 70942938.6739 | 78517287.2223 | 83073902.1068 | 87941318.5892 | 92419415.0666 | 99478781.4979 | 107697620.0403 | 118040850.1063 | 125239494.9758 | 131108659.6361 | 128378874.7595 | 1490000000
Total | 9087047.9422 | 18491860.3808 | 26418819.0512 | 33972755.3832 | 41123175.6513 | 47906341.5913 | 69278898.1478 | 77599569.4711 | 85890499.5325 | 94449222.3887 | 143735189.2018 | 154742717.9899 | 161364682.796 | 168438324.4051 | 174946181.2295 | 185205304.9972 | 197149447.9531 | 212180892.8339 | 222642424.955 | 231171871.2232 | 227204772.8752 | 2583000000
Running Total | 9087047.9422 | 27578908.323 | 53997727.3742 | 87970482.7574 | 129093658.4087 | 177000000 | 246278898.1478 | 323878467.6189 | 409768967.1515 | 504218189.5402 | 647953378.742 | 802696096.7319 | 964060779.5279 | 1132499103.933 | 1307445285.1624 | 1492650590.1596 | 1689800038.1127 | 1901980930.9466 | 2124623355.9016 | 2355795227.1248 | 2583000000
Total per Year with Inflation (3%) | 9087047.9422 | 19046616.1923 | 28027725.1315 | 37122947.0716 | 46284496.4908 | 55536579.8013 | 82722627.4344 | 95437682.4608 | 108803515.0833 | 123234812.6063 | 193168075.0565 | 214200111.4895 | 230067453.2489 | 247357358.0261 | 264621796.1303 | 288543830.5672 | 316366988.595 | 350702686.3338 | 379033825.0781 | 405361275.4911 | 410357092.8604 | 3905084543.0912
Running total with Inflation | 9087047.9422 | 28133664.1344 | 56161389.2659 | 93284336.3375 | 139568832.8282 | 195105412.6295 | 277828040.0639 | 373265722.5247 | 482069237.6079 | 605304050.2143 | 798472125.2708 | 1012672236.7603 | 1242739690.0092 | 1490097048.0353 | 1754718844.1656 | 2043262674.7328 | 2359629663.3279 | 2710332349.6617 | 3089366174.7397 | 3494727450.2308 | 3905084543.0912
Total - Delta from Jeff | 0 | 554755.8114 | 1608906.0802 | 3150191.6884 | 5161320.8394 | 7630238.21 | 13443729.2866 | 17838112.9896 | 22913015.5507 | 28785590.2176 | 49432885.8546 | 59457393.4997 | 68702770.4529 | 78919033.6211 | 89675614.9009 | 103338525.57 | 119217540.642 | 138521793.4999 | 156391400.123 | 174189404.2679 | 183152319.9852
Running Total - Delta from Jeff | 0 | 554755.8114 | 2163661.8916 | 5313853.5801 | 10475174.4195 | 18105412.6295 | 31549141.9161 | 49387254.9057 | 72300270.4565 | 101085860.6741 | 150518746.5287 | 209976140.0284 | 278678910.4813 | 357597944.1023 | 447273559.0032 | 550612084.5732 | 669829625.2152 | 808351418.7151 | 964742818.8381 | 1138932223.106 | 1322084543.0912
High Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission & Switching Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 496000000
Distribution Substations | 6970295.5438 | 14123706.4044 | 19992896.6602 | 25579562.8968 | 31014662.1861 | 36318876.3087 | 65457317.1626 | 73686155.137 | 81930243.708 | 90270527.2411 | 98521288.4617 | 103713193.1398 | 104536716.3253 | 105967123.8234 | 107241049.9251 | 111933076.5947 | 117520559.5299 | 124985883.8145 | 128099432.8753 | 129594222.7939 | 120543209.4678 | 1698000000
Distribution Substation T-Lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50818181.8182 | 50818181.8182 | 50818181.8182 | 50818181.8182 | 50818181.8182 | 50818181.8182 | 50818181.8182 | 50818181.8182 | 50818181.8182 | 50818181.8182 | 50818181.8182 | 559000000
Distribution Feeders and Service Transformers | 12796214.2072 | 25928595.3395 | 36703377.4509 | 46959496.0644 | 56937364.9087 | 66674952.0293 | 105133491.5041 | 118350141.7545 | 131591286.5694 | 144986933.7786 | 158238795.7901 | 166577711.7437 | 167900403.7143 | 170197835.7061 | 172243936.9641 | 179779979.7991 | 188754249.0659 | 200744590.8836 | 205745380.6796 | 208146219.7304 | 193609042.3165 | 2758000000
Total | 19766509.7509 | 40052301.7439 | 56696274.1112 | 72539058.9612 | 87952027.0948 | 102993828.338 | 170590808.6667 | 192036296.8915 | 213521530.2774 | 235257461.0197 | 352669175.1608 | 366199995.7927 | 368346210.9488 | 372074050.4386 | 375394077.7982 | 387622147.3028 | 402183899.5049 | 421639565.6071 | 429753904.464 | 433649533.4333 | 410061342.6934 | 5511000000
Running Total | 19766509.7509 | 59818811.4948 | 116515085.606 | 189054144.5672 | 277006171.662 | 380000000 | 550590808.6667 | 742627105.5582 | 956148635.8356 | 1191406096.8553 | 1544075272.0161 | 1910275267.8088 | 2278621478.7575 | 2650695529.1962 | 3026089606.9944 | 3413711754.2972 | 3815895653.8022 | 4237535219.4093 | 4667289123.8733 | 5100938657.3066 | 5511000000
Inflation (3%) | 19766509.7509 | 41253870.7962 | 60149077.2045 | 79265388.2815 | 98990781.3526 | 119398075.0051 | 203694346.8553 | 236180422.7598 | 270482686.2875 | 306957626.4342 | 473957880.9884 | 506906437.6353 | 525173620.3887 | 546403286.9696 | 567817224.8491 | 603902675.4507 | 645387093.2374 | 696905957.6858 | 731627255.1565 | 760407081.7894 | 740616397.9421 | 8235243696.8207 | 2724243696.8207
Running total with Inflation | 19766509.7509 | 61020380.5472 | 121169457.7517 | 200434846.0332 | 299425627.3857 | 418823702.3909 | 622518049.2461 | 858698472.0059 | 1129181158.2935 | 1436138784.7277 | 1910096665.7161 | 2417003103.3514 | 2942176723.7402 | 3488580010.7098 | 4056397235.5588 | 4660299911.0095 | 5305687004.2469 | 6002592961.9327 | 6734220217.0892 | 7494627298.8786 | 8235243696.8207
Total - Delta from Jeff | 0 | 1201569.0523 | 3452803.0934 | 6726329.3203 | 11038754.2578 | 16404246.6671 | 33103538.1885 | 44144125.8683 | 56961156.0101 | 71700165.4146 | 121288705.8276 | 140706441.8427 | 156827409.44 | 174329236.531 | 192423147.0508 | 216280528.1478 | 243203193.7325 | 275266392.0787 | 301873350.6925 | 326757548.3561 | 330555055.2487
Running Total - Delta from Jeff | 0 | 1201569.0523 | 4654372.1457 | 11380701.466 | 22419455.7237 | 38823702.3909 | 71927240.5794 | 116071366.4477 | 173032522.4578 | 244732687.8724 | 366021393.7 | 506727835.5427 | 663555244.9826 | 837884481.5136 | 1030307628.5644 | 1246588156.7123 | 1489791350.4447 | 1765057742.5234 | 2066931093.2159 | 2393688641.572 | 2724243696.8207
Substation and Distribution costs were spread out over the 20-year period proportional to the incremental load growth. The period form 2020-2025 and 2026-2040 were accounted for separately to align with the costs.
The transmission system was deemed sufficient to accommodate the additional load growth until 2030. From 2030 to 2040, transmission costs (including those associated with substations) were spread equally across the 2030-2040 timeframe.
Transmission and distribution substations were allocated to transmission. Distribution feeders and service transformers were allocated to distribution.
Incremental Decarbonization Costs Transmission/Distribution with inflation per year
Carbon Out | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission | 666648.1417 | 1450904.451 | 2226205.5308 | 3006551.4553 | 3723016.5183 | 4367011.0469 | 14542925.2879 | 16257788.7038 | 18009875.5682 | 20055138.4205 | 71520991.341 | 76515877.146 | 80965213.4393 | 85582880.0203 | 89544224.7857 | 93465194.9548 | 96712099.7709 | 100387558.128 | 103759131.276 | 108384105.5862 | 111077804.6117 | 1102221146.1842
Distribution | 571412.6929 | 1243632.3866 | 1908176.1692 | 2577044.1046 | 3191157.0157 | 3743152.3259 | 4622916.6478 | 5168038.7932 | 5724993.5581 | 6375143.339 | 7161577.94 | 8282149.0604 | 9215284.254 | 10187491.7123 | 10936197.2684 | 11656752.6197 | 12147260.1681 | 12757748.0226 | 13254900.5123 | 14133246.9837 | 14379922.8116 | 159238198.3864
Carbon Out + Add'l Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Transmission | 1796873.8869 | 3766280.038 | 5542205.5345 | 7340695.7486 | 9152301.566 | 10981809.5652 | 25800676.5505 | 29766423.6771 | 33935144.3164 | 38436176.8772 | 97826697.7738 | 105513823.079 | 111623932.9073 | 118212566.8725 | 124829138.5234 | 133559130.3503 | 143543924.2408 | 155599146.7242 | 165821968.2583 | 175461447.2084 | 178490564.863 | 1677000928.5615
Distribution | 7290174.0553 | 15280336.1542 | 22485519.597 | 29782251.323 | 37132194.9248 | 44554770.2361 | 56921950.8839 | 65671258.7836 | 74868370.7668 | 84798635.7291 | 95341377.2827 | 108686288.4105 | 118443520.3416 | 129144791.1536 | 139792657.6069 | 154984700.2169 | 172823064.3543 | 195103539.6095 | 213211856.8198 | 229899828.2827 | 231866527.9974 | 2228083614.5297
High Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Transmission | 6970295.5438 | 14547417.5966 | 21210464.0669 | 27951479.0256 | 34907275.5296 | 42103531.7123 | 78159459.8826 | 90624676.4466 | 103786781.4901 | 117782563.2343 | 261298171.4784 | 276323926.9319 | 285787791.8871 | 296462027.2787 | 307282815.6286 | 323811324.7665 | 342491934.3541 | 365105735.9525 | 381359516.8902 | 395421425.5671 | 390936931.4807 | 4164325546.7442
Distribution | 12796214.2072 | 26706453.1996 | 38938613.1377 | 51313909.2559 | 64083505.823 | 77294543.2928 | 125534886.9726 | 145555746.3132 | 166695904.7974 | 189175063.1999 | 212659709.51 | 230582510.7035 | 239385828.5016 | 249941259.691 | 260534409.2204 | 280091350.6841 | 302895158.8834 | 331800221.7333 | 350267738.2663 | 364985656.2223 | 349679466.4614 | 4070918150.0765
20-Year Portfolio with Incremental Decarbonization Costs
Carbon Out | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission | 114848706.0043 | 134648398.451 | 151849131.5308 | 114293914.4553 | 121531166.5183 | 103942827.0882 | 105657124.6478 | 208132038.0182 | 111117626.4369 | 114287436.2795 | 166855014.4318 | 114741589.8427 | 120337697.5169 | 1012683962.1069 | 1017861916.6304 | 136488571.3634 | 141026177.4719 | 146031058.1599 | 150771936.3089 | 156807294.7701 | 160953689.4711 | 4604867277.5043
Distribution | 286337483.3522 | 310507342.3866 | 351082903.1692 | 455929800.1046 | 421262304.507 | 406880308.3259 | 517457247.1039 | 510978882.5665 | 460680021.6928 | 533163972.7796 | 432518195.1109 | 736239173.9049 | 741836392.6215 | 775816143.0381 | 734772016.0204 | 728981562.2536 | 735304772.4708 | 744038591.4704 | 767694297.0019 | 779908214.6089 | 799887485.2334 | 12231277109.7232
Carbon Out + Add'l Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission | 115978931.7494 | 136963774.038 | 155165131.5345 | 118628058.7486 | 126960451.566 | 110557625.6066 | 116914875.9104 | 221640672.9916 | 127042895.1851 | 132668474.7362 | 193160720.8646 | 143739535.7757 | 150996416.9849 | 1045313648.9592 | 1053146830.3681 | 176582506.759 | 187858001.9417 | 201242646.7562 | 212834773.2912 | 223884636.3923 | 228366449.7224 | 5179647059.8817
Distribution | 293056244.7146 | 324544046.1542 | 371660246.597 | 483135007.323 | 455203342.4161 | 447691926.2361 | 569756281.34 | 571482102.5569 | 529823398.9015 | 611587465.1698 | 520697994.4536 | 836643313.255 | 851064628.7091 | 894773442.4794 | 863628476.3588 | 872309509.8508 | 895980576.6569 | 926384383.0572 | 967651253.3093 | 995674795.908 | 1017374090.4193 | 14300122525.8665
High Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission | 121152353.4063 | 147744911.5966 | 170833390.0669 | 139238842.0256 | 152715425.5296 | 141679347.7537 | 169273659.2425 | 282498925.7611 | 196894532.3587 | 212014861.0933 | 356632194.5693 | 314549639.6286 | 325160275.9647 | 1223563109.3653 | 1235600507.4733 | 366834701.1752 | 386806012.055 | 410749235.9845 | 428372321.9231 | 443844614.751 | 440812816.3401 | 7666971678.0643
Distribution | 298562284.8665 | 335970163.1996 | 388113340.1377 | 504666665.2559 | 482154653.3143 | 480431699.2928 | 638369217.4287 | 651366590.0865 | 621650932.9321 | 715963892.6406 | 638016326.6808 | 958539535.5479 | 972006936.8691 | 1015569911.0167 | 984370227.9724 | 997416160.318 | 1026052671.186 | 1063081065.181 | 1104707134.7559 | 1130760623.8475 | 1135187028.8833 | 16142957061.4134

## 20-Year Summary Costs
20-Year Baseline Portfolio
Year |  |  |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Capex by Category
Generation |  |  |  | 75.3285 | 169.0167 | 145.634 | 135.176 | 93.182 | 53.743 | 389.7143 | 803.4793 | 509.0805 | 92.4157 | 361.2957 | 507.262 | 99.5241 | 145.3357 | 103.2892 | 487.4005 | 109.5501 | 384.7195 | 114.3691 | 528.122 | 121.5156
Transmission |  |  |  | 114.1821 | 133.1975 | 149.6229 | 111.2874 | 117.8081 | 99.5758 | 91.1142 | 191.8742 | 93.1078 | 94.2323 | 95.334 | 38.2257 | 39.3725 | 927.1011 | 928.3177 | 43.0234 | 44.3141 | 45.6435 | 47.0128 | 48.4232 | 49.8759
Distribution |  |  |  | 285.7661 | 309.2637 | 349.1747 | 453.3528 | 418.0711 | 403.1372 | 512.8343 | 505.8108 | 454.955 | 526.7888 | 425.3566 | 727.957 | 732.6211 | 765.6287 | 723.8358 | 717.3248 | 723.1575 | 731.2808 | 754.4394 | 765.775 | 785.5076
Natural Gas |  |  |  | 356.4979 | 228.2073 | 245.1561 | 282.4015 | 281.3475 | 274.8842 | 272.9722 | 281.0458 | 289.8833 | 299.263 | 311.2972 | 302.06 | 311.2737 | 273.4029 | 274.6427 | 283.4054 | 292.5836 | 302.1707 | 313.4228 | 325.1099 | 337.2493
PLNG |  |  |  | 25.6511 | 7.0574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Common |  |  |  | 120.4161 | 114.2561 | 84.8528 | 152.9059 | 119.4599 | 87.2814 | 157.3213 | 139.7605 | 131.6453 | 135.3119 | 134.6821 | 144.9022 | 154.5022 | 151.2811 | 163.8784 | 151.0657 | 169.0494 | 163.2565 | 141.0508 | 156.1533 | 145.8987
Total CapEx |  |  |  | 977.8418 | 960.9987 | 974.4406 | 1135.1235 | 1029.8687 | 918.6217 | 1423.9563 | 1921.9707 | 1478.6719 | 1148.0117 | 1327.9657 | 1720.407 | 1337.2936 | 2262.7494 | 2193.9638 | 1682.2198 | 1338.6547 | 1627.0711 | 1370.2949 | 1823.5834 | 1440.047
Total Depreciation |  |  |  | 641.8141 | 704.8109 | 626.3714 | 672.307 | 714.0264 | 754.8761 | 751.3961 | 724.2406 | 781.3324 | 824.4526 | 861.5808 | 906.1854 | 959.9456 | 1007.9983 | 1038.8283 | 1087.4346 | 1140.3826 | 1145.9283 | 1195.6334 | 1188.5448 | 1161.8892
CapEx/Depreciation Ratio |  |  |  | 0.65636 | 0.73341 | 0.6428 | 0.59228 | 0.69332 | 0.82175 | 0.52768 | 0.37682 | 0.5284 | 0.71816 | 0.6488 | 0.52673 | 0.71783 | 0.44548 | 0.47349 | 0.64643 | 0.85189 | 0.70429 | 0.87254 | 0.65176 | 0.80684
20-Year Incremental Costs
Carbon Out | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission & Switching Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 24090909.0909 | 265000000
Distribution Substations | 666648.1417 | 1408645.0981 | 2098412.2262 | 2751420.4877 | 3307851.9557 | 3767022.0905 | 12179470.9747 | 13219069.9882 | 14217162.0824 | 15370593.6549 | 16763788.9897 | 18822152.1933 | 20332826.2473 | 21823231.3757 | 22744735.9595 | 23537206.5929 | 23813237.7453 | 24281578.1711 | 24493008.7479 | 25355395.4898 | 25046541.7872 | 316000000
Distribution Substation T-Lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 99000000
Distribution Feeders | 571412.6929 | 1207410.0841 | 1798639.051 | 2358360.4181 | 2835301.6763 | 3228876.0776 | 3871619.9125 | 4202088.4731 | 4519362.7812 | 4886016.5261 | 5328886.5662 | 5983200.6972 | 6463414.966 | 6937186.1327 | 7230114.7421 | 7482025.9368 | 7569770.9389 | 7718647.3656 | 7785857.0854 | 8059993.2683 | 7961814.6078 | 108000000
Total | 1238060.8346 | 2616055.1821 | 3897051.2772 | 5109780.9058 | 6143153.6321 | 6995898.1681 | 16051090.8872 | 17421158.4613 | 18736524.8636 | 20256610.181 | 55183584.6468 | 57896261.9815 | 59887150.3042 | 61851326.5993 | 63065759.7925 | 64110141.6207 | 64473917.7751 | 65091134.6276 | 65369774.9243 | 66506297.849 | 66099265.4859 | 788000000
Running Total | 1238060.8346 | 3854116.0168 | 7751167.294 | 12860948.1998 | 19004101.8319 | 26000000 | 42051090.8872 | 59472249.3485 | 78208774.2121 | 98465384.3931 | 153648969.0399 | 211545231.0214 | 271432381.3256 | 333283707.9249 | 396349467.7174 | 460459609.3381 | 524933527.1132 | 590024661.7408 | 655394436.6651 | 721900734.5141 | 788000000
Carbon Out + Add'l Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission & Switching Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 28272727.2727 | 311000000
Distribution Substations | 1796873.8869 | 3656582.5612 | 5224060.2644 | 6717776.4882 | 8131701.4 | 9473005.3994 | 21607660.4228 | 24202826.4149 | 26788716.2912 | 29458129.086 | 32155886.8915 | 35589067.1312 | 37654417.0529 | 39860642.1795 | 41890402.5265 | 45090159.8629 | 48815464.2764 | 53503679.0912 | 56766566.3429 | 59426847.9508 | 58189534.4793 | 646000000
Distribution Substation T-Lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 9000000 | 99000000
Distribution Feeders and Service Transformers | 7290174.0553 | 14835277.8196 | 21194758.7869 | 27254978.895 | 32991474.2514 | 38433336.1919 | 47671237.725 | 53396743.0562 | 59101783.2414 | 64991093.3027 | 70942938.6739 | 78517287.2223 | 83073902.1068 | 87941318.5892 | 92419415.0666 | 99478781.4979 | 107697620.0403 | 118040850.1063 | 125239494.9758 | 131108659.6361 | 128378874.7595 | 1490000000
Total | 9087047.9422 | 18491860.3808 | 26418819.0512 | 33972755.3832 | 41123175.6513 | 47906341.5913 | 69278898.1478 | 77599569.4711 | 85890499.5325 | 94449222.3887 | 140371552.8382 | 151379081.6262 | 158001046.4324 | 165074688.0414 | 171582544.8658 | 181841668.6336 | 193785811.5894 | 208817256.4702 | 219278788.5914 | 227808234.8596 | 223841136.5115 | 2546000000
Running Total | 9087047.9422 | 27578908.323 | 53997727.3742 | 87970482.7574 | 129093658.4087 | 177000000 | 246278898.1478 | 323878467.6189 | 409768967.1515 | 504218189.5402 | 644589742.3784 | 795968824.0046 | 953969870.437 | 1119044558.4784 | 1290627103.3443 | 1472468771.9778 | 1666254583.5672 | 1875071840.0375 | 2094350628.6289 | 2322158863.4885 | 2546000000
High Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Total
Transmission & Switching Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 45090909.0909 | 496000000
Distribution Substations | 6970295.5438 | 14123706.4044 | 19992896.6602 | 25579562.8968 | 31014662.1861 | 36318876.3087 | 65457317.1626 | 73686155.137 | 81930243.708 | 90270527.2411 | 98521288.4617 | 103713193.1398 | 104536716.3253 | 105967123.8234 | 107241049.9251 | 111933076.5947 | 117520559.5299 | 124985883.8145 | 128099432.8753 | 129594222.7939 | 120543209.4678 | 1698000000
Distribution Substation T-Lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36818181.8182 | 36818181.8182 | 36818181.8182 | 36818181.8182 | 36818181.8182 | 36818181.8182 | 36818181.8182 | 36818181.8182 | 36818181.8182 | 36818181.8182 | 36818181.8182 | 405000000
Distribution Feeders and Service Transformers | 12796214.2072 | 25928595.3395 | 36703377.4509 | 46959496.0644 | 56937364.9087 | 66674952.0293 | 105133491.5041 | 118350141.7545 | 131591286.5694 | 144986933.7786 | 158238795.7901 | 166577711.7437 | 167900403.7143 | 170197835.7061 | 172243936.9641 | 179779979.7991 | 188754249.0659 | 200744590.8836 | 205745380.6796 | 208146219.7304 | 193609042.3165 | 2758000000
Total | 19766509.7509 | 40052301.7439 | 56696274.1112 | 72539058.9612 | 87952027.0948 | 102993828.338 | 170590808.6667 | 192036296.8915 | 213521530.2774 | 235257461.0197 | 338669175.1608 | 352199995.7927 | 354346210.9488 | 358074050.4386 | 361394077.7982 | 373622147.3028 | 388183899.5049 | 407639565.6071 | 415753904.464 | 419649533.4333 | 396061342.6934 | 5357000000
Running Total | 19766509.7509 | 59818811.4948 | 116515085.606 | 189054144.5672 | 277006171.662 | 380000000 | 550590808.6667 | 742627105.5582 | 956148635.8356 | 1191406096.8553 | 1530075272.0161 | 1882275267.8088 | 2236621478.7575 | 2594695529.1962 | 2956089606.9944 | 3329711754.2972 | 3717895653.8022 | 4125535219.4093 | 4541289123.8733 | 4960938657.3066 | 5357000000
20-Year Portfolio with Incremental Decarbonization Costs
Carbon Out | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Transmission | 114.1821 | 133.1975 | 149.6229 | 111.2874 | 117.8081 | 99.5758 | 91.1142 | 191.8742 | 93.1078 | 94.2323 | 128.4249 | 71.3166 | 72.4634 | 960.192 | 961.4086 | 76.1143 | 77.405 | 78.7344 | 80.1037 | 81.5141 | 82.9668
Distribution | 287.0041 | 311.8798 | 353.0718 | 458.4625 | 424.2143 | 410.1331 | 528.8854 | 523.232 | 473.6916 | 547.0454 | 447.4493 | 752.7624 | 759.4173 | 794.3891 | 753.8107 | 748.344 | 754.5405 | 763.2811 | 786.7183 | 799.1904 | 818.5159
Carbon Out + Add'l Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Transmission | 114.1821 | 133.1975 | 149.6229 | 111.2874 | 117.8081 | 99.5758 | 91.1142 | 191.8742 | 93.1078 | 94.2323 | 132.6068 | 75.4984 | 76.6452 | 964.3738 | 965.5904 | 80.2961 | 81.5868 | 82.9162 | 84.2855 | 85.6959 | 87.1486
Distribution | 294.8531 | 327.7556 | 375.5935 | 487.3255 | 459.1943 | 451.0435 | 582.1132 | 583.4104 | 540.8455 | 621.2381 | 528.4554 | 842.0634 | 853.3494 | 893.4306 | 858.1456 | 861.8938 | 879.6706 | 902.8254 | 936.4455 | 956.3105 | 972.076
High Electrification | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Transmission | 114.1821 | 133.1975 | 149.6229 | 111.2874 | 117.8081 | 99.5758 | 91.1142 | 191.8742 | 93.1078 | 94.2323 | 177.2431 | 120.1348 | 121.2816 | 1009.0102 | 1010.2268 | 124.9325 | 126.2232 | 127.5526 | 128.9219 | 130.3323 | 131.785
Distribution | 305.5326 | 349.316 | 405.871 | 525.8918 | 506.0232 | 506.131 | 683.4251 | 697.8471 | 668.4766 | 762.0463 | 682.1167 | 998.2479 | 1005.0582 | 1041.7936 | 1003.3208 | 1009.0379 | 1029.4323 | 1057.0113 | 1088.2842 | 1103.5154 | 1099.6598
Assumptions:
Transmission improvements and transmission needed to support additional distribution substations have been added to the transmission costs.
Disribution substations, feeder improvements and service transformers have been added to the distribution costs.
This is based on feedback from Shuang Wu who said "From my understanding of UI, the capital projects/WBS are not categorized by asset class such as feeder, transformer etc. If it’s a distribution project, there is no split and it’s 100% distribution. "
Distribution substations are assumed to be directly attributed to customer load growth and not to transmission capacity constraints.

## Transmission Summary
Transmission Assumptions:
Assumptions
Study addresses thermal overloads found during analysis of NERC TPL-001-4 P1/P2+/P6 contingencies
summer & winter peak base case used only
no BPA / SCL / neighboring contingencies
steady state powerflow analysis for PSE P1/P2+/P6 contingencies
SCL/SnoPUD/Tacoma incremental loads included
no transportation load growth
no neighbor load growth after 2030 (except for incremental electrification growth)
Load forecast baseline 2030 and 2039 values from F20 load forecast, spread across system
High Electrification - Heavy Winter case for 2040 (Year 20)
Cost incremental assumptions are in 2019 dollars and would use 3%/year escalation rate to reflect future year costs:
Incremental Upgrade Cost of upgrades in 2040 rate
2025 upgrades are assumed to be covered by ongoing initiation projects; baseline costs are anticipated due to normal load growth
Transmission Results:
|  |  | Baseline Upgrades (due to normal load growth) | Electrification Incremental (excluding Baseline) | Year 5 | [15 empty] | Year 20
[5 empty] | S1 (Baseline) |  |  |  | S4 (Carbon + Electrification) |  |  |  | S2 (Carbon) |  |  |  | S3 (High Electrification) |  |  |  | S1 (Baseline) |  |  |  | S4 (Carbon + Electrification) |  |  |  | S2 (Carbon) |  |  |  | S3 (High Electrification)
Notes | Season | County |  |  | Line 115kV (miles) | Line 230kV (miles) | Bulk XFMR (230/115) | Station | Line 115kV (miles) | Line 230kV (miles) | Bulk XFMR (230/115) | Station | Line 115kV (miles) | Line 230kV (miles) | Bulk XFMR (230/115) | Station | Line 115kV (miles) | Line 230kV (miles) | Bulk XFMR (230/115) | Station | Line 115kV (miles) | Line 230kV (miles) | Bulk XFMR (230/115) | Station | Line 115kV (miles) | Line 230kV (miles) | Bulk XFMR (230/115) | Station | Line 115kV (miles) | Line 230kV (miles) | Bulk XFMR (230/115) | Station | Line 115kV (miles) | Line 230kV (miles) | Bulk XFMR (230/115) | Station
Summer (Base) | Both | North King | Yes | no | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | North King | No | Yes
| Winter | North King
| Winter | North King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.72 | 0 | 0 | 0
| Winter | North King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0
| Winter | North King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.38 | 0 | 0 | 0
| Winter | North King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.53 | 0 | 0 | 0
| Winter | North King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 0 | 0 | 0
| Both | South King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
| Winter | South King |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | South King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25
| Winter | South King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
| Winter | South King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0
| Winter | South King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0
Summer (Base) | Both | South King | Yes | no | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer (Base) | Both | South King | Yes | no | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | South King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7 | 0 | 0 | 0
| Winter | South King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0
| Both | South King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 0 | 0 | 0 | 8.4 | 0 | 0 | 0 | 8.4 | 0 | 0 | 0
| Both | South King | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.077 | 0 | 0 | 0 | 3.077 | 0 | 0 | 0 | 3.077 | 0 | 0 | 0
| Both | Pierce | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 1 | 0
| Winter | Pierce |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | Pierce | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0
| Winter | Pierce |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0
| Both | Pierce | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.2 | 0 | 0 | 1 | 13.2 | 0 | 0 | 1 | 13.2 | 0 | 0 | 1
| Both | Pierce
| Both | Pierce
Summer (Base) | Both | Pierce | Yes | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer (Base) | Both | Pierce | Yes | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Both (Elec) | Both | Pierce | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0
Summer (Base) | Both | Pierce | Yes | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Summer | Pierce | Yes | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | Pierce | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 0
| Winter | Pierce | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0
| Winter | Pierce | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0 | 0 | 0
| Summer | Pierce | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0
| Summer | Pierce | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.462 | 0 | 1.7 | 1 | 14.462 | 0 | 1.7 | 1 | 14.462 | 0 | 1.7 | 1
Winter (Elec), Summer (Base) | Both | Thurston | Yes | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Thurston
Thurston
Thurston
| Winter | Thurston | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0
| Winter | Thurston | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0
| Both | Thurston | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.823 | 0 | 0 | 0 | 1.823 | 0 | 0 | 0 | 1.823 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.193 | 1 | 2 | 0 | 52.882 | 3.2 | 4.7 | 2.25 | 46.462 | 2 | 3.7 | 2 | 94.162 | 4.2 | 5.7 | 2.25
[9 empty] | Year 5 | [18 empty] | Year 20
[10 empty] | Line 115kV (per mile) | Line 230kV (per mile) | Bulk XFMR | Switching Station | Total (in Millions) | [13 empty] | Summer/Winter | Line 115kV (per mile) | Line 230kV (per mile) | Bulk XFMR | Switching Station | Total (in Millions)
[9 empty] | 2025 Unit Cost (in Millions) | 4.7762 | 7.1643 | 9.5524 | 17.9108 | [14 empty] | 2040 Unit Cost (in Millions) | 2.667 | 4 | 5.33 | 10
[9 empty] | S1 (Baseline) | 0 | 0 | 0 | 0 | 0 | [13 empty] | S1 (Baseline) | 64.5227 | 4 | 10.66 | 0 | 79.1827
[9 empty] | S4 (Car + Elec) | 0 | 0 | 0 | 0 | 0 | [13 empty] | S4 (Car + Elec) | 141.0363 | 12.8 | 25.051 | 22.5 | 201.3873
[9 empty] | S2 (Carbon) | 0 | 0 | 0 | 0 | 0 | [13 empty] | S2 (Carbon) | 123.9142 | 8 | 19.721 | 20 | 171.6352
[9 empty] | S3 (High Elec) | 0 | 0 | 0 | 0 | 0 | [13 empty] | S3 (High Elec) | 251.1301 | 16.8 | 30.381 | 22.5 | 320.8111
[28 empty] | 2020 Planning | 4 | 6 | 8 | 15
[28 empty] | 2020 Base | 2.667 | 4 | 5.33 | 10
[28 empty] | 2020 Contingency | 49.98% | 50% | 50.09% | 50%
Year 20 Transmission Line Count
[29 empty] | 115 kV | 230 kV
[28 empty] | S4 (Car + Elec) | 11 | 3
[28 empty] | S2 (Carbon) | 9 | 1
[28 empty] | S3 (High Elec) | 28 | 4

## Substation Transmission Summary
Substation transmission:
Substation Transmission Assumptions:
2040
|  |  |  | S1 (Baseline) |  | S2 (Carbon) |  | S4 (Car + Elec) |  | S3 (High Elec) |  | 115kV and 55kV lines only (i.e. no new distribution substations connected at 230 kV)
Region | Line | Baseline | Incremental | New Line | Switching Station | New Line | Switching Station | New Line | Switching Station | New Line | Switching Station | No Radial Lines - All substations will have two sources
N King | Lake Tradition - Sahalee | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | No Gen Lead Lines
N King | Sammamish - Ardmore | No | Yes | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | Maximum: Six XFMRs per line (6x25MVA=150MVA) per the Transmission Planning Guidelines
N King | Sammamish - Lochleven | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | No Lines connecting to a single industrial customer
N King | Sammamish - Moorlands #1 | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | The mileage for new lines is the average for the region
N King | Sammamish - N Bellevue | Yes | No | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Costs were assumed to be $6M/mile for 115 kV assuming that these are all greenfield lines and based on costs for SAM-JUA and LHL-PHA projects
North King Total: |  |  |  | 8.1731 | 0 | 8.1731 | 0 | 8.1731 | 0 | 32.6923 | 1
S King | Christopher - Starwood | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | Region | Average Line Length
South King Total: |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 10.9047 | 1 | Whatcom | 11.9824
Skagit | Sedro Woolley - Fredonia | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Skagit | 13.7923
Skagit | Sedro Woolley - March Point #3 | No | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | North King | 8.1731
Skagit Total: |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 27.5846 | 1 | South King | 10.9047
Whatcom | Terrell - Bellingham #1 | No | Yes | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | Kittitas | 20.6797
Whatcom Total: |  |  |  | 0 | 0 | 11.9824 | 1 | 11.9824 | 1 | 11.9824 | 1 | Pierce | 13.8799
|  |  | Total: | 8.1731 | 0 | 20.1554 | 1 | 20.1554 | 1 | 83.164 | 4 | Thurston | 8.7336
[12 empty] | Kitsap | 13.3571
|  |  |  | Year 20 | [7 empty] | System | 11.5
[5 empty] | Line 115kV (per mile) | Switching Station | Total (in Millions) | New Lines | New Switching Stations
|  |  |  | 2040 Unit Cost (in Millions) | 7.4412 | 27.9044
|  |  |  | S1 (Baseline) | 60.8173 | 0 | 60.8173 | 1 | 0
|  |  |  | S4 (Car + Elec) | 149.9803 | 27.9044 | 177.8847 | 2 | 1
|  |  |  | S2 (Carbon) | 149.9803 | 27.9044 | 177.8847 | 2 | 1
|  |  |  | S3 (High Elec) | 618.838 | 111.6177 | 730.4557 | 8 | 4
2020 Dollars
[5 empty] | Line 115kV (per mile) | Switching Station | Total (in Millions) | New Lines | New Switching Stations
|  |  |  | 2040 Unit Cost (in Millions) | 6 | 15
|  |  |  | S1 (Baseline) | 60.8173 | 0 | 60.8173 | 1 | 0
|  |  |  | S4 (Car + Elec) | 120.9327 | 15 | 135.9327 | 2 | 1
|  |  |  | S2 (Carbon) | 120.9327 | 15 | 135.9327 | 2 | 1
|  |  |  | S3 (High Elec) | 498.9838 | 60 | 558.9838 | 8 | 4

## Dist Transformer Summary
Distribution Transformer/Substation Assumptions:
Method:
1. Model existing PSE distribution system, with SCUBA tool, and apply 2020 load forecast to establish baseline electrical demand and distribution transformer system needs for 2020, 2025, and 2040.
2. Determine existing individual substation bank loading % compared to a total county electrical demand
3. Add appropriate % demand associated with potential gas to electric conversion (de-carbonization) to the baseline load to determine overloaded substation transformers 2020, 2025, and 2040.
4. Determine delta between overloaded distribution transformer banks due to natural load growth vs. de-carbonization.
5. Adjust final vales with 100% additional planning cost to account for land purchase, permitting, and ROW work.
Assumptions:
1. If the existing single banked substation is overloaded, a second bank is added to the existing substation.
2. If the existing multiple-banked distribution substation is overloaded, an additional substation is added to the overall cost.
3. Addition of (1) distribution substation bank to existing substation assumed $9.35M
a. Materials:
i. Distribution transformer $0.75M
ii. Metalclad gear $0.75M
iii. Control house $0.5M
iv. Getaway feeders $1M
v. Transmission bus $1M:
1. Dead ends
2. Switches
3. 115kV bus
vi. Transmission loop $1.5M:
1. (1) mile of 115kV transmission
b. Labor (assumed 70% of the material cost at $3.85M)
i. Construction
ii. Engineering
iii. Project management
4. The cost associated with building a new distribution substation assumed $14.5M
Additional costs are associated with a greenfield site which includes property acquisition, civil work, etc. These are captured in the 50% contingency added to the costs above.
Total Cost due to De-carbonization | 2020 |  |  | 2025 |  |  | 2040
| # of Subs | $M | +50% | # of Subs | $M | +50% | # of Subs | $M | +50%
Carbon Out | 3 | 33 | 50 | 1 | 9 | 14 | 20 | 210 | 302 | 10.5 | 9
Carbon Out + Add'l Electrification | 4 | 42 | 63 | 2 | 23 | 35 | 41 | 430 | 611 | 10.4878 | 11.5
High Electrification | 4 | 47 | 71 | 9 | 89 | 134 | 107 | 1131 | 1564 | 10.5701 | 9.8889

## Distribution Assumptions
DISTRIBUTION FEEDERS - ASSUMPTIONS
Feeders that reach 400A with forecasted loads will require new construction equal to 3 miles of feeder.
Expected feeder loading is based on the forecast data provided (E3 Data) for the County level.
County load growth due to electrification is assumed to be evenly spread across the circuits in each county for the purposes of this estimate.
Feeders that are associated with anticipated substation needs are not counted in the feeder section. They have been accounted for with the substation estimates.
Feeder costs vary widely. For this analysis, the average cost was assumed to equal the cost of an underground feeder classified as "difficult" to construct (see Distribution System Data tab for feeder cost information)
DISTRIBUTION FEEDERS - METHODS
Circuit Data is from CAR (Circuits at Risk) planning tool spreadsheet.
Load growth is extracted from E3 Data (See E3 Data tab)
For each growth scenario, the circuits with a loading level that exceeds a threshold that can accommodate the growth level is identified and these are the circuits that are counted (subtracting out those which have already been identified with a substation project).
SERVICE TRANSFORMERS - ASSUMPTIONS
Conversion by customers of SPACE HEAT will drive need for service transformer upgrades. Space heat conversion was present in the Carbon Out + Additional Electric and High Electrification scenarios.
Residential transformers usually serve more than one customer and can serve many customers. Assumed that for every 5 customer conversions, 1 transformer upgrade would be required.
Cost of underground or overhead residential transformer upgrade is assumed to be the same.
Commercial transformers vary widely in with # of customers served and cost to upgrade due to wide range of transformer sizes that serve commercial customers. For this analysis, it was assumed for every 2 commercial space heat conversions, 1 transformer upgrade would be required.
Cost of commercial transformer assumed to = average of lowest and highest transformer costs.
SERVICE TRANSFORMERS - METHODS
2021 REGIONAL PLANNING BUDGET TOOL (spreadsheet tool) used for transformer upgrade cost estimates.
Estimated # of customers converting SH in 2025 and 2040 by extrapolating from E3 Data: Scenarios identify space heat conversion levels as a percentage of customers for 2030.
Cascade Natural Gas customer counts in PSE Electric Counties are not provided in the E3 Data, so this was further estimated using load data.
NET NEW FEEDER COUNT - 2020 dollars
| 2021-2025 |  |  | 2026-2040
| CO | CO+E | HE | CO | CO+E | HE | Transformer Upgrade Cost (each) - $M
King | 0 | 0 | 3 | 7 | 28 | 0 | 2020 dollars | 0.0135
Pierce | 2 | 3 | 5 | 3 | 0 | 0 | 2025 dollars | 0.01565
Skagit | 0 | 0 | 1 | 1 | 0 | 0 | 2040 dollars | 0.024383
Kitsap | 0 | 1 | 2 | 2 | 0 | 0
Whatcom | 0 | 0 | 0 | 1 | 1 | 0
Kittitas | 0 | 0 | 0 | 0 | 0 | 0
Thurston | 0 | 0 | 0 | 2 | 7 | 19
TOTAL | 2 | 4 | 11 | 16 | 36 | 19
COST $M | 12 | 24 | 66 | 96 | 216 | 114
| 2020 DOLLARS |  |  | 2020 DOLLARS
UPGRADED RESIDENTIAL TRANSFORMER COUNT - 2020 dollars
| 2021-2025 |  |  | 2026-2040
| CO | CO+E | HE | CO | CO+E | HE
King | 0 | 3514.3791 | 5372.6107 | 0 | 32421.236 | 38908.0988
Kittitas | 0 | 17.9678 | 27.4006 | 0 | 165.7582 | 198.4332
Pierce | 0 | 763.8225 | 1167.6944 | 0 | 7046.499 | 8456.3672
Thurston | 0 | 624.7135 | 955.0314 | 0 | 5763.1754 | 6916.2754
Whatcom | 0 | 424.0384 | 648.2492 | 0 | 3911.8859 | 4694.5786
Skagit | 0 | 379.0647 | 579.4955 | 0 | 3496.9889 | 4196.6688
Kitsap | 0 | 301.9668 | 461.632 | 0 | 2785.7369 | 3343.109
TOTAL | 0 | 6025.9526 | 9212.1137 | 0 | 55591.2802 | 66713.5312
COST $M | 0 | -81.3504 | 124.3635 | 0 | 750.4823 | 900.6327
| 2020 DOLLARS |  |  | 2020 DOLLARS
|  | 2025 $$ |  |  | 2040 $$
|  | 94.3074 | 0 |  | 18.2986 | 1626.6428

## Overall Summary
Existing System Summary | Number of Assets (Full PSE Ownership) | Number of Assets (Partial PSE Ownership) | Miles of Assets (PSE Owned)
55 kV Transmission | 4 | 0 | 78
115 kV Transmission | 179 | 6 | 1691
230 kV Transmission | 19 | 10 | 366
Total Transmission* | 202 | 16 | 2135
Bulk 230/115 kV Transformers | 19
Transmission Switching Stations | 39
Distribution Substation Transformers | 320
*Excludes Colstrip transmission
**Does not account for system elements that may be added through projects that are already in the planning stage.
System Upgrade Summary | 2020-2025 |  |  | 2026-2040 |  |  | Total
| Carbon Out | Carbon Out + Add'l Electrification | High Electrification | Carbon Out | Carbon Out + Add'l Electrification | High Electrification | Carbon Out | Carbon Out + Add'l Electrification | High Electrification
115 kV Transmission (incl. substation transmission) | 0 mi | 0 mi | 0 mi | 66.7 mi | 73.1 mi | 177.4 mi | 66.7 mi | 73.1 mi | 177.4 mi
230 kV Transmission | 0 mi | 0 mi | 0 mi | 2 mi | 3.2 mi | 4.2 mi | 2 mi | 3.2 mi | 4.2 mi
Bulk 230/115 kV Transformers1 | 0 | 0 | 0 | 3.7 | 4.7 | 5.7 | 3.7 | 4.7 | 5.7
Transmission Switching Stations2 | 0 | 0 | 0 | 3 | 3.25 | 6.25 | 3 | 3.25 | 6.25
Distribution Substation Transformers | 1 | 2 | 9 | 20 | 41 | 107 | 21 | 43 | 116
Distribution Feeder | 6 mi | 12 mi | 33 mi | 48 mi | 108 mi | 57 mi | 54 mi | 120 mi | 90 mi
Distribution Service Transformers | 0 | 6, 026 | 9212 | 0 | 55591 | 66714 |  | 61617 | 75926
1 Fractions represent substation being converted from one voltage to another (i.e. conversion of 55 kV to 115 kV), which would be a fraction of the cost of a new switching substation.
2 Considers both the addition of new switching stations as well as major reconfiguration of existing switching stations, which would be a fraction of the cost of a new switching station
The 2025 column represents
Year 20 New Transmission Line Count | 115 kV | 230 kV
S2 (Carbon) | 9 | 1
S4 (Car + Elec) | 11 | 3
S3 (High Elec) | 28 | 4