- Washington Utilities and Transportation Commission

- Intrastate Gas Distribution

- Inspection Guide and Report

Puget Sound Energy

PG-050331

Pipeline Company Name 							Docket#

Jim Hogan

99

- Pipeline Company Contact        	                                                                              Operator ID#

PO Box 90868, EST-07W

983

- Address							                          Facility Insp.#

Bellevue, WA 98009-0868

- City

(425) 462-3748

(425) 462-3770

Telephone  		                  	           Fax

# Pipeline Inspection Facility (Unit):

Pierce County

Name

Same

- Address

- City

- Telephone					Fax

- Operator Representative

Don Hunt, Compliance Coordinator Standards & Compliance

- Name and Title

Persons Interviewed/Title

- WUTC Representative

Scott Rukke, Pipeline Safety Engineer

- Name and Title

Inspection Dates

Various dates October 2005 thru June 2006

2004

- Date of Last Inspection

- Pipeline System Operations

Age (Range)                                                            Size (Range)

Early 1900’s to Present

½-inch thru 16-inch

Unaccounted for Gas?                                               Number of Services

Approx. 0.78%

Approx. 740,000

Material Type                                                         Specifications

See annual report

Various

Approx. 11,200

Various up to 19.5%

Miles of Pipeline                                                     % of SMYS

Williams – Northwest Pipeline

Gas Transportation Company

Class 1- 4

Pipeline Class locations

No

Any transmission pipelines in this unit?

Approx. 2,500

Number of Deferred Leaks

Reporting Procedures

1.	Are there procedures to gather data for incident reporting? 	                 __yes___________________________________________

- Telephonic notice of certain incidents within two hours for Federal reports? 191.5, 192.605(b)(4), six hours for Commission reports associated with certain accidents, incidents, or hazardous conditions? WAC 480-93-200(1)

____yes__2425.1100________________________________

- Submitting follow-up written report within 30 days? 191.9(a), 192.605(b)(4), WAC 480-93-200(2)(a-g)

___yes 2425.1100 ___________________________________

- Supplemental reports (to the follow-up report)? 191.15(b), 192.605(b)(4)

___ yes 2425.1100 ___________________________________

- Updated emergency contact list filed with the Commission and all municipalities

where gas companies have facilities? When changes occur, is notification immediate? WAC 480-93-200(4)

___ yes 2425.1100 ___________________________________

2.	Procedures for reporting safety-related conditions?  191.23, 192.605(a)

____ yes 2425.1200 _________________________________

3.	Safety related condition reports filed within 5 days of determination, but not later than 10 days from discovery?  191.25, 192.605(a)

___ yes 2425.1200 __________________________________

4.	Procedures for instructing personnel in operations and maintenance to recognize Safety Related Conditions? 192.605(d)

____ yes 2425.1200 _________________________________

5.	Procedures for pipeline and system pressure reports when: WAC 480-93-20, 480-93-30, 480-93-183

  - A pipeline or system pressure exceeds the established MAOP? Including Commission notification within six hours, followed by a written explanation within thirty days.  WAC 480-93-183(1)

__ yes 2425.1100 _____________________________________

6.	Annual report submitted no later than March 15? 191.11, WAC 480-93-200

___ yes 2425.1100 ____________________________________

7.	Has the operator notified each customer (not later than August 14, 1996, or 90 days after the customer first receives gas at a particular location) of potential hazards as listed in the rule? 192.16, 192.13(c)

_yes_2425.1900_____________________________________

8.	Has the operator established procedures to require notification to customers that the installation of an excess flow valve is available to customers that have a new natural gas service line installed or a service line replaced, provided that the customer bears the cost of the installation?  CFR 192.383,

__yes 2550.1600_____________________________________

a.	Does the excess flow valve meet the performance standards prescribed under Section CFR 192.381?

__yes______________________________________

Normal Operating Procedures

9.	Is the procedure manual reviewed and updated annually not exceeding 15 months, and at least once each calendar year? 192.605(a)

__yes 2425.1000______________________________________

10.	Are appropriate parts of the manual kept at locations where operations and maintenance activities are conducted? 192.605(a)

___ yes 2425.1000_____________________________________

11.	Construction records, maps, and operating history made available to appropriate operating personnel? 192.605(b)(3)

__yes 2500.0500______________________________________

12.	Starting up and shutting down any part of the pipeline in a manner designed to assure operation within the MAOP?  192.605(b)(5)

__yes ______________________________________

13.	Periodically reviewing the work done by Pipeline Company personnel to determine the effectiveness and adequacy of the procedures used in normal operation and maintenance and modifying the procedure when deficiencies are found? 192.605(b)(8)

__yes 2425.1800______________________________________

14.	Take adequate precautions in excavated trenches to protect personnel from the hazards of unsafe accumulations of vapors or gas and making available emergency rescue equipment including breathing apparatus, a rescue harness, and line? 192.605(b)(9)

__yes 0100.3100______________________________________

15.	Systematic and routine testing and inspection of pipe-type or bottle-type holders? 192.605(b)(10)(i-iii)

__n/a______________________________________

16.	Responding promptly to a report of a gas odor inside or near a building, unless specifically addressed under the operators emergency procedures under 192.615(a)(3). 192.605(b)(11)

_yes 2475.1100_________________________________

Transmission Lines-Abnormal Operating Procedures

17.	Are there procedures for responding to, investigating, and correcting the cause of: 192.605(c)(1)

- Unintended closure of valves or shutdowns? 192.605(c)(1)(i)

_____n/a______________________________

- Increase or decrease in pressure or flow rate outside of normal operating limits? 192.605(c)(1)(ii)

___n/a________________________________

- Lose of communications? 192.605(c)(1)(iii)

____n/a_______________________________

- The operation of any safety device? 192.605(c)(1)(iv)

___n/a________________________________

- Any other foreseeable malfunction of a component, deviation from normal operation, or personnel error, which may result in a hazard to persons or property. 192.605(c)(1)(v)

___n/a________________________________

- Checking variations from normal operation after abnormal operation has ended at sufficient critical locations in the system to determine continued integrity and safe operation? 192.605(c)(2)

____n/a_________________________________

19.	Notifying responsible operator personnel when notice of an abnormal operation is received? 192.605(c)(3)

___n/a__________________________________

20.	Periodically reviewing the response of operating personnel to determine the effectiveness of the procedures and taking corrective action where deficiencies are found. 192.605(c)(4)

___n/a__________________________________

Change In Class Location Procedures

21.	Are there procedures in place for determining change in class location? Date last study was completed? 192.605(a), 192.609

__n/a___________________________________

22.	Was there a confirmation or revision of the MAOP? If yes, was it completed within 18 months of the change in the class location? 192.605(a), 192.611

__n/a___________________________________

Continuing Surveillance Procedures

23.	Are there procedures for the continuing surveillance of the operator’s facilities? 192.613(a)

- Change in class location?

__n/a in Pierce unit_____________________________________

- Failures?

__yes 2575.2700  and 2575.1900_____________________________________

- Leakage History?

___yes____2575.2700________________________________

- Corrosion?

__yes 2575.2700_____________________________________

- Substantial changes in cathodic protection requirements?

_yes 2575.2700______________________________________

- Any other unusual operating and maintenance conditions?

_yes 2575.2700_____________________________________

24.	If a segment of pipeline is in unsatisfactory condition, is a program initiated to re-condition or retire the segment involved? If not, was the MAOP of the segment reduced? 192.613(b)

__yes 2575.2700___________________________________

Damage Prevention Program Procedures

25.	Does the company have a written program for the prevention of damage to pipeline facilities due to excavation activities? Does it belong to a qualified one-call system? 192.605(a), 192.614, WAC 480-93-190

____yes 2525.1600_________________________________

26.	Does the damage prevention program at the minimum:

- Identify persons who normally engage in excavating activities? 192.614(c)(1)

____yes_____________________________________

- Provide for the notification of the public and persons engaged in excavating activities as often as needed to make them aware of the damage prevention program? 192.614(c)(2)

____yes_____________________________________

- Provide a means for receiving and recording notifications of planned excavations? 192.614(c)(3)

____yes_____________________________________

- Provide notification to excavators on the type of temporary markings to be provided and how to identify the markings? 192.614(c)(4)

___yes______________________________________

- Provide for a means of temporarily marking the pipeline in the area of the excavation activity? 192.614(c)(5)

______yes___________________________________

- Provide for a follow-up inspection when there is reason to believe the pipeline could be damaged? 192.614(c)(6)

_____yes____________________________________

- Is it done as frequently as necessary to verify the integrity of the pipeline? 192.614(c)(6)(i)

_______yes__________________________________

- After blasting, is a leak survey conducted as part of the inspection? 192.614(c)(6)(ii)

____yes 2625.1100_____________________________________

Best Practices: Damage Prevention

Questions i thru o not required if answered/noted during a previous inspection and answers have not changed.

- Has the operator reviewed the “Common Ground” Study of One-Call Systems and Damage Prevention Best Practices?

Yes/No____no_____________________________

- Common Ground (CG) – Best Practice - Does the operator’s damage prevention program include actions to protect their facilities when directional drilling or boring operations are conducted in proximity to the facilities?

Yes/No___no______________________________

- CG - Best Practice - Are trained/qualified personnel used for pipeline locating & marking?  Is a third party contractor used for locating? What does their training consist of? How is quality control ensured when using a third party locating service?

Yes/No___no______________________________

- CG – Best Practice - Does the operator’s damage prevention program include pro-active liaison with public construction project and land-use officials, engineers, and contractors?

Yes/No____no_____________________________

- CG – Best Practice - Does the operator’s damage prevention program include pro-active liaison with local school officials, where the pipeline traverses or is adjacent to school property?

Yes/No___no______________________________

- CG – Best Practice - Has the operator implemented any of the best practices in addition to their existing damage prevention activities a result of reviewing the Common Ground Study?

Yes/No___no______________________________

- CG – Best Practice - Has the operator improved communication with other stakeholders in damage prevention as a result of best practices?

Yes/No__no_______________________________

Emergency Procedures

27.	Does the pipeline company have a written Emergency Plan to minimize the hazard resulting from a gas pipeline emergency? 192.615

___yes 2575.1600 references ERP plan__________________________________

28.	At a minimum does the manual contain provisions for:

a.	Receiving, identifying, and classifying notices of events, which require immediate response by the Pipeline Company? 192.615(a)(1)

__ yes 2575.1600 ______________________________________

b.	Establishing and maintaining adequate means of communication with appropriate fire, police and other public officials? 192.615(a)(2)

___ yes 2575.1600 _____________________________________

c.	Gas detected inside or near a building? 192.615(a)(3)(i)

__ yes 2575.1600 ______________________________________

d.	Fire located near or directly involving a pipeline facility? 192.615(a)(3)(ii)

__ yes 2575.1600 _______________________________________

e.	Explosion occurring near or directly involving a pipeline facility? 192.615(a)(3)(iii)

__ yes 2575.1600 _______________________________________

f.	Natural disaster? 192.615(a)(3)(iv)

__ yes 2575.1600 _______________________________________

g.	Availability of personnel, equipment, tools and materials as needed at the scene of an emergency? 192.615(a)(4)

___ yes 2575.1600 ______________________________________

h.	The actions directed toward protecting people first and then property? 192.615(a)(5)

__ yes 2575.1600 _______________________________________

i.	Emergency shutdown and pressure reduction in any section of the company’s pipeline system necessary to minimize hazards to life or property? 192.615(a)(6)

__ yes 2575.1400 _______________________________________

j.	Investigating and rendering safe any actual or potential hazard to life and property? 192.615(a)(7)

__ yes 2575.1600 _______________________________________

k.	Direction for notification of other public officials of gas pipeline emergencies and coordinating with them both planned responses and actual responses during an emergency? 192.615(a)(8)

__yes_______________________________________

- Safely restoring any service outages after the emergency has been rendered safe? 192.615(a)(9)

___yes______________________________________

m.	Begin action under 192.617 for analyzing failures as soon as possible after emergencies? 192.615(a)(10)

___ yes 2575.1900 ______________________________________

29.	Does the operator:

a.	Furnish its supervisors who are responsible for emergency action a copy of that portion of the latest edition of the emergency procedures as necessary for compliance with those procedures? 192.615(b)(1)

__yes_______________________________________

b.	Have written procedures to train the appropriate operating personnel to assure that they are knowledgeable of the emergency procedures and verify that the training is effective? 192.615(b)(2)

__yes_______________________________________

c.	Review employee activities to determine whether the procedures are effectively followed in each emergency? 192.615(b)(3)

__yes_______________________________________

30.	Does the operator establish and maintain liaisons with appropriate fire, police and other public officials to: 192.615(c)

a.	(c)(1) Learn the responsibilities and resources of each government organization that may respond to a gas pipeline emergency?

__yes_______________________________________

- (c)(2) Acquaint the officials with the operator’s ability in responding to a gas pipeline emergency?

__yes_______________________________________

c.	(c)(3) Identified the types of gas pipeline emergencies of which the operator notifies the officials?

___yes______________________________________

d.	(c)(4) Plan how the operator and officials can engage in mutual assistance to minimize hazards to life or property?

___yes______________________________________

Public Education Procedures

31.	Does the operator have a continuing education program (in English and other pertinent languages) that informs the public in how to recognize and report a gas pipeline emergency? 192.605(a), 192.616

___yes 2425.1500____________________________________

Failure Investigation Procedures

32.	Does the operator have written procedures for analyzing accidents and failures where appropriate to determine cause and prevention of recurrence? 192.617

__yes 2575.1900_____________________________________

MAOP Procedures

33.	Has the MAOP been established for each pipeline? 192.605(a) 192.619

___No ___ PSE has a distribution system in the Tacoma tideflats industrial area that has a 	maximum allowable operating pressure (MAOP) that PSE indicated was 100 psig.

PSE procedure 6.14, section 6.2, dated 04/07/1997, requires each steel service line less than 2-inches in diameter, and installed from mains designed to operate above 60 psig to be tested to 450 psig.

Records indicate that a 1-inch steel service line at 2000 Taylor Way, Tacoma was tested 	to 96 psig and not 450 psig as required. This service was installed in 1998.                     	In addition to not meeting the requirements of PSE’s procedure manual, this service line 	cannot have a 100 psig MAOP due to the requirements of 49 CFR §192.619(a)(2)(ii).  	The MAOP of this distribution system cannot exceed 99 psig.

34.	How was the MAOP determined?

a.	Design and test criteria? 192.619(a)(1-4), 192.605(a)

_2425.3300_________________________________________

Or

b.	By the highest actual operating pressure to which the line was subjected between July 1, 1965 and July 1 1970? 192.619(c), 192.605(a)

__2525.1400________________________________________

35.	Does the pipeline company request commission approval at least 30 days prior to a planned increase in the previously established MAOP? WAC 480-93-155

_yes_2575.2500_____________________________________

Pressure Testing Procedures

36.	Does the pipeline company have general leak and strength testing procedures? 192.13(c), 192.503

__yes 2525.3300_____________________________________

37.	If applicable, does the company have strength test procedures for pipelines that operate at a hoop stress of 30% or more of SMYS? 192.505(a)

___yes 2525.3300______________________________

38.	If applicable, does the company have leak test procedures for pipelines that are to be operated at a hoop stress less than 30% SMYS and at or above 100 psig? 192.507(b)

__yes 2525.3300______________________________________

Odorization of Gas Procedures

39.	Is all gas being transported and used by an end use customer odorized? If not, does the pipeline company have prior written approval from the commission not to odorize?

WAC 480-93-015

__yes 2650.1000______________________________________

40.	Does the Pipeline Company conduct periodic samplings to insure proper concentrations of odorant? 192.625(f), 192.605(a)

__yes______________________________________

41.	Is the odorant detectable at 1/5 LEL (1% gas or less)? 192.625(a), 192.605(a)

__yes______________________________________

Tapping Pipelines Under Pressure Procedures

42.	Does the company have procedures for tapping pipelines under pressure? Are crews conducting taps qualified? 192.605(a), 192.627

__yes 2700.1000______________________________________

Pipeline Purging Procedures

43.	Does the pipeline company have procedures for purging pipelines of both air and gas? 192.605(a), 192.629

___yes 2525.3400_____________________________________

Maintenance Procedures

44.	Is each segment that becomes unsafe replaced, repaired, or removed from service? 192.605(a), 192.703(b)

__yes 2575.2700______________________________________

45.	Are hazardous leaks repaired promptly? 192.703(c)

_yes 2625.1200 and 1300_______________________________________

Patrolling Procedures

46.	Does the pipeline company have a patrol program for observing surface conditions on and adjacent to transmission line right-of-way, including frequency of patrols and methods used for traversing the right-of-way? 192.705(a)(b)(c), 192.605(b)(1)

__n/a______________________________________

47.	Does the Pipeline Company designate personnel who are responsible for pipeline and service line patrolling? WAC 480-93-184

_n/a due to rule change_______________________________________

48.	Procedures for Distribution Patrolling?  (192.605(b)

a.	Have patrolling areas been identified? 192.721,

_yes 2575.3100_________________________________

b.	Have mains located in business districts been patrolled at intervals not exceeding 4½ months but at least 4 times each calendar year where anticipated physical movement or external loading could cause failure or leakage? 192.721(b)(1)

__yes________________________________

c.	Have mains located outside business districts been patrolled at intervals not exceeding 7½ months but at least twice each calendar year where anticipated physical movement or external loading could cause failure or leakage?  192.721(b)(2)

__yes________________________________

Leakage Survey Procedures

49.       Does the operator have non-odorized natural gas transmission lines? CFR 192.706, 192.605(b)

__n/a___________________________

a.	Is the operator in compliance with WAC 480-93-015?

__n/a________________________________________

b.	Are leak surveys using a gas detector conducted in class 3 locations, at intervals not exceeding 7½ months, but at least twice each calendar year? 192.706(a)

_n/a_________________________________________

c.	Are leak surveys using a gas detector conducted in class 4 locations not exceeding 4½ months, but at least four times each calendar year?  192.706(b)

__n/a________________________________________

50.       Procedures for Leakage Surveys? CFR 192.723, 192.605(b), WAC 480-93-188

______yes 2625.1100___________________________________

a.	Have business district areas been defined and identified?

____ yes 2625.1100______________________________________

b.	Have gas detector surveys been conducted in the business districts at intervals not exceeding 15 months, but at least once each calendar year? 192.723(b)(1)

___yes_______________________________________

c.	Have leakage surveys of the distribution system outside of the principal business areas been conducted as frequently as necessary, but at intervals not exceeding five years? 192.723(b)(2)

__no

Finding(s):

- PSE leak survey contractor, Heath Consultants, conducted residential leak

surveys in a development known as Crystal Ridge in Puyallup, OP map number 248.074.  Records indicate that the mains in the development were surveyed starting on 02/06/2003 by mobile flame ionization equipment and that the services were surveyed between the dates of 02/24/2003 and 04/19/2003 by portable walking flame ionization equipment. Records do not show that the main was walked with portable flame ionization equipment but PSE personnel indicated that it was. PSE personnel also stated that not all of the main would have been walked with portable equipment but that most of it would have because the survey technician leaves the equipment on while walking between services.

WAC 480-93-188 requires that leak surveys be conducted “over” all mains and services. The main in this development is in a joint trench easement located in the front yards of the residences approximately 15 to 20 feet from the paved street where the mobile leak survey was conducted. Between the main and the street is a curb, grass strip, sidewalk and more grass. A mobile survey can’t be conducted over the main as required because the main is approximately 15 to 20-feet from the street.

b)	919 Valley Ave, Puyallup (11105 Valley Ave) PSE provided several maps indicating what was leak surveyed at this address. The maps indicate that portions of the main serving this address were thought to be in a different location and were not leak surveyed as required.

c)	PSE has a rooftop service to Spinning Elementary located at 1306 E. Pioneer Ave. in Puyallup. PSE was unable to provide documentation showing that the service has been leak surveyed on an annual basis as required for high occupancy structures.

________________________________________

d.        	Have leakage surveys of cast iron, wrought iron, ductile iron, or non-cathodically protected steel pipe been conducted at intervals not exceeding eight months, but at least twice each calendar year? WAC 480-93-188(e)

__________________________________________

51.	Procedures for investigated promptly the notification of any leak, explosion or fire that may involve a gas pipeline? WAC 480-93-185

__yes 2425.1400 and 2475.1100_______________________________________

  - For taking appropriate action to protect life and property when leak indications are found to originate from a foreign source? WAC 480-93-185

__yes 2625.1200________________________________________

b.	For the proper notification of the property owner or adult person occupying the premises, providing of odor sniff cards, and notification by mail within 24hrs if an adult is unavailable the results of the leak investigation? WAC 480-93-185

__yes 2625.1300________________________________________

c.	For the retention and maintenance of letters, reports (including name of gas company employee), and files associated with all leak investigated?  WAC 480-93-185

__ yes 2625.1300________________________________________

52.	Are leaks classified by grade as required and action criteria established? Are there provisions for conducting follow-up inspections for residual gas after a leak repair? WAC 480-93-186

__ not reviewed due to impending leak investigation__________________________________

53.	Procedures for preparing and maintaining permanent gas leak repair records including the gathering and recording of data and information required under WAC 480-93-187?

not reviewed due to impending leak investigation __________________________________

54.	Has a program been established and self audits conducted, which demonstrate the effectiveness of the leak repair program? Do audits evaluate repair scheduling, repair effectiveness, and adequacy of leak survey records?  WAC 480-93-187

___ not reviewed due to impending leak investigation _________________________________

55.	Has the operator provided for calibration and maintenance of leak detection instruments? WAC 480-93-188(2)

__missed numerous instruments

Finding(s):

The following instruments were not calibrated according to the schedule outlined in PSE’s procedure manual, procedure 2450.1600.

Note:  PSE procedure 2450.1600 requires monthly calibration after 6/1/2005 and 4X year prior to this date for MSA-60 gas scopes.

Pilchuck Contractors, 100% record review:

a)	Pilchuck records indicate that Gascope #475 was calibration checked on 12/13/2003 and then sent for repair on 06/15/2004. This exceeds the maximum 4 month timeframe between calibration checks in effect at the time.

b)	Pilchuck records indicate that Gascope #5425 was calibration checked on 08/25/2003 and sent in for calibration again on 02/14/2004. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

c)	Pilchuck records indicate that Gascope #5729 was calibration checked on 08/02/2004 and sent in for calibration again on 02/25/2005. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

d)	Pilchuck records indicate that Gascope #5729 was calibration checked on 02/25/2005 and sent in for calibration again on 06/29/2005. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

e)	Pilchuck records indicate that Gascope #6359 was calibration checked on 07/23/2004 and sent in for calibration again on 01/31/2005. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

f)	Pilchuck records indicate that Gascope #6758 was calibration checked on 02/03/2004 and sent in for calibration again on 06/09/2004. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

g)	Pilchuck records indicate that Gascope #12160 was calibration checked on 10/02/2004 and sent in for calibration again on 03/14/2005. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

Puget Sound Energy crews, approximately 15% of records reviewed:

a)	PSE records indicate that Gascope #6241 was calibration checked on 09/30/2004 and again on 11/02/2005. This exceeds the maximum 4 month timeframe between calibration checks in effect at the time.

b)	PSE records indicate that Gascope #4652 was calibration checked on 03/30/2004 and again on 09/02/2004. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

c)	PSE records indicate that Gascope #9970 was calibration checked on 02/09/2005 and again on 06/29/2005. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

d)	PSE records indicate that Gascope #1282 was calibration checked on 04/28/2004 and again on 09/09/2004. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

e)	PSE records indicate that Gascope #11081 was calibration checked on 04/19/2004 and sent in for calibration again on 10/05/2004. This exceeds the maximum 4-month timeframe between calibration checks in effect at the time.

Potelco Contractors, 100% of records reviewed: (10/2005 thru 5/2006)

The following combustible gas indicators (CGI) missed the monthly NTE 45 day calibration requirements as outlined in PSE procedure 2450.1600.

a)	CGI #960, missed 11/05, 02/06 and 04/06.

b)	CGI #963, missed 11/05, 01/06, 02/06 and 04/06.

c)	CGI #1013, missed 11/05, 01/06, 02/06 and 04/06.

d)	CGI #1018, missed 10/05, 12/05, 01/06, 03/06, 04/06 and 05/06

e)	CGI #1023, missed 11/05, 01/06, 02/06 and 04/06.

f)	CGI #1109, missed 11/05, 01/06, 02/06, 04/06 and 05/06.

g)	CGI #1121, missed 10/05, 12/05, 02/06 and 04/06.

h)	CGI #1124, missed 10/05, 12/05, 02/06 and 04/06.

i)	CGI #1217, missed 10/05, 11/05, 12/05, 02/06 and 04/06.

j)	CGI #1240, missed 11/05, 01/06, 02/06, 03/06 and 05/06.

k)	CGI #1248, missed 11/05, 01/06 and 03/06.

l)	CGI #1390, missed 10/05, 11/05, 01/06 and 03/06.

m)	CGI #1699, missed 10/05, 12/05, 02/06 and 04/06.

n)	CGI #2140, missed 10/05, 11/05, 01/06, 02/06 and 04/06.

o)	CGI #2305, missed 11/05, 01/06, 02/06, 04/06 and 05/06.

p)	CGI #2467, missed 11/05, 12/05, 01/06 and 03/06.

q)	CGI #2701, missed 11/05, 01/06, 02/06, 03/06, 04/06 and 05/06.

r)	CGI #3564, missed 11/05, 12/05, 01/06, 02/06, 03/06, 04/06 and 05/06.

s)	CGI #3821, missed 11/05, 01/06, 02/06, 03/06 and 05/06.

t)	CGI #3882, missed 11/05, 12/05, 01/06, 03/06 and 04/06.

u)	CGI #3999, missed 11/05, 12/05, 01/06, 02/06 and 03/06.

v)	CGI #4433, missed 10/05, 12/05 and 02/06.

w)	CGI #4606, missed 11/05, 12/05, 01/06, 02/06, 03/06 and 05/06.

x)	CGI #5188, missed 10/05, 12/05, 01/06, 03/06 and 04/06.

y)	CGI #5411, missed 11/05, 01/06, 02/06 and 04/06.

z)	CGI #5707, missed 11/05, 01/06, 03/06 and 05/06.

aa)	CGI #5708, missed 11/05, 01/06, 02/06, 03/06 and 05/06.

bb)	CGI #5723, missed 10/05, 12/05, 01/06, 02/06 and 03/06.

cc)	CGI #5737, missed 10/05, 12/05, 01/06, 02/06, 03/06 and 05/06.

dd)	CGI #6072, missed 10/05, 11/05, 02/06 and 04/06.

ee)	CGI #6225, missed 10/05, 11/05, 01/06, 02/06, 04/06 and 05/06.

ff)	CGI #6405, missed 10/05, 12/05 and 02/06.

gg)	CGI #6780, missed 10/05, 12/05, 01/06, 03/06 and 04/06.

hh)	CGI #7641, missed 11/05, 01/06, 02/06 and 04/06.

ii)	CGI #8060, missed 11/05, 01/06, 02/06 and 04/06.

jj)	CGI #9977, missed 10/05, 11/05, 12/05, 02/06 and 04/06.

kk)	CGI #9988, missed 10/05, 11/05, 12/05, 02/06, 03/06 and 05/06.

ll)	CGI #9933, missed 10/05, 12/05, 01/06, 02/06, 04/06 and 05/06.

mm)	CGI #9998, missed 01/06, 03/06 and 05/06.

nn)	CGI #11377, missed 11/05, 12/05, 01/06, 03/06, 04/06 and 05/06.

Line Marker Procedures

56.	Does the company have written procedures for the placing and labeling of line markers as required? 192.605(b), 192.707, WAC 480-93-124

__yes 2525.2500__________________________________

- Are line markers installed at class 1 & 2 locations?

__no class one or two areas reviewed_______________________________

b.      Are line markers installed at all bridge, railroad, irrigation and drainage ditch crossings?

__no

PSE has several pipeline markers with Washington Natural Gas (WNG) logos on them.  In addition, PSE did not have pipeline markers at certain locations as required by WAC 480-93-124(2)(b).

a)	49 CFR §192.707(a) requires that markers be installed over each main and transmission line in class 1 and 2 locations and in areas where potential damage could occur to the pipeline. These areas of concern could become probable violations if it is found that markers with improper company names are found in these areas.

The following are areas where WNG markers were present at the time of this inspection:

(1)	7th St Se and 11th Ave SE, (SE corner) Puyallup.

(2)	18th Ave E and 152nd St E, (NE corner) Puyallup.

(3)	25th St SE and 12th Ave SE, (SW corner) Puyallup.

(4)	83rd Ave E and 160th St E, (NE corner) Puyallup.

(5)	17 East Valley Hwy, (W side) Pacific.

(6)	North of 17 East Valley Hwy, (W side) Puyallup.

c.       Do line markers include the current name, telephone number, and the word Warning, Caution, or Danger?

__no

PSE has several pipeline markers with Washington Natural Gas (WNG) logos on them.  In addition, PSE did not have pipeline markers at certain locations as required by WAC 480-93-124(2)(b).

a)	49 CFR §192.707(a) requires that markers be installed over each main and transmission line in class 1 and 2 locations and in areas where potential damage could occur to the pipeline. These areas of concern could become probable violations if it is found that markers with improper company names are found in these areas.

The following are areas where WNG markers were present at the time of this inspection:

(1)	7th St Se and 11th Ave SE, (SE corner) Puyallup.

(2)	18th Ave E and 152nd St E, (NE corner) Puyallup.

(3)	25th St SE and 12th Ave SE, (SW corner) Puyallup.

(4)	83rd Ave E and 160th St E, (NE corner) Puyallup.

(5)	17 East Valley Hwy, (W side) Pacific.

(6)	North of 17 East Valley Hwy, (W side) Puyallup.

Exposed Pipelines Procedures

57.	Does the company have procedures for the placement, inspection and maintenance of warning signs in areas where pipelines and associated equipment & facilities are exposed?  WAC 480-93-120

_yes 2525.2500___________________________________

Record Keeping Procedures – Transmission Lines

58.	Are there procedures for the retention of records as required? 192.605(b), 192.709(a)(b)(c)

a.	Repairs to the pipe - Life of system

__n/a______________________________________

b.	Repairs to pipeline components – 5 years

___n/a_____________________________________

c.	Patrols, surveys and tests required by subparts L & M – 5 years or until next, whichever is longer.

__n/a______________________________________

Repair Procedures for Imperfections and Damages -Transmission Lines

59.	Does the Pipeline Company make permanent repairs for imperfections or damage on steel transmission lines operating at or greater than 40% of SMYS?

a.	By taking the segment of line out of service, removing by cutting out a cylindrical piece of pipe and replacing it with pipe of similar or greater design strength. 192.605(b), 192.713(a)(1)

__n/a_______________________________________

b.	Use of reliable engineering repair method. 192.605(b), 192.713(a)(2)

__ n/a _______________________________________

c.	Lowering the operating pressure to a safe level during repair operation. 192.605(b), 192.713(b)

__ n/a _______________________________________

Repair Procedures/Permanent Field Repair of Welds – Transmission Lines

60.	Are welds, which are found unacceptable under CFR 192.241(c) repaired as followed: 192.605(b), 192.715(a)(b)(c)

a.	Take the line out of service and repair in accordance with CFR 192.245

__ n/a _______________________________________

b.	Are welds with cracks longer than 8% of the weld length removed?

__ n/a _______________________________________

c.	For each weld repaired, is the defect removed down to clean metal and the pipe preheated if conditions, which, may adversely affect the quality of the weld, repair?

__ n/a _______________________________________

d.	Are repairs inspected to insure acceptability?

__ n/a _______________________________________

e.	Are repair of cracks or any defect in an area where it has been previously repaired, repaired in accordance with written weld procedures qualified under 192.225?

__ n/a _______________________________________

61.	For lines remaining in service, the weld may be repaired in accordance with CFR 192.245 if:

a.	The weld is not leaking.

__ n/a _______________________________________

b.	The pressure in the segment is reduced to produce a hoop stress equal to or less than 20% of SMYS.

_ n/a _______________________________________

c.	Grinding limited so that at least 1/8-inch thickness in pipe weld remains.

__ n/a ______________________________________

d.	If the weld cannot be repaired in accordance with (a) or (b) above, a full encirclement welded split sleeve must be installed.

__ n/a ______________________________________

Repair Procedures/Permanent Field Repair of Leaks – Transmission Lines

62.	Are permanent field repair’s of a leak on a transmission line made by: 192.605(b), 192.717(a)(b)

a.	(a) Cutting out a cylinder and replacing segment with pipe similar or of greater design strength or

__ n/a ______________________________________

b.	(b)(1) Install a full encirclement welded split sleeve of an appropriate design unless the pipe is joined by mechanical couplings or operates at less than 40% SMYS

_ n/a _______________________________________

c.	(b)(2) A leak due to a corrosion pit may be repaired by installing a properly designed bolt-on leak clamp

___ n/a _____________________________________

d.	(b)(3) For a corrosion pit leak, if a pipe is not more than 40,000 psi SMYS, the pits may be repaired by fillet welding a steel plate. The plate must have rounded corners and the same thickness or greater than the pipe, and not more than one-half of the diameter of the pipe in size.

__ n/a ______________________________________

e.	(b)(4) Submerged offshore pipe or pipe in inland navigable waterways may be repaired with a mechanically applied full encirclement split sleeve of appropriate design.

___ n/a _______________________________

f.	(b)(5) Apply reliable engineering methods, which permanently restore the serviceability of the pipe.

__ n/a _______________________________________

Repair Procedures/Testing of Repairs – Transmission Lines

63.	Is replacement pipe pressure tested to meet the requirements of a new pipeline installed in the same location? 192.605(b), 192.719(a)

____ n/a _______________________________

64.	Are repairs on lines of 6-inch in diameter or larger and that operate at 20% or more of SMYS, non-destructively tested in accordance with 192.241? 192.719(b)

_____ n/a ______________________________

Abandonment or Deactivation of Facilities

65.	Are there procedures for conducting abandonment or deactivation of pipelines in accordance with the following requirements? 192.605(b), 192.727

a.	192.727(b) Disconnected both ends, purge, and seal each end before abandonment or a period of period of deactivation where the pipeline is not maintained. If the volume of gas is so small that there is no potential hazard, then the pipeline need not be purged.

___yes 2525.3600_______________________________

b.	(c) Except service lines, each inactive pipeline that is not being maintained under Part 192 must be disconnected from all gas sources/supplies, purged, and sealed at each end.

__yes 2525.3600________________________________

c.	(d) When service to a customer is discontinued, do the procedures indicate one of the following?

i.  A valve, which is closed to prevent the flow of gas to the customer, must be provided with a locking device or other means to prevent opening of the valve by unauthorized persons.

__yes 2575.2200_______________________________

ii.  Installation of a mechanical device or fitting in the service line or meter set assembly, which will prevent the flow of gas.

_____n/a____________________________

iii.  Physical disconnection of the customers piping from the gas supply and open end’s sealed.

____n/a_____________________________

d.	(e)  When air is used for purging, does the operator insure that a combustible mixture is not present after purging?

___yes 2525.3400_______________________________

e.	(g)  If applicable, does the operator file reports when abandoning each offshore or onshore pipeline facility that crosses over, under, or through commercially navigable waterway.

______n/a____________________________

Pressure Limiting and Regulating Stations – Inspection & Testing

66.	Procedures for inspecting and testing of each pressure limiting station, relief device’s (except rupture discs), pressure regulating stations and it’s equipment once each calendar year not to exceed 15 months? 192.739, 192.605(b)

a.	192.739(a) in good mechanical condition

___yes 2575.1000_______________________________

b.	(b) Adequate from the standpoint of capacity and reliability of operation

___ yes 2575.1000_______________________________

c.	(c) Set to function at the correct pressure

___ yes 2575.1000_______________________________

d.	(d) Properly installed and protected from dirt, liquids or other conditions that might prevent proper operation.

____ yes 2575.1000______________________________

67.	Procedures for Telemetry and Recording gauges. 192.741, 192.605(b)

a.	Are tele-metering or recording gauges installed on systems supplied by more than one district regulating station?

__yes 2575.1300________________________________

b.	for determining the need for such devices on systems served by one district regulating station?

___yes 2575.1300_______________________________

c.	for the inspection of equipment and taking corrective measures when indications of abnormally high or low-pressure conditions?

___yes 2575.1300_______________________________

68.	Procedures for the testing of relief devices (except rupture discs) including provisions for: 192.743, 192.605(b)

a.	The testing in place (if feasible) devices once each calendar year not to exceed 15 months to determine adequate capacity.

___yes 2575.1000_______________________________

b.	If test is not feasible, a review and calculation of the required capacity for the device at each station must be made once each calendar year not to exceed 15 months

____yes 2575.1000______________________________

c.	Correcting deficiencies by installing new or additional relief devices.

___yes 2575.1000_______________________________

Valve Maintenance Procedures – Transmission Lines

69.	Procedures for inspecting and the partial operation of each transmission line valve not to exceed 15 months, but at least once each calendar year 192.605(b), 192.745

(a) Inspect and partially operate each transmission valve that might be required during an emergency.  ____n/a_____________________________

(b) Prompt remedial action required, or designate alternative valve. 192.745(b)

___n/a______________________________

Valve Maintenance Procedures – Distribution Lines

70.	Procedures for checking and servicing each distribution line valve necessary for the safe operation of a distribution system, not to exceed 15 months, but at least once each calendar year 192.605(b), 192.747(a)

___no 2575.1200  and 4700.1610

Findings:

a)	Records indicate that emergency valve #VA-01113, located at S. 112 St and

I-5 in Tacoma was not operated during calendar year 2004. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

b)	Records indicate that emergency valve #VA-06209, located at 1120 Milwaukee Way in Tacoma was checked and serviced on 09/02/2003 and again on 12/06/2004. This exceeds the 15-month maximum time limit allowed. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

c)	Records indicate that emergency valve #VA-05831, located at S. 25th and Yakima in Tacoma was not operated during calendar year 2003.  (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

d)	Records indicate that emergency valve #VA-05812, located at 23 Ave SE and Shaw Rd in Puyallup has a start up date of 12/11/1995 but that it was not checked and serviced until 08/13/2004. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

e)	Records indicate that emergency valve #VA-04282, located at Plant Rd & Dutch Rd in Fort Lewis had a required start date of 10/14/1995 but was not serviced and checked until 08/05/2005. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

f)	Records indicate that emergency valve #VA-02135, located at Bridgeport Way and Mt Tacoma Dr SW in Tacoma was checked and serviced on 02/27/1997 and again on 04/08/2004. If these records are correct it indicates that over 7 years elapsed between maintenance. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

Prompt remedial action required, or designate alternative valve. 192.747(b)

__yes 2575.1200_____________________________________

Vault Maintenance Procedures

71.	Inspection of vaults equal to or greater than 200 cubic feet in area, not to exceed 15 months, but at least once each calendar year. 192.605(b), 192.749

__yes 2575.1000_______________________________

b.	Inspection for leaks on equipment and the repair there of.

__yes 4700.1600____________________________________

c.	Inspection of ventilation equipment for proper operation.

__yes 4700.1600____________________________________

d.	Inspection of vault covers to insure that they do not present a hazard to public safety.

__yes____________________________________

Prevention of Accidental Ignition

72.	Procedure for taking steps to minimize the danger of accidental ignition of gas where the presence constitutes a hazard of fire or explosion including:  192.605(b), 192.751

a.	Removal of ignition sources in the presence of gas and providing for a fire extinguisher.

__2575.2000______________________________

b.	Preventing welding or cutting on a pipeline containing a combustible mixture.

___2575.2000_____________________________

c.	The posting of warning signs

__2575.2000______________________________

Caulked Bell And Spigot Joints Procedures

73.	If applicable, does the operator have procedures for the repair of caulked bell and spigot joints? 192.753, 192.605(b).

a.	When subject to more than 25 psig, sealed with mechanical clamp, or with material/device, which does not reduce flexibility, permanently bonds; and seals/bonds as prescribes in 192.753(a)(2)(iii).

_______n/a_________________________

b.	When subject to 25 psig or less, joints, when exposed for any reason, must be sealed by means other than caulking.

___2575.2100_____________________________

Protecting Cast-Iron Pipeline Procedures

74.	Procedure for when the operator has knowledge that the support for a segment of a buried cast-iron pipeline segment is disturbed, must provide protection, which addresses? 192.605(b), 192.755.

a.	Vibrations from heavy construction equipment, trains, trucks, buses or blasting?

_yes 2575.2100__________________________________

b.	Impact forces by vehicles?

__yes_2575.2100________________________________

c.	Earth Movement?

_yes__2575.2100________________________________

d.	Other foreseeable outside forces which, might subject the segment of the pipeline to a bending stress?

_yes_2575.2100_________________________________

e.	Provides permanent protection for the disturbed section as soon as feasible?					_yes__2575.2100________________________________

Corrosion Control Procedures

75.	Are corrosion procedures established for Design, Operations, Installation, and Maintenance of cathodic protection systems? Are the procedures carried out by, or under the direction of a person qualified in pipeline corrosion control methods? 192.453, 192.605(b)

___yes 2600.1000________________________________

76.	Are buried pipelines installed after July 31, 1971 externally coated and cathodically protected within one year of installation? 192.455(a)(b), 192.605(b)

a.	If the pipeline was installed bare, can the operator prove that a corrosive environment does not exist? Were tests conducted within 6 months to confirm this?

__yes 2600.1000________________________________

b.	Was a report and supporting data submitted to the Commission indicating why such protection is not required? WAC 480-93-110

_n/a_________________________________

c.	When cathodic protection deficiencies are found, is remedial action completed within ninety days to correct the problem? WAC 480-93-110

__no

Finding(s):

Records indicate that for the following cathodic protection deficiencies, PSE 	exceeded the 90 day remedial action timeframe allowed.

a)	EPCR – ID #77004, low read found on 1/20/2004 and remediated on 9/17/2004.

b)	EPCR – ID #78572, low read found on 1/26/2004 and remediated on 7/30/2004.

c)	EPCR – ID #78574, low read found on 1/26/2004 and remediated on 7/30/2004.

d)	EPCR – ID #78571, low read found on 1/26/2004 and remediated on 7/30/2004.

e)	EPCR – ID #77319, low read found on 1/27/2004 and remediated on 5/12/2004.

f)	EPCR – ID #78109, low read found on 3/10/2004 and remediated on 7/19/2004.

g)	EPCR – ID #77680, low read found on 3/11/2004 and remediated on 9/14//2004.

h)	EPCR – ID #77892, low read found on 3/15/2004 and remediated on 12/06/2004.

i)	EPCR – ID #77934, low read found on 3/18/2004 and remediated on 06/23/2004.

j)	EPCR – ID #78056, low read found on 3/31/2004 and remediated on 2/09/2005.

k)	EPCR – ID #78899, low read found on 4/5/2004 and remediated on 8/10/2004.

l)	EPCR – ID #78568, low read found on 4/12/2004 and remediated on 9/9/2004.

m)	EPCR – ID #78616, low read found on 4/27/2004 and remediated on 8/2/2004.

n)	EPCR – ID #78630, low read found on 5/4/2004 and remediated on 8/9/2004.

o)	EPCR – ID #78651, low read found on 5/4/2004 and remediated on 8/9/2004.

p)	EPCR – ID #78817, low read found on 5/4/2004 and remediated on 10/18/2004.

q)	EPCR – ID #80645, low read found on 5/5/2004 and the main was replaced on 			4/12/2006.

r)	EPCR – ID #78739, low read found on 5/17/2004 and remediated on 9/30/2004.

s)	EPCR – ID #78977, low read found on 5/17/2004 and remediated on 10/26/2004.

t)	EPCR – ID #80384, low read found on 6/2/2004 and remediated on 11/9/2004.

u)	EPCR – ID #79500, low read found on 6/3/2004 and remediated on 9/16/2004.

v)	EPCR – ID #78039, low read found on 6/9/2004 and remediated on 11/3/2004.

w)	EPCR – ID #79449, low read found on 6/22/2004 and remediated on 10/12/2004.

x)	EPCR – ID #79406, low read found on 6/23/2004 and remediated on 5/9/2005.

y)	EPCR – ID #79409, low read found on 6/23/2004 and remediated on 10/22/2004.

z)	EPCR – ID #79559, low read found on 7/8/2004 and remediated on 11/11/2004.

aa)	EPCR – ID #79787, low read found on 7/20/2004 and remediated on 11/9/2004.

bb)	EPCR – ID #79935, low read found on 7/26/2004 and remediated on 11/13/2004.

cc)	EPCR – ID #79989, low read found on 8/9/2004 and remediated on 4/27/2005.

dd)	EPCR – ID #79970, low read found on 8/17/2004 and remediated on 1/12/2005.

ee)	EPCR – ID #80272, low read found on 8/26/2004 and remediated on 1/25/2005.

ff)	EPCR – ID #80843, low read found on 9/1/2004 and remediated on 1/24/2005.

gg)	EPCR – ID #80842, low read found on 9/1/2004 and remediated on 1/24/2005.

hh)	EPCR – ID #80849, low read found on 9/1/2004 and remediated on 12/7/2004.

ii)	EPCR – ID #80389, low read found on 9/2/2004 and remediated on 8/8/2005.

jj)	EPCR – ID #86179, low read found on 10/28/2005 and remediated on 3/24/2006.

kk)	EPCR – ID #81725, low read found on 10/19/2004 and remediated on 2/14/2005.

ll)	EPCR – ID #81052, low read found on 10/21/2004 and remediated on 3/17/2005.

mm)	EPCR – ID #81135, low read found on 10/22/2004 and remediated on 3/17/2005.

nn)	EPCR – ID #81724, low read found on 10/23/2004 and remediated on 2/14/2005.

oo)	EPCR – ID #81270, low read found on 11/8/2004 and remediated on 3/23/2005.

pp)	EPCR – ID #81343, low read found on 11/9/2004 and remediated on 3/23/2005.

qq)	EPCR – ID #81389, low read found on 11/16/2004 and remediated on 3/8/2005.

rr)	EPCR – ID #81695, low read found on 12/2/2004 and remediated on 3/8/2005.

ss)	EPCR – ID #81743, low read found on 1/5/2005 and remediated on 5/25/2005.

tt)	EPCR – ID #81757, low read found on 2/2/2005 and remediated on 5/6/2005.

uu)	EPCR – ID #81809, low read found on 2/2/2005 and remediated on 5/26/2005.

vv)	EPCR – ID #81773, low read found on 2/7/2005 and remediated on 5/9/2005.

ww)	EPCR – ID #81828, low read found on 2/17/2005 and remediated on 6/1/2005.

xx)	EPCR – ID #81796, low read found on 2/22/2005 and remediated on 6/1/2005.

yy)	EPCR – ID #82506, low read found on 4/15/2005 and remediated on 7/19/2005.

zz)	EPCR – ID #83826, low read found on 4/29/2005 and appears to still have low 			cathodic protection levels according to records.

aaa)	EPCR – ID #83808, low read found on 7/18/2005 and remediated on 11/15/2005.

bbb)	EPCR – ID #83584, low read found on 7/21/2005 and remediated on 11/14/2005.

ccc)	EPCR – ID #85216, low read found on 8/5/2005 and remediated on 11/28/2005.

ddd)	EPCR – ID #85219, low read found on 8/17/2005 and remediated on 12/19/2005.

eee)	EPCR – ID #85041, low read found on 9/29/2005 and remediated on 1/4/2006.

77.	Are effectively coated steel mains and service lines install prior to August 1, 1971 cathodically protected? 192.457(a), 192.605(b)

a.	Is cathodic protection provided in areas of active corrosion on existing bare or ineffectively coated pipelines? 192.457(b)

_yes 2600.1900_________________________________

78.	Are there procedures for the examination of pipelines for evidence of corrosion and coating deterioration whenever the operator has knowledge that a pipeline is exposed?  192.459, 192.605(b)

a.	Do the procedures include provisions for investigating circumferentially and longitudinally beyond the exposed portion to determine whether additional corrosion exists? 192.459, WAC 480-93-112

__yes 2575.2800________________________________

b.	Remedial action taken within ninety days of discovery to correct an unsafe condition? WAC 480-93-112

__n/a________________________________

c.	Provisions made for documenting the condition of all exposed underground gas facilities and the retention of records for the life of that facility? WAC 480-93-112

___yes 2575.2800_______________________________

79.	Are there procedures addressing external corrosion control with applied protective coatings? Do the procedures include provisions for: 192.461, 192.605(b)

a.	Application on a properly prepared surface.

___yes 2600.1000_______________________________

b.	Sufficient adhesion properties to effectively resist under film migration of moisture.

__ yes 2600.1000________________________________

c.	Be sufficiently ductile to resist cracking.

__ yes 2600.1000________________________________

d.	Have sufficient strength to resist damage to handling and soil stress.

__ yes 2600.1000________________________________

e.	Have properties compatible with any supplemental cathodic protection.

__ yes 2600.1000________________________________

f.	If an electrically insulating type coating is used; does it have low moisture absorption and high electrical resistance?

__ yes 2600.1000_________________________________

g.	Provisions for inspection of coatings prior to lowering pipe into a ditch and backfilling, and the repair of defects when found?

___ yes 2600.1000________________________________

h.	Provisions for the protection of coatings resulting from adverse ditch conditions or damage supporting blocks?

___ yes 2600.1000________________________________

80.	Does the criterion for cathodic protection meet one of the requirements of Part 192 Appendix D? 192.463, 192.605(b)

__ yes 2600.1500___________________________________

81.	Has each pipeline that is cathodically protected been tested at least once each calendar year not exceeding 15 months?  192.465(a), 192.605(b)

a.	Are 10% of the separately protected or isolated lines monitored each calendar year with a different 10% checked each subsequent year, so that the entire system is tested in each 10 years period?  192.465(a)

__no 2600.1500

Finding(s):

a)	PSE has a main serving approximately 13 services located at 919 Valley Ave (11105 Valley Ave.) in Puyallup. We met on-site with PSE personnel on November 28, 2005, to take pipe-to-soil potential readings. PSE personnel conducted electrical isolation tests and determined that there are two separate segments of isolated steel main in excess of 100 feet each. Pipe-to-soil potential readings indicate that cathodic protection (CP) levels meet the minimum requirements set forth in Appendix D of the CFR. PSE records and employees both indicate that these two segments are not on the annual survey as required but are instead on PSE’s 10% survey list which only requires that they be tested once every 10 years.

b)	PSE has an isolated steel wrapped service extension located at 4445 185 Ave E, Sumner. We met on-site with PSE personnel and verified that this service extension had adequate levels of CP applied. PSE personnel were not able to provide any records indicating that this isolated steel wrapped service has been monitored for proper CP levels at least once every 10 years as required.  PSE installed a test site (TS-051563) at this location on 11/23/2005. (We believe this is related to the settlement agreement and that this facility would have been found by the isolated facilities program).

c)	PSE has an isolated steel wrapped service riser located at 22225 Mountain Highway E in Spanaway which has not been monitored for proper levels of CP.  PSE added a test site (TS-051872) at this location on 01/19/2006. (We believe this is related to the settlement agreement and that this facility would have been found by the isolated facilities program).

d)	PSE has an isolated steel wrapped service riser located at 22225 Mountain Highway E in Spanaway which has not been monitored for proper levels of CP.  PSE added a test site (TS-051868) at this location on 01/19/2006. (We believe this is related to the settlement agreement and that this facility would have been found by the isolated facilities program).

e)	PSE has an isolated steel wrapped service riser located at 22219 Mountain Highway E in Spanaway which has not been monitored for proper levels of CP.  PSE added a test site (TS-051867) at this location on 01/19/2006. (We believe this is related to the settlement agreement and that this facility would have been found by the isolated facilities program).

f)	PSE has an isolated steel wrapped service located at 302 S. 9 St in Tacoma. We met on-site with PSE personnel on 12/01/2005 to verify whether the service had adequate CP. Reads obtained were -1.382 v. PSE personnel were unable to find a test site for this location and were also unable to provide evidence this service had been monitored for proper levels of CP as required. (We believe this is related to the settlement agreement and that this facility would have been found by the isolated facilities program).

g)	PSE has an isolated steel wrapped service located at 714 Pacific Ave in Tacoma.  PSE personnel were unable to find a test site for this location and were also unable to provide evidence this service had been monitored for proper levels of CP as required. (We believe this is related to the settlement agreement and that this facility would have been found by the isolated facilities program).

h)	PSE has an isolated steel wrapped service located 317 S. 7th St. We met on-site with PSE personnel on 12/01/2005 to verify whether the service had adequate CP.  Reads obtained were -1.410v. PSE personnel were unable to find a test site for this location and were also unable to provide evidence this service had been monitored for proper levels of CP as required. (We believe this is related to the settlement agreement and that this facility would have been found by the isolated facilities program).

i)	PSE has an isolated steel wrapped service located at 629 St Helens Ave, Tacoma (Meter #389484). We met on-site with PSE personnel on 12/01/2005 to verify whether the service had adequate levels CP. Adequate reads were obtained. PSE personnel were unable to find a test site for this location and were also unable to provide evidence this service had been monitored for proper levels of CP as required. (We believe this is related to the settlement agreement and that this facility would have been found by the isolated facilities program).

j)	PSE has a CP test site (TS-004408), located at S Pearl St & S 19 St in Tacoma.  Records indicate that tests were performed on 05/02/2003 and again on 08/03/2005. No test was performed in calendar year 2004 and the 15 month maximum timeframe was also exceeded between tests. (We believe this to be SAP related and that it would have been remedied by the SAP reprogramming in 2005).

b.	Has each cathodic protection rectifier been inspected at least six times each calendar year, but with intervals not exceeding 2 1/2 months?  192.465(b)

_no

Finding(s):

a)	Records indicate that rectifier #PS-0205, located at 1302 Magnolia Dr. in Fircrest was inspected on 12/11/2003 and again on 03/25/2004. This timeframe exceeds the maximum time limit of 2-1/2 months between inspections. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

b)	Records indicate that rectifier #PS-0205, located at 1302 Magnolia Dr. in Fircrest was only inspected 5 times in 2004. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

c)	Records indicate that rectifier #PS-0214, located at Wildwood Park Dr and King in Puyallup was inspected on 05/21/2004 and again on 08/11/2004. This exceeds the maximum time limit of 2-1/2 months between inspections. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

d)	Records indicate that rectifier #PS-0215, located at Firgrove Dr and 108 Ave E in Puyallup was inspected on 05/21/2004 and again on 08/12/2004. This exceeds the maximum time limit of 2-1/2 months between inspections. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

e)	Records indicate that rectifier #PS-0218, located at 24 St E and 142 Ave E in Sumner was inspected on 05/21/2004 and again on 08/09/2004. This exceeds the maximum time limit of 2-1/2 months between inspections. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

f)	Records indicate that rectifier #PS-0220, located at E Valley Hwy and 24 St E in Sumner was inspected on 05/19/2004 and again on 08/09/2004. This exceeds the maximum time limit of 2-1/2 months between inspections. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

g)	Records indicate that rectifier #PS-0229, located at 7 Ave SE and 14 St SE in Puyallup was inspected on 05/21/2004 and again on 08/09/2004. This exceeds the maximum time limit of 2-1/2 months between inspections. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

h)	Records indicate that rectifier #PS-0237, located at Washington St and Wood Ave in Sumner was inspected on 05/21/2004 and again on 08/09/2004.  This exceeds the maximum time limit of 2-1/2 months between inspections. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

i)	Records indicate that rectifier #PS-0240, located at S 40 St and S Fawcett Ave in Tacoma was inspected on 09/13/2004 and again on 12/07/2004. This exceeds the maximum time limit of 2-1/2 months between inspections. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

j)	Records indicate that rectifier #PS-0257, located at 18 St NW and 10 Ave NW in Puyallup was inspected on 05/21/2004 and again on 08/09/2004. This exceeds the maximum time limit of 2-1/2 months between inspections. (We believe that this scheduling issue would have been remedied by the SAP reprogramming in 2005).

c.	Provisions for interference bond monitoring as required? 192.465(c)

__yes 2600.1500_________________________________

d.	Provisions for conducting electrical surveys on bare/unprotected pipelines every three years?  192.465(e)

__yes 2600.1500_________________________________

e.	Are records retained for all test readings taken? WAC 480-93-110

_yes 2600.1500__________________________________

82.	Are there procedures for electrical isolation of buried pipelines (including casings) from other metallic structures including; 192.467, 192.605(b), WAC 480-93-115?

a.	Provisions for assuring through inspection and tests that electrical isolation is adequate. 192.467

___yes 2600.1400________________________________

b.	Are tests performed annually?  WAC 480-93-115

__yes 2600.1500_________________________________

c.	Are shorts evaluated within ninety days to determine whether a hazardous condition exists, and leak tests conducted on a ninety-day schedule until the condition is corrected? WAC 480-93-115

____yes 2625.1100_______________________________

d.	Provisions made for protection against damage from fault currents or lightening due to close proximity of pipelines to electrical transmission tower footings, ground cables, counterpoise, or other areas of risk. 192.467(f)

___yes 2600.1400________________________________

83.	Are sufficient test stations or other contact points installed for determining the adequacy of the cathodic protection? 192.469, 192.605(b)

__yes 2600.1200__________________________________

84.	Procedures for the installation of test lead wires? 192.471, 192.605(b)

__yes 4515.1020 field procedures__________________________________

85.	Is there a program in place for minimizing the effects of stray currents? IS CP systems design and installed to minimize any adverse effects on existing adjacent underground metallic structures? 192.473, 192.605(b)

_yes 2600.1300 and 1500___________________________________

86.	Are there procedures for internal corrosion control, which address?

a.	If applicable, for the transportation of corrosive gas? 192.475(a), 192.605(b)

__yes 2600.1700___________________________________

b.	The inspection of pipe segments, which have been removed? 192.475(b)

__yes 2600.1700_

Finding(s):

PSE personnel provided us with inspection records for the 16-inch re-locate project located at 24th St E and 138th Ave E in Sumner, job #109001662. We were given a list of 6 areas that had sections of the existing 16-inch pipeline removed during the course of construction. They included exposed pipe condition reports (EPCR’s) with the following identification numbers:  75643, 75644, 75645, 75646, 75647 and 75648. Of the six areas identified, PSE records indicate that only one site, 75646, had an internal corrosion assessment completed.

c.	Investigation of adjacent pipe if internal corrosion is found? 192.475(b)(1)

_yes 2600.1700____________________________________

d.	Replacement of pipe based on the requirements of 192.485? 192.475(b)(2)

_yes 2600.1900____________________________________

e.	Steps taken to minimize internal corrosion? 192.475(b)(3)

__yes 2600.1700___________________________________

87.	If corrosive gas is being transported, are coupons or other suitable means used to determine the effectiveness of program to minimize internal corrosion as required? Is monitoring conducted twice each calendar year at intervals not exceeding 7 ½ months? 192.477, 192.605(b)

__n/a________________________________

88.	Have above ground facilities installed after 7/31/71, been cleaned and coated? 192.479(a), 192.605(b)

__yes 2600.1900________________________________

89.	Have above ground facilities, installed before 8/1/71, been investigated for atmospheric corrosion. If atmospheric corrosion exists, are remedial measures taken as required by 192.485?  Is the facility cleaned and coated with suitable materials? 192.479(b)(1)(2)(3), 192.605(b)

___yes 2600.1900_______________________________

90.	Has the Pipeline Company reevaluated piping exposed to the atmosphere at intervals not to exceed 3 years for   onshore piping and where necessary, taken remedial action to maintain protection? 192.481, 192.605(b)

No

Finding(s):

a)	PSE has an idle service with no meter located at 10712 62 St. Ct. E. (space 18) in Puyallup. The service is located in the Golden Rose mobile home park. The riser has heavy atmospheric corrosion. PSE was unable to provide records that this riser was surveyed for atmospheric corrosion within the 3 year, not to exceed 39 month timeframe as required.

b)	PSE has a roof top service located at 1306 E. Pioneer Ave in Puyallup. The riser is in front of the building and the service goes up and over the roof to the meter set which is located in back of the building. PSE was unable to provide records indicating that the rooftop service has ever been surveyed for atmospheric corrosion.

91.	Are there procedures addressing the replacement or repair of pipe, or for reducing the MAOP if general or localized corrosion has reduced the wall thickness of a segment of pipe?  Is ASME B31G or RSTRENG utilized for determining the strength of the pipe based on the remaining wall thickness of the pipe? 192.485, 192.605(b)

___n/a_______________________________

92.	Are corrosion control records or maps maintained as required? 192.491, 192.605(b)

a.	Showing the location of cathodically protected pipe, cathodic protection facilities, galvanic anodes, and neighboring structures bonded to the cp system?

__yes 2600.2000________________________________

b.	For each test, survey, or inspection required by Subpart I in sufficient detail to demonstrate the adequacy of the corrosion control measures.

__yes 2600.1000________________________________

c.	Retained for at least 5 years with the exception of records related to 192.465(a)(e) and 192.475(b) which must be retained for as long as the pipeline remains in service?

__yes 2600.1500________________________________

Welding Procedures

93.	Are there qualified welding procedures for butt welds, fillet, and or maintenance welding? Are welding procedures qualified in accordance with Section 5 of API Standard 1104 or Section IX ASME Boiler and Pressure Vessel Code?  Are welding procedures qualified by destructive testing? 192.225, 192.13(c)

____yes 2700.1100_________________________________

94.	Is each welding procedure recorded in detail including the results of the qualifying test? Are the procedures retained and followed whenever welding is conducted? 192.225, 192.13(c)

___yes 2425.1000__________________________________

95.	Are welders qualified in accordance with Section 6 of API Standard 1104 or Section IX ASME Boiler and Pressure Vessel Code? Pipelines operating below 20% of SMYS may qualify welders under CFR 192, Appendix C – Section I. 192.227(a)(b), 192.13(c)

____yes 2700.1400_________________________________

96.	Limitations of API 1104 and ASME Section IX welders: 192.229, 129.13(c)

a.	Welders who have successfully completed a destructive test may weld on compressor station piping and components. 192.229(a)

_n/a in Pierce_______________________________________

b.	Welders must have performed that particular welding process within the preceding 6 months. 192.229(b)

_yes 2700.1100_______________________________________

c.	Welders must have had within the preceding 6 months; one weld tested and found acceptable under Section 6 or 9 of API 1104. 192.229(c)(1)

__yes 2700.1100______________________________________

d.	Welders may not weld on pipelines operated at less than 20% of SMYS unless they have been tested in accordance with 192.227(b) or have re-qualified under Appendix C, Section I. 192.229(c)(2)

__yes 2700.1100______________________________________

97.	Limitations of Appendix C welders: 192.229, 129.13(c)

a.	Welders must be re-qualified once each calendar year not to exceed 15 months

__yes 2700.1100______________________________________

b.	Within the preceding 7 ½ months but at least twice each calendar, had a production weld tested, and found acceptable in accordance with the qualifying test.

__yes 2700.1100______________________________________

98.	Do general welding procedures include provisions for;

a.	Protection from weather?  192.231

__yes 2525.2700______________________________________

b.	Miter Joints?  192.233

__yes 2525.2700______________________________________

c.	Welding preparation including cleanliness of welding surface and alignment of pipe and components?  192.235

__yes 2525.2700______________________________________

99.	Is welding visually inspected to ensure.

a.	Welding is performed in accordance with the welding procedure?  192.241(a)(1)

__yes 2700.1200______________________________________

b.	Acceptability of weld in accordance with Section 9 of API 1104? 192.241(a)(2)

___yes 2700.1200_____________________________________

100.	Do welding procedures include provisions for non-destructive testing of welds on pipelines operated at

20% or more of SMYS in accordance with 192.243?  192.241, 192.13(c)

Note: Welds which are visually inspected and approved by a qualified welding inspector are exempt if;

a.	The welds are on a pipeline less than 6 inches in diameter or, 192.241(b)(1)

__yes 2700.1200_______________________________________

b.	The pipeline is operated at less than 40% SMYS and the welds are so limited in number that nondestructive testing is impractical.  192.241(b)(2)

__yes 2700.1200_______________________________________

Nondestructive Testing Procedures

101.	Is nondestructive testing done by a process other than trepanning which will clearly indicate defects that may affect the integrity of the weld? 192.243(a)

a.	In accordance with written procedures and by a qualified person trained in the procedures and test equipment used and; 192.243(b)(1)(2)

__yes 2700.1200_______________________________________

b.	Include provisions for the proper interpretation of each tested weld to insure acceptability under 192.241(c)?  192.243(c)

___yes 2700.1200______________________________________

102.	When nondestructive testing is required under 192.241(b), are the following percentages of each days field butt welds tested? Welds must be randomly selected and the weld tested over the entire circumference. 192.243(d)

a.	Class 1………at least 10%

_yes 2700.1200___________________________

b.	Class 2………at least 15%

__ yes 2700.1200 __________________________

c.	Class 3 & 4.…crossings at navigable rivers, offshore, railroad & public highway

____ yes 2700.1200________________________

d.	Rights-of-way, tunnels, bridges, and overhead road crossings, 100% unless impractical, then 90%.

__ yes 2700.1200__________________________

e.	All tie-ins…100%

__ yes 2700.1200__________________________

f.	When nondestructive testing is required under 192.241(b), is a sample of each welders work tested? 192.243(e)

_ yes 2700.1200___________________________

103.	Are records of nondestructive testing retained for the life of the pipeline? Do records show by milepost, engineering station, or geographic feature, the number of welds tested, number of welds rejected, and the disposition of the rejected welds?  192.243(f)

_ yes 2700.1200___________________________________________

Repair and Removal of Weld Defects Procedures

104.	    Are there procedures for the repair and removal of weld defects? 192.13(c), 192.245.

a. 		Each weld which, is unacceptable under 192.241(c), must be removed or repaired.   Removal of welds which, have a crack more than 8% of the weld length.

__ yes 2700.1200_______________________________________

b.  		Each weld that is repaired must have the defect removed down to sound metal, and the segment pre-heated if conditions exist which could adversely affect the quality of the weld repair. After repair, the weld must be inspected and found acceptable.3

_ yes 2700.1200_________________________________________

c.		Repair of a crack or ant other defect in a previously repaired area must be in accordance with a written repair procedure, qualified under 192.255.

__ yes 2700.1200________________________________________

Joining of Plastic Materials

105.	Are there procedures for the joining of plastic pipe? 192.273(b), 192.281

a.	Manufacturer and type of plastic used?

__Performance________________________________________

b.	Are all materials properly marked in accordance with §192.63?

__yes________________________________________

c.	Types of joints used?

_mechanical, fusion, compression hydraulic  2700.1600_________________________________________

106.	Written procedures established for joining in accordance with §192.273?

__yes________________________________

107.	Have procedures been properly qualified prior to use? 192.283

__yes ________________________________

108.	Have individuals making joints been qualified? 192.285

__yes 2700.1600________________________________

109.	Are the individuals who inspect joints qualified? 192.287

__yes 2700.1600_____________________________________

Operator Qualification

110.	Does the Pipeline Company have a written Pipeline Company Operator Qualification program? 192.801 - 192.809, WAC 480-93-082

Note: If necessary, utilize Operator Qualification Checklist for review of company OQ plan.

________________________________________

The following questions are to be used in determining a need for a more intensive OQ field inspection.

111.	Do supervisors know what action to take, as required by the operator’s OQ program, when an individual’s performance of a covered task may have contributed to an incident?

__not inspected due to recent OQ inspection______________________________________

112.	Do supervisors know what action to take, as required by the operator’s OQ program, when an individual is identified who may no longer be qualified to perform a covered task?

__ not inspected due to recent OQ inspection ______________________________________

113.	Do individual’s performing covered tasks know how to recognize and react to abnormal operating conditions (AOCs) that may be encountered while performing tasks?

__ not inspected due to recent OQ inspection ______________________________________

114.	Are operator employee and/or contractor individuals observed performing covered tasks qualified per OQ program requirements?

_ not inspected due to recent OQ inspection _______________________________________

115.	Are the individuals who observed performing covered tasks adhering to the operator’s procedures?

___ not inspected due to recent OQ inspection _____________________________________

Design & Construction

116.	Has the pipeline owner constructed additional or replaced segments of the pipeline system since the last standard audit was conducted?

Note: If necessary, Utilize Gas Pipeline Construction Checklist for review of construction activity.

___yes_____________________________________

117.	Are new transmission line sections where the pipeline, valve, fitting, or other line components have been replaced after May 12, 1994, designed and constructed to accommodate the passage of instrumented internal inspection devices? 192.150

____n/a____________________________________

SCADA Systems

The following questions are to be used in determining if a more intensive SCADA evaluation is warranted.

118.	Does the operator use SCADA or other forms of automation to comply with the Pipeline Safety Regulations?

Yes/No_____no____________________________

119.	If yes, does the operator have processes and procedures which, if applicable address the following

a.	§192.605(c)(1)(iii) – Loss of communications

- Offsite Backup Center

- Data Transfer to Redundant or Offsite Processors

- Battery and/or Emergency Generator

- Redundant Data Communications Paths, Automatic Restoration or Manual

- Data Reduction & Archiving

- Indication of Stale, Forced or Manually Overridden Data, or System Lockup

- Operating Practices During Data Communication Outages

________________________________________

b.	§192.731(c) & .745 – Testing SCADA controlled valves and safety devices

- Frequency and Scope in Testing of SCADA Controlled Devices’ Functionality

- Inclusion of SCADA Component in the Tests

- Frequency and Scope of Testing Emergency Shutdown Devices

________________________________________

c.	§192.603	General provisions

(b)	Each operator shall keep records necessary to administer the procedures established under §192.605.

- Ensure SCADA screens/status board are updated to reflect current pipeline configurations

- Ensure pipeline safety parameters are current (i.e., MAOP, alarm set points, etc.)

- Review any emergency or abnormal operating condition records generated by the SCADA system (alarm logs, trending data, etc.).  Compare abnormal operating conditions noted in the SCADA data with the Operator’s report and reporting procedures as related to those abnormal operating conditions.

________________________________________

120.		Has the operator reviewed the following Advisory Bulletins?

- July 7, 1999 Advisory Bulletin ADB-99-03 (Ref. fr16jy99N Potential Service Interruptions in Supervisory Control and Data Acquisition Systems) – SCADA system performance.

- December 16, 2003 Advisory Bulletin ADB-03-09 (Ref. fr23de03N Pipeline Safety: Potential Service Disruptions in Supervisory Control and Data Acquisition Systems) – Consideration of possible SCADA system disruptions caused by system maintenance or upgrade.

Yes/No____yes_____________________________

Best Practices

121.	What process does the operator have to address DOT Alert Notices?

___WinDOT_____________________________________

122.	Is the operator reviewing their system for the potential of SCC as part of developing their Gas integrity program?  (Pipeline Safety Advisory Bulletin ADB-03-05 dated 10/8/2004) (Ref. Fr06oc03N Pipeline Safety: Stress Corrosion Cracking Threat to Gas and Liquid Pipelines).

Yes/No______no___________________________

123.        Do you know of any other pipelines in your area?

___no_____________________________________