Washington Utilities and Transportation Commission

2002 Gas Pipeline Safety Inspection

Avista Utilities, Spokane/Ritzville and Goldendale/Stevenson, Washington

## VIOLATION REPORT

The following violations of the Washington Administrative Code (WAC) Chapter 480-93 and Title 49 CFR Part 192 rules were found as a result of the February 6, 2002 through February 22, 2002, Spokane/Ritzville district and June 17 through June 22, 2002 Goldendale/Stevenson district, pipeline safety inspection of Avista Utilities’ facilities and operations.  The inspection included a review of the procedures, records, inventory, and natural gas facilities.

- WAC 480-93-015 Odorization of Gas   All gas being transported by pipeline in this state, and all gas consumed by an end use customer, shall be odorized in accordance with 49 CFR, Part 192.625, unless waiver is approved in advance of such transportation, in writing, by the commission.

Findings:

##### Spokane/Ritzville District:

This finding is based on an Avista adopted Lower Explosive Limit (LEL) of five percent gas in air.  Odorization records indicated that for the month of May 2001, Avista did not have readily detectable odorization at the required levels.  Records for the seven test sites in the Spokane area indicated that the systems were odorized to a level that was not readily detectible until a concentration of gas in air of 1.3 percent.  This does not meet the minimum requirement that the systems be odorized at a readily detectible level of approximately one percent gas in air (based on an LEL of five percent).  No documentation was provided indicating Avista personnel recognized the inadequate levels of odorization or that any corrective actions were taken.

- WAC 480-93-110 Corrosion Control  Every gas company must ensure that all of its metallic gas pipelines, except cast iron and ductile iron, are protected by a recognized method or combination of methods of cathodic protection.

REPEAT VIOLATION

Findings:

Avista has an undetermined number of short sections of steel main and isolated steel service risers that do not have adequate cathodic protection applied.  The following were found to have inadequate or no levels of cathodic protection applied:

#### Spokane/Ritzville District:

- 2901 N. Argonne, Suite 5, Spokane.  Reading of –0.59 volt.

- 6606 N. Division, Spokane.  Reading of –0.54 volt.

Goldendale/Stevenson:

  - 320 Columbus St., Goldendale.  Reading of –0.40 volt.

  - 908 Columbus St., Goldendale.  Reading of –0.43 volt.

  - 125 Brooks St., Goldendale.  Reading of –0.77 volt.

  - 127 Brooks St., Goldendale.  Reading of –0.38 volt.

  - 608 Golden St., Goldendale.  Reading of –0.12 volt.

  - 610 Golden St., Goldendale.  Reading of –0.56 volt.

  - 525 Collins, Goldendale.  Reading of –0.43 volt.

  - NW Manufacturing, Cascade Ave, Stevenson.  Reading of –0.49 volt.

  - Two-inch steel wrapped main on Mill St Bridge over Little Klickitat River.  Reading of –0.52 volt.

  - Three quarter inch main in the 600 block of Golden St., Goldendale.  Readings taken from services.

Our inspection report dated March 27, 2001, docket number UG-001851, previously identified this violation.

- WAC 480-93-110 Corrosion Control   “…Every gas company shall record and retain all cathodic protection test readings taken and complete remedial action within ninety days to correct any cathodic protection deficiencies known and indicated by the company's record.

REPEAT VIOLATION

Findings:

Spokane/Ritzville District:

Documentation indicates the following carrier pipe Cathodic Protection (CP) readings did not meet the minimum level of –0.85 volt and were not corrected within 90 days:

- Erie & Front, Spokane. 10-25-2001 surveys.  Records indicate that the carrier pipe had a reading of  -0.75 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

- Freya & Track at Riverside, Spokane.   10-25-2001 surveys.  Records indicate that the carrier pipe had a reading of  -0.6 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

- Greene & Tracks at Ralph, Spokane.  10-25-2001 surveys.  Records indicate that the carrier pipe had a reading of  -0.47 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

- Lenedeke & 8TH (E casing), Fairchild to Spokane.  10-18-2001 surveys.  Records indicate that the carrier pipe had a reading of  -0.78 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

- Starr Rd & Trent, Spokane Valley.  10-02-2001 surveys.  Records indicate that the carrier pipe had a reading of  -0.64 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

- Starr Rd & Tracks S of Trent, Spokane Valley.  10-02-2001 surveys.  Records indicate that the carrier pipe had a reading of  -0.64 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

- Btwn Freeway & Appleway at 22425 E, Spokane Valley. 10-02-2001 surveys.  Records indicate that the carrier pipe had a reading of  -0.76 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

- Dyer & north tracks N of Sprague, Spokane Valley.  10-04-2001 surveys.  Records indicate that the carrier pipe had a reading of  -0.7 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

- Dyer & south tracks N of Sprague, Spokane Valley.  10-04-2001 surveys. Records indicate that the carrier pipe had a reading of  -0.72 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

- Sprague & Dyer, Spokane Valley.  10-04-2001 surveys.  Records indicate that the carrier pipe had a reading of  -0.7 volt, which doesn’t meet the Avista adopted criteria of –0.85 volt.  Avista was unable to provide documentation indicating that the low CP reading was corrected within the 90-day requirement.

Spokane/Ritzville District:

Documentation indicates the following casing reads exceeded the maximum level adopted by Avista of -.730v and were not addressed or followed up with electrical isolation testing within 90 days:

- White Rd & ¾ mile S of Hwy 902, Spokane.  10-17-2001 surveys.  Records indicate that the casing had a reading of –0.77 volt, which is above the potential adopted by Avista that requires follow up testing for electrical isolation.  As of April 2002 Avista had not conducted follow up electrical isolation testing.

- I-90 & ¾ mile S of Hwy 902 at White Rd, Fairchild to Spokane.  10-18-2001 surveys.  Records indicate that the casing had a reading of –0.75 volt, which is above the potential adopted by Avista requiring follow up testing for electrical isolation.  As of April 2002 Avista had not conducted follow up electrical isolation testing.

- Hwy 395 & Crawford So side, Kettle Falls to Spokane.  10-23-2001 surveys.   Records indicate that the casing had a reading of –0.74 volt, which is above the potential adopted by Avista requiring follow up testing for electrical isolation.  As of April 2002 Avista had not conducted follow up electrical isolation testing.

- Hwy 395 & Monroe Rd north side, Kettle Falls to Spokane.  10-23-2001 surveys.  Records indicate that the casing had a reading of –0.73 volt, which is at the potential adopted by Avista requiring follow up testing for electrical isolation.  As of April 2002 Avista had not conducted follow up electrical isolation testing.

- Trent & Park, Spokane Valley.  10-01-2001 surveys.  Records indicate that the casing had a reading of –0.78 volt, which is above the potential adopted by Avista requiring follow up testing for electrical isolation.  As of April 2002 Avista had not conducted follow up electrical isolation testing.

- Euclid & Center, Spokane Valley.  10-01-2001 surveys.  Records indicate that the casing had a reading of –1.02 volt, which is above the potential adopted by Avista requiring follow up testing for electrical isolation.  As of April 2002 Avista had not conducted follow up electrical isolation testing.

- Tracks S of Trent & Progress, Spokane Valley.  10-02-2001 surveys.  Records indicate that the casing had a reading of –0.95 volt, which is above the potential adopted by Avista requiring follow up testing for electrical isolation.  As of April 2002 Avista had not conducted follow up electrical isolation testing.

- Tracks ½ mile E of Van Marter & N of Columbia, Ritzville.  10-24-2001 surveys.  Records indicate that the casing had a reading of –0.93 volt, which is above the potential adopted by Avista requiring follow up testing for electrical isolation.  As of April 2002 Avista had not conducted follow up electrical isolation testing.

- Sprague & Fancher, Spokane Valley.  10-04-2001 surveys.  Records indicate that the casing had a reading of –0.82 volt, which is above the potential adopted by Avista requiring follow up testing for electrical isolation.  As of April 2002 Avista had not conducted follow up electrical isolation testing.

Our inspection report dated March 27, 2001, docket number UG-001851 and August 2, 2001, docket number UG-010855, previously identified this violation.

- WAC 480-93-183 Pipeline and System Pressure Reporting   All gas companies shall establish a maximum operating pressure for a pipeline or system, in accordance with this chapter, and notify the commission of the following pressure related changes:

    - When a pipeline or system pressure exceeds the established maximum operating pressure, the commission shall be notified within six hours, to be followed by written explanation within thirty days.

Findings:

Spokane/Ritzville District:

Staff reviewed system pressure “exception reports” for the Spokane district and found the following systems that exceeded the established Maximum Allowable Operating Pressure (MAOP).  Avista did not make Commission notification as required.

- Spokane West Gate #3.  Records indicate that the MAOP is 366 psig and that a pressure of 367.3 psig was reached on May 9, 2001.

- Mead City Gate.  Records indicate that the MAOP is 174 psig and that a pressure of 179.2 psig was reached on May 8, 2001.

- Mead City Gate.  Records indicate that the MAOP is 174 and that a pressure of 175.2 was reached on May 4, 2001.

- WAC 480-93-186(1)(c) Leakage Classification and Action Criteria

(1) Gas leak classification and repair.

(c) Follow-up inspections.  The adequacy of leak repairs shall be checked by acceptable methods while the excavation is open.  The perimeter of the leak area shall be checked with a CGI.  In the case of repair of a Grade 1 leak, where there is residual gas in the ground, a follow-up inspection shall be made as soon as practical but in no case later than one month following the repair.  In the case of Grade 2 or Grade 3 leaks, which have been repaired, the need for a follow-up inspection shall be determined by qualified personnel employed or retained by the gas company.

REPEAT VIOLATION

##### Findings:

Spokane/Ritzville District:

Documentation indicates that the following grade 1 leaks did not have follow up inspections made within the 30-day limit:

- 7026 S. Crestview, Spokane, 9/20/01.   Avista’s documentation indicates residual gas was left in the ground after a leak repair, which requires a follow up inspection within 30 days.  Documentation indicates that a follow up inspection was not conducted until 1/15/02.

- 8324 E. Sinto, Spokane, 4/27/01 Avista’s documentation indicates residual gas was left in the ground after a leak repair which requires a follow up inspection within 30 days.  No documentation was provided which indicated that a 30-day follow up was conducted.

- N. 13615 River Bluff Ln, 10/11/01.  Avista’s documentation indicates residual gas was left in the ground after a leak repair, which requires a follow up inspection within 30 days.  Documentation indicates that a follow up was not conducted until 12/20/01.

- 7909 N. Rye, 10/15/01.  The “leak/odor investigation” section of Avista’s  leak documentation indicates that 55% residual gas was left after repair but the “re-inspection required” section of the leak document is not marked.  A follow up recheck was not conducted until 12/26/01.

Our inspection report dated March 27, 2001, docket number UG-001851, previously identified this violation.

- WAC 480-93-186(b) Leakage Classification and Action Criteria

Leak grades.  Based on an evaluation of the location and/or magnitude of a leak, one of the following leak grades shall be assigned, thereby establishing the leak repair priority.  A gas company may utilize an alphabetical grade classification, i.e. Grade A for Grade 1, Grade B for Grade 2, and Grade C for Grade 3 if it has historically utilized such a grading designation.

Grade 1 - Grade 1 means a leak that represents an existing or probable hazard to persons or property and requiring immediate repair or continuous action until conditions are no longer hazardous.

Grade 2 - Grade 2 means a leak recognized as being non-hazardous at the time of detection but requiring scheduled repair based on probable future hazard.

Grade 3-Grade 3 means a leak that is non-hazardous at the time of detection and can reasonably be expected to remain non-hazardous.

Leakage classification and control requirements are provided in Table 1.  The examples of leakage provided in the table are guidelines and are not exclusive.  The judgment of the gas company personnel at the scene is of primary importance in determining the grade assigned to a leak.

Findings:

Goldendale/Stevenson District:

Avista personnel discovered a leaking valve while performing routine annual valve maintenance.  This leak was not graded as required by WAC 480-93-186.

- WAC 480-93-187(2) Records and Self-Audit   The following data and information shall be recorded and maintained.  Every gas company, which by law must report leaks to a regulatory agency charged by law with environmental protection, shall file copies of those reports with the commission.  Data and information which cannot reasonably be expected to be available under the particular circumstances of a leak situation need not be reported, but at a minimum will include the following:

(a) 	Date and time detected, date and time reported, date and time and name of employees dispatched, and the date and time the leak was investigated;

(b) 	Date and time the leak was reevaluated before repair, and the name of the employee involved;

(c) 	Date and time of repair, when a Grade 1 leak is involved, and the name of the employee in charge of the repair;

(d) 	Date and time the leak was rechecked after repair and the employee involved;

(e) 	If leak was reportable to an environmental agency, date and time report made to regulatory authority and name of reporting employee;

(f) 	Location of leak (sufficiently described to allow ready location by other competent personnel);

(g) 	Leak grade;

(h) 	Line use (distribution, transmission, etc.);

(i) 	Method of leak detection (if reported by outside party, list name and address);

(j) 	Part of system where leak occurred  (main, service, etc.);

(k) 	Part of system which leaked  (pipe, valve, fitting, compressor or regulator station, etc.);

(l) 	Material which leaked (steel, plastic, cast iron, etc.);

(m) Origin of leak;

(n) 	Pipe description;

(o) 	Type repair;

(p) 	Leak cause;

(q) 	Date pipe installed (if known);

(r) 	Whether under cathodic protection; and

(s) 	Magnitude of CGI readings at appropriate locations which are a part of the classification procedures contained in Table 1 of WAC 480-93-186 (codified as WAC 480-93-18601).

REPEAT VIOLATION

Findings:

##### Spokane/Ritzville District:

Staff reviewed leak records for the Spokane district and observed leak records and documentation without the required information as defined in 480-93-187.  Follow-up records for some grade 1 leaks with residual gas were incomplete with no re-check documentation.  Following are examples of noted documentation deficiencies:

- 1509 N. Locust, Valley, 10/18/01.   Documentation did not indicate the magnitude of Combustible Gas Indicator (CGI) readings, which are a part of the classification procedures.  Paperwork indicates that the broken pipeline may have been leaking for 30 days but no CGI readings are recorded.

- 18019 N. Lidgerwood, Colbert, 11/6/01.   Documentation did not indicate the magnitude of CGI readings, which are a part of the classification procedures.  A follow up was conducted 30 days after the leak was evaluated but the original leak form does not indicate whether there were any residual readings, which would require a 30-day follow up.

- 6252 Gunner, Nine Mile, 12/3/01.  Documentation did not indicate the magnitude of CGI readings, which are a part of the classification procedures.  A follow up was conducted within 30 days after the leak was evaluated but the original leak form does not indicate whether there were any residual readings, which would require a 30-day follow up.

- 16101 N. Chronicle, 11/27/01.  Documentation did not indicate the magnitude of CGI readings, which are a part of the classification procedures.

- 2319 S. Newer Ct., Veradale, 12/05/01.  Avista was unable to produce a leak document or record for this damaged, broken and blowing meter set.

Our inspection report dated March 27, 2001, docket number UG-001851, previously identified this violation.

### WAC 480-93-188 (6) Gas leak Surveys  Leak survey records.  For the most current and immediately preceding survey of an area, the following information shall be maintained:

### (a) Description of system and area surveyed (this could include maps and leak survey logs);

### (b) Survey results;

### (c) Survey method;

### (d) Names of those making survey;

### (e) Survey dates; and

### (f) In addition to the above, the following records shall be kept for pressure drop test:

### (i) The name of the gas company, the name of the gas company employee responsible for making the test, and the name of any test company used;

### (ii) Test medium used;

### (iii) Test pressure;

### (iv) Test duration;

### (v) Pressure recording charts, or other record of pressure readings; and

### (vi) Test results.

Findings:

##### Spokane/Ritzville District:

- 8324 E. Sinto, Spokane, 4/27/01.  No pressure drop test information was documented after leak repair.

- 4914 N. Stone, 12/13/01.  Avista’s documentation indicates that a short section of replacement pipeline was installed to repair a broken service line.  No pressure drop test information was documented after leak repair.

- 18019 N. Lidgerwood, Colbert, 11/6/01.  No pressure drop test information was documented.

- 6252 Gunner, Nine Mile, 12/3/01.  Documentation does not indicate whether a pressure drop test was conducted or whether pre-tested pipe was used in the repair.

- 1509 N. Locust, Valley, 10/18/01.   No pressure drop test information was documented.

- Part 192.469 External Corrosion Control: Test Stations  Each pipeline under cathodic protection required by this subpart must have sufficient test stations or other contact points for electrical measurement to determine the adequacy of cathodic protection.

REPEAT VIOLATION

Findings:

Goldendale/Stevenson District:

Staff located a section of 2 inch Steel Wrapped (STW) pipe that does not have cathodic protection.  The pipeline is attached to the Mill St. Bridge.

Staff located a three quarter inch main, located in the 600 block of Brooks St., which serves four individual services that do not have cathodic protection.

The existing test sites for these systems did not detect the deficiencies.

Our inspection report dated March 27, 2001, docket number UG-001851, previously identified this violation.

- Part 192.383(b) Excess Flow Valves Customer Notification   Which customers must receive notification.  Notification is required on each newly installed service line or replaced service line that operates continuously throughout the year at a pressure not less than 68.9 kPa (10 psig) and that serves a single residence.  On these lines an operator of a natural gas distribution system must notify the service line customer once in writing.

Findings:

Spokane/Ritzville District:

Avista’s Spokane office was unable to provide records of the required notification for new construction plat customers.

- Part 192.467(d) Casing of Pipelines  Inspection and electrical tests must be made to assure that electrical isolation is adequate.

Findings:

Spokane/Ritzville District:

Avista’s records indicate that the following casings do not have contact points for testing of electrical isolation between casing and carrier pipe.  Avista is currently leak surveying these casings. Leak surveys are not an edequate method of assuring electrical isolation between casings and carrier pipe.

- Division & Cataldo, Spokane

- Trent & Sherman, Spokane

- Rebecca & Freeway, Spokane

- Geiger Blvd & Garden Springs, Fairchild to Spokane

- Darden Springs & 100’ E of Geiger, Fairchild to Spokane

- Lenedeke & 8th (W casing), Fairchild to Spokane

- Trent & Tracks at Airport, Spokane Valley

- Trent & Rolling Mill Rd, Spokane Valley

- Trent & 14015 E, Spokane Valley

- Harvard & Wellesley, Spokane Valley

- Tracks & 5 SE (1/2 mile E of U or Bruce Rd), Ritzville

- Part 192.491(c) Corrosion Control Records  Each operator shall maintain a record of each test, survey, or inspection required by this subpart in sufficient detail to demonstrate the adequacy of corrosion control measures or that a corrosive condition does not exist.  These records must be retained for at least 5 years, except that records related to §§192.465(a) and (e) and 192.475(b) must be retained for as long as the pipeline remains in service.

Findings:

##### Spokane/Ritzville District:

Ritzville was unable to provide records that an atmospheric corrosion-monitoring program was in place at the time of this inspection.