###### 2010

###### Electric Service Reliability Report

 2011 Avista Corporation. All Right Reserved

Permission of the Copyright owner is granted to users to copy, download, reproduce, transmit or distribute any part of this document provided that: (1) the user includes Avista’s copyright notice on all copies, and (2) the materials are not used in any misleading or inappropriate manner. Furthermore, no portion of the attached work shall be republished in printed or digital form without the written permission of the Copyright owner.

Table of Contents

Introduction 	1

Definitions 	2

Data Collection and Calculation Changes 	3

Data Collection 	3

Interruption Cause Codes 	3

Customers Experiencing Multiple Interruptions 	4

Major Events 	4

Table 1.1 – 2010 Major Event Days 	5

Customer Complaints 	5

System Indices 	6

Table 2.1 - Reliability Statistic Target by Indice 	6

Chart 2.1 – SAIFI - Sustained Interruptions / Customer 	7

Chart 2.2 – Sustained Interruptions / Customer Historic Comparison 	7

Chart 2.3 - SAIFI Linear Trend Line Chart 	8

Chart 2.4 - MAIFI Momentary Interruption Events / Customer 	9

Chart 2.5 – Momentary Interruptions/ Customer Historic Comparison 	9

Chart 2.6 - SAIDI – Average Outage Time / Customer 	10

Chart 2.7 - SAIDI Linear Trend Line Chart 	11

Chart 2.8 - CAIDI – Average Restoration Time 	11

OFFICE Indices 	12

Chart 3.1 – SAIFI - Sustained Interruptions / Customer 	12

Chart 3.2 - MAIFI Momentary Interruption Events / Customer 	12

Chart 3.3 - SAIDI – Average Outage Time / Customer 	13

Chart 3.4 - CAIDI – Average Restoration Time 	13

Areas of Concern 	14

Cause Information 	14

Colville Area Work Plans 	16

Table 4.1 - Colville Area Major Reliability Projects by Feeder 	18

Table 4.2 - Colville Area Historical & Proposed Future Reliability Projects by Feeder 	18

Avista System Wide Work Plans 	19

Chart 4.1 – Squirrel Related Outages 	19

Avista System Wide Vegetation Management Plan 	20

Customers Experiencing Multiple Interruptions 	21

Chart 5.1 - Avista Service Territory - CEMIn 	21

Chart 5.2 - Colville Office - CEMIn 	22

Chart 5.3 - Davenport Office - CEMIn 	23

Chart 5.4 - Deer Park Office - CEMIn 	24

Chart 5.5 - Othello Office - CEMIn 	25

Chart 5.6 - Palouse Office - CEMIn 	26

Chart 5.7 - Lewis-Clark Office - CEMIn 	27

Chart 5.8 - Spokane Office - CEMIn 	28

Chart 5.9 - Sandpoint Office - CEMIn 	29

Chart 5.10 - Kellogg Office - CEMIn 	30

Chart 5.11 - Coeur d’Alene - CEMIn 	31

Chart 5.12 - Grangeville Office - CEMIn 	32

Monthly Indices 	33

Chart 6.1 – SAIFI - Sustained Interruptions / Customer 	33

Chart 6.2 - MAIFI Momentary Interruption Events / Customer 	33

Chart 6.3 - SAIDI – Average Outage Time / Customer 	34

Chart 6.4 - CAIDI – Average Restoration Time 	34

Customer Complaints 	35

Table 7.1 - Commission Complaints 	35

Table 7.2 - Customer Complaints 	36

Sustained Interruption Causes 	38

Table 8.1 - % SAIFI per Cause by Office 	38

Chart 8.1 – % SAIFI per Cause by Office 	39

Table 8.2 - % SAIDI per Cause by Office 	40

Chart 8.2 – % SAIDI per Cause by Office 	41

Table 8.3 - % SAIFI per Cause by Month 	42

Chart 8.3 – % SAIFI per Cause by Month 	43

Table 8.4 - % SAIDI per Cause by Month 	44

Table 8.4.1 Average Outage Time 	45

Chart 8.4 – % SAIDI per Cause by Month 	46

Momentary Interruption Causes 	47

Table 9.1 - % MAIFI per Cause by Office 	47

Table 9.1.1 - % MAIFI per Cause by Office (Washington only) 	48

Chart 9.1 – % MAIFI per Cause by Office 	49

Table 9.2 - % MAIFI per Cause by Month 	50

Chart 9.2 – % MAIFI per Cause by Month 	51

Major Event Day Causes 	52

Chart 10.1 – % SAIFI by Cause Code for the Major Event Days 	52

Table 10.1 – % SAIFI by Sub Cause Code for the Major Event Days 	53

Table 10.2 – Yearly Summary of the Major Event Days 	54

Interruption Cause Codes 	55

Table 11.1 – Interruption Cause Codes 	55

Office Areas 	57

Chart 12.1 – Office Areas 	57

Indices Calculations 	58

Sustained Interruption 	58

Momentary Interruption Event 	58

SAIFI – System Average Interruption Frequency Index 	58

MAIFIE – Momentary Average Interruption Event Frequency Index 	58

SAIDI – System Average Interruption Duration Index 	58

CAIDI – Customer Average Interruption Duration Index 	59

CEMIn – Customers Experiencing Multiple Sustained Interruptions more than n. 	59

CEMSMIn – Customers experiencing multiple sustained interruption and momentary interruption events. 	59

MED - Major Event Day 	60

Numbers of Customers Served 	61

Table 13.1 – Numbers of Customers Served 	61

Attachment 1 – SAIDI and SAIFI Historical Summary 	61

Company Contact 	61

# Introduction

Pursuant to WAC 480-100-393 and WAC 480-100-398, Avista Corporate dba Avista Utilities (“Avista” or “the Company”) submits its annual Electric Service Reliability Report.  The report describes the Company’s reliability monitoring and reliability metrics for 2010.  All numbers included in this report are based on system-data.  The Company’s system includes 11 geographical divisions with two of those divisions overlapping the Washington and Idaho border leading to a commingling of jurisdictional customers.  A map of Avista’s operating area is included on page 58 of this report.

WAC 480-100-393 (3)(b) requires the establishment of baseline reliability statistics. The Company’s baseline statistics are included in this report and compare the current year data to the baseline year of 2005 and years in between. The Company also provides a statistical target that represents an analysis based on an average over a time period and adding two standard deviations. Year to year variations should be below this target, but may provide information that shows continuing trends.

Avista has reported in its previous annual reports that the completion of the transition to the Outage Management Tool (OMT) system had caused an increase in the variability of the data collected from 2001 to 2007. The 2009 Annual Report (UE-100659) indicated that a gradual increase in the SAIFI and SAIDI numbers that cannot be attributed to the transition to the OMT system was occurring. This trend line is still showing a gradual increase but at a slower rate after including the 2010 data. The charts on pages 9 and 12 show a trend line for SAIFI and SAIDI historical data.

Continued scrutiny will be important over the next year or two to determine if the rate of increase for SAIFI/SAIDI continues to slow, due to the reliability improvement programs implemented in 2009, 2010, and currently underway in 2011.

The 2010 SAIFI and SAIDI reliability indices are higher than the 2005 baseline, which may be due to the under reporting that may have occurred during the transition to OMT in 2005. On another note both the 2010 MAIFI and CAIDI reliability indices are below the 2005 baseline.

Avista added a new section beginning in the 2007 annual report (UE-080787) which analyzes the areas where customers are experiencing multiple sustained outages. This new section provides analysis of a reliability indice called CEMIn, which implies Customers Experiencing Multiple sustained Interruptions more than n times.

Avista continues to review its annual baseline reliability statistics in light of operational experience under current regulatory protocol.  Avista may modify its baseline statistics as appropriate and will update the Commission accordingly.

# Definitions

“Reliability Statistic” – Standard Statistics measures and calculation methods are per the IEEE Standard 1366-2003 (or latest version) Titled “IEEE Guide for Electric Power Distribution Reliability Indices”. Same as Reliability Indices.

"Major event" – Modified this definition to the IEEE Standard 1366-2003 (or latest version) of Major Event Day (MED), which uses a process “Beta Method” to identify a Major Event Day. The previous definition was “An event that impacts more than 5% of the Company’s customers and causes outages of more than 24 hours in duration in any given division within its territory”.

“Sustained Interruption” - An interruption lasting longer than 5 minutes.

“Momentary Event Interruption” – An interruption(s) of duration 5 minutes or less.  Each event consists of one trip and one reclose operation that occur within 5 minutes.  For example, if an interrupting device operates three times and then holds, this would be counted as three events with the number of customers affected as three times the Ni.

"Baseline reliability statistic" – Avista will compare its reliability statistics to the year 2005.

“Reliability Target” - A statistical method was developed in 2004 for baseline statistics. The method is defined as the average over a specific timeframe and 2 times the standard deviation. For 95% of the time, the Reliability Statistic should be below the target.

“Customer Complaint” - When a customer is not satisfied with the Company as it relates to Electric Reliability and makes a complaint directly to a Company representative.

“Commission Complaint” – When a customer is not satisfied with the Company as it relates to Electric Reliability and files a complaint directly with the Commission.

# Data Collection and Calculation Changes

WAC 480-100-398 (2) requires the Company to report changes made in data collection or calculation of reliability information after initial baselines are set.  This section addresses changes that the Company has made to data collection.

### Data Collection

Since Avista’s Electric Service Reliability Monitoring and Reporting Plan was filed in 2001 (UE-011428), there have been several improvements in the methods used to collect outage data. In late 2001, centralizing the distribution trouble dispatch and data collection function for Avista’s entire service territory began.  The distribution dispatch office is located in the Spokane main complex.  At the end of September 2005, 100% of the Company’s feeders, accounting for 100% of the customers, are served from offices that employ central dispatching.

The data collected for 2010 represents the fifth full year of outage data collected through the Outage Management Tool (OMT). For 2010, all data was collected using the “Outage Management Tool” (OMT) based on the Company’s Geographic Information System (GIS).  The OMT system automates the logging of restoration times and customer counts.

Avista discovered a software coding error that has been within the OMT system since 2002 that caused a small increase in the SAIDI and CAIDI for 2008. Previous years were also evaluated to determine the overall impact to the Avista baseline statistics and at this time Avista is not proposing a change to the baseline numbers. The software error only occurred during very specific outage conditions when a group of customers with an initial outage starting time were “rolled” up into another group of customers that were determined to be part of the first group outage. The second group may have had a later outage starting time. When the first group of customer outage information was rolled up, the original outage starting time was lost and the second group outage starting time was used for both groups of customers instead of using the first outage starting time. The number of customers was counted correctly.

Even as good as the OMT system is at quantifying the number of customers and duration of the outage duration, there still are areas where the data collection is not precise. Determining the exact starting time of an outage is dependent on when a customer calls in, how well the Avista Distribution Dispatcher determines where the outage is and defines the device that has opened to remove the faulted section.

As AMR/AMI metering is implemented in the future and the customer meter provides outage information to the OMT system through an interface, the SAIDI and CAIDI numbers are expected to increase. This is similar to the above discussion.

Use of the OMT system and GIS data has improved the tracking of the numbers of customers without power, allowed for better prioritization of the restoration of service, and the improved dispatching of crews.

### Interruption Cause Codes

Cause code information is provided in this report to give readers a better understanding of outage sources. Further, the Company uses cause information to analyze past outages and, if possible, reduce the frequency and duration of future outages.

For 2011, Avista will stop using the subcategory “protected” under the “Animal” category. Almost all birds are considered protected, so there is little differentiation between the “Bird” and “Protected” subcategories. Avista will include additional information in the Remarks section as reported from the field personnel.

### Customers Experiencing Multiple Interruptions

The IEEE Standard 1366P-2003 provides for two methods to analyze data associated with customers experiencing multiple momentary interruptions and/or sustained interruptions. Avista’s Outage Management Tool (OMT) and Geographical Information System (GIS) provide the ability to geospatially associate an outage to individual customer service points. This association allows for graphically showing Customers Experiencing Multiple sustained Interruptions (CEMIn) with Major Event Day data included onto GIS produced areas. Data can be exported to MS Excel to also create graphs representing different values of n. 2010 information is provided in the  new section added to the 2007 report (UE-080787) after the Areas of Concern Section to summarize the analysis Avista performed on the 2010 outage data. The calculation for CEMIn and Customers Experiencing Multiple Sustained and Momentary Interruptions CEMSMIn is provided in the Indices Section.

### Major Events

Major Events and Major Event Days as used in this report are defined per the IEEE Guide for Electric Power Distribution Reliability Indices, IEEE P1366-2003. The following definitions are taken from this IEEE Guide.

Major Event – Designates an event that exceeds reasonable design and or operation limits of the electric power system. A Major Event includes at least one Major Event Day (MED).

Major Event Day – A day in which the daily system SAIDI exceeds a threshold value, TMED. For the purposes of calculating daily system SAIDI, any interruption that spans multiple calendar days is accrued to the day on which the interruption began. Statistically, days having a daily system SAIDI greater than TMED are days on which the energy delivery system experienced stresses beyond that normally expected (such as severe weather).  Activities that occur on major event days should be separately analyzed and reported.

The Company will use the process defined in IEEE P1366 to calculate the threshold value of TMED and to determine MED’s.  All indices will be reported both including and excluding MED’s. The comparisons of service reliability to the baseline statistics in subsequent years will be made using the indices calculated without MED’s.

#### Table 1.1 – 2010 Major Event Days

| Major Event Days | SAIDI (Customer-Minutes) | Cause |
| --- | --- | --- |
| 2010 Major Event Day Threshold | 11.110 |  |
| May 3, 2010 | 21.04 | Wind Storm |
| November 16, 2010 | 68.67 | Wind and Snow Storm |

Additional analysis of the 2010 Major Event Days is provided in this Annual Report as was done in previous years in the Major Event Day Causes section on page 52.

### Customer Complaints

The Company tracks reliability complaints in two areas, Commission Complaints and Customer Complaints, which are defined in the Definitions section. See the Customer Complaints section on Page 37 for a summary of results for this year.

# System Indices

The charts below show indices for Avista’s Washington and Idaho (“system”) electric service territory by year.  Breakdown by division is included later in this report.  Each chart shows seven years of data along with the baseline reliability statistic which is highlighted in green. The Company also has calculated a reliability target that is the average over the previous five years plus two standard deviations. This target is shown in yellow on the reliability indice charts.

The reliability targets have been adjusted by removing Major Event Days, MED’s, as defined in the previous section.

#### Table 2.1 - Reliability Statistic Target by Indice

| Indice | 2005-2009 Average (Excluding Major Events) | 2005 Baseline | Reliability Target (Ave + 2 Standard Deviations) |
| --- | --- | --- | --- |
| SAIFI | 1.26 | 0.97 | 1.70 |
| MAIFI | 4.9 | 3.58 | 4.17 |
| SAIDI | 210 | 108 | 147 |
| CAIDI | 116 | 112 | 137 |

Additional comparisons of the Reliability Indices are provided in the Office and Monthly Indices section of this report.

The Company continues to use the definition of major events as described above to be consistent with IEEE Standards.  Therefore, the following charts show statistics including the effect of major events per this definition. Both the Baseline Statistic is shown for the year 2005 (green bar), along with the Avista Target Statistic which is shown as the yellow bar.

Refer to Attachment 1 – SAIDI and SAIFI Historical Summary for additional historical information.

### Chart 2.1 – SAIFI - Sustained Interruptions / Customer

Baseline Year 2005

### Chart 2.2 – Sustained Interruptions / Customer Historic Comparison

SAIFI for 2010 was over the 2005 baseline statistic and does represent an increasing trend, but at a slower rate than previously reported in the 2009 Annual Report (UE-100659). The 2010 SAIFI number is lower than the two previous years and may represent decreases due to Company expenditures specifically targeting reliability. Using a simple linear regression to establish a trend line, it would look like about a 6.7% growth in the number of customers affected. The R2 coefficient of determination shows a much stronger correlation to the data than last year. A chart of this analysis has been provided just after this discussion. Planned outages were a major contributor to the number of customers affected along with trees and substation equipment.

There were 76,321 customers affected by sustained outages caused by weather in 2010.  This compares to the 2004–2009 average of 92,655 customers.

23,355 customers were affected by sustained outages associated with animal related incidents. This compares to the 2004-2009 average of 32,032 customers. The vast majority of the animal related reasons were associated with squirrel caused incidents.

Planned maintenance activities and forced repairs affected 45,673 customers as compared to the 2004-2009 average of 29,511 customers. Continued maintenance activities associated with the Company equipment replacement program contributed to the increase in this cause and reduced the Overhead Equipment outage causes.

Outages associated with Tree causes affected 80,920 customers as compared to the 2004–2009 average of 49,465.

### Chart 2.3 - SAIFI Linear Trend Line Chart

### Chart 2.4 - MAIFI Momentary Interruption Events / Customer

Baseline Year 2005

Chart 2.5 – Momentary Interruptions/ Customer Historic Comparison

The 2010 results for MAIFI show a large decrease over both 2008 and 2009 data and also below the 2005 baseline year number. There was a reduction in weather related momentary outages that cannot be explained on weather conditions alone. There was a corresponding decrease in the number of undetermined outages, which can reflect that weather conditions did cause outages. The overall improvements in the MAIFI numbers maybe due to tree trimming efforts along with Overhead Equipment replacement and Underground Equipment replacement. Some of the Urban areas have had the instantaneous trip function blocked, which reduces the total feeder customer momentary impacts, but may increase both SAIFI and SAIDI numbers for a few customers located downstream of a fuse lateral.

Distribution Dispatch continues to make improvements in correlating the momentary outages with subsequent sustained outages, which reduces the undetermined causes.

All other categories showed a slight decrease that would be consistent with previous years.

### Chart 2.6 - SAIDI – Average Outage Time / Customer

Baseline Year 2005

### Chart 2.7 - SAIDI Linear Trend Line Chart

Chart 2.8 - CAIDI – Average Restoration Time

Baseline Year 2005

125

112

111

116

113

127

118

137

0

40

80

120

160

200

2004

2005

2006

2007

2008

2009

2010

Target

Ave. Restoration Time / Customer (min)

CAIDI

Excluding Major Events

Major Events

# OFFICE Indices

### Chart 3.1 – SAIFI - Sustained Interruptions / Customer

### Chart 3.2 - MAIFI Momentary Interruption Events / Customer

### Chart 3.3 - SAIDI – Average Outage Time / Customer

### Chart 3.4 - CAIDI – Average Restoration Time

# Areas of Concern

As in previous years, Colville continues to have the lowest reliability of Washington’s operating areas. However, the Colville area continues to show improvement over previous years as work plans are implemented.  Colville was judged lowest based on its performance in the yearly indices for SAIFI, SAIDI, CAIDI, and MAIFI.  Within the Colville area, six feeders were identified as the Areas of Concern for 2010. These feeders are Gifford 34F1, Gifford 34F2, Colville 34F1, Chewelah 12F3, Chewelah 12F4, and Spirit 12F1. The first four feeders listed were also identified in the 2009 report (UE-100659) as Areas of Concern.

### Cause Information

Generally rural areas have a greater number of outages per customer.  Colville is a predominately rural and forested area. There are approximately 2,342 miles of distribution line exposed to weather, underground cable failures and tree problems.  Unlike most of the Company’s system, lines in this area are built on the narrow, cross-country rights-of-way, typical of PUD construction practices prior to Avista acquiring the system. These conditions make patrolling, tree trimming, right of way clearing and other maintenance difficult. When cost effective, Avista moves sections of these overhead lines to road rights of way and/or converts them to underground.

Further, when outages occur in rural areas, the time required to repair damage is longer. More time is required for first responders to arrive and assess the damage and more time is required for the crew to reach the site.  Often the damage is off road and additional time is required to transport materials and equipment to the site.

Listed below is a summary of the specific cause data for each feeder.  This is a compilation of data from the Avista Outage Management Tool and the reporting from our local servicemen to Distribution Dispatch. Data from the reporting system is shown as a percentage of total customer-outages, (SAIFI) for that feeder.

Snow loading on green healthy trees growing beyond the rights-of-way often causes them to bend or break and contact distribution lines. These trees are not cut as part of our vegetation management program because they are outside our right of way and are considered healthy marketable timber.

Gifford 34F1

- 28.7% Weather: snow, wind and lightning storms

- 22.8% Equipment

- 27.6% Public

- 5.7% Trees

- 2.8% Planned outages

Gifford 34F2

- 1.8% Weather: Wind, snow, and lightning storms

- 12.2% Equipment

- 20.2% Public

- 49.2% Trees

- 8.7% Planned outages

- 14.5% Animal: birds or squirrels

Colville 34F1

- 37.4% Weather; snow, wind and lightning storms

- 8.6% Equipment

- 0.0% Pole fires

- 28.5% Trees

- 9.2% Planned outages

Chewelah 12F3

- 6.6% Weather: snow, wind and lightning storms

- 19.3% Equipment

- 9.2% Trees

- 62.6% Planned outages

Chewelah 12F4

- 8.2% Weather: wind and lightning storms

- 4.0% Equipment

- 7.5% Trees

- 76.7% Planned outages

Spirit 12F1

- 45.8% Weather: snow, wind and lightning storms

- 2.4% Equipment

- 37.4% Trees

- 12.4% Pole Fire

### Colville Area Work Plans

The improvement work that has been accomplished or planned for each feeder is listed below.  The Company’s reliability working group is continuing to study these feeders to develop additional work plans. Each of the identified feeders also had planned outages that correspond to the maintenance and replacement activities in the area.

Gifford 34F1

- 10,300’ of URD cable was replaced in 2009, and 12,850’ of URD cable is planned for replacement in 2010. Completed in 2010.

- A reliability improvement project is scheduled for 2010 in the Pleasant Valley area of this feeder to replace (42) 1940 class poles with new poles and replace approximately 2.2 miles of 1-phase #6A, #6CW, and #9 1/2D wire (all in poor shape) with 2-phases of #2ACSR wire. Completed in 2010.

- Vegetation Management completed tree trimming of 698 trims and two tree removals in 2010. No work planned for 2011.

Gifford 34F2

- 2,775’ of URD cable was replaced in 2009, and 8,510’ of URD cable is planned for replacement in 2010. 2009 Cable work was completed. Due to Cultural review issues on some of the Tribal lands only 3,000 feet was replaced in 2010. Continued work and negotiations for the remaining 5,000 feet in 2011.

- A reliability improvement project is planned for 2010 to convert 3.5 miles of 3-phase overhead line to URD in the Twin Lakes area near Inchelium. Plan not implemented again due to Cultural review issues on the Tribal lands. Project will be completed overhead in 2011.

Colville 34F1

- A reliability improvement project is planned for 2010 to perform an RF survey of the trunk of this feeder and perform follow-up work to address issues that are found. Completed in 2010 and repairs made on four or five pieces of equipment.

- Vegetation Management completed 14 tree trims and 373 tree removals in 2010. No work planned for 2011.

- $100k has been budgeted in 2011 to replace outage prone overhead sections with URD cable.

- $62k has been budgeted in 2011 to install Wild Life Guards in 2011.

Chewelah 12F3

- 7,700’ of URD cable was replaced in 2009, and 5,200’ of URD cable is planned for replacement in 2010. Completed in 2010.

- A reliability improvement project was completed in 2009 to split the Chewelah 12F3 into two feeders (Chewelah 12F3 and Chewelah 12F4).  Also, another reliability project was completed to convert two miles of 1-phase overhead line with bad access with 2-phases of URD. Completed in 2010.

- Late December 2009 saw the completion of the new Chewelah 12F4 feeder, which split the existing 12F3 into two parts. The original 12F3 feeder was almost 66 miles in circuit miles and is now about 26 circuit miles. 12F4 will be about 40 circuit miles. Completed in 2010.

- Vegetation Management completed 2,051 tree trims and 1,642 tree removals in 2010. No work planned for 2011.

Valley 12F1

- No URD cable was replaced in 2009, but 300’ of URD cable is planned for replacement in 2010. Completed in 2010.

- A reliability improvement project was completed in 2009 to convert 1.9 miles of 1-phase overhead line to URD in the Hesseltine Rd. area. Completed in 2010.

- Another reliability improvement project is planned for 2010 to convert 3.2 miles of 2-phase overhead line to 1-phase URD in the Jepsen Rd area. Completed in 2010.

- Wood Pole Inspection was completed in 2010, with capital follow-up work scheduled for 2011.

- Vegetation Management completed 1,661 tree trims and 2,508 tree removals along with extensive brush removal in 2010. No work planned for 2011.

- This feeder will not appear in 2011 report due to improvements over the previous years.

Valley 12F3

- 1,300’ of URD cable was replaced in 2009, and 700’ of URD cable is planned for replacement in 2010.

- This feeder will not appear in 2011 report due to improvements over the previous years.

- Vegetation Management completed 287 tree trims and 101 tree removals along with some brush removal in 2010. No work planned for 2011.

Avista typically uses several different protective devices on its feeders to isolate faulted or overloaded sections and also continue to serve the remaining customers. Generally, two different protection schemes are used to either “save” the lateral fuse or “blow” the lateral fuse by using or not using the instantaneous over current trip. Depending on the feeder, number of customers, types of faults, (temporary or permanent), customer type, time of year, etc. both of these schemes may be used on an individual feeder at different times at the discretion of the field personnel. With the better data and cause code collection that OMT provides and the customer growth on some of the Colville feeders, changes to the type of scheme used has been reviewed. Listed below are major reliability projects specifically identified by feeder.

#### Table 4.1 - Colville Area Major Reliability Projects by Feeder

| Feeder | Decisions/ basis | 2011 | 2011 and Beyond |
| --- | --- | --- | --- |
| Gifford 34F1 | Reliability improvements | Budgeted | Planned |
| Gifford 34F2 | Reliability improvements | Budgeted | Planned |
| Colville 34F1 | Reliability improvements | Budgeted | Planned |
| Chewelah 12F4 | With the recent splitting of the Chewelah 12F3 feeder into two separate feeders, some additional monitoring needs to be done. |  | Planned |
| Colville 12F2 | Reliability improvements and voltage drop improvement. | Budgeted | Reconductor and replace recloser |
| SPI12F1 | A major portion of this feeder will be reconductored for voltage drop improvement. Some additional reliability improvement should be done with this project. | Budgeted | Planned |
| Orin 12F1 | Reliability Improvements | Budgeted | Add recloser |
| Orin 12F3 | Reliability Improvements | Budgeted | Add recloser |

#### Table 4.2 - Colville Area Historical & Proposed Future Reliability Projects by Feeder

| Feeder Name | Last WPM Inspection | Proposed WPM Inspection | Proposed WPM Follow-up | Transformer Change-outs | Last Veg Management | Veg Management Proposed Year | Wildlife Guards Proposed Year |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GIF34F1 |  | 25% in 2011 | 25% in 2012 | 78 in 2012 or 2013 | 2009 | 2014/2014 | 2013 |
| GIF34F2 | 1995 |  |  | 50 in 2014, 2015, or 2016 | 2006 | 2012 | 2011 |
| CHW12F3 | 1997 |  |  | 42 in 2014, 2015, or 2016 | 2000 | 2011 |  |
| CHW12F4 | 1997 |  |  | 28 in 2014, 2015, or 2016 | 2000 | 2011 |  |
| CLV34F1 | 1999 |  |  | 39 in 2014, 2015, or 2016 | 2007 | 2013 | 2011 |
| VAL12F3 | 1998 |  |  | 37 in 2014, 2015, or 2016 | 2010 | 2015 |  |
| SPI12F1 | 1194 |  |  | 42 in 2014 |  |  |  |

### Avista System Wide Work Plans

Avista develops a detailed annual budget for various improvements to the facilities it owns and operates. For 2010, several reliability feeder projects were completed and described above. The reliability improvement should show up over the next couple of years. Valley 12F1 and Valley 12F3 have improved reliability enough to be removed from the Area of Concern list in 2011. Additionally Asset Management has developed some specific projects that are expected to improve reliability on several feeders system wide. These projects are summarized in the table above.

Material records show that some wildlife guards were installed on new distribution transformers installations starting in the mid 1980’s. With the recognition of increases in animal caused outages, new materials and improvements have been made in the construction standards for new distribution transformer installations to reduce these types of outages. Initial indications show that the outage reduction on a feeder after wildlife guards are installed is significant.

2009 was the start of the multiyear wildlife guard installation program to reduce the squirrel and bird related outages on approximately sixty feeders in Washington and Idaho. Most of the wildlife guards were installed with a hot stick on existing transformers that do not have an existing wildlife guard.

Avista installed a total of 2,043 wildlife guards on 21 feeders in 2010. There were 1,676 wildlife guards installed in Idaho on 15 feeders and 367 wildlife guards installed in Washington on six feeders.

Avista plans to install wildlife guards on seven Idaho feeders and four Washington feeders in 2011 and plans to install wildlife guards on two Colville feeders (Gifford 34F2 and Colville 34F1) in 2011.  The chart below shows the effectiveness of the wildlife guard program in reducing squirrel related outages.

#### Chart 4.1 – Squirrel Related Outages

Asset Management in conjunction with the Wood Pole Management Program stubbed or replaced numerous poles and additionally replaced numerous pole top transformers and associated cutouts/arresters.

### Avista System Wide Vegetation Management Plan

Avista has an annual vegetation management plan and budget to accomplish the plan. The budget is allocated into distribution, transmission, administration, and gas line re-clearing.

Distribution

Our current plan for Avista’s distribution system is managed by Asplundh Tree Expert Co. Every distribution circuit is scheduled to be line clearance pruned on a regular maintenance cycle of four years urban and seven years rural. Other distribution vegetation management activities include hazard tree patrol and herbicide application.

Transmission

The transmission system is managed by Avista’s forester.  All 230 kV lines are patrolled annually for hazard trees and other issues, and mitigation is done in that same year.  Approximately one third of the 115 kV transmission system is patrolled annually for hazard tree identification and assessment of right of way clearing needs.  Right of way clearing maintenance is scheduled and performed approximately every ten to fifteen years (for each line).  Interim spot work is done as identified and needed. Engineering specifications for various voltages, line configurations are followed when clearing the right of way.  Currently, the work is bid to a variety of contractors.

# Customers Experiencing Multiple Interruptions

Avista has used the data from the OMT system integrated with the GIS system to geospatially display reliability data for specific conditions. The specific conditions imply looking at the number of sustained interruptions for each service point (meter point). This would be similar to the SAIFI indice, but would be related to a certain number of sustained interruptions. Avista includes all sustained interruptions including those classified under Major Event Days. This provides a view of what each customer on a specific feeder experiences on an annual basis. Momentary Interruptions are not included in the CEMIn indice, because by IEEE definition is only applies to sustained outages. Other Momentary Indices are not included because of the lack of indication at many rural substations and line locations.

The first chart below provides a view of the percentage of customers served from the Avista system that have sustained interruptions. 65 % of Avista customers had one or fewer sustained interruptions and 4.0% of Avista customers had six or more sustained interruptions during 2010.

The remaining geographic plots show the sustained interruptions by color designation according to the legend on each plot for each office area. Note the office area is designated as the area in white for each plot and that there is overlap between adjacent office area plots. The adjacent office areas are shown in light yellow.

The plots provide a quick visual indication of varying sustained interruptions, but significant additional analysis is required to determine underlying cause(s) of the interruptions and potential mitigation.

### Chart 5.1 - Avista Service Territory - CEMIn

### Chart 5.2 - Colville Office - CEMIn

### Chart 5.3 - Davenport Office - CEMIn

Chart 5.4 - Deer Park Office - CEMIn

### Chart 5.5 - Othello Office - CEMIn

Chart 5.6 - Palouse Office - CEMIn

Chart 5.7 - Lewis-Clark Office - CEMIn

Chart 5.8 - Spokane Office - CEMIn

Chart 5.9 - Sandpoint Office - CEMIn

Chart 5.10 - Kellogg Office - CEMIn

### Chart 5.11 - Coeur d’Alene - CEMIn

### Chart 5.12 - Grangeville Office - CEMIn

Monthly Indices

Each of the following indices, reported by month, shows the variations from month to month. These variations are partially due to inclement weather and, in some cases, reflect incidents of winter snowstorms, seasonal windstorms, and in mid- and late summer lightning storms. They also reflect varying degrees of animal activity causing disruptions in different months of the year.

### Chart 6.1 – SAIFI - Sustained Interruptions / Customer

### Chart 6.2 - MAIFI Momentary Interruption Events / Customer

### Chart 6.3 - SAIDI – Average Outage Time / Customer

### Chart 6.4 - CAIDI – Average Restoration Time

# Customer Complaints

### Table 7.1 - Commission Complaints

The following is a list of Complaints made to the Commission during this year.

| Customer Address | Complaint | Complaint Category | Resolution |
| --- | --- | --- | --- |
| Spokane WA Fort Wright 12F3 # 110716 | Older neighborhood has experienced two power outages so far this season. Neighbors' service is on but she is part of 19 households that did not have power. Yesterday's outage was 6 1/2 hours in duration. Customer believes the company needs to reinvest in the infrastructure in those neighborhoods that have aging facilities. …*Customer wants to know what Avista's plans are for reinvesting in the infrastructure/facilities | Outages | Fed by 50KVA 18 Customers C Ph. 9 outages since 11/03. 3 outages in 2010 3/16/10 0:16 Company Hot Line Hold 6/20/10 2:07 Tree/Tree Growth 12/29/10 5:35 Weather snow/Ice Avista responded with a lengthy explanation on February 9, 2011 concerning the Customer recorded outages compared to the Company recorded outages. Customer was satisfied with the explanation and the complaint was closed. |

### Table 7.2 - Customer Complaints

The following is a list of complaints made to our Customer Service Representatives.

| Customer / Feeder | Complaint | Complaint Category | Resolution |
| --- | --- | --- | --- |
| Post Falls ID Pleasant View 243 | Feeder trip 09/08/10 at 7:20 p m customer upset that it has caused co. money exp the trip is to protect our equip from damaging lines and longer outages wants an incident report emailed to him for their records. | Outages | Avista Account Executive met with customer to go over outages 9/30/10. Customer satisfied with outage information. Customer thought he had automatic transfer switch but it is manual for his company. |
| Clarkston WA Dry Creek 1208 | Wind Outage 11-16-10 Concerned neighbor upset that elderly customer w/out power for long period during outage. Feels should have better communication with agencies to come to aid of elderly. She does not want a call back. | Outages | No callback documented. |
| Colville WA Orin 12F1 | Customer upset that power has been interrupted several time this week. Would like notice if planned outages. | Outages | No Resolution Documented. |
| Kamiah ID Kamiah 1291 | Customer quite upset that her power goes out, and thinks she is the only one. Also wants to complain about call center reps not putting an order for her when she calls. Avista will register complaints. | Outages | No Resolution Documented. |
| Spokane Valley WA Chester 12F3 | Customer outage complaint, says customer feels like when the neighbor called and told us there were sparks in the tree we should have responded before the power went out. Avista to explain that when we have a big wind storm we try to get to everything as quickly as possible. She also wanted me to know that she was frustrated with the lack of information customer service could provide. | Outages | No Resolution Documented. |

| Customer / Feeder | Complaint | Complaint Category | Resolution |
| --- | --- | --- | --- |
| Coeur d’Alene Appleway 111 | Customer called to say he is frustrated that our power keeps going out when he is doing important things such as watching movies and working on the computer. Customer said it happened 3-4 times in 1 month alone. | Outages | No Resolution Documented. |
| Grangeville ID Grangeville 1274 | Customer said he is having more outages then normal this year. Thinks maintenance is not being done properly. Avista advised him of the weather we are having along with wind storms this year. Customer responded the weather was bad last year also. | Outages | No Resolution Documented. |
| Chewelah WA Chewelah 12F2 | Customer reported power has been going off and on about 9 - 10 times in the last 30 days. Customer not sure if neighbors are impacted and wants to know what the cause is and why power keeps going off and on | Outages | No Resolution Documented. |

# Sustained Interruption Causes

### Table 8.1 - % SAIFI per Cause by Office

The following table lists the percentage SAIFI contribution by causes for outages excluding major event days.

| Reason | CDC | COC | DAC | GRC | KEC | LCC | OTC | PAC | SAC | SPC | DPC | All Offices |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ANIMAL | 1.5% | 1.2% | 0.3% | 3.3% | 6.0% | 17.4% | 5.4% | 2.0% | 13.7% | 5.1% | 10.3% | 5.2% |
| MISCELLANEOUS | 0.1% | 0.0% | 0.0% | 0.8% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.1% |
| POLE FIRE | 28.7% | 1.9% | 1.3% | 3.2% | 0.3% | 1.2% | 1.6% | 6.9% | 0.1% | 17.9% | 1.9% | 8.8% |
| WEATHER | 4.9% | 18.1% | 29.6% | 24.2% | 17.0% | 25.4% | 49.4% | 31.7% | 2.5% | 13.4% | 6.2% | 17.1% |
| UNDETERMINED | 8.7% | 8.5% | 15.1% | 2.9% | 22.8% | 1.1% | 9.1% | 5.8% | 5.6% | 5.7% | 0.2% | 7.0% |
| TREE | 13.3% | 18.3% | 17.8% | 13.4% | 15.3% | 29.7% | 4.1% | 26.0% | 24.4% | 15.8% | 20.9% | 18.2% |
| PUBLIC | 7.9% | 8.6% | 4.3% | 6.8% | 7.8% | 7.7% | 1.2% | 10.5% | 4.5% | 14.4% | 7.7% | 9.7% |
| COMPANY | 1.5% | 0.4% | 3.7% | 16.8% | 0.0% | 0.0% | 0.0% | 3.0% | 3.1% | 7.5% | 6.4% | 5.2% |
| EQUIPMENT OH | 25.8% | 12.6% | 8.3% | 10.6% | 16.2% | 5.9% | 14.0% | 5.0% | 15.8% | 4.3% | 9.4% | 9.5% |
| EQUIPMENT UG | 0.3% | 0.5% | 3.7% | 0.8% | 0.5% | 2.0% | 0.2% | 1.1% | 0.1% | 0.4% | 0.6% | 0.7% |
| EQUIPMENT SUB | 3.6% | 4.8% | 2.9% | 1.5% | 5.8% | 0.0% | 0.8% | 0.8% | 26.4% | 9.3% | 22.9% | 8.3% |
| PLANNED | 3.7% | 25.1% | 13.0% | 15.7% | 8.3% | 9.5% | 14.2% | 7.3% | 3.8% | 6.1% | 13.6% | 10.2% |

| CDC | Coeur d’Alene | LCC | Lewiston-Clarkston |
| --- | --- | --- | --- |
| COC | Colville | OTC | Othello |
| DAC | Davenport | PAC | Palouse |
| DPC | Deer Park | SAC | Sandpoint |
| GRC | Grangeville | SPC | Spokane |
| KEC | Kellogg/ St. Maries |  |  |

Chart 8.1 – % SAIFI per Cause by Office

The following chart shows the percentage SAIFI contribution by causes for outages excluding major event days.

### Table 8.2 - % SAIDI per Cause by Office

The following table lists the percentage SAIDI contribution by causes for outages excluding major event days.

| Reason | CDC | COC | DAC | GRC | KEC | LCC | OTC | PAC | SAC | SPC | DPC | All Offices |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ANIMAL | 1.3% | 0.5% | 0.2% | 7.8% | 3.7% | 5.2% | 6.1% | 1.3% | 9.1% | 3.4% | 12.9% | 3.9% |
| MISCELLANEOUS | 0.0% | 0.0% | 0.0% | 1.4% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.2% |
| POLE FIRE | 23.4% | 2.8% | 0.8% | 2.4% | 0.6% | 2.5% | 3.9% | 3.6% | 0.2% | 15.5% | 4.7% | 6.3% |
| WEATHER | 8.5% | 34.3% | 25.4% | 21.3% | 14.7% | 32.9% | 54.3% | 43.6% | 3.9% | 21.5% | 15.3% | 25.5% |
| UNDETERMINED | 3.4% | 3.9% | 7.9% | 2.3% | 13.5% | 1.0% | 6.0% | 2.8% | 1.9% | 4.6% | 0.3% | 4.3% |
| TREE | 16.9% | 25.4% | 22.5% | 31.7% | 22.7% | 22.0% | 8.7% | 23.3% | 47.6% | 21.6% | 26.4% | 25.1% |
| PUBLIC | 5.5% | 6.0% | 2.1% | 5.4% | 7.4% | 9.1% | 1.4% | 9.9% | 6.7% | 10.7% | 9.8% | 7.5% |
| COMPANY | 1.3% | 0.2% | 0.3% | 2.7% | 0.0% | 0.0% | 0.0% | 0.7% | 0.6% | 2.9% | 1.8% | 1.3% |
| EQUIPMENT OH | 34.6% | 9.7% | 9.6% | 11.9% | 14.9% | 15.2% | 10.3% | 7.0% | 13.1% | 5.9% | 10.4% | 10.9% |
| EQUIPMENT UG | 0.4% | 1.1% | 0.2% | 1.9% | 1.1% | 5.4% | 0.3% | 0.8% | 0.5% | 1.4% | 0.8% | 1.2% |
| EQUIPMENT SUB | 3.2% | 5.3% | 7.9% | 1.1% | 6.1% | 0.0% | 0.0% | 0.6% | 14.7% | 6.6% | 5.7% | 4.8% |
| PLANNED | 1.5% | 10.8% | 23.0% | 10.2% | 15.3% | 6.7% | 8.9% | 6.5% | 1.8% | 5.8% | 11.9% | 9.0% |

| CDC | Coeur d’Alene | LCC | Lewiston-Clarkston |
| --- | --- | --- | --- |
| COC | Colville | OTC | Othello |
| DAC | Davenport | PAC | Palouse |
| DPC | Deer Park | SAC | Sandpoint |
| GRC | Grangeville | SPC | Spokane |
| KEC | Kellogg/ St. Maries |  |  |

### Chart 8.2 – % SAIDI per Cause by Office

The following chart shows the percentage SAIDI contribution by causes for outages excluding major event days.

### Table 8.3 - % SAIFI per Cause by Month

The following table lists the percentage SAIFI contribution by causes for all outages, excluding major event days.

| Reason | Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec | Yearly |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ANIMAL | 8.5% | 15.4% | 1.7% | 4.9% | 0.9% | 9.6% | 7.2% | 8.1% | 1.3% | 2.1% | 6.8% | 1.1% | 5.2% |
| MISCELLANEOUS | 0.1% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.5% | 0.0% | 0.1% |
| POLE FIRE | 3.9% | 4.6% | 4.1% | 6.1% | 0.9% | 5.1% | 0.2% | 42.3% | 8.6% | 1.2% | 0.1% | 7.0% | 8.8% |
| WEATHER | 0.4% | 0.0% | 36.5% | 19.7% | 5.1% | 18.8% | 36.1% | 5.8% | 0.4% | 0.4% | 25.7% | 28.9% | 17.1% |
| UNDETERMINED | 5.3% | 6.0% | 4.5% | 13.8% | 5.0% | 6.6% | 5.6% | 3.6% | 10.8% | 21.0% | 8.0% | 1.3% | 7.0% |
| TREE | 2.6% | 7.7% | 15.8% | 23.8% | 28.2% | 14.6% | 25.0% | 8.4% | 4.8% | 15.1% | 11.8% | 36.8% | 18.2% |
| PUBLIC | 5.4% | 12.7% | 13.9% | 10.0% | 4.0% | 2.6% | 5.9% | 10.9% | 19.6% | 10.5% | 18.5% | 5.5% | 9.7% |
| COMPANY | 9.1% | 0.0% | 13.4% | 5.9% | 3.6% | 3.0% | 0.0% | 1.7% | 7.2% | 18.0% | 10.5% | 0.0% | 5.2% |
| EQUIPMENT OH | 11.0% | 24.6% | 6.0% | 6.2% | 18.9% | 4.7% | 5.4% | 4.9% | 3.1% | 19.8% | 8.7% | 14.7% | 9.5% |
| EQUIPMENT UG | 0.8% | 6.7% | 0.4% | 0.6% | 0.2% | 0.4% | 1.9% | 0.5% | 0.7% | 0.0% | 0.2% | 0.3% | 0.7% |
| EQUIPMENT SUB | 43.2% | 12.0% | 0.0% | 3.0% | 31.2% | 20.4% | 1.7% | 4.3% | 4.1% | 0.0% | 0.0% | 0.1% | 8.3% |
| PLANNED | 9.7% | 10.3% | 3.8% | 6.0% | 1.8% | 14.1% | 11.0% | 9.4% | 39.2% | 11.7% | 9.1% | 4.3% | 10.2% |

### Chart 8.3 – % SAIFI per Cause by Month

The following chart shows the percentage SAIFI contribution by causes for all outages, excluding major event days.

### Table 8.4 - % SAIDI per Cause by Month

The following table lists the percentage SAIDI contribution by causes for outages excluding major event days.

| REASON | Jan | Feb | Mar | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Yearly |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ANIMAL | 2.4% | 12.3% | 1.2% | 2.9% | 0.8% | 10.5% | 2.2% | 11.8% | 1.3% | 2.7% | 2.8% | 0.5% | 3.9% |
| MISCELLANEOUS | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 1.3% | 0.0% | 0.2% |
| POLE FIRE | 7.1% | 14.1% | 8.9% | 7.7% | 1.7% | 2.9% | 0.6% | 16.6% | 9.3% | 2.1% | 0.2% | 8.8% | 6.3% |
| WEATHER | 1.2% | 0.0% | 42.2% | 20.3% | 7.8% | 23.8% | 46.0% | 5.9% | 0.4% | 0.8% | 46.2% | 37.1% | 25.5% |
| UNDETERMINED | 8.4% | 4.6% | 4.0% | 8.2% | 2.4% | 3.1% | 3.3% | 4.4% | 5.2% | 13.9% | 4.8% | 0.3% | 4.3% |
| TREE | 10.6% | 9.6% | 18.6% | 32.2% | 41.3% | 12.8% | 25.7% | 21.0% | 8.5% | 19.6% | 23.6% | 35.2% | 25.1% |
| PUBLIC | 4.4% | 21.3% | 8.6% | 10.0% | 6.6% | 3.3% | 8.0% | 11.0% | 18.6% | 12.1% | 3.8% | 2.8% | 7.5% |
| COMPANY | 3.2% | 0.0% | 5.3% | 1.1% | 0.5% | 2.6% | 0.0% | 0.1% | 1.9% | 5.1% | 2.5% | 0.0% | 1.3% |
| EQUIPMENT OH | 21.2% | 13.0% | 8.4% | 5.9% | 24.5% | 7.6% | 6.8% | 4.7% | 6.8% | 31.4% | 9.5% | 13.3% | 10.9% |
| EQUIPMENT UG | 2.5% | 5.7% | 0.6% | 1.6% | 0.8% | 1.3% | 2.5% | 1.1% | 1.3% | 0.1% | 0.5% | 0.4% | 1.2% |
| EQUIPMENT SUB | 28.2% | 13.0% | 0.0% | 6.1% | 11.9% | 14.4% | 1.4% | 5.5% | 5.5% | 0.0% | 0.0% | 0.0% | 4.8% |
| PLANNED | 10.7% | 6.2% | 2.2% | 4.0% | 1.6% | 17.8% | 3.5% | 17.9% | 41.4% | 12.2% | 4.9% | 1.6% | 9.0% |

| Table 8.4.1 Average Outage Time (HH:MM) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reason | Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec | Yearly |
| ANIMAL | 0:20 | 1:30 | 1:19 | 1:14 | 1:17 | 1:52 | 0:42 | 2:40 | 1:40 | 1:54 | 0:49 | 1:19 | 1:27 |
| COMPANY | 0:25 | 0:00 | 0:44 | 0:24 | 0:11 | 1:28 | 1:31 | 0:09 | 0:27 | 0:25 | 0:29 | 1:38 | 0:29 |
| EQUIPMENT OH | 2:17 | 1:00 | 2:38 | 2:00 | 1:56 | 2:46 | 2:50 | 1:47 | 3:44 | 2:21 | 2:13 | 2:34 | 2:15 |
| EQUIPMENT SUB | 0:46 | 2:03 | 0:00 | 4:12 | 0:34 | 1:12 | 1:51 | 2:22 | 2:20 | 0:00 | 0:00 | 0:05 | 1:08 |
| EQUIPMENT UG | 3:48 | 1:36 | 3:12 | 5:46 | 5:04 | 5:06 | 2:56 | 4:07 | 2:58 | 2:50 | 5:43 | 4:18 | 3:28 |
| MISCELLANEOUS | 0:19 | 0:00 | 0:00 | 0:00 | 0:00 | 2:56 | 0:00 | 0:00 | 0:00 | 0:00 | 4:51 | 2:25 | 4:27 |
| PLANNED | 1:19 | 1:07 | 1:05 | 1:24 | 1:23 | 2:10 | 0:43 | 3:30 | 1:50 | 1:33 | 1:06 | 1:01 | 1:43 |
| POLE FIRE | 2:10 | 5:49 | 4:02 | 2:40 | 2:44 | 0:59 | 6:16 | 0:43 | 1:52 | 2:36 | 3:26 | 3:33 | 1:25 |
| PUBLIC | 0:57 | 3:10 | 1:09 | 2:07 | 2:27 | 2:07 | 3:02 | 1:51 | 1:39 | 1:42 | 0:25 | 1:27 | 1:31 |
| TREE | 4:49 | 2:20 | 2:12 | 2:52 | 2:12 | 1:31 | 2:19 | 4:36 | 3:05 | 1:55 | 4:04 | 2:42 | 2:43 |
| UNDETERMINED | 1:55 | 1:26 | 1:41 | 1:15 | 0:43 | 0:48 | 1:19 | 2:16 | 0:50 | 0:59 | 1:12 | 0:41 | 1:11 |
| WEATHER | 3:21 | 0:00 | 2:10 | 2:10 | 2:15 | 2:10 | 2:52 | 1:50 | 1:35 | 2:46 | 3:39 | 3:38 | 2:56 |

### Chart 8.4 – % SAIDI per Cause by Month

The following chart shows the percentage SAIFI contribution by causes for outages excluding major event days.

# Momentary Interruption Causes

The cause for many momentary interruptions is unknown. Because faults are temporary, the cause goes unnoticed even after the line is patrolled.   Momentary outages are recorded using our SCADA system (System Control and Data Acquisition). On average, about 88% of Avista’s customers are served from SCADA controlled stations.

### Table 9.1 - % MAIFI per Cause by Office

The following table lists the percentage MAIFI contribution by causes for outages excluding major event days.

| REASON | CDC | COC | DAC | GRC | KEC | LCC | OTC | PAC | SAC | SPC | DPC | All Offices |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ANIMAL | 0.0% | 1.9% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 2.8% | 1.6% | 2.4% | 0.0% | 1.2% |
| POLE FIRE | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.9% | 0.0% | 0.7% | 0.0% | 0.3% |
| WEATHER | 26.0% | 15.5% | 19.5% | 13.2% | 12.1% | 26.0% | 10.8% | 40.9% | 31.7% | 29.7% | 0.0% | 25.9% |
| TREE | 0.0% | 0.0% | 0.0% | 0.0% | 13.7% | 1.0% | 0.0% | 0.3% | 1.1% | 0.6% | 0.0% | 0.6% |
| PUBLIC | 1.4% | 0.0% | 1.0% | 0.0% | 0.0% | 0.0% | 0.0% | 1.2% | 0.9% | 4.3% | 0.0% | 1.5% |
| COMPANY | 0.0% | 1.9% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 1.0% | 0.8% | 0.0% | 0.4% |
| UNDETERMINED | 69.6% | 78.7% | 78.5% | 85.6% | 72.0% | 71.8% | 85.9% | 52.0% | 62.8% | 55.0% | 0.0% | 67.5% |
| EQUIPMENT UG | 0.0% | 0.0% | 0.0% | 0.5% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% |
| EQUIPMENT OH | 2.3% | 1.9% | 0.0% | 0.0% | 0.0% | 0.6% | 0.0% | 0.0% | 0.9% | 2.8% | 0.0% | 1.1% |
| PLANNED | 0.0% | 0.0% | 0.0% | 0.6% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.1% |
| EQUIPMENT SUB | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 1.3% | 0.0% | 0.4% |
| FORCED OUTAGE | 0.7% | 0.0% | 0.9% | 0.1% | 2.3% | 0.5% | 3.3% | 1.9% | 0.0% | 2.3% | 0.0% | 1.0% |

| CDC | Coeur d’Alene | LCC | Lewiston-Clarkston |
| --- | --- | --- | --- |
| COC | Colville | OTC | Othello |
| DAC | Davenport | PAC | Palouse |
| DPC | Deer Park | SAC | Sandpoint |
| GRC | Grangeville | SPC | Spokane |
| KEC | Kellogg/ St. Maries |  |  |

### Table 9.1.1 - % MAIFI per Cause by Office (Washington only)

The following table lists the percentage MAIFI contribution by causes for outages excluding major event days.

| REASON | COC | DAC | OTC | SPC | DPC | PAC-WA | LCC-WA | All WA Offices |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ANIMAL | 1.17% | 0.25% | 5.43% | 5.08% | 10.26% | 3.12% | 1.63% | 4.45% |
| COMPANY | 0.44% | 3.73% | 0.00% | 7.52% | 6.45% | 5.82% | 0.04% | 5.37% |
| MISCELLANEOUS | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% | 0.02% | 0.00% | 0.00% |
| POLE FIRE | 1.86% | 1.31% | 1.62% | 17.95% | 1.90% | 11.55% | 0.00% | 10.90% |
| PUBLIC | 8.63% | 4.27% | 1.20% | 14.40% | 7.66% | 10.79% | 0.71% | 11.10% |
| TREE | 18.26% | 17.80% | 4.05% | 15.85% | 20.87% | 14.52% | 62.71% | 16.84% |
| UNDETERMINED | 8.53% | 15.09% | 9.13% | 5.74% | 0.20% | 7.91% | 1.71% | 6.45% |
| WEATHER | 18.10% | 29.65% | 49.40% | 13.35% | 6.17% | 32.16% | 7.93% | 17.29% |
| EQUIPMENT OH | 12.64% | 8.27% | 14.04% | 4.32% | 9.44% | 4.96% | 17.91% | 7.19% |
| EQUIPMENT UG | 0.52% | 3.68% | 0.18% | 0.38% | 0.58% | 1.66% | 1.67% | 0.73% |
| EQUIPMENT SUB | 4.77% | 2.93% | 0.76% | 9.33% | 22.89% | 1.50% | 0.00% | 8.52% |
| PLANNED | 25.08% | 13.03% | 14.18% | 6.09% | 13.59% | 5.99% | 5.68% | 11.17% |

| COC | Colville | OTC | Othello |
| --- | --- | --- | --- |
| DAC | Davenport | PAC-WA | Palouse Washington |
| DPC | Deer Park | SPC | Spokane |
| LCC-WA | Lewiston-Clarkston Washington |  |  |

### Chart 9.1 – % MAIFI per Cause by Office

The following chart shows the percentage MAIFI contribution by causes for outages excluding major event days.

### Table 9.2 - % MAIFI per Cause by Month

The following table lists the percentage MAIFI contribution by causes for outages excluding major event days.

| REASON | Jan | Feb | Mar | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Yearly |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ANIMAL | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 3.1% | 0.0% | 4.4% | 10.5% | 0.0% | 0.0% | 1.2% |
| POLE FIRE | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 2.0% | 0.3% |
| WEATHER | 7.2% | 0.0% | 12.8% | 32.0% | 50.9% | 5.6% | 27.8% | 1.7% | 0.0% | 0.0% | 47.0% | 33.0% | 25.9% |
| TREE | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 1.3% | 0.0% | 0.0% | 0.0% | 0.6% | 2.9% | 0.6% |
| PUBLIC | 7.1% | 0.0% | 2.1% | 0.6% | 0.0% | 0.0% | 1.9% | 0.0% | 1.0% | 3.1% | 4.0% | 0.0% | 1.5% |
| COMPANY | 0.0% | 0.0% | 2.1% | 0.2% | 0.0% | 0.0% | 1.1% | 0.0% | 0.0% | 0.0% | 0.0% | 1.1% | 0.4% |
| UNDETERMINED | 82.3% | 83.9% | 80.2% | 66.8% | 47.6% | 93.8% | 64.8% | 97.6% | 94.7% | 82.8% | 43.6% | 56.5% | 67.5% |
| EQUIPMENT UG | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.7% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% |
| EQUIPMENT OH | 3.3% | 14.2% | 0.0% | 0.0% | 0.0% | 0.7% | 0.0% | 0.0% | 0.0% | 3.1% | 0.9% | 1.8% | 1.1% |
| PLANNED | 0.0% | 1.9% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.1% |
| EQUIPMENT SUB | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 0.0% | 1.0% | 1.6% | 0.4% |
| FORCED OUTAGE | 0.0% | 0.0% | 2.8% | 0.5% | 1.5% | 0.0% | 0.0% | 0.0% | 0.0% | 0.6% | 2.8% | 1.1% | 1.0% |

### Chart 9.2 – % MAIFI per Cause by Month

The following chart shows the percentage MAIFI contribution by causes for outages excluding major event days.

# Major Event Day Causes

### Chart 10.1 – % SAIFI by Cause Code for the Major Event Days

The following chart shows the percentage SAIFI contribution by causes for outages during major event days

### Table 10.1 – % SAIFI by Sub Cause Code for the Major Event Days

The following table shows the SAIFI contribution and Customer hours by sub causes code for the three main outage causes during major event days.

| Cause Code | Sub reason | Sum of Ni | Sum of ri x Ni (hours) |
| --- | --- | --- | --- |
| EQUIPMENT OH | Crossarm-rotten | 648 | 3682:48 |
|  | Pole-rotten | 22 | 1127:30 |
|  | Regulator | 269 | 493:10 |
| Total |  | 939 | 5303:28 |
| POLE FIRE | Pole Fire | 55 | 58:40 |
| Total |  | 55 | 58:40 |
| TREE | Tree Fell | 2327 | 4109:02 |
|  | Weather | 15675 | 73352:33 |
| Total |  | 18002 | 77461:35 |
| WEATHER | Lightning | 1034 | 740:14 |
|  | Wind | 72951 | 450847:30 |
| Total |  | 73985 | 451587:44 |

### Table 10.2 – Yearly Summary of the Major Event Days

Table 10.2 is provided as an initial review of Major Event Day information. The main premise of the IEEE Major Event Day calculation is that using the 2.5b method should classify 2.3 days each year as MED’s. The following table shows the previous major event days, the daily SAIDI value and the relationship of the yearly TMED.

| Year | Date | SAIDI | TMED |
| --- | --- | --- | --- |
| 2004 | 05-21-2004 | 7.11 | 6.35 |
|  | 08-02-2004 | 7.36 |  |
|  | 12-08-2004 | 31.00 |  |
| 2005 | 06-21-2005 | 39.53 | 4.916 |
|  | 06-22-2005 | 9.03 |  |
|  | 08-12-2005 | 19.60 |  |
| 2006 | 01-11-2006 | 12.10 | 7.058 |
|  | 03-09-2006 | 8.58 |  |
|  | 11-13-2006 | 30.79 |  |
|  | 12-14-2006 | 29.26 |  |
|  | 12-15-2006 | 158.31 |  |
| 2007 | 01-06-2007 | 9.98 | 8.017 |
|  | 06-29-2007 | 32.64 |  |
|  | 07-13-2007 | 12.79 |  |
|  | 08-31-2007 | 21.30 |  |
| 2008 | 01-27-2008 | 17.57 | 9.224 |
|  | 07-10-2008 | 36.74 |  |
|  | 08-18-2008 | 9.49 |  |
| 2009 | None |  | 9.925 |
| 2010 | 5/3/2010 | 21.04 | 11.110 |
|  | 11/16/2010 | 68.67 |  |
| 2011 |  |  | 10.848 |

# Interruption Cause Codes

#### Table 11.1 – Interruption Cause Codes

| MAIN CATEGORY | Proposed (Changes Only) | SUB CATEGORY | Proposed (Changes Only) | Definition |
| --- | --- | --- | --- | --- |
| ANIMAL |  | Bird |  | Outages caused by animal contacts. Specific animal called out in sub category. |
|  |  | Protected | Delete in 2011 | No longer a need to use this subreason. |
|  |  | Squirrel |  |  |
|  |  | Underground |  |  |
|  |  | Other |  |  |
| PUBLIC |  | Car Hit Pad |  | Underground outage due to car, truck, construction equipment etc. contact with pad transformer, junction enclosure etc... |
|  |  | Car Hit Pole |  | Overhead outage due to car, truck, construction equipment etc. contact with pole, guy, neutral etc. |
|  |  | Dig In |  | Dig in by a customer, a customer’s contractor, or another utility. |
|  |  | Fire |  | Outages caused by or required for a house/structure or field/forest fire. |
|  |  | Tree |  | Homeowner, tree service, logger etc. fells a tree into the line. |
|  |  | Other |  | Other public caused outages |
| COMPANY |  | Dig in |  | Dig in by company or contract crew. |
|  |  | Other |  | Other company caused outages |
| EQUIPMENT OH |  | Arrestors |  | Outages caused by equipment failure. Specific equipment called out in sub category. |
|  |  | Capacitor |  |  |
|  |  | Conductor - Pri |  |  |
|  |  | Conductor - Sec |  |  |
|  |  | Connector - Pri |  |  |
|  |  | Connector - Sec |  |  |
|  |  | Crossarm- rotten |  |  |
|  |  | Cutout / Fuse |  |  |
|  |  | Insulator |  |  |
|  |  | Insulator Pin |  |  |
|  |  | Other |  |  |
|  |  | Pole - Rotten |  |  |
|  |  | Recloser |  |  |
|  |  | Regulator |  |  |
|  |  | Switch / Disconnect |  |  |
|  |  | Transformer - OH |  |  |
|  |  | Wildlife Guard |  | Wildlife guard failed or caused an outage |
| EQUIPMENT UG |  | URD Cable - Pri |  | Outages caused by equipment failure. Specific equipment called out in sub category. |
|  |  | URD Cable- Sec |  |  |
|  |  | Connector - Sec |  |  |
|  |  | Elbow |  |  |
|  |  | Junctions |  |  |
|  |  | Primary Splice |  |  |
|  |  | Termination |  |  |
|  |  | Transformer - UG |  |  |
|  |  | Other |  |  |
| MAIN CATEGORY | Proposed (Changes Only) | SUB CATEGORY | Proposed (Changes Only) | Definition |
| EQUIPMENT SUB |  | High side fuse |  |  |
|  |  | Bus Insulator |  |  |
|  |  | High side PCB |  |  |
|  |  | High side Swt / Disc |  |  |
|  |  | Low side OCB/Recloser |  |  |
|  |  | Low side Swt / Disc |  |  |
|  |  | Relay Misoperation |  |  |
|  |  | Regulator |  |  |
|  |  | Transformer |  |  |
|  |  | Other |  |  |
| MISCELLANEOUS |  | SEE REMARKS |  | For causes not specifically listed elsewhere |
| NOT OUR PROBLEM (Outages in this category are not included in reported statistics) |  | Customer Equipment SEE REMARKS |  | Customer equipment causing an outage to their service. If a customer causes an outage to another customer this is covered under Public. |
|  |  | Other Utility |  | Outages when another utility’s facilities cause an outage on our system. |
| POLE FIRE |  |  |  | Used when water and contamination causes insulator leakage current and fire. If insulator is leaking due to material failure list under equipment failure. If cracked due to gunfire use customer caused other. |
| PLANNED |  | Maintenance / Upgrade |  | Outage, normally prearranged, needed for normal construction work |
|  |  | Forced |  | Outage scheduled to repair outage damage |
| TREE |  | Tree fell |  | For outages when a tree falls into distribution primary/secondary or transmission during normal weather |
|  |  | Tree growth |  | Tree growth causes a tree to contact distribution primary/secondary or transmission during normal weather. |
|  |  | Service |  | For outages when a tree falls or grows into a service. |
|  |  | Weather |  | When snow and wind storms causes a tree or branch to fall into, or contact the line. Includes snow loading and unloading. |
| UNDETERMINED |  |  |  | Use when the cause cannot be determined |
| WEATHER |  | Snow / Ice |  | Outages caused by snow or ice loading or unloading on a structure or conductor. Use weather tree for snow and ice loading on a tree. |
|  |  | Lightning |  | Lightning flashovers without equipment damage. Equipment failures reported under the equipment type. |
|  |  | Wind |  | Outages when wind causes conductors to blow into each other, another structure, building etc. |

# Office Areas

#### Chart 12.1 – Office Areas

Coeur d’Alene –CDC Colville – COC

Davenport – DAC

Deer Park - DPC

Grangeville – GRC

Kellogg – KEC

Lewis-Clark – LCC

Othello – OTC

Palouse – PAC

Sandpoint – SAC

Spokane - SPC

Indices Calculations

### Sustained Interruption

- An interruption lasting longer than 5 minutes.

### Momentary Interruption Event

- An interruption lasting 5 minutes or less. The event includes all momentary interruptions occurring within 5 minutes of the first interruption. For example, when an interrupting device operates two, three, or four times and then holds, it is considered a single event.

### SAIFI – System Average Interruption Frequency Index

- The average number of sustained interruptions per customer

- =	The number of customers which had sustained interruptions

Total number of customers served

- =

### MAIFIE – Momentary Average Interruption Event Frequency Index

- The average number of momentary interruption events per customer

- =	The number of customers which had momentary interruption events

Total number of customers served

- =

- MAIFI can be calculated by one of two methods. Using the number of momentary interruptions or the number momentary events. This report calculates MAIFIE using momentary events.  The event includes all momentary interruptions occurring within 5 minutes of the first interruption. For example, when an automatic interrupting device opens and then recloses two, or three times before it remains closed, it is considered a single event.

### SAIDI – System Average Interruption Duration Index

- Average sustained outage time per customer

- =	Outage duration multiplied by the customers effected for all sustained interruptions

Total number of customers served

- =

### CAIDI – Customer Average Interruption Duration Index

- Average restoration time

- =	Outage duration multiplied by the customers effected for all sustained interruptions

The number of customers which had sustained interruptions

- =

Quantities

i = An interruption event;

ri  = Restoration time for each interruption event;

T = Total;

IDE  = Number of interrupting device events;

Ni = Number of interrupted customers for each interruption event during the reporting period;

NT = Total number of customers served for the area being indexed;

### CEMIn – Customers Experiencing Multiple Sustained Interruptions more than n.

- CEMIn

- =	Total Number of Customers that experience more than n sustained interruptions

Total Number of Customers Served

- =   CN(k>n)

NT

### CEMSMIn – Customers experiencing multiple sustained interruption and momentary interruption events.

- CEMSMIn

- =	Total Number of Customers experiencing more than n interruptions

Total Number of Customers Served

- =   CNT(k>n)

NT

### MED - Major Event Day

A major event day is a day in which the daily system SAIDI exceeds a threshold value. Its purpose is to allow major events to be studied separately from daily operation, and in the process, to better reveal trends in daily operation that would be hidden by the large statistical effect of major events.

TMED is calculated (taken from the IEEE 1366-2003 Standard)

The major event day identification threshold value, TMED, is calculated at the end of each reporting period (typically one year) for use during the next reporting period as follows:

a) Collect values of daily SAIDI for five sequential years ending on the last day of the last complete reporting period. If fewer than five years of historical data are available, use all available historical data until five years of historical data are available.

b) Only those days that have a SAIDI/Day value will be used to calculate the TMED (do not include days that did not have any interruptions).

c) Take the natural logarithm (ln) of each daily SAIDI value in the data set.

d) Find a(Alpha), the average of the logarithms (also known as the log-average) of the data set.

e) Find b(Beta), the standard deviation of the logarithms (also known as the log-standard deviation) of the data set.

f) Compute the major event day threshold, TMED, using equation (25).

TMED = ea2.5 b							(25)

g) Any day with daily SAIDI greater than the threshold value TMED that occurs during the subsequent reporting period is classified as a major event day. Activities that occur on days classified as major event days should be separately analyzed and reported.

# Numbers of Customers Served

The following numbers of customers were based on the customers served at the beginning of the year. These numbers were used to calculate indices for this report.

#### Table 13.1 – Numbers of Customers Served

| Office | Customers | % of Total |
| --- | --- | --- |
| Coeur d'Alene | 50,118 | 13.9% |
| Colville | 18,059 | 5.0% |
| Davenport | 6,911 | 1.9% |
| Deer Park | 10,451 | 2.9% |
| Grangeville | 10,165 | 2.8% |
| Kellogg/St. Maries | 14,283 | 4.0% |
| Lewis-Clark | 29,231 | 8.1% |
| Othello | 6,686 | 1.9% |
| Palouse | 38,067 | 10.5% |
| Sandpoint | 14,583 | 4.0% |
| Spokane | 162,389 | 45.0% |
| System Total | 360,943 |  |

# Attachment 1 – SAIDI and SAIFI Historical Summary

See attachment.

# Company Contact

For further information regarding this document, please contact:

WUTC Electric Service Reliability Report

Avista Utilities

E. 1411 Mission Avenue

Spokane, WA 99220

(509) 495 - 2034 (phone)

(509) 495 - 4975 (phone)

(509) 495 - 4060 (fax)