Exhibit A - GENERAL INFORMATION

Background:

Currently there is a series of 8” and 12” HP pipelines feeding  northern King County via the Duvall Gate Station #2499 (214th Ave NE & NE Woodinville Duvall Rd). Modeling shows that future demand in the area will require reinforcements to this HP system. Installation of a new gate station and 16” HP line from the intersection of 132th Ave NE and 143rd Pl NE to approximately 800’N of 216th Ave NE will alleviate the demand on station #2499 and strengthen the natural gas system in north King County.  This pipeline will be installed in the portion of Woodinville known as the “Tolt Pipeline Corridor”, and is thus named the “Tolt16-inch Natural Gas Line Project”.

Project Description:

There are three phases to this project.  The attached map (Exhibit B) illustrates the proposed route and location for these facilities.

- Phase 1: Construct a 16” steel pipeline from 155th Ave NE to Mink Rd NE, connecting two existing 8” pipelines and reinforcing the existing system. The pipeline will be designed, constructed, and tested for an MAOP of 500 psig.  This pipeline will operate at 250 psig until phase 3 is constructed.

- Phase 2: Construct a new gate station at 14510 216th Ave NE, and extend new 16” steel pipeline from this location to Mink Rd where it will tie in to phase 1.  These segments will also be designed, constructed, and tested for an MAOP of 500 psig.  This pipeline will operate at 250 psig until phase 3 is constructed.

- Phase 3:  General Plan: Construct/extend the 16” steel pipeline westward from 155th Ave NE and tie into the 12” HP main at 132nd Ave NE.  Sever the tie-ins that were made between the 16” and the 8” pipelines during phase 1.  Increase the pressure in phases 1 and 2, and operate phases 1, 2, and 3 at 500 psig.  Note:  This route is preliminary and may be subject to change.

Scope of this Request:

The scope of this request is to operate the 16” Phase 1 pipeline at 500 psig.

Phase 1 will begin by tying in to an existing 8” pipeline at the intersection of the Tolt Pipeline corridor and 155th Ave NE, and will follow the corridor approximately 2.8 miles east until Mink Rd NE, where it will tie in with another existing 8” pipeline.  The scope of this request includes all pipelines associated with and constructed between the two 8” pipelines.

MAOP:

The Tolt Corridor supply main will be designed and tested for a MAOP of 500 psig.

Pipe and Fitting Specifications:

The proposed pipeline will be constructed from 16” x 0.375” API 5L-X60 steel pipe with a fusion bonded epoxy (FBE) coating.  The pipe and fitting specifications with the corresponding percentage of specified minimum yield strength at MAOP and normal operating pressure for the supply main is shown in the table below.

Supply Main:

| Material Specification | % SMYS @ MAOP (500 psig) | % SMYS @ Normal Operating Pressure (300 psig) |
| --- | --- | --- |
| 16” x 0.375” w.t. API 5L-X60 wrapped pipe | 17.78 | 10.67 |
| 16” x 0.375” w.t. WPHY-56 fittings | 19.05 | 11.43 |

All other pipeline components will have a working pressure rating of at least 500 psig.

Damage Prevention:

Pipeline markers will be installed and monitored in accordance with PSE Gas Operating Standard 2525.2500 and 2575.1100.  PSE is an active member in the local One-Call System and works closely with the local municipalities and permitting agencies prior to any construction starting in the vicinity of its facilities.  Additionally, it is PSE standard practice to monitor construction work taking place in the vicinity of its high pressure systems.

Construction Details:

All construction shall conform to Class 4 Standards.

Cover -All buried mains will be installed with a minimum of 3 feet of cover.  Four feet of cover will be achieved wherever possible.

Backfill - All shading and bedding material will be free of sharp rocks with a maximum particle size of ½” unless an approved rock shield material is utilized.  When rock shield material is used, the backfill material shall be free from sharp objects and large clods that could damage the pipe.

Clearance - At least 12 inches of separation will be maintained between the pipeline and other underground facilities.  If 12 inches separation is not possible, the pipeline will be protected from damage caused by proximity to the other structure, by using a bare steel casing, or a fiberglass shield.

Cathodic Protection:

The corrosion control program will be designed and installed in accordance with the requirements of section 2600 of the PSE Gas Operating Standards. The following standards are applicable to the supply main:

  - Cathodic Protection Requirements

2600.1100	Field Coatings for Pipe and Fittings

2600.1200	Test Stations Requirements

2600.1300	Designing and Installing Cathodic Protection Systems

2600.1400	Electrical Isolation and Grounding Requirements

2600.1500	Monitoring Cathodic Protection

2600.1700	Monitoring and Remedial Measures for Internal Corrosion

  - Remedial Measures for Corrosion Control

  - Galvanic Anode Installation Requirements

Coating:

As outlined in Operating Standard 2600.1100 an external protective coating shall be applied to the pipeline.  Any field joints and fittings not supplied with protective coatings will have field applied coating. All above-ground piping will be painted in accordance with written specifications. Field applied coatings will meet the requirements of Operating Standard 2600.1100, Field Coatings for Pipe and Fittings.

Several sections of the proposed pipe will be installed via directional drill. That pipe will have an abrasion resistant overlay (ARO) coating applied per Operating Standard 2600.1100.

All coating specifications will be included in the notice of proposed construction.

Testing:

The test medium will be water and the test pressure will be at least 750 psig.  Elevation changes approximately 270 feet over the route of the supply main.  Therefore, the test pressure at the lowest elevation will be at least 870 psig to ensure 750 psig is obtained at the highest point on the pipeline.  All testing will be done in accordance with PSE Gas Operating Standard 2525.3300  and in accordance with an approved procedure.

Welding:

All welding and welding inspection will conform to the following PSE Gas Operating Standards:

2525.2700	Installation Requirements for Steel Pipe and Fittings

2700.1100	Welder Qualification Requirements

2700.1200	Weld Inspection and Repair

2700.1300	Weld Inspector Qualification Requirements

2700.1400	Welder Qualification Test Requirements

In addition, PSE has a comprehensive set of welding procedures that are included in the Gas Standards Procedures Manual.  All welding to be done on this project will be governed by these procedures.  If any new procedures are required for the welding on this project, they will be qualified in accordance with PSE Operating Standards and added to the Gas Field Procedures Manual.  The 16” supply main welds will be performed using Gas Field Procedure 4900.1330 which is attached for reference.

A minimum of 90 percent of the welds will be x-rayed.

Pressure Monitoring:

The pressure in this system will be monitored by remote telemetry units (RTUs).  The RTUs will poll system pressure every 3 seconds.  These pressures will be monitored 24 hours a day in PSE’s 24 Hour Operations Center.

Leakage Surveys:

Leakage surveys will be conducted in accordance with PSE Gas Operating Standard 2625.1100 (Leakage Survey Program).  This Operating Standard requires leak surveys to be conducted every year for supply mains (supply mains are all high pressure mains other than transmission mains).  This provides more frequent surveying than required by state and federal regulations.

Exhibit B – ROUTE AND FACILITIES MAP

Exhibit C – STRUCTURE LIST

| Tolt Pipeline Corridor Addresses, Land Use, and Distance of Structures from the Proposed Pipeline |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Route / Street | Parcel Number | Address | City | Zip Code | Side of Route | Distance in feet of Structure from Pipeline | Land Use |
| TOLT PIPELINE CORRIDOR | 3401700086 | 15032 152ND AVE NE | WOODINVILLE | 98072 | SOUTH | 88* | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 3401700087 | 15406 NE 152ND PL | WOODINVILLE | 98072 | NORTH | 70* | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1426059091 | 14826 156TH PL NE | WOODINVILLE | 98072 | SOUTH | 80 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 3401700092 | 15015 159TH AVE NE | WOODINVILLE | 98072 | NORTH | 83 | SPORT COURT |
| TOLT PIPELINE CORRIDOR | 3401700092 | 15015 159TH AVE NE | WOODINVILLE | 98072 | NORTH | 63 | SHED |
| TOLT PIPELINE CORRIDOR | 3401700102 | 14907 159TH AVE NE | WOODINVILLE | 98072 | SOUTH | 68 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 3401700102 | 14907 159TH AVE NE | WOODINVILLE | 98072 | SOUTH | 49 | GARAGE |
| TOLT PIPELINE CORRIDOR | 3401700110 | 15006 159TH AVE NE | WOODINVILLE | 98072 | NORTH | 95 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 3401700104 | 14904 159TH AVE NE | WOODINVILLE | 98072 | SOUTH | 89 | SHED |
| TOLT PIPELINE CORRIDOR | 3401700108 | 16025 NE 153RD ST | WOODINVILLE | 98072 | NORTH | 86 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 3401700108 | 16025 NE 153RD ST | WOODINVILLE | 98072 | NORTH | 72 | GARAGE |
| TOLT PIPELINE CORRIDOR | 3401700108 | 16025 NE 153RD ST | WOODINVILLE | 98072 | NORTH | 79 | SHED |
| TOLT PIPELINE CORRIDOR | 3401700129 | 15200 163RD PL NE | WOODINVILLE | 98072 | NORTH | 87 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1426059045 | 14837 164TH PL NE | WOODINVILLE | 98072 | SOUTH | 86 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 3401700146 | 14838 164TH PL NE | WOODINVILLE | 98072 | SOUTH | 51 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 3401700146 | 14838 164TH PL NE | WOODINVILLE | 98072 | SOUTH | 55 | SHED |
| TOLT PIPELINE CORRIDOR | 2050000130 | 16422 NE 148TH PL | WOODINVILLE | 98072 | SOUTH | 66 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 2050000130 | 16422 NE 148TH PL | WOODINVILLE | 98072 | SOUTH | 58 | GARAGE |
| TOLT PIPELINE CORRIDOR | 3401700135 | 15116 164TH AVE NE | WOODINVILLE | 98072 | NORTH | 98 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1326059021 | 15019 166TH PL NE | WOODINVILLE | 98072 | NORTH | 104 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 3612000050 | 15030 167TH CT NE | WOODINVILLE | 98072 | NORTH | 70 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 3401700138 | 14949 168TH AVE NE | WOODINVILLE | 98072 | SOUTH | 44 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1326059080 | 15010 168TH AVE NE | WOODINVILLE | 98072 | NORTH | 89 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1326059080 | 15010 168TH AVE NE | WOODINVILLE | 98072 | NORTH | 72 | GARAGE |
| TOLT PIPELINE CORRIDOR | 1326059077 | 16848 150TH AVE NE | WOODINVILLE | 98072 | NORTH | 78 | GARAGE |
| TOLT PIPELINE CORRIDOR | 1326059073 | 16860 NE 150TH ST | WOODINVILLE | 98072 | NORTH | 76 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1326059053 | 16869 NE 150TH ST | WOODINVILLE | 98072 | SOUTH | 96 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1326059053 | 16869 NE 150TH ST | WOODINVILLE | 98072 | SOUTH | 80 | GARAGE |
| TOLT PIPELINE CORRIDOR | 1326059145 | 14707 172ND AVE NE | WOODINVILLE | 98072 | SOUTH | 71 | SHED |
| TOLT PIPELINE CORRIDOR | 1326059106 | 17115 NE 152ND ST | WOODINVILLE | 98072 | NORTH | 90 | SHED |
| TOLT PIPELINE CORRIDOR | 1326059146 | 14733 172ND AVE NE | WOODINVILLE | 98072 | SOUTH | 88 | SHED |
| TOLT PIPELINE CORRIDOR | 1326059147 | 14724 173RD AVE NE | WOODINVILLE | 98072 | SOUTH | 75 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1326059147 | 14724 173RD AVE NE | WOODINVILLE | 98072 | SOUTH | 90 | SHED |
| TOLT PIPELINE CORRIDOR | 1326059194 | 15105 176TH AVE NE | WOODINVILLE | 98072 | NORTH | 108 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 2195700130 | 15100 176TH AVE NE | WOODINVILLE | 98072 | NORTH | 89 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1326059059 | 14900 176TH AVE NE | WOODINVILLE | 98072 | SOUTH | 94 | SHED |
| TOLT PIPELINE CORRIDOR | 2195700200 | 15110 177TH PL NE | WOODINVILLE | 98072 | NORTH | 91 | SPORT COURT |
| TOLT PIPELINE CORRIDOR | 2195700210 | 15114 177TH PL NE | WOODINVILLE | 98072 | NORTH | 53 | SHED |
| TOLT PIPELINE CORRIDOR | 2195700300 | 15304 179TH AVE NE | WOODINVILLE | 98073 | NORTH | 60 | SHED |
| TOLT PIPELINE CORRIDOR | 2195700310 | 15300 179TH AVE NE | WOODINVILLE | 98072 | NORTH | 96 | SHED |
| TOLT PIPELINE CORRIDOR | 2195700310 | 15300 179TH AVE NE | WOODINVILLE | 98072 | NORTH | 75 | SHED |
| TOLT PIPELINE CORRIDOR | 1137300970 | 14630 181ST PL NE | WOODINVILLE | 98072 | SOUTH | 99 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1137300620 | 15302 182ND PL NE | WOODINVILLE | 98072 | NORTH | 57 | SHED |
| TOLT PIPELINE CORRIDOR | 1137300610 | 15306 182ND PL NE | WOODINVILLE | 98072 | NORTH | 75 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1137300860 | 18318 NE 146TH WAY | WOODINVILLE | 98072 | SOUTH | 81 | SHED |
| TOLT PIPELINE CORRIDOR | 1137300850 | 18334 NE 146TH WAY | WOODINVILLE | 98072 | SOUTH | 85 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1137300850 | 18334 NE 146TH WAY | WOODINVILLE | 98072 | SOUTH | 50 | GARAGE |
| TOLT PIPELINE CORRIDOR | 1137310060 | 15102 184TH PL NE | WOODINVILLE | 98072 | NORTH | 83 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1137310060 | 15102 184TH PL NE | WOODINVILLE | 98072 | NORTH | 98 | SPORT COURT |
| TOLT PIPELINE CORRIDOR | 1137310010 | 15207 186TH AVE NE | WOODINVILLE | 98072 | NORTH | 106 | SHED |
| TOLT PIPELINE CORRIDOR | 1137300270 | 15206 186TH AVE NE | WOODINVILLE | 98072 | NORTH | 109 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1137301340 | 18450 NE 146TH WAY | WOODINVILLE | 98072 | SOUTH | 54 | SHED |
| TOLT PIPELINE CORRIDOR | 1137301350 | 18600 NE 146TH WAY | WOODINVILLE | 98072 | SOUTH | 49 | SHED |
| TOLT PIPELINE CORRIDOR | 1137301370 | 18628 NE 146TH WAY | WOODINVILLE | 98072 | SOUTH | 105 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1137301390 | 18656 NE 146TH WAY | WOODINVILLE | 98072 | SOUTH | 72 | PLAYGROUND |
| TOLT PIPELINE CORRIDOR | 1152600470 | 18907 NE 150TH ST | WOODINVILLE | 98072 | NORTH | 104 | SPORT COURT |
| TOLT PIPELINE CORRIDOR | 1152600490 | 18923 NE 150TH ST | WOODINVILLE | 98072 | NORTH | 90 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1152600490 | 18923 NE 150TH ST | WOODINVILLE | 98072 | NORTH | 55 | SHED |
| TOLT PIPELINE CORRIDOR | 1137301440 | 14623 189TH AVE NE | WOODINVILLE | 98072 | SOUTH | 81 | SHED |
| TOLT PIPELINE CORRIDOR | 1137301440 | 14623 189TH AVE NE | WOODINVILLE | 98072 | SOUTH | 80 | SHED |
| TOLT PIPELINE CORRIDOR | 1152600520 | 18951 NE 150TH ST | WOODINVILLE | 98072 | NORTH | 72 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1152600530 | 18955 NE 150TH ST | WOODINVILLE | 98072 | NORTH | 91 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1137301520 | 14645 191ST AVE NE | WOODINVILLE | 98072 | SOUTH | 98 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1826069018 | 15020 BEAR CREEK RD NE | WOODINVILLE | 98077 | NORTH | 102 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1826069018 | 15020 BEAR CREEK RD NE | WOODINVILLE | 98077 | NORTH | 103 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 6838800170 | 19204 NE 149TH ST | WOODINVILLE | 98077 | SOUTH | 99 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 6838800170 | 19204 NE 149TH ST | WOODINVILLE | 98077 | SOUTH | 79 | GAZEBO |
| TOLT PIPELINE CORRIDOR | 3443500010 | 14917 BEAR CREEK RD NE | WOODINVILLE | 98077 | SOUTH | 90 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1826069016 | 14910 BEAR CREEK RD NE | WOODINVILLE | 98077 | SOUTH | 68 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1826069016 | 14910 BEAR CREEK RD NE | WOODINVILLE | 98077 | SOUTH | 53 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1726069215 | 14738 BEAR CREEK RD NE | WOODINVILLE | 98077 | SOUTH | 49 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1726069198 | 15014 MINK RD NE | WOODINVILLE | 98077 | NORTH | 61 | SHED |
| TOLT PIPELINE CORRIDOR | 1726069199 | 19723 NE 150TH PL | WOODINVILLE | 98077 | NORTH | 80 | GAZEBO |
| TOLT PIPELINE CORRIDOR | 1726069010 | 19809 NE 150TH PL | WOODINVILLE | 98077 | NORTH | 83 | GARAGE |
| TOLT PIPELINE CORRIDOR | 1726069010 | 19809 NE 150TH PL | WOODINVILLE | 98077 | NORTH | 65 | PADDOCK |
| TOLT PIPELINE CORRIDOR | 1726069043 | 19802 NE 148TH ST | WOODINVILLE | 98077 | SOUTH | 43 | PADDOCK |
| TOLT PIPELINE CORRIDOR | 1726069043 | 19802 NE 148TH ST | WOODINVILLE | 98077 | SOUTH | 42 | PADDOCK |
| TOLT PIPELINE CORRIDOR | 1726069043 | 19802 NE 148TH ST | WOODINVILLE | 98077 | SOUTH | 55 | PADDOCK |
| TOLT PIPELINE CORRIDOR | 1726069043 | 19802 NE 148TH ST | WOODINVILLE | 98077 | SOUTH | 54 | PADDOCK |
| TOLT PIPELINE CORRIDOR | 1726069043 | 19802 NE 148TH ST | WOODINVILLE | 98077 | SOUTH | 57 | PADDOCK |
| TOLT PIPELINE CORRIDOR | 1726069043 | 19802 NE 148TH ST | WOODINVILLE | 98077 | SOUTH | 49 | PADDOCK |
| TOLT PIPELINE CORRIDOR | 1726069043 | 19802 NE 148TH ST | WOODINVILLE | 98077 | SOUTH | 61 | PADDOCK |
| TOLT PIPELINE CORRIDOR | 1726069043 | 19802 NE 148TH ST | WOODINVILLE | 98077 | SOUTH | 60 | PADDOCK |
| TOLT PIPELINE CORRIDOR | 1726069021 | 20207 NE 148TH ST | WOODINVILLE | 98077 | SOUTH | 36 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1726069227 | 20519 NE 150TH ST | WOODINVILLE | 98077 | NORTH | 63 | SPORT COURT |
| TOLT PIPELINE CORRIDOR | 1726069227 | 20519 NE 150TH ST | WOODINVILLE | 98077 | NORTH | 76 | PLAYGROUND |
| TOLT PIPELINE CORRIDOR | 1726069159 | 14712 204TH PL NE | WOODINVILLE | 98077 | SOUTH | 110 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1685800110 | 14321 214TH WAY NE | WOODINVILLE | 98077 | SOUTH | 58 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1685810030 | 21458 NE 143RD ST | WOODINVILLE | 98077 | NORTH | 105 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1685810020 | 21454 NE 143RD ST | WOODINVILLE | 98077 | NORTH | 60 | SHED |
| TOLT PIPELINE CORRIDOR | 1685810010 | 21450 NE 143RD ST | WOODINVILLE | 98077 | NORTH | 71 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1685810070 | 21447 NE 143RD ST | WOODINVILLE | 98077 | NORTH | 71 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1685810070 | 21447 NE 143RD ST | WOODINVILLE | 98077 | NORTH | 60 | SPORT COURT |
| TOLT PIPELINE CORRIDOR | 1685800120 | 14314 214TH WAY NE | WOODINVILLE | 98077 | SOUTH | 105 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1685800150 | 21432 NE 143RD ST | WOODINVILLE | 98077 | SOUTH | 44 | RESIDENTIAL |
| TOLT PIPELINE CORRIDOR | 1685800150 | 21432 NE 143RD ST | WOODINVILLE | 98077 | SOUTH | 45 | SHED |
| TOLT PIPELINE CORRIDOR | 1685800160 | 21433 NE 143RD ST | WOODINVILLE | 98077 | SOUTH | 66 | RESIDENTIAL |
| 216TH AVENUE NE | 4054520110 | 21531 NE 144TH PL | WOODINVILLE | 98077 | WEST | 78 | RESIDENTIAL |
| 216TH AVENUE NE | 2126069088 | 21637 NE 144TH PL | WOODINVILLE | 98077 | EAST | 101 | RESIDENTIAL |
| 216TH AVENUE NE | 2126069088 | 21637 NE 144TH PL | WOODINVILLE | 98077 | EAST | 98 | SPORT COURT |
| 216TH AVENUE NE | 4054520070 | 21530 NE 144TH PL | WOODINVILLE | 98077 | WEST | 70 | RESIDENTIAL |
| 216TH AVENUE NE | 1626069011 | 14509 216TH AVE NE | WOODINVILLE | 98077 | WEST | 85*** | RESIDENTIAL |
| 216TH AVENUE NE | 1626069131 | 14510 216TH AVE NE | WOODINVILLE | 98077 | EAST | 7 | SPORT COURT |
| 216TH AVENUE NE | 1041200010 | 21550 NE 146TH PL | WOODINVILLE | 98077 | WEST | 72*** | RESIDENTIAL |
| Distances are from proposed pipeline as shown on design plans provided. Where no plans have been developed, distances shown are based on the following assumptions: * Distance from Pipeline at an assumed 5 feet south of center-line ROW ** Distance from Pipeline at an assumed center-line ROW *** Distance from Pipeline at an assumed 10 feet west of center-line ROW |  |  |  |  |  |  |  |