# NOTES-FIELD INSPECTION

Company:  ____Puget Sound Energy______					Date(s):  _ November 14 – 18, 2005____________

## Unit:  __King County_______________

| Field Readings |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Line & Location | Line |  | CP Volts |  | Rectifier |  | Pressures |  | Remarks |
|  | Size | In. | P/S on | P/S off | Volts | Amps | Set | Actual |  |
| #130 Vasa Park |  |  | -2.032 | -1.530 | 3.02 | 4.1 |  |  | Rectifier wires are labeled. |
| #129 Newport Way |  |  | -13313 | -0.710 | 12.5 | 4.0 |  |  | Rectifier wires are labeled. |
| #170 Allen |  |  | -2.120 | -1.030 | 4.02 | 1.9 |  |  | Rectifier wires are labeled. |
| #171 SE 69 th. |  |  | -1.850 | -0.940 | na | na |  |  | Fuse failed during volt read. Rectifier wires are labeled. |
| #162 SE 56 th |  |  | -1.490 | -0.832 | 11.83 | 3.5 |  |  | Rectifier wires are labeled. |
| #147 Lake WA |  |  | -2.019 | -1.303 | 11.18 | 0.48 |  |  | Rectifier wires are labeled. |
| SE 20 & 107 Ave |  |  | -2.070 | -1.203 | 8.99 | 1.64 |  |  | Rectifier wires are labeled. |
| #169 140th Ave NE |  |  | -2.328 | -1.269 | 16.23 | 3.56 |  |  | Rectifier wires are labeled. |
| #137 NE 24th |  |  | -1.982 | -0.803 | 21.06 | 3.07 |  |  | Rectifier wires are labeled. |
| #136 NE 4th Pl |  |  | -2.009 | -0.999 | 5.40 | 3.71 |  |  | Rectifier wires are labeled. |
| #165 |  |  | -1.840 | -1.202 | 10.06 | 2.30 |  |  | Rectifier wires are labeled. |
| #160 |  |  | -1.996 | -1.258 | 13.01 | 3.52 |  |  | Rectifier wires are labeled. |
| 1726 Vashon Hwy Vashon Island |  |  | -0.751 |  |  |  |  |  |  |
| 10105 SW Bank Rd. Vashon Island |  |  | -0.413 |  |  |  |  |  | Customer has attached a ground wire to service line. |
| Field inspected exposed pipe at potential slide areas: |  |  |  |  |  |  |  | City | Comment |
| 600 96th Ave SE |  |  |  |  |  |  |  | Bellevue | Distribution pipe is located on a steep hillside and monitored |
| 16219 160 Pl. SE, Jones Rd. |  |  |  |  |  |  |  | Renton | for soil movement. Pipes are typically 2-inch diameter and |
| 16003 SE 159 Pl North to SE 157 |  |  |  |  |  |  |  | Renton | steel wrapped. |