## GHG Analysis
Mint Farm Energy Company Operating Data for Washinton GHG EPS Compliance Analysis -- 2008 Year To Date (January through September)*
Combustion Turbine Operating Hours | 3534.16
Total Natural Gas Use (MMBtu) | 5585769.8841
Total Greenhouse Gas Emissions (lb)** | 650786877.6532
Total Net MW-hrs Produced | 616155.677
Average GHG emissions/MW-hr (lb/MW-hr) | 1056.2053
*Based on MFEC's Q3 2008 emissions report to SWCAA unless noted otherwise.
**Based on Climate Registry Green House Gas Emission Factors (lb/MMBtu)
| Gas Turbine | Duct Burners
CO2 | 116.5 | 116.5
N2O | 0.006 | 0.002
CH4 | 0.002 | 0.002
Total GHG | 116.508 | 116.504
***Digital MW-hr production and natural gas use data only available for January-September from MFEC
****Jan-Feb data from hard copy Q1 report (mmBtu) | MMBtu | CT hours
January | 1030000 | 579.2
February | 557000 | 333.93

## QTRLY-SUM
Mint Farm Energy Center, LLC
3rd QUARTER 2008
CT/HRSG |  |  |  | Total
|  |  |  | THIS | PREV | 12 Mth
Month | Jul | Aug | Sep | QTR | 3 QTRs | RLG TOT
CT Hours | 218.5833 | 559.2667 | 344.35 | 1122.2 | 2411.96 | 3534.16
HRSG - Duct Burners Hrs | 19.5667 | 58.5 | 22.1333 | 100.2 | 51.25 | 151.45
Fuel Use (KSCF) | 307452.86 | 918795.91 | 534569.62 | 1760818.39 | 3686606.7 | 5447425.09
BTU/SCF | 1029 | 1029 | 1027
Heat Input (MMBTU) | 316368.9929 | 945440.9914 | 549002.9997 | 1810812.9841 | 3774956.9 | 5585769.8841
Annual Capacity Factor |  | N/A
Factor (lb/MMBtu) |  | From CEMS
NOx (lbs) | 7800 | 9200 | 9000 | 26000 | 53881.1 | 79881.1
Factor (lb/MMBtu) |  | From CEMS
CO (lbs) | 2400 | 2000 | 2400 | 6800 | 66455.3 | 73255.3
Factor (lb/MMBtu) |  | 0.0014
SO2 (lbs) | 442.9166 | 1323.6174 | 768.6042 | 2535.1382 | 2265 | 4800.1382
Factor (lb/MMBtu) |  | 0.0043
PM (lbs) | 1360.3867 | 4065.3963 | 2360.7129 | 7786.4958 | 18292.1 | 26078.5958
Factor (lb/MMBtu) |  | 0.0003
VOC (lbs) | 94.9107 | 283.6323 | 164.7009 | 543.2439 | 15675.6 | 16218.8439
Factor (lb/MMBtu) |  | From PEMS
NH3 (lbs) | 159.3 | 514.9 | 328.6 | 1002.8 | 1627.1 | 2629.9
Cooling Tower Hrs* | 218.5833 | 559.2667 | 344.35 | 1122.2 | 2411.96 | 3534.16
Diesel Fire Pump Hrs | N/A | N/A | N/A | N/A | N/A | N/A
Emergency Generator Hrs | 7 | 2 | 1 | 10 | 5 | 15
Fuel Preheater Hrs | N/A | N/A | N/A | N/A | N/A | N/A
*Assume Cooling Tower Operating hours equals Combustion Turbine operating hours
Note on D22: .0043 utilized based on Feb 08 stack testing
Note on D24: .0003 utilized based on Feb 08 stack testing

## Summary of CT hours
Summary of GT Fired Hours
Date | CT Fire St Hr | CT Fire St Min | Trip/End Hr | Trip/ End Min | Total Fired Hrs
2008-07-01 |  |  |  |  | 0
2008-07-02 | 4 | 7 | 15 | 39 | -11.5333
2008-07-02 | 16 | 41 | 18 | 22 | -1.6833
2008-07-03 |  |  |  |  | 0
2008-07-04 |  |  |  |  | 0
2008-07-05 |  |  |  |  | 0
2008-07-06 |  |  |  |  | 0
2008-07-07 |  |  |  |  | 0
2008-07-08 |  |  |  |  | 0
2008-07-09 | 3 | 6 | 20 | 29 | -17.3833
2008-07-10 | 10 | 2 | 20 | 12 | -10.1667
2008-07-11 |  |  |  |  | 0
2008-07-12 |  |  |  |  | 0
2008-07-13 |  |  |  |  | 0
2008-07-14 | 6 | 12 | 20 | 20 | -14.1333
2008-07-15 | 10 | 5 | 24 | 0 | -13.9167
2008-07-16 |  |  | 22 | 18 | -22.3
2008-07-17 | 4 | 8 | 22 | 19 | -18.1833
2008-07-18 |  |  |  |  | 0
2008-07-19 |  |  |  |  | 0
2008-07-20 |  |  |  |  | 0
2008-07-21 | 0 | 14 | 22 | 24 | -22.1667
2008-07-22 | 4 | 2 | 22 | 19 | -18.2833
2008-07-23 | 4 | 6 | 12 | 18 | -8.2
2008-07-24 | 4 | 3 | 22 | 20 | -18.2833
2008-07-25 | 0 | 0 |  |  | 0
2008-07-26 |  |  |  |  | 0
2008-07-27 |  |  |  |  | 0
2008-07-28 |  |  |  |  | 0
2008-07-29 | 8 | 10 | 20 | 20 | -12.1667
2008-07-30 | 10 | 1 | 20 | 20 | -10.3167
2008-07-31 | 4 | 8 | 24 | 0 | -19.8667
0
0
0
-218.5833
| CT Fire St Hr | CT Fire St Min | Trip/End Hr | Trip/ End Min | Total Fired Hrs
2008-08-01 |  |  | 24 |  | -24
2008-08-02 |  |  | 24 |  | -24
2008-08-03 |  |  | 24 |  | -24
2008-08-04 |  |  | 24 |  | -24
2008-08-05 |  |  | 16 | 30 | -16.5
2008-08-06 | 4 | 4 | 24 |  | -19.9333
2008-08-07 |  |  | 24 |  | -24
2008-08-08 |  |  | 24 |  | -24
2008-08-09 |  |  | 0 | 16 | -0.26667
2008-08-09 | 5 | 2 | 24 |  | -18.9667
2008-08-10 |  |  | 24 |  | -24
2008-08-11 |  |  | 24 |  | -24
2008-08-12 |  |  | 0 | 19 | -0.31667
2008-08-12 | 4 | 8 | 24 |  | -19.8667
2008-08-13 |  |  | 24 |  | -24
2008-08-14 |  |  | 24 |  | -24
2008-08-15 |  |  | 24 |  | -24
2008-08-16 |  |  | 24 |  | -24
2008-08-17 |  |  | 24 |  | -24
2008-08-18 |  |  | 24 |  | -24
2008-08-19 |  |  | 24 |  | -24
2008-08-20 |  |  | 0 | 19 | -0.31667
2008-08-21 | 4 | 1 | 22 | 18 | -18.2833
2008-08-22 |  |  | 0 |  | 0
2008-08-23 | 23 | 0 | 24 |  | -1
2008-08-24 | 0 |  | 5 |  | -5
2008-08-25 | 3 | 0 | 24 |  | -21
2008-08-25 |  |  |  |  | 0
2008-08-26 |  |  | 24 |  | -24
2008-08-27 |  |  | 0 | 20 | -0.33333
2008-08-27 | 4 | 10 | 22 | 19 | -18.15
2008-08-28 | 5 | 8 | 22 | 18 | -17.1667
2008-08-29 | 4 | 8 | 22 | 18 | -18.1667
2008-08-30 |  |  | 0 |  | 0
2008-08-31 |  |  | 0 |  | 0
-559.2667
| CT Fire St Hr | CT Fire St Min | Trip/End Hr | Trip/ End Min | Total Fired Hrs
2008-09-01 |  |  |  |  | 0
2008-09-02 |  |  |  |  | 0
2008-09-03 |  |  |  |  | 0
2008-09-04 | 2 | 9 | 22 | 20 | -20.1833
2008-09-05 | 4 | 7 | 22 | 20 | -18.2167
2008-09-06 | 4 | 6 | 15 | 45 | -11.65
2008-09-07 | 4 | 7 | 22 | 19 | -18.2
2008-09-08 | 4 | 7 | 22 | 20 | -18.2167
2008-09-09 | 4 | 8 | 22 | 21 | -18.2167
2008-09-10 | 4 | 5 | 22 | 20 | -18.25
2008-09-11 | 4 | 2 | 22 | 20 | -18.3
2008-09-12 | 4 | 2 | 22 | 20 | -18.3
2008-09-13 | 5 | 5 | 22 | 20 | -17.25
2008-09-14 | 4 | 5 | 13 | 42 | -9.6167
2008-09-15 | 18 | 1 | 24 | 0 | -5.9833
2008-09-16 |  |  | 24 | 0 | -24
2008-09-17 |  |  | 0 | 19 | -0.31667
2008-09-17 | 4 | 4 | 22 | 22 | -18.3
2008-09-18 |  |  |  |  | 0
2008-09-19 |  |  |  |  | 0
2008-09-20 |  |  |  |  | 0
2008-09-21 | 1 | 8 | 22 | 20 | -21.2
2008-09-22 |  |  |  |  | 0
2008-09-23 |  |  |  |  | 0
2008-09-24 |  |  |  |  | 0
2008-09-25 |  |  |  |  | 0
2008-09-26 | 1 | 8 | 22 | 22 | -21.2333
2008-09-27 | 4 | 5 | 22 | 19 | -18.2333
2008-09-28 | 4 | 5 | 22 | 20 | -18.25
2008-09-29 | 4 | 6 | 23 | 21 | -19.25
2008-09-30 | 4 | 4 | 15 | 15 | -11.1833
-344.35
Note on E3: GE Transportation: Time that flame is out.
Note on E42: GE Transportation: Time that flame is out.
Note on E82: GE Transportation: Time that flame is out.

## Summary of Duct burner hours
Summary of Duct Burner Fired Hours
Date | Duct Fire St Hr | Duct Fire St Min | Duct End Hr | Duct End Min | Total Fired Hrs
2008-07-01 |  |  |  |  | 0
2008-07-02 |  |  |  |  | 0
2008-07-02 |  |  |  |  | 0
2008-07-03 |  |  |  |  | 0
2008-07-04 |  |  |  |  | 0
2008-07-05 |  |  |  |  | 0
2008-07-06 |  |  |  |  | 0
2008-07-07 |  |  |  |  | 0
2008-07-08 |  |  |  |  | 0
2008-07-09 | 14 | 41 | 19 | 47 | -5.1
2008-07-10 |  |  |  |  | 0
2008-07-11 |  |  |  |  | 0
2008-07-12 |  |  |  |  | 0
2008-07-13 |  |  |  |  | 0
2008-07-14 | 12 | 38 | 13 | 8 | -0.5
2008-07-15 |  |  |  |  | 0
2008-07-16 |  |  |  |  | 0
2008-07-17 |  |  |  |  | 0
2008-07-18 |  |  |  |  | 0
2008-07-19 |  |  |  |  | 0
2008-07-20 |  |  |  |  | 0
2008-07-21 | 14 | 28 | 18 | 14 | -3.7667
2008-07-22 | 13 | 32 | 19 | 56 | -6.4
2008-07-23 | 8 | 9 | 11 | 52 | -3.7167
2008-07-24 |  |  |  |  | 0
2008-07-25 |  |  |  |  | 0
2008-07-26 |  |  |  |  | 0
2008-07-27 |  |  |  |  | 0
2008-07-28 |  |  |  |  | 0
2008-07-29 |  |  |  |  | 0
2008-07-30 |  |  |  |  | 0
2008-07-31 | 11 | 48 | 11 | 53 | -0.083333
0
0
0
-19.5667
| Duct Fire St Hr | Duct Fire St Min | Duct End Hr | Duct End Min | Total Fired Hrs
2008-08-01 |  |  |  |  | 0
2008-08-02 |  |  |  |  | 0
2008-08-03 | 13 | 47 | 14 | 55 | -1.1333
2008-08-04 | 12 | 50 | 16 | 3 | -3.2167
2008-08-05 |  |  |  |  | 0
2008-08-06 |  |  |  |  | 0
2008-08-07 | 13 | 32 | 13 | 35 | -0.05
2008-08-08 | 17 | 38 | 17 | 48 | -0.16667
2008-08-09 |  |  |  |  | 0
2008-08-09 |  |  |  |  | 0
2008-08-10 |  |  |  |  | 0
2008-08-11 | 16 | 9 | 21 | 59 | -5.8333
2008-08-12 | 12 | 11 | 19 | 31 | -7.3333
2008-08-12 | 19 | 42 | 20 | 42 | -1
2008-08-13 | 8 | 59 | 22 | 21 | -13.3667
2008-08-14 | 12 | 50 | 24 |  | -11.1667
2008-08-15 | 8 | 51 | 24 |  | -15.15
2008-08-16 |  |  | 0 | 5 | -0.083333
2008-08-17 |  |  |  |  | 0
2008-08-18 |  |  |  |  | 0
2008-08-19 |  |  |  |  | 0
2008-08-20 |  |  |  |  | 0
2008-08-21 |  |  |  |  | 0
2008-08-22 |  |  |  |  | 0
2008-08-23 |  |  |  |  | 0
2008-08-24 |  |  |  |  | 0
2008-08-25 |  |  |  |  | 0
2008-08-25 |  |  |  |  | 0
2008-08-26 |  |  |  |  | 0
2008-08-27 |  |  |  |  | 0
2008-08-27 |  |  |  |  | 0
2008-08-28 |  |  |  |  | 0
2008-08-29 |  |  |  |  | 0
2008-08-30 |  |  |  |  | 0
2008-08-31 |  |  |  |  | 0
-58.5
| Duct Fire St Hr | Duct Fire St Min | Duct End Hr | Duct End Min | Total Fired Hrs
2008-09-01 |  |  |  |  | 0
2008-09-02 |  |  |  |  | 0
2008-09-03 |  |  |  |  | 0
2008-09-04 |  |  |  |  | 0
2008-09-05 |  |  |  |  | 0
2008-09-06 |  |  |  |  | 0
2008-09-07 |  |  |  |  | 0
2008-09-08 |  |  |  |  | 0
2008-09-09 |  |  |  |  | 0
2008-09-10 |  |  |  |  | 0
2008-09-11 |  |  |  |  | 0
2008-09-12 |  |  |  |  | 0
2008-09-13 |  |  |  |  | 0
2008-09-14 |  |  |  |  | 0
2008-09-15 | 20 | 25 | 21 | 1 | -0.6
2008-09-16 |  |  |  |  | 0
2008-09-17 |  |  |  |  | 0
2008-09-17 |  |  |  |  | 0
2008-09-18 |  |  |  |  | 0
2008-09-19 |  |  |  |  | 0
2008-09-20 |  |  |  |  | 0
2008-09-21 |  |  |  |  | 0
2008-09-22 |  |  |  |  | 0
2008-09-23 |  |  |  |  | 0
2008-09-24 |  |  |  |  | 0
2008-09-25 |  |  |  |  | 0
2008-09-26 |  |  |  |  | 0
2008-09-27 |  |  |  |  | 0
2008-09-28 | 13 | 50 | 18 | 5 | -4.25
2008-09-29 | 11 | 46 | 22 | 1 | -10.25
2008-09-30 | 8 | 14 | 15 | 16 | -7.0333
-22.1333

## July CEMS data
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-01
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-02
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 61.1 | 2.1 | 117.7 | 85 | 99.5 | 7.23 | 0 | 0.3 | 0 | 346.9 | 15.4CS | 3:07
4 | 62 | 2.1 | 127.5 | 14.1 | 17.6 | 7.24 | 0 | 0.3 | 0 | 592 | 17.1CS
5 | 59 | 2.1 | 121.4 | 15.9 | 19.8 | 7.24 | 0 | 0.3 | 0 | 580.5 | 17.3CS
6 | 58.6 | 2.1 | 121 | 17 | 21.3 | 7.25 | 0 | 0.3 | 0 | 579.4 | 17.1CS
7 | 59.8 | 2.1 | 124.7 | 17.3 | 21.9 | 7.26 | 0 | 0.3 | 0 | 581.7 | 17.8CS
8 | 45.2 | 2.1 | 123 | 8.8 | 14.5 | 7.26 | 0 | 0.3 | 0 | 588.8 | 40.3S |  | 8:58 |  |  | ET 5:51 | Close to 6
9 | 2.1 | 2.1 | 10.7 | 0 | 0 | 7.26 | 0.2 | 0.3 | 0.4 | 623.6 | 117.1
10 | 2.1 | 2.1 | 10.6 | 0 | 0 | 7.25 | 0.2 | 0.3 | 0.4 | 624.7 | 116.8
11 | 2.1 | 2.1 | 10.8 | 0 | 0 | 7.24 | 0.2 | 0.3 | 0.3 | 625.1 | 119.2
12 | 2 | 2.1 | 14 | 0 | 0 | 7.24 | 0.4 | 0.3 | 0.9 | 649.2 | 170.4
13 | 2.1 | 2.1 | 14.1 | 0 | 0 | 7.23 | 0.4 | 0.3 | 0.9 | 660.3 | 171.8
14 | 2.1 | 2.1 | 14.1 | 0 | 0 | 7.22 | 0.4 | 0.3 | 0.9 | 662.6 | 172.2 |  |  | 14:49 | 14:39
15 | 36.6 | 4.1 | 73 | 19.5 | 23.6 | 7.23 | 0.5 | 0.3 | 0.4 | 559.6 | 22 | 15:41
16 | 46.1 | 6.7 | 129.6 | 24.8 | 42.3 | 7.25 | 3.3 | 0.5 | 3.4 | 609.4 | 40.1 | [5 empty] | ET 1:33
17 | 45.4 | 9.3 | 91.7 | 35.5 | 43.7 | 7.28 | 3.5 | 0.7 | 2.6 | 610.1 | 25.6 |  |  |  | 17:22 | Note: The unit was shutdown prior to completing the start-up
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-03
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-04
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-05
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-06
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-07
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-08
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-09
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | 61.9X | 9.7 | 119.8 | 78.4X | 92.2 | 7.34 | 0 | 0.7 | 0 | 359.9 | 16.5CS | 2:06
3 | 64.8X | 10.2 | 136.1 | 18.1X | 23.1 | 7.35 | 0 | 0.7 | 0 | 600.3 | 18.1CS
4 | 58.6X | 10.8 | 123.7 | 19.5X | 25 | 7.36 | 0 | 0.7 | 0 | 587.6 | 19.0CS
5 | 59.4X | 11.5 | 125.4 | 20.5X | 26.3 | 7.37 | 0 | 0.8 | 0 | 585.7 | 19.3CS
6 | 39.5X | 12.2 | 88.8 | 53.0X | 72.1 | 7.41 | 0 | 0.8 | 0 | 595.9 | 20.4S
7 | 18.0X | 13.2 | 85.9 | 13.3X | 38.6 | 7.42 | 0 | 0.9 | 0 | 618.4 | 112.6CS |  | 7:18 |  |  | ET 5:12 | <6
8 | 1.7 | 13.1 | 8.1 | 0 | 0 | 7.41 | 0.1 | 0.9 | 0.2 | 625.1 | 119.2
9 | 1.6 | 13.1 | 8.4 | 0 | 0 | 7.4 | 0.2 | 0.9 | 0.5 | 627.9 | 126.5
10 | 1.9 | 12.2 | 12.1 | 0 | 0 | 7.4 | 0.8 | 0.9 | 1.9 | 651.6 | 168.3
11 | 2 | 11.4 | 13.2 | 0 | 0 | 7.39 | 0.6 | 0.8 | 1.7 | 657.1 | 166.1
12 | 2 | 10.7 | 11.9 | 0 | 0 | 7.38 | 0.8 | 0.8 | 1.9 | 656.7 | 164.7
13 | 1.9 | 10.1 | 15.4 | 0 | 0 | 7.38 | 0.4 | 0.8 | 1.1 | 674.5 | 163.3
14 | 1.2 | 9.6 | 8.8 | 0 | 0 | 7.37 | 0.6 | 0.8 | 1.7 | 739.2 | 162.7
15 | 1.5 | 9.1 | 13.3 | 0 | 0 | 7.36 | 0.4 | 0.8 | 1.3 | 738.8 | 163.2
16 | 1.9 | 8.7 | 16 | 0 | 0 | 7.36 | 0.4 | 0.7 | 1.3 | 742.8 | 171.1
17 | 1.8 | 8.7 | 16.1 | 0 | 0 | 7.35 | 0.3 | 0.8 | 0.9 | 723.8 | 174.8
18 | 1.8 | 8.7 | 15.7 | 0 | 0 | 7.35 | 0.3 | 0.8 | 0.8 | 743.2 | 166
19 | 15.7 | 9 | 55.1 | 5.4 | 11.4 | 7.34 | 0 | 0.8 | 0 | 635.8 | 73.0SD |  |  | 19:16 | 19:29
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-10
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | 0 | 9.5 | 0 | 0 | 0 | 7.34 | 0 | 0.8 | 0 | 406.9 | 0.4WS | 9:00
9 | 64.7X | 10 | 130.7 | 9.5X | 11.6 | 7.34 | 0 | 0.8 | 0 | 542.3 | 17.4WS
10 | 20.0X | 10.5 | 82.8 | 6.7X | 16.8 | 7.34 | 0 | 0.9 | 0 | 616.1 | 88.5WS |  | 10:27 |  |  | ET 1:27
11 | 1.4X | 8 | 7.2 | 0.0X | 0 | 7.33 | 0.2 | 0.9 | 0.3 | 631.5 | 132.7
12 | 1.9 | 4.9 | 9.9 | 0 | 0 | 7.33 | 0.1 | 0.6 | 0.2 | 633.8 | 129.7
13 | 2.2 | 1.8 | 11.2 | 0 | 0 | 7.32 | 0.2 | 0.4 | 0.3 | 635 | 127.9
14 | 2.2 | 1.8 | 11.2 | 0 | 0 | 7.31 | 0.2 | 0.4 | 0.3 | 635.4 | 127.6
15 | 2 | 1.8 | 9.8 | 0 | 0 | 7.31 | 0.2 | 0.4 | 0.3 | 635 | 127.4
16 | 2 | 1.8 | 9.8 | 0 | 0 | 7.3 | 0.2 | 0.4 | 0.3 | 635.4 | 127.4
17 | 2 | 1.8 | 9.8 | 0 | 0 | 7.29 | 0.2 | 0.3 | 0.3 | 635.4 | 127.4
18 | 2 | 1.8 | 9.7 | 0 | 0 | 7.29 | 0.2 | 0.3 | 0.3 | 635 | 125.2
19 | 45.6 | 1.8 | 90.4 | 26.9 | 32.3 | 7.3 | 0 | 0.3 | 0 | 628.3 | 26.5SD |  |  | 19:00 | 19:15
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-11
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-12
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-13
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-14
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | 61.8X | 1.9 | 118.5 | 95.5X | 111.1 | 7.38 | 0 | 0.4 | 0 | 336.2 | 16.5CS | 5:12
6 | 71.2X | 1.9 | 155.2 | 9.6X | 12.6 | 7.38 | 0 | 0.4 | 0 | 575.4 | 21.7CS
7 | 50.0X | 1.9 | 122.6 | 46.6X | 69.5 | 7.42 | 0 | 0.3 | 0 | 598.7 | 28.2CS
8 | 50.7X | 1.9 | 134.5 | 33.2X | 53.5 | 7.44 | 0 | 0.3 | 0 | 603 | 35.2CS
9 | 55.9X | 1.8 | 154.8 | 29.8X | 50.2 | 7.46 | 0 | 0.3 | 0 | 612.9 | 39.7CS
10 | 5.6X | 2.1 | 30.6 | 0.0X | 0 | 7.45 | 0.7 | 0.3 | 1.3 | 631.1 | 134.5 |  | 10:07 |  |  | ET 4:55
11 | 2 | 2.2 | 18.3 | 0.1 | 0.4 | 7.45 | 0.4 | 0.3 | 1.2 | 665 | 173.5
12 | 2 | 2.2 | 16.1 | 0 | 0 | 7.44 | 0.3 | 0.3 | 1 | 666.6 | 173.8
13 | 2 | 2.2 | 13.7 | 0 | 0 | 7.43 | 0.7 | 0.3 | 1.7 | 660.7 | 167.1
14 | 2 | 2.2 | 12.1 | 0 | 0 | 7.43 | 0.8 | 0.3 | 1.9 | 658.7 | 166.4
15 | 2 | 2.2 | 12.1 | 0 | 0 | 7.42 | 0.7 | 0.4 | 1.7 | 658.7 | 168.4
16 | 2 | 2.2 | 12.1 | 0 | 0 | 7.41 | 0.8 | 0.4 | 1.9 | 658.7 | 166.5
17 | 2 | 2.2 | 11.9 | 0 | 0 | 7.41 | 0.8 | 0.4 | 1.9 | 657.1 | 165.9
18 | 1.9 | 2.2 | 11.9 | 0 | 0 | 7.4 | 0.8 | 0.4 | 1.9 | 657.1 | 163.9
19 | 28.4 | 2.2 | 63.1 | 16.5 | 22.2 | 7.41 | 0 | 0.4 | 0 | 637.8 | 34.9SD |  |  | 19:00 | 19:20
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-15
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | 0 | 2.2 | 0 | 0 | 0 | 7.4 | 0 | 0.5 | 0 | 383.6 | 0.4WS
9 | 56.2 | 2.3 | 115.8 | 15.7 | 19.7 | 7.41 | 0 | 0.5 | 0 | 540.7 | 19.7WS | 9:05
10 | 48.2 | 2.3 | 170.2 | 19.2 | 41 | 7.42 | 0 | 0.5 | 0 | 615.7 | 65.9WS |  | 10:56 |  |  | ET 1:51
11 | 1.6 | 2.2 | 10.6 | 0 | 0 | 7.41 | 0.5 | 0.5 | 1.2 | 650.4 | 173.3
12 | 1.8 | 2.2 | 10.6 | 0 | 0 | 7.41 | 0.6 | 0.6 | 1.5 | 650 | 172.9
13 | 1.8 | 2.2 | 12.4 | 0 | 0 | 7.4 | 0.6 | 0.6 | 1.5 | 663 | 172.4
14 | 1.9 | 2.2 | 12.4 | 0 | 0 | 7.39 | 0.6 | 0.6 | 1.5 | 663.8 | 172.5
15 | 1.8 | 2.2 | 12.4 | 0 | 0 | 7.39 | 0.5 | 0.6 | 1.1 | 662.6 | 172.1
16 | 1.9 | 2.2 | 12.4 | 0 | 0 | 7.38 | 0.6 | 0.6 | 1.3 | 662.6 | 172.6
17 | 1.8 | 2.1 | 12.4 | 0 | 0 | 7.38 | 0.6 | 0.6 | 1.3 | 663 | 173.7
18 | 1.8 | 2.1 | 12.4 | 0 | 0 | 7.37 | 0.6 | 0.6 | 1.4 | 663.8 | 174.4
19 | 1.5 | 2.1 | 8.9 | 0 | 0 | 7.36 | 0.6 | 0.6 | 1.4 | 665.8 | 174.1
20 | 1.5 | 2 | 10.8 | 0 | 0 | 7.36 | 0.6 | 0.6 | 1.4 | 667.8 | 176.8
21 | 1.5 | 2 | 9 | 0 | 0 | 7.35 | 0.6 | 0.6 | 1.4 | 668.6 | 177
22 | 1.6 | 1.8 | 10.6 | 0 | 0 | 7.34 | 0.6 | 0.6 | 1.4 | 668.6 | 175
23 | 0.7 | 1.8 | 2.7 | 0.1 | 0.2 | 7.34 | 0.5 | 0.6 | 0.9 | 637.8 | 122.3
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-16
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 1.4 | 1.7 | 6.9 | 0.1 | 0.2 | 7.33 | 0.6 | 0.6 | 1.1 | 632.2 | 125.2
1 | 1.8 | 1.7 | 9.7 | 0.1 | 0.2 | 7.33 | 0.4 | 0.6 | 0.8 | 632.2 | 124.7
2 | 1.8 | 1.7 | 9.7 | 0.2 | 0.5 | 7.32 | 0.5 | 0.6 | 0.9 | 631.9 | 124.9
3 | 1.8 | 1.7 | 9.7 | 0.2 | 0.5 | 7.31 | 0.5 | 0.6 | 1 | 631.9 | 125.6
4 | 1.7 | 1.7 | 8.3 | 0.2 | 0.5 | 7.31 | 0.6 | 0.6 | 1.1 | 631.9 | 125.3
5 | 1.7 | 1.7 | 8.7 | 0.1 | 0.2 | 7.3 | 0.6 | 0.6 | 1.2 | 637 | 134.7
6 | 1.9 | 1.7 | 10.2 | 0 | 0 | 7.3 | 0.5 | 0.6 | 1 | 636.6 | 134.6
7 | 1.9 | 1.7 | 10.3 | 0.1 | 0.2 | 7.29 | 0.6 | 0.6 | 1.2 | 636.2 | 136.2
8 | 1.4 | 1.7 | 8.7 | 0 | 0 | 7.28 | 0.5 | 0.6 | 1.2 | 661.1 | 170.4
9 | 1.7 | 1.7 | 10.4 | 0 | 0 | 7.28 | 0.4 | 0.6 | 1 | 663 | 169.5
10 | 1.2 | 1.6 | 6.9 | 0 | 0 | 7.27 | 0.4 | 0.5 | 1 | 663.8 | 169.5
11 | 1.8 | 1.7 | 12.2 | 0 | 0 | 7.26 | 0.3 | 0.5 | 0.8 | 665 | 171.2
12 | 2 | 1.7 | 12.5 | 0 | 0 | 7.26 | 0.5 | 0.5 | 1.2 | 667 | 175.7
13 | 2 | 1.7 | 12.5 | 0 | 0 | 7.25 | 0.5 | 0.5 | 1.2 | 664.6 | 175.2
14 | 2 | 1.7 | 12.7 | 0 | 0 | 7.25 | 0.5 | 0.5 | 1.2 | 666.6 | 178
15 | 2 | 1.7 | 12.7 | 0 | 0 | 7.24 | 0.5 | 0.5 | 1.2 | 665.8 | 177.7
16 | 2 | 1.7 | 12.7 | 0 | 0 | 7.23 | 0.5 | 0.5 | 1.2 | 665.8 | 177.2
17 | 2 | 1.7 | 12.7 | 0 | 0 | 7.23 | 0.5 | 0.5 | 1.2 | 665.8 | 177.8
18 | 2 | 1.7 | 12.6 | 0 | 0 | 7.22 | 0.5 | 0.5 | 1.2 | 666.2 | 177.9
19 | 1.8 | 1.7 | 10.2 | 0 | 0 | 7.22 | 0.2 | 0.5 | 0.3 | 642.5 | 135.6
20 | 2 | 1.7 | 10.3 | 0 | 0 | 7.21 | 0.3 | 0.5 | 0.5 | 639.4 | 137.8
21 | 25.8 | 1.7 | 54.1 | 24.9 | 31.7 | 7.22 | 0 | 0.5 | 0 | 631.1 | 29.5SD |  |  | 21:00 | 21:18
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-17
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 53.1 | 1.8 | 109.8 | 25.2 | 31.6 | 7.24 | 0 | 0.5 | 0 | 559.6 | 20.3HS | 3:08
4 | 41.7 | 1.8 | 140.6 | 23.2 | 47.4 | 7.25 | 0 | 0.5 | 0 | 625.1 | 60.4HS |  | 4:50 |  |  | ET 1:42
5 | 1.8 | 1.8 | 10.3 | 0.1 | 0.2 | 7.25 | 0.1 | 0.4 | 0.2 | 638.2 | 136.2
6 | 2.1 | 1.8 | 11.6 | 0 | 0 | 7.24 | 0.2 | 0.4 | 0.3 | 639 | 134.3
7 | 2 | 1.8 | 10.4 | 0.1 | 0.2 | 7.24 | 0.3 | 0.4 | 0.5 | 639 | 136.9
8 | 2 | 1.9 | 10.4 | 0.1 | 0.2 | 7.23 | 0.3 | 0.4 | 0.5 | 635.8 | 137.1
9 | 2 | 1.9 | 10.3 | 0.1 | 0.2 | 7.22 | 0.3 | 0.4 | 0.5 | 633 | 136.8
10 | 2 | 1.9 | 10.3 | 0 | 0 | 7.22 | 0.3 | 0.4 | 0.5 | 636.6 | 136.5
11 | 2 | 1.9 | 10.3 | 0 | 0 | 7.21 | 0.3 | 0.4 | 0.5 | 637.8 | 137.6
12 | 2 | 1.9 | 10.4 | 0 | 0 | 7.21 | 0.3 | 0.4 | 0.5 | 637.8 | 139
13 | 2 | 1.9 | 10.5 | 0 | 0 | 7.2 | 0.3 | 0.4 | 0.5 | 638.6 | 138.9
14 | 2 | 1.9 | 10.5 | 0 | 0 | 7.19 | 0.2 | 0.3 | 0.5 | 638.6 | 139.1
15 | 2 | 2 | 10.4 | 0 | 0 | 7.19 | 0.2 | 0.3 | 0.5 | 637.8 | 139.3
16 | 2 | 2 | 10.4 | 0 | 0 | 7.18 | 0.3 | 0.3 | 0.7 | 637.8 | 138.5
17 | 2 | 2 | 10.4 | 0 | 0 | 7.18 | 0.2 | 0.3 | 0.5 | 637.8 | 138.8
18 | 2 | 2 | 10.4 | 0 | 0 | 7.17 | 0.2 | 0.3 | 0.5 | 637 | 139.3
19 | 2 | 2 | 10.3 | 0.1 | 0.2 | 7.16 | 0.2 | 0.3 | 0.5 | 635.8 | 137.3
20 | 3.6 | 2.1 | 18.8 | 0.2 | 0.8 | 7.16 | 0.4 | 0.3 | 0.8 | 635.4 | 132.7
21 | 47.9 | 2.1 | 85.1 | 41.4 | 44.6 | 7.19 | 0 | 0.3 | 0 | 624.4 | 20.0SD |  |  | 21:00 | 21:19
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-18
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-19
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-20
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | 63.5X | 2.1 | 120.2 | 90.2 | 103.8 | 7.25 | 0 | 0.3 | 0 | 342.9 | 16.0CS | 23:14
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-21
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 58.7X | 2.1 | 134.4 | 36.1X | 50.2 | 7.28 | 0 | 0.3 | 0 | 594 | 23.3CS
1 | 49.5X | 2.1 | 125.2 | 42.9X | 66 | 7.31 | 0 | 0.3 | 0 | 621.6 | 30.9S
2 | 55.1X | 2.1 | 135.2 | 31.9X | 47.5 | 7.33 | 0 | 0.3 | 0 | 597.1 | 29.6CS
3 | 51.4X | 2.1 | 141.4 | 45.4X | 76 | 7.36 | 0 | 0.3 | 0 | 586.1 | 38.8CS
4 | 2.3X | 2.1 | 13.1 | 0.2X | 0.5 | 7.35 | 0.7 | 0.3 | 1.3 | 621.6 | 134.1 |  | 4:12 |  |  | ET 4:26
5 | 0.4 | 2 | 2.9 | 0 | 0 | 7.35 | 0.7 | 0.3 | 1.4 | 628.3 | 134.9
6 | 1.7 | 2 | 8.7 | 0.2 | 0.8 | 7.34 | 0.2 | 0.3 | 0.3 | 635 | 134.6
7 | 2 | 2 | 10.2 | 0.2 | 0.5 | 7.34 | 0.2 | 0.3 | 0.5 | 635 | 134.5
8 | 2 | 2 | 10.2 | 0.2 | 0.5 | 7.33 | 0.2 | 0.3 | 0.5 | 636.2 | 136.3
9 | 2 | 2 | 10.3 | 0.2 | 0.5 | 7.32 | 0.2 | 0.3 | 0.5 | 637.4 | 137.2
10 | 2.1 | 2 | 12 | 0.2 | 0.5 | 7.32 | 0.3 | 0.3 | 0.7 | 636.6 | 140.4
11 | 1.9 | 2 | 12.5 | 0.2 | 0.6 | 7.31 | 0.6 | 0.3 | 1.4 | 661.1 | 175.5
12 | 2 | 2 | 12.4 | 0.2 | 0.6 | 7.31 | 0.5 | 0.3 | 1.2 | 661.8 | 174.1
13 | 2.1 | 2 | 14.9 | 0.1 | 0.3 | 7.3 | 0.5 | 0.3 | 1.2 | 674.5 | 172.7
14 | 2.1 | 2 | 16.6 | 0 | 0 | 7.29 | 0.6 | 0.4 | 1.7 | 757 | 171.2
15 | 2 | 2 | 14.7 | 0 | 0 | 7.29 | 0.6 | 0.4 | 1.7 | 760.1 | 172.8
16 | 2 | 2 | 14.9 | 0 | 0 | 7.28 | 0.6 | 0.4 | 1.7 | 760.1 | 175.3
17 | 1.9 | 2 | 11.8 | 0 | 0 | 7.28 | 0.3 | 0.4 | 0.7 | 676.1 | 143.6
18 | 1.9 | 2 | 10.4 | 0.1 | 0.2 | 7.27 | 0.2 | 0.4 | 0.5 | 639 | 140
19 | 2.1 | 2 | 11.7 | 0.1 | 0.2 | 7.27 | 0.2 | 0.4 | 0.5 | 638.6 | 136.6
20 | 2 | 2 | 10.2 | 0.1 | 0.2 | 7.26 | 0.2 | 0.4 | 0.5 | 637.4 | 135
21 | 37.7 | 1.9 | 82.9 | 31.3 | 41.7 | 7.28 | 0 | 0.4 | 0 | 625.9 | 29.8SD |  |  | 21:06 | 21:24
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-22
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 54.4 | 1.9 | 111.6 | 33.8 | 42 | 7.3 | 0 | 0.4 | 0 | 567.1 | 19.7HS | 3:02
4 | 33.3 | 1.9 | 126.2 | 12.3 | 28.2 | 7.3 | 0 | 0.4 | 0 | 625.5 | 75.5HS |  | 4:39 |  |  | ET 1:37
5 | 1.4 | 1.9 | 7.4 | 0 | 0 | 7.3 | 0.3 | 0.4 | 0.7 | 636.2 | 136.6
6 | 2 | 1.9 | 10.3 | 0.2 | 0.8 | 7.29 | 0.2 | 0.4 | 0.5 | 639.4 | 136.8
7 | 2 | 1.9 | 10.3 | 0.3 | 1 | 7.29 | 0.2 | 0.4 | 0.5 | 639.4 | 137
8 | 2 | 1.9 | 10.2 | 0.3 | 1 | 7.28 | 0.3 | 0.4 | 0.7 | 639 | 135.6
9 | 2.1 | 1.9 | 12.2 | 0.2 | 0.8 | 7.28 | 0.4 | 0.4 | 0.9 | 640.5 | 143
10 | 2 | 2 | 12.8 | 0.2 | 1 | 7.27 | 0.5 | 0.3 | 1.2 | 668.2 | 179.4
11 | 2 | 2 | 14.5 | 0.2 | 1 | 7.26 | 0.5 | 0.4 | 1.2 | 668.6 | 178.9
12 | 2 | 2 | 14.5 | 0.2 | 0.6 | 7.26 | 0.6 | 0.4 | 1.4 | 680 | 178.5
13 | 2.1 | 2 | 14.5 | 0.1 | 0.6 | 7.25 | 0.7 | 0.4 | 1.6 | 710 | 177.8
14 | 2 | 2 | 12.7 | 0.1 | 0.2 | 7.25 | 0.7 | 0.4 | 1.8 | 721.8 | 177.1
15 | 2 | 2 | 12.7 | 0.1 | 0.3 | 7.24 | 0.7 | 0.4 | 1.8 | 716.7 | 177
16 | 2 | 2 | 14.4 | 0.1 | 0.2 | 7.24 | 0.7 | 0.5 | 1.8 | 718.3 | 177
17 | 2 | 2 | 14.5 | 0.1 | 0.2 | 7.23 | 0.7 | 0.5 | 1.8 | 721.1 | 177.5
18 | 1.9 | 2 | 12.7 | 0.1 | 0.3 | 7.22 | 0.6 | 0.5 | 1.5 | 701.7 | 178.3
19 | 2 | 2 | 10 | 0.2 | 0.5 | 7.22 | 0.2 | 0.4 | 0.3 | 641.3 | 131.1
20 | 2 | 2 | 10 | 0.2 | 0.5 | 7.21 | 0.3 | 0.4 | 0.5 | 637 | 132.2
21 | 44.9 | 2 | 89.8 | 31.4 | 38.2 | 7.23 | 0 | 0.4 | 0 | 627.9 | 26.8SD |  |  | 21:00 | 21:19
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-23
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 62.3 | 2 | 128.3 | 22.8 | 28.5 | 7.24 | 0 | 0.4 | 0 | 562 | 19.6HS | 3:06
4 | 42.6 | 2 | 142.6 | 22.8 | 46.3 | 7.26 | 0 | 0.4 | 0 | 623.6 | 60.2HS |  | 4:50 |  |  | ET 1:44
5 | 1 | 1.9 | 5.9 | 0 | 0 | 7.25 | 0.3 | 0.5 | 0.7 | 636.6 | 136.6
6 | 2 | 1.9 | 10.3 | 0.3 | 0.8 | 7.25 | 0.3 | 0.5 | 0.5 | 639 | 136.6
7 | 2.1 | 1.9 | 14.7 | 0.3 | 1.2 | 7.24 | 0.7 | 0.5 | 1.7 | 694.6 | 180.6
8 | 1.9 | 1.9 | 12.9 | 0.2 | 0.9 | 7.23 | 0.7 | 0.5 | 1.7 | 712 | 182.1
9 | 1.9 | 1.9 | 12.7 | 0.2 | 0.9 | 7.23 | 0.5 | 0.5 | 1.2 | 693.4 | 178.5
10 | 1.9 | 1.9 | 12.6 | 0.2 | 0.9 | 7.22 | 0.6 | 0.5 | 1.4 | 690.3 | 177.7 |  |  | 10:59
11 | 35.9 | 1.9 | 87.1 | 18.6 | 27.4 | 7.23 | 0 | 0.5 | 0 | 647.6 | 40.8SD |  |  |  | 11:18
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-24
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 63.3 | 1.9 | 116.8 | 15.2 | 17.1 | 7.24 | 0 | 0.5 | 0 | 529.6 | 13.6WS | 3:03
4 | 41.3 | 1.9 | 119 | 6 | 10.5 | 7.24 | 0 | 0.5 | 0 | 627.9 | 46.2WS |  | 4:41 |  |  | ET 1:38
5 | 1.5 | 1.9 | 7.8 | 0 | 0 | 7.23 | 0.2 | 0.5 | 0.4 | 638.6 | 146.7
6 | 2 | 1.9 | 11.2 | 0.4 | 1.4 | 7.23 | 0.2 | 0.5 | 0.5 | 650.4 | 153.8
7 | 2 | 1.9 | 11.2 | 0.6 | 2 | 7.22 | 0.2 | 0.5 | 0.5 | 651.6 | 154
8 | 2 | 1.9 | 11.2 | 0.6 | 2 | 7.22 | 0.2 | 0.5 | 0.5 | 652 | 154.1
9 | 2 | 1.9 | 11.2 | 0.5 | 1.7 | 7.21 | 0.2 | 0.4 | 0.5 | 652 | 154.2
10 | 2 | 1.9 | 11.2 | 0.5 | 1.7 | 7.21 | 0.2 | 0.4 | 0.5 | 652 | 154.1
11 | 2 | 1.9 | 11.2 | 0.5 | 1.7 | 7.2 | 0.2 | 0.4 | 0.5 | 652 | 153.9
12 | 2.1 | 1.9 | 12.8 | 0.5 | 1.7 | 7.2 | 0.2 | 0.4 | 0.5 | 652.8 | 153.6
13 | 2 | 1.9 | 11 | 0.5 | 1.7 | 7.19 | 0.2 | 0.3 | 0.5 | 651.2 | 151.8
14 | 2 | 1.9 | 11.2 | 0.4 | 1.4 | 7.18 | 0.2 | 0.3 | 0.5 | 653.2 | 153.5
15 | 2 | 1.9 | 11.1 | 0.4 | 1.4 | 7.18 | 0.2 | 0.3 | 0.5 | 653.2 | 152.6
16 | 2 | 1.9 | 11.1 | 0.5 | 1.7 | 7.17 | 0.2 | 0.3 | 0.5 | 652.4 | 152.4
17 | 2 | 1.9 | 11.1 | 0.4 | 1.4 | 7.17 | 0.2 | 0.3 | 0.5 | 652 | 152.6
18 | 2 | 1.9 | 11.2 | 0.4 | 1.4 | 7.16 | 0.2 | 0.3 | 0.5 | 651.2 | 153.4
19 | 2 | 1.9 | 11.2 | 0.4 | 1.4 | 7.16 | 0.2 | 0.3 | 0.5 | 651.6 | 153.8
20 | 2 | 2 | 11 | 0.3 | 1.1 | 7.15 | 0.2 | 0.3 | 0.5 | 650.4 | 151
21 | 41 | 2 | 88.3 | 27.6 | 36.1 | 7.17 | 0 | 0.3 | 0 | 634.2 | 31.1SD |  |  | 21:00 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-25
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-26
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-27
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-28
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-29
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | 61.5 | 2 | 111.1 | 94.4 | 103.9 | 7.24 | 0 | 0.3 | 0 | 371 | 12.7CS | 7:10
8 | 70.7 | 2 | 144.4 | 18.6 | 23.1 | 7.25 | 0 | 0.2 | 0 | 603.8 | 17.5CS
9 | 52.2 | 2 | 133.6 | 34 | 52.9 | 7.27 | 0 | 0.2 | 0 | 619.6 | 32.5CS
10 | 53.5 | 2 | 145.9 | 35.3 | 58.5 | 7.29 | 0 | 0.2 | 0 | 618.8 | 38.0CS
11 | 5.1 | 2.2 | 26.7 | 0 | 0 | 7.28 | 0.9 | 0.2 | 1.6 | 626.7 | 128.1 |  | 11:06 |  |  | ET 3 :56
12 | 1.4 | 2.1 | 7.1 | 0.5 | 1.5 | 7.28 | 0.2 | 0.2 | 0.5 | 627.5 | 131
13 | 2 | 2.1 | 10.1 | 0.7 | 2.1 | 7.27 | 0.2 | 0.2 | 0.5 | 630.7 | 134.4
14 | 2 | 2.1 | 10.1 | 0.7 | 2.1 | 7.27 | 0.2 | 0.2 | 0.5 | 631.1 | 134.6
15 | 2 | 2.1 | 10.1 | 0.6 | 1.8 | 7.26 | 0.2 | 0.2 | 0.5 | 632.2 | 134.7
16 | 2 | 2.1 | 10.1 | 0.6 | 1.8 | 7.26 | 0.2 | 0.2 | 0.5 | 631.9 | 134.2
17 | 2 | 2.1 | 10.1 | 0.6 | 1.8 | 7.25 | 0.2 | 0.2 | 0.5 | 631.9 | 133.8
18 | 2 | 2.1 | 11.5 | 0.5 | 1.5 | 7.25 | 0.2 | 0.2 | 0.5 | 634.6 | 132.4
19 | 44.4 | 2.1 | 86.7 | 31.9 | 38 | 7.27 | 0 | 0.2 | 0 | 625.9 | 25.6SD |  |  | 19:00 | 19:20
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-30
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | 68.2 | 2.2 | 130 | 15.6 | 18.1 | 7.27 | 0 | 0.2 | 0 | 528 | 15.6WS | 9:01
10 | 41.6 | 2.2 | 142.4 | 17.6 | 36.6 | 7.28 | 0 | 0.2 | 0 | 618.8 | 62.8WS |  | 10:50 |  |  | ET 1:49
11 | 1.8 | 2.1 | 10.2 | 0 | 0 | 7.27 | 0.2 | 0.2 | 0.3 | 630.3 | 134.3
12 | 2 | 2.1 | 10.2 | 0.5 | 1.6 | 7.27 | 0.2 | 0.2 | 0.3 | 637.8 | 134.2
13 | 2 | 2.1 | 10.1 | 0.6 | 1.8 | 7.26 | 0.2 | 0.2 | 0.5 | 637.8 | 133.2
14 | 2 | 2.1 | 10.1 | 0.6 | 1.8 | 7.26 | 0.2 | 0.2 | 0.5 | 639 | 133.5
15 | 2 | 2.1 | 10.1 | 0.6 | 1.8 | 7.25 | 0.2 | 0.2 | 0.5 | 638.2 | 132.4
16 | 2 | 2.1 | 10.1 | 0.6 | 1.8 | 7.25 | 0.2 | 0.2 | 0.5 | 638.6 | 133
17 | 2 | 2.1 | 10.1 | 0.5 | 1.6 | 7.24 | 0.2 | 0.2 | 0.5 | 637.8 | 132.8
18 | 2.1 | 2.2 | 11.4 | 0.5 | 1.6 | 7.24 | 0.2 | 0.2 | 0.5 | 637.8 | 131.2
19 | 49.7 | 2.2 | 94.2 | 28.8 | 33.2 | 7.25 | 0 | 0.2 | 0 | 628.3 | 23.7SD |  |  | 19:00 | 19:20
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-07-31
| Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
TM | ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 65.1 | 2.2 | 125.7 | 11 | 12.9 | 7.26 | 0 | 0.2 | 0 | 561.6 | 16.3HS | 3:08
4 | 47.8 | 2.2 | 157.1 | 21.4 | 42.7 | 7.27 | 0 | 0.2 | 0 | 615.3 | 57.7HS |  | 4:55 |  |  | ET 1:47
5 | 1.9 | 2.1 | 11.4 | 0 | 0 | 7.26 | 0.3 | 0.2 | 0.6 | 638.2 | 158.7
6 | 2 | 2.1 | 11.3 | 0.5 | 1.7 | 7.26 | 0.2 | 0.2 | 0.5 | 636.2 | 156.7
7 | 2 | 2 | 12.8 | 0.7 | 2.3 | 7.25 | 0.2 | 0.2 | 0.5 | 642.1 | 154.7
8 | 2 | 2 | 12.7 | 0.6 | 2 | 7.25 | 0.2 | 0.2 | 0.5 | 650.8 | 153.3
9 | 2.1 | 2 | 12.9 | 0.6 | 2 | 7.24 | 0.4 | 0.2 | 0.9 | 650 | 155
10 | 2 | 2 | 12.7 | 0.6 | 2.2 | 7.24 | 0.5 | 0.2 | 1.2 | 666.2 | 177.8
11 | 2 | 2 | 12.6 | 0.5 | 1.9 | 7.23 | 0.4 | 0.2 | 1 | 664.2 | 177.1
12 | 2 | 2 | 12.5 | 0.5 | 1.8 | 7.23 | 0.5 | 0.3 | 1.1 | 663.4 | 176.5
13 | 2 | 2 | 12.5 | 0.5 | 1.8 | 7.22 | 0.5 | 0.3 | 1.1 | 663 | 175.7
14 | 2 | 2 | 12.5 | 0.5 | 1.8 | 7.22 | 0.4 | 0.3 | 1 | 661.8 | 175.3
15 | 2 | 2 | 12.4 | 0.5 | 1.8 | 7.21 | 0.5 | 0.3 | 1.1 | 663 | 174.7
16 | 2 | 2 | 11.1 | 0.4 | 1.4 | 7.21 | 0.2 | 0.3 | 0.5 | 652 | 152.6
17 | 2 | 2 | 12.4 | 0.4 | 1.4 | 7.2 | 0.2 | 0.3 | 0.5 | 646.5 | 147.9
18 | 2 | 2 | 12.5 | 0.4 | 1.4 | 7.2 | 0.3 | 0.3 | 0.7 | 646.9 | 150.4
19 | 2 | 2 | 12.7 | 0.4 | 1.4 | 7.19 | 0.3 | 0.3 | 0.7 | 649.2 | 153.2
20 | 2 | 2 | 12.7 | 0.3 | 1.1 | 7.19 | 0.2 | 0.3 | 0.5 | 652.4 | 153.1
21 | 2 | 2 | 11.5 | 0.3 | 1 | 7.18 | 0.2 | 0.3 | 0.5 | 639.7 | 134
22 | 2 | 2 | 10.1 | 0.3 | 1 | 7.18 | 0.2 | 0.3 | 0.5 | 638.6 | 134.6
23 | 2 | 2 | 12.5 | 0.3 | 1.1 | 7.17 | 0.2 | 0.3 | 0.5 | 648 | 148.9
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
[7 empty] | Sum NH3 (lbs): |  | 159.3

## July CEMS Raw data
This data is raw hourly CEMs database data which may include invalid data such as values obtained during calibration checks.
July | 2008
Combustion
[7 empty] | Turbine |  | Plant MW
[7 empty] | Nat Gas |  | Output
Record# | DATE | TIME | BOILER11 | CATTMP12 | CO_COR13 | CO_HCOR14 | GAS15 | GEN16 | GEN27 | HGAS18 | HGASON19 | NH3110 | NH3COR111 | NH3FLO112 | NOX113 | NOX1I14 | NOXCOR115 | NOXH116 | NOXHCOR117 | NOXHRT118 | NOXRT119 | OXY120
1 | 2008-07-01 | 0 | -9999 | 81.5 | 2.7 | -82.4 | 0.03 | 0.5 | 1.2 | -8.593 | -9999 | -4.98 | -156.7 | 1.1 | 0 | 0 | 0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.71
2 | 2008-07-01 | 10000 | -9999 | 81.5 | 2.5 | -72.9 | 0.03 | 0.5 | 1.2 | -8.587 | -9999 | -4.98 | -155.6 | 1.1 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.71
3 | 2008-07-01 | 20000 | -9999 | 81.5 | 2.7 | -82.8 | 0.04 | 0.5 | 1.2 | -8.586 | -9999 | -4.98 | -160.2 | 1 | 0 | 0 | 0.1 | 0.02 | 0.5 | 0.003 | 0 | 20.72
4 | 2008-07-01 | 30000 | -9999 | 81.5 | 2.7 | -83.3 | 0.03 | 0.5 | 1.2 | -8.591 | -9999 | -4.98 | -162.9 | 1 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.72
5 | 2008-07-01 | 40000 | -9999 | 81.6 | 2.5 | -78 | 0.03 | 0.5 | 1.2 | -8.581 | -9999 | -4.98 | -162.9 | 1.2 | 0 | 0 | 0.1 | 0.02 | 0.4 | 0.003 | 0 | 20.72
6 | 2008-07-01 | 50000 | -9999 | 81.5 | 2.5 | -72.5 | 0.03 | 0.5 | 1.2 | -8.572 | -9999 | -4.98 | -157.8 | 1 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.64
7 | 2008-07-01 | 60000 | -9999 | 80.9 | 2.7 | -84.7 | 0.03 | 0.5 | 1.2 | -8.568 | -9999 | -4.98 | -157.7 | 1.2 | 0 | 0 | 0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.71
8 | 2008-07-01 | 70000 | -9999 | 79.7 | 3.2 | -80.4 | 0.03 | 0.5 | 1.2 | -8.582 | -9999 | -4.98 | -162.9 | 1.1 | 0 | 0 | 0.1 | 0.02 | 0.6 | 0.004 | 0 | 20.72
9 | 2008-07-01 | 80000 | -9999 | 79.7 | 3.7 | -75.8 | 0.03 | 0.5 | 1.2 | -8.574 | -9999 | -4.98 | -166.3 | 1.1 | 0 | 0 | 0.1 | 0.01 | 0.5 | 0.003 | 0 | 20.72
10 | 2008-07-01 | 90000 | -9999 | 82.7 | 4.5 | -83.3 | 0.03 | 0.5 | 1.2 | -8.563 | -9999 | -4.98 | -168.1 | 1.1 | 0 | 2.15 | 0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.65
11 | 2008-07-01 | 100000 | -9999 | 84.3 | 4 | -80.7 | 0.05 | 0.5 | 1.2 | -8.623 | -9999 | -4.98 | -156.6 | 1.2 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.71
12 | 2008-07-01 | 110000 | -9999 | 85.1 | 10.2 | -46.1 | 0.04 | 0.5 | 1.2 | -8.626 | -9999 | -4.98 | -132.6 | 1.2 | 1.72 | 0 | 2 | 7.95 | 4 | 0.015 | 0.008 | 17.21
13 | 2008-07-01 | 120000 | -9999 | 84.9 | 3 | -67.3 | 0.04 | 0.5 | 1.2 | -8.619 | -9999 | -4.98 | -132.8 | 1.2 | 0.01 | 0 | 0.3 | 0.01 | 0.2 | 0.003 | 0.001 | 20.68
14 | 2008-07-01 | 130000 | -9999 | 82.9 | 3.4 | -62.8 | 0.04 | 0.5 | 1.2 | -8.614 | -9999 | -4.98 | -122.9 | 1.2 | 0.01 | 0 | 0.2 | 0.01 | 0.3 | 0.002 | 0.001 | 20.66
15 | 2008-07-01 | 140000 | -9999 | 83.2 | 3.2 | -63.4 | 0.21 | 0.5 | 1.3 | -8.607 | -9999 | -4.98 | -115.5 | 1.1 | 0.01 | -0.01 | 0.2 | 0.02 | 0.3 | 0.002 | 0.001 | 20.65
16 | 2008-07-01 | 150000 | -9999 | 83.6 | 2.9 | -57.9 | 0.19 | 0.5 | 1.2 | -8.601 | -9999 | -4.98 | -109.1 | 1.1 | 0.01 | 0 | 0.2 | 0.02 | 0.4 | 0.002 | 0.001 | 20.63
17 | 2008-07-01 | 160000 | -9999 | 85.6 | 1.9 | -47.2 | 0.04 | 0.5 | 1.2 | -8.613 | -9999 | -4.98 | -99.2 | 1.4 | 0.01 | 0 | 0.2 | 0.01 | 0.3 | 0.002 | 0.001 | 20.6
18 | 2008-07-01 | 170000 | -9999 | 87.6 | 1 | -45.6 | 0.04 | 0.5 | 1.2 | -8.604 | -9999 | -4.98 | -99.4 | 1.3 | 0 | 0 | 0.1 | 0.02 | 0.3 | 0.002 | 0 | 20.6
19 | 2008-07-01 | 180000 | -9999 | 88 | 0.6 | -47.1 | 0.04 | 0.5 | 1.2 | -8.601 | -9999 | -4.98 | -97 | 1.3 | 0.01 | 0 | 0.1 | 0.01 | 0.3 | 0.002 | 0.001 | 20.6
20 | 2008-07-01 | 190000 | -9999 | 88.7 | 0.5 | -49.7 | 0.04 | 0.5 | 1.2 | -8.593 | -9999 | -4.98 | -98.5 | 1.2 | 0.01 | 0 | 0.1 | 0.01 | 0.3 | 0.002 | 0.001 | 20.6
21 | 2008-07-01 | 200000 | -9999 | 88.9 | 0.5 | -55.2 | 0.1 | 0.5 | 1.2 | -8.635 | -9999 | -4.98 | -102.3 | 1.1 | 0.01 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0.001 | 20.61
22 | 2008-07-01 | 210000 | -9999 | 88.9 | 0.5 | -55.4 | 0.04 | 0.5 | 1.2 | -8.618 | -9999 | -4.98 | -107.4 | 1.1 | 0.01 | 0 | 0.1 | 0.01 | 0.3 | 0.002 | 0.001 | 20.63
23 | 2008-07-01 | 220000 | -9999 | 87.7 | 0.4 | -53.9 | 0.04 | 0.5 | 1.3 | -8.612 | -9999 | -4.98 | -110.7 | 1 | 0.01 | 0 | 0.1 | 0.01 | 0.3 | 0.002 | 0.001 | 20.63
24 | 2008-07-01 | 230000 | -9999 | 87.5 | 0.4 | -59.1 | 0.04 | 0.5 | 1.3 | -8.628 | -9999 | -4.98 | -113 | 1 | 0.01 | 0 | 0.1 | 0.01 | 0.3 | 0.002 | 0.001 | 20.64
25 | 2008-07-02 | 0 | -9999 | 87.5 | 0.3 | -58.3 | 0.04 | 0.5 | 1.3 | -8.612 | -9999 | -4.98 | -115.5 | 1.1 | 0 | 0 | 0.1 | 0.02 | 0.4 | 0.003 | 0 | 20.65
26 | 2008-07-02 | 10000 | -9999 | 87.5 | 0.2 | -58.5 | 0.04 | 0.5 | 1.3 | -8.593 | -9999 | -4.98 | -115.4 | 1.1 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.64
27 | 2008-07-02 | 20000 | -9999 | 87.5 | 0.2 | -53 | 0.04 | 0.5 | 1.3 | -8.619 | -9999 | -4.98 | -111.3 | 1.1 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0.002 | 0 | 20.64
28 | 2008-07-02 | 30000 | -9999 | 86 | 0.3 | -63.7 | 0.04 | 0.5 | 1.3 | -8.604 | -9999 | -4.97 | -106.3 | 1.2 | 0.01 | 0 | 0.1 | 0.01 | 0.3 | 0.003 | 0.001 | 20.62
29 | 2008-07-02 | 40000 | -9999 | 330.4 | 21.3 | 82.1 | 5.92 | 14.4 | 14.9 | -8.605 | -9999 | -4.96 | -18.9 | 1.3 | 8.59 | 24.8 | 12.1 | 37.93 | 53.1 | 0.196 | 0.045 | 17.24
30 | 2008-07-02 | 50000 | -9999 | 592 | 14 | 5 | 6.76 | 17.1 | 17.5 | -8.614 | -9999 | -4.96 | -7.1 | 1.1 | 10.29 | 30.02 | 14.7 | 43.13 | 61.7 | 0.227 | 0.054 | 16.77
31 | 2008-07-02 | 60000 | -9999 | 580.5 | 16 | 6.6 | 6.76 | 17.4 | 17.8 | -8.64 | -9999 | -4.96 | -7.1 | 1.2 | 10.29 | 30.01 | 14.6 | 42.04 | 59.8 | 0.22 | 0.054 | 16.75
32 | 2008-07-02 | 70000 | -9999 | 579.5 | 17.2 | 7.2 | 6.76 | 17.2 | 17.6 | -8.593 | -9999 | -4.96 | -7.1 | 0.9 | 10.29 | 30.01 | 14.6 | 41.76 | 59.4 | 0.219 | 0.054 | 16.75
33 | 2008-07-02 | 80000 | -9999 | 582.1 | 14.1 | 19.9 | 6.84 | 17.8 | 18.2 | -8.649 | -9999 | -4.96 | -12.9 | 11.7 | 9.31 | 30.01 | 11.8 | 38.79 | 48 | 0.177 | 0.043 | 14.63
34 | 2008-07-02 | 90000 | -9999 | 589 | 15.7 | 18.2 | 8.94 | 40.2 | 40.6 | -8.642 | -9999 | -4.96 | -6.9 | 37.1 | 8.89 | 23.91 | 12 | 39.35 | 50.2 | 0.185 | 0.044 | 15.66
35 | 2008-07-02 | 100000 | -9999 | 623.8 | 0 | -2.1 | 16.09 | 117.1 | 117.4 | -8.622 | -9999 | -4.96 | -4.1 | 52.1 | 2.58 | 7.74 | 2.1 | 2.51 | 2 | 0.008 | 0.008 | 13.68
36 | 2008-07-02 | 110000 | -9999 | 625.1 | 0 | -2.8 | 16.06 | 116.8 | 137.4 | -8.618 | -9999 | -4.96 | -4.1 | 49.6 | 2.58 | 7.54 | 2.1 | 2.5 | 2 | 0.008 | 0.008 | 13.67
37 | 2008-07-02 | 120000 | -9999 | 625.2 | 0 | -2.5 | 16.27 | 119.1 | 151.8 | -8.638 | -9999 | -4.96 | -4.1 | 49.7 | 2.59 | 7.46 | 2.1 | 2.52 | 2.1 | 0.008 | 0.008 | 13.67
38 | 2008-07-02 | 130000 | -9999 | 649.4 | 0 | -2.5 | 21.15 | 170.4 | 252.9 | -8.635 | -9999 | -4.96 | -3.9 | 115.2 | 2.61 | 11.18 | 2.1 | 2.54 | 2 | 0.007 | 0.008 | 13.43
39 | 2008-07-02 | 140000 | -9999 | 660.6 | 0 | -2.5 | 21.33 | 171.8 | 257.3 | -8.587 | -9999 | -4.96 | -3.9 | 111.9 | 2.68 | 11.11 | 2.1 | 2.6 | 2.1 | 0.008 | 0.008 | 13.42
40 | 2008-07-02 | 150000 | -9999 | 637.5 | 1 | -18.2 | 12.98 | 104.8 | 157.5 | -8.632 | -9999 | -4.96 | -33.2 | 70.1 | 1.67 | 6.94 | 1.4 | 1.62 | 1.4 | 0.006 | 0.005 | 16.07
41 | 2008-07-02 | 160000 | -9999 | 519.6 | 7 | -24.6 | 2.68 | 9.2 | 9.8 | -8.601 | -9999 | -4.96 | -57.3 | 0.8 | 3.16 | 10.07 | 3.9 | 10.83 | 12.6 | 0.047 | 0.014 | 18.96
42 | 2008-07-02 | 170000 | -9999 | 609.7 | 20.6 | 25.5 | 9.21 | 40.1 | 40.4 | -8.576 | -9999 | -4.96 | -5.1 | 25.7 | 10.26 | 29.93 | 10.5 | 45.29 | 46.4 | 0.171 | 0.039 | 15.14
43 | 2008-07-02 | 180000 | -9999 | 542.5 | 18.5 | -2.7 | 2.12 | 8.4 | 9 | -8.62 | -9999 | -4.96 | -47.1 | 21.2 | 2.96 | 8.96 | 4.6 | 11.54 | 14.1 | 0.052 | 0.017 | 19.03
44 | 2008-07-02 | 190000 | -9999 | 410.2 | 1.5 | -50.1 | 0.11 | 0.5 | 1.2 | -8.612 | -9999 | -4.97 | -89.6 | 1.3 | 0.04 | 0.15 | 0.8 | 0.05 | 0.8 | 0.004 | 0.003 | 20.57
45 | 2008-07-02 | 200000 | -9999 | 382.7 | 0.5 | -57.3 | 0.08 | 0.5 | 1.2 | -8.607 | -9999 | -4.97 | -93 | 0.6 | 0.03 | 0.06 | 0.6 | 0.04 | 0.7 | 0.004 | 0.002 | 20.58
46 | 2008-07-02 | 210000 | -9999 | 373.7 | 0.4 | -53.2 | 0.04 | 0.5 | 1.2 | -8.611 | -9999 | -4.97 | -96.8 | 0.5 | 0.01 | 0.04 | 0.3 | 0.02 | 0.4 | 0.003 | 0.001 | 20.6
47 | 2008-07-02 | 220000 | -9999 | 368.1 | 0.4 | -60.6 | 0.04 | 0.5 | 1.2 | -8.613 | -9999 | -4.97 | -98.1 | 0.6 | 0.01 | 0.03 | 0.3 | 0.01 | 0.2 | 0.002 | 0.001 | 20.6
48 | 2008-07-02 | 230000 | -9999 | 362.4 | 0.4 | -53.4 | 0.04 | 0.5 | 1.2 | -8.619 | -9999 | -4.97 | -100 | 0.6 | 0.01 | 0.03 | 0.2 | 0.01 | 0.2 | 0.002 | 0.001 | 20.61
49 | 2008-07-03 | 0 | -9999 | 359 | 0.3 | -58.2 | 0.04 | 0.5 | 1.2 | -8.613 | -9999 | -4.97 | -102.4 | 0.6 | 0.01 | 0.02 | 0.2 | 0.02 | 0.3 | 0.003 | 0.001 | 20.61
50 | 2008-07-03 | 10000 | -9999 | 360.3 | 0.5 | -47.5 | 0.04 | 0.5 | 1.2 | -8.606 | -9999 | -4.97 | -94.5 | 0.4 | 0.01 | 0.02 | 0.2 | 0.01 | 0.2 | 0.002 | 0.001 | 20.58
51 | 2008-07-03 | 20000 | -9999 | 358 | 0.7 | -31.1 | 0.04 | 0.5 | 1.2 | -8.637 | -9999 | -4.97 | -57.7 | 0.2 | 0.01 | 0.03 | 0.1 | 0.01 | 0.1 | 0.001 | 0 | 20.39
52 | 2008-07-03 | 30000 | -9999 | 354.2 | 0.4 | -34.9 | 0.04 | 0.5 | 1.1 | -8.609 | -9999 | -4.97 | -53.9 | 0.2 | 0.01 | 0.04 | 0.1 | 0.02 | 0.2 | 0.002 | 0 | 20.36
53 | 2008-07-03 | 40000 | -9999 | 351.3 | 1.5 | -7.3 | 0.04 | 0.6 | 1.2 | -8.77 | -9999 | -4.99 | -53.3 | 0.1 | 0 | 0.06 | 0 | 0 | 0 | 0.001 | 0 | 20.35
54 | 2008-07-03 | 50000 | -9999 | 347.5 | 4 | -99 | 0.02 | 0.5 | 1.1 | -8.705 | -9999 | -4.98 | -167.3 | 0.3 | 0.15 | 0.13 | 11.3 | -0.27 | 6.8 | 509.683 | 541.336 | 20.57
55 | 2008-07-03 | 60000 | -9999 | 342.7 | 0.1 | -45.7 | 0.03 | 0.4 | 1.2 | -8.612 | -9999 | -4.97 | -91.7 | 0.4 | 0.01 | -0.01 | 0.2 | 0.01 | 0.2 | 0.002 | 0.001 | 20.58
56 | 2008-07-03 | 70000 | -9999 | 339.2 | 0.3 | -53.8 | 0.02 | 0.4 | 1.2 | -8.629 | -9999 | -4.97 | -89.9 | 0.4 | 0.01 | -0.01 | 0.1 | 0.01 | 0.1 | 0.002 | 0.001 | 20.57
57 | 2008-07-03 | 80000 | -9999 | 335.8 | 0.3 | -49.8 | 0.03 | 0.5 | 1.2 | -8.628 | -9999 | -4.97 | -90.4 | 0.6 | 0.01 | 0 | 0.1 | 0.01 | 0.1 | 0.002 | 0.001 | 20.57
58 | 2008-07-03 | 90000 | -9999 | 332.2 | 0.2 | -57.2 | 0.03 | 0.5 | 1.2 | -8.6 | -9999 | -4.97 | -91.1 | 0.6 | 0.01 | 2.08 | 0.1 | 0.01 | 0.3 | 0.002 | 0.001 | 20.58
59 | 2008-07-03 | 100000 | -9999 | 328.3 | 0.5 | -51.3 | 0.03 | 0.5 | 1.2 | -8.589 | -9999 | -4.97 | -91.6 | 0.6 | 0.01 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0.001 | 20.58
60 | 2008-07-03 | 110000 | -9999 | 324.9 | 0.4 | -45.4 | 0.03 | 0.5 | 1.2 | -8.591 | -9999 | -4.97 | -90.6 | 0.6 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.58
61 | 2008-07-03 | 120000 | -9999 | 321.7 | 0.3 | -45.3 | 0.03 | 0.5 | 1.2 | -8.586 | -9999 | -4.97 | -89.8 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.57
62 | 2008-07-03 | 130000 | -9999 | 317 | 0.4 | -49.5 | 0.03 | 0.5 | 1.2 | -8.602 | -9999 | -4.97 | -88 | 0.6 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.57
63 | 2008-07-03 | 140000 | -9999 | 308.2 | 0.3 | -44.1 | 0.2 | 0.5 | 1.2 | -8.638 | -9999 | -4.97 | -85.3 | 0.5 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.56
64 | 2008-07-03 | 150000 | -9999 | 301.5 | 0.3 | -49.6 | 0.13 | 0.5 | 1.2 | -8.606 | -9999 | -4.96 | -83.5 | 0.4 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.55
65 | 2008-07-03 | 160000 | -9999 | 296.9 | 0.2 | -48.3 | 0.04 | 0.5 | 1.2 | -8.584 | -9999 | -4.97 | -82.6 | 0.5 | 0 | 0 | 0.1 | 0.02 | 0.3 | 0.002 | 0 | 20.54
66 | 2008-07-03 | 170000 | -9999 | 292.8 | 0.1 | -42.1 | 0.04 | 0.5 | 1.2 | -8.594 | -9999 | -4.97 | -81.7 | 0.4 | 0 | -0.01 | 0.1 | 0.02 | 0.3 | 0.002 | 0 | 20.54
67 | 2008-07-03 | 180000 | -9999 | 289.2 | 0.1 | -40.2 | 0.04 | 0.5 | 1.2 | -8.602 | -9999 | -4.97 | -81.5 | 0.5 | 0 | 0 | 0.1 | 0.02 | 0.3 | 0.002 | 0 | 20.54
68 | 2008-07-03 | 190000 | -9999 | 286.1 | 0 | -43 | 0.03 | 0.5 | 1.2 | -8.601 | -9999 | -4.97 | -80.8 | 0.5 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0.002 | 0 | 20.54
69 | 2008-07-03 | 200000 | -9999 | 283.1 | 0 | -48.8 | 0.03 | 0.5 | 1.2 | -8.633 | -9999 | -4.97 | -82 | 0.7 | 0 | 0 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.54
70 | 2008-07-03 | 210000 | -9999 | 280 | -0.1 | -45.3 | 0.04 | 0.5 | 1.2 | -8.616 | -9999 | -4.97 | -81.2 | 0.7 | 0 | 0 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.54
71 | 2008-07-03 | 220000 | -9999 | 276.6 | -0.1 | -44.7 | 0.03 | 0.5 | 1.2 | -8.553 | -9999 | -4.97 | -83 | 0.6 | 0 | 0 | 0.1 | 0.02 | 0.3 | 0.002 | 0 | 20.55
72 | 2008-07-03 | 230000 | -9999 | 274.1 | -0.1 | -40.9 | 0.04 | 0.5 | 1.2 | -8.604 | -9999 | -4.97 | -84.1 | 0.7 | 0.01 | -0.01 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.55
73 | 2008-07-04 | 0 | -9999 | 271.1 | 0 | -41.1 | 0.03 | 0.5 | 1.2 | -8.574 | -9999 | -4.97 | -84.9 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.55
74 | 2008-07-04 | 10000 | -9999 | 268.1 | -0.1 | -48 | 0.04 | 0.5 | 1.2 | -8.607 | -9999 | -4.97 | -85.8 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.56
75 | 2008-07-04 | 20000 | -9999 | 265.4 | -0.2 | -54.5 | 0.04 | 0.5 | 1.2 | -8.616 | -9999 | -4.97 | -87.1 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.56
76 | 2008-07-04 | 30000 | -9999 | 262.6 | -0.1 | -51.7 | 0.04 | 0.5 | 1.2 | -8.596 | -9999 | -4.97 | -90.4 | 0.7 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.57
77 | 2008-07-04 | 40000 | -9999 | 259.7 | -0.2 | -50.1 | 0.04 | 0.5 | 1.2 | -8.581 | -9999 | -4.97 | -89.2 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.57
78 | 2008-07-04 | 50000 | -9999 | 256.8 | -0.1 | -50.8 | 0.04 | 0.5 | 1.2 | -8.627 | -9999 | -4.96 | -90.9 | 0.6 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.58
79 | 2008-07-04 | 60000 | -9999 | 254.4 | -0.3 | -48.4 | 0.04 | 0.5 | 1.2 | -8.618 | -9999 | -4.97 | -92.7 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.58
80 | 2008-07-04 | 70000 | -9999 | 251.6 | -0.2 | -50.7 | 0.04 | 0.5 | 1.2 | -8.617 | -9999 | -4.97 | -92.9 | 0.5 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.58
81 | 2008-07-04 | 80000 | -9999 | 249.2 | -0.2 | -55.5 | 0.03 | 0.5 | 1.2 | -8.656 | -9999 | -4.97 | -91.9 | 0.5 | 0.01 | -0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.58
82 | 2008-07-04 | 90000 | -9999 | 246.7 | -0.2 | -52.7 | 0.04 | 0.5 | 1.1 | -8.653 | -9999 | -4.97 | -90.9 | 0.5 | 0.01 | 2.1 | 0.1 | 0.01 | 0.3 | 0.002 | 0.001 | 20.58
83 | 2008-07-04 | 100000 | -9999 | 244.3 | -0.2 | -46.7 | 0.04 | 0.5 | 1.2 | -8.641 | -9999 | -4.97 | -89.3 | 0.4 | 0 | 0 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.57
84 | 2008-07-04 | 110000 | -9999 | 242.2 | -0.1 | -53.7 | 0.04 | 0.5 | 1.2 | -8.645 | -9999 | -4.97 | -90.6 | 0.3 | 0.01 | -0.01 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.58
85 | 2008-07-04 | 120000 | -9999 | 239.8 | 0.1 | -55 | 0.04 | 0.5 | 1.2 | -8.599 | -9999 | -4.97 | -92.1 | 0.3 | 0.01 | 0 | 0.2 | 0.02 | 0.3 | 0.002 | 0.001 | 20.58
86 | 2008-07-04 | 130000 | -9999 | 237.2 | -0.2 | -53.1 | 0.04 | 0.5 | 1.2 | -8.637 | -9999 | -4.96 | -93.4 | 0.2 | 0.01 | -0.01 | 0.1 | 0.02 | 0.3 | 0.002 | 0.001 | 20.59
87 | 2008-07-04 | 140000 | -9999 | 235 | -0.4 | -51.7 | 0.04 | 0.5 | 1.2 | -8.646 | -9999 | -4.97 | -94 | 0.2 | 0 | -0.01 | 0.1 | 0.01 | 0.3 | 0.002 | 0 | 20.59
88 | 2008-07-04 | 150000 | -9999 | 233 | -0.3 | -59.6 | 0.04 | 0.5 | 1.2 | -8.584 | -9999 | -4.97 | -94.9 | 0.1 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.59
89 | 2008-07-04 | 160000 | -9999 | 230.6 | -0.4 | -50.4 | 0.04 | 0.5 | 1.2 | -8.63 | -9999 | -4.97 | -93.4 | 0.2 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.59
90 | 2008-07-04 | 170000 | -9999 | 228.4 | -0.2 | -42.4 | 0.04 | 0.5 | 1.2 | -8.613 | -9999 | -4.97 | -92.6 | 0.1 | 0.02 | 0 | 0.3 | 0.02 | 0.4 | 0.002 | 0.001 | 20.58
91 | 2008-07-04 | 180000 | -9999 | 225.4 | -0.4 | -49.4 | 0.04 | 0.5 | 1.2 | -8.613 | -9999 | -4.97 | -93.7 | 0.2 | 0.02 | -0.01 | 0.3 | 0.03 | 0.4 | 0.003 | 0.001 | 20.59
92 | 2008-07-04 | 190000 | -9999 | 222.1 | -0.5 | -54.2 | 0.04 | 0.5 | 1.2 | -8.574 | -9999 | -4.97 | -94.8 | 0.2 | 0 | 0 | 0.1 | 0.02 | 0.4 | 0.002 | 0 | 20.59
93 | 2008-07-04 | 200000 | -9999 | 219.1 | -0.5 | -49.8 | 0.04 | 0.5 | 1.3 | -8.599 | -9999 | -4.97 | -93 | -0.1 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.58
94 | 2008-07-04 | 210000 | -9999 | 216.4 | 0.8 | -51.6 | 0.04 | 0.5 | 1.3 | -8.604 | -9999 | -4.97 | -94.5 | -0.1 | 0.01 | 0 | 0.2 | 0.01 | 0.2 | 0.002 | 0.001 | 20.59
95 | 2008-07-04 | 220000 | -9999 | 213.9 | 0.6 | -51.4 | 0.04 | 0.5 | 1.2 | -8.621 | -9999 | -4.97 | -94.5 | -0.1 | 0.01 | 0 | 0.1 | 0.01 | 0.3 | 0.002 | 0 | 20.59
96 | 2008-07-04 | 230000 | -9999 | 211.6 | 2.2 | -53.6 | 0.04 | 0.5 | 1.3 | -8.642 | -9999 | -4.97 | -92.5 | -0.1 | 0.01 | 0 | 0.3 | 0.02 | 0.4 | 0.003 | 0.001 | 20.58
97 | 2008-07-05 | 0 | -9999 | 209 | 3.5 | -44.7 | 0.04 | 0.5 | 1.2 | -8.639 | -9999 | -4.97 | -91.2 | -0.1 | 0.02 | 0 | 0.3 | 0.02 | 0.4 | 0.003 | 0.001 | 20.58
98 | 2008-07-05 | 10000 | -9999 | 206.9 | 1.6 | -51.5 | 0.04 | 0.5 | 1.2 | -8.63 | -9999 | -4.97 | -90 | 0 | 0.01 | -0.01 | 0.2 | 0.01 | 0 | 0.002 | 0.001 | 20.57
99 | 2008-07-05 | 20000 | -9999 | 204.7 | 1.4 | -46.7 | 0.04 | 0.5 | 1.2 | -8.635 | -9999 | -4.97 | -88.6 | 0 | 0.01 | -0.01 | 0.1 | 0.02 | 0.2 | 0.002 | 0.001 | 20.57
100 | 2008-07-05 | 30000 | -9999 | 202.3 | 1.1 | -53.3 | 0.04 | 0.5 | 1.2 | -8.641 | -9999 | -4.97 | -89.9 | 0.2 | 0.01 | 0 | 0.3 | 0.01 | 0.1 | 0.002 | 0.001 | 20.57
101 | 2008-07-05 | 40000 | -9999 | 200.2 | 0.6 | -49.3 | 0.04 | 0.5 | 1.2 | -8.645 | -9999 | -4.97 | -89.5 | 0 | 0.01 | 0 | 0.3 | 0.02 | 0.4 | 0.002 | 0.001 | 20.57
102 | 2008-07-05 | 50000 | -9999 | 198 | -0.2 | -52.7 | 0.04 | 0.5 | 1.3 | -8.674 | -9999 | -4.97 | -91.4 | 0.1 | 0 | 0 | 0.1 | 0 | 0.1 | 0.002 | 0 | 20.58
103 | 2008-07-05 | 60000 | -9999 | 195.9 | 0 | -46.9 | 0.04 | 0.5 | 1.2 | -8.611 | -9999 | -4.97 | -93 | 0 | 0.01 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0.001 | 20.58
104 | 2008-07-05 | 70000 | -9999 | 193.6 | 0.2 | -53 | 0.04 | 0.5 | 1.3 | -8.622 | -9999 | -4.96 | -95 | 0 | 0.01 | -0.01 | 0.2 | 0.02 | 0.3 | 0.002 | 0.001 | 20.59
105 | 2008-07-05 | 80000 | -9999 | 191.6 | -0.1 | -49.3 | 0.04 | 0.5 | 1.3 | -8.598 | -9999 | -4.97 | -96.7 | -0.1 | 0.01 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0.001 | 20.6
106 | 2008-07-05 | 90000 | -9999 | 189.3 | 0.3 | -56.7 | 0.04 | 0.5 | 1.2 | -8.61 | -9999 | -4.97 | -99.3 | -0.1 | 0.01 | 2.11 | 0.1 | 0.02 | 0.2 | 0.002 | 0.001 | 20.6
107 | 2008-07-05 | 100000 | -9999 | 187.2 | 0.2 | -60.7 | 0.04 | 0.5 | 1.2 | -8.596 | -9999 | -4.97 | -102.5 | -0.1 | 0.01 | 0 | 0.2 | 0.02 | 0.4 | 0.003 | 0.001 | 20.61
108 | 2008-07-05 | 110000 | -9999 | 185.3 | 0.1 | -55.9 | 0.04 | 0.5 | 1.2 | -8.595 | -9999 | -4.96 | -107 | -0.4 | 0.01 | -0.01 | 0.1 | 0.02 | 0.3 | 0.003 | 0.001 | 20.63
109 | 2008-07-05 | 120000 | -9999 | 183.4 | 0.2 | -57.7 | 0.04 | 0.5 | 1.2 | -8.622 | -9999 | -4.97 | -109.6 | -0.5 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.63
110 | 2008-07-05 | 130000 | -9999 | 181.6 | 0.3 | -56.4 | 0.04 | 0.5 | 1.2 | -8.621 | -9999 | -4.97 | -109.4 | -0.6 | 0 | 0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.63
111 | 2008-07-05 | 140000 | -9999 | 179.7 | 0.1 | -62.8 | 0.04 | 0.5 | 1.2 | -8.601 | -9999 | -4.97 | -112.7 | -0.4 | 0.01 | -0.01 | 0.2 | 0.01 | 0.3 | 0.003 | 0.001 | 20.64
112 | 2008-07-05 | 150000 | -9999 | 177.8 | -0.2 | -61.6 | 0.04 | 0.5 | 1.2 | -8.606 | -9999 | -4.96 | -114.9 | -0.1 | 0 | -0.01 | 0.1 | 0.02 | 0.3 | 0.003 | 0 | 20.64
113 | 2008-07-05 | 160000 | -9999 | 176.2 | 0 | -59.7 | 0.04 | 0.5 | 1.2 | -8.594 | -9999 | -4.96 | -114.6 | 0 | 0 | -0.01 | 0.1 | 0.01 | 0.3 | 0.003 | 0.001 | 20.64
114 | 2008-07-05 | 170000 | -9999 | 174.3 | 0.1 | -59.8 | 0.04 | 0.5 | 1.2 | -8.602 | -9999 | -4.96 | -117.1 | 0 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.65
115 | 2008-07-05 | 180000 | -9999 | 172.4 | 0.2 | -68 | 0.04 | 0.5 | 1.2 | -8.598 | -9999 | -4.97 | -118.7 | 0.1 | 0 | 0 | 0.1 | 0.02 | 0.2 | 0.003 | 0 | 20.65
116 | 2008-07-05 | 190000 | -9999 | 170.3 | 0.1 | -77.3 | 0.04 | 0.5 | 1.2 | -8.591 | -9999 | -4.97 | -123 | 0.2 | 0 | 0 | 0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.66
117 | 2008-07-05 | 200000 | -9999 | 168.7 | 0 | -65.6 | 0.04 | 0.5 | 1.2 | -8.601 | -9999 | -4.96 | -125.7 | 0.3 | 0 | 0 | 0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.67
118 | 2008-07-05 | 210000 | -9999 | 166.7 | 0 | -67.5 | 0.03 | 0.5 | 1.2 | -8.606 | -9999 | -4.97 | -130.5 | 0.5 | 0 | -0.01 | 0.1 | 0.02 | 0.3 | 0.003 | 0 | 20.67
119 | 2008-07-05 | 220000 | -9999 | 165.2 | 0 | -77.6 | 0.04 | 0.5 | 1.2 | -8.612 | -9999 | -4.97 | -136.4 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.68
120 | 2008-07-05 | 230000 | -9999 | 163.4 | 0.2 | -76.3 | 0.04 | 0.5 | 1.2 | -8.631 | -9999 | -4.97 | -139.8 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.69
121 | 2008-07-06 | 0 | -9999 | 161.5 | 0 | -76.9 | 0.04 | 0.5 | 1.2 | -8.592 | -9999 | -4.97 | -142.3 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.69
122 | 2008-07-06 | 10000 | -9999 | 160 | 0 | -80.8 | 0.04 | 0.5 | 1.2 | -8.59 | -9999 | -4.97 | -144.5 | 0.4 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.7
123 | 2008-07-06 | 20000 | -9999 | 158.1 | -0.1 | -66.3 | 0.04 | 0.5 | 1.2 | -8.589 | -9999 | -4.97 | -143 | 0.5 | 0 | -0.01 | 0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.69
124 | 2008-07-06 | 30000 | -9999 | 156.7 | 0 | -85.6 | 0.04 | 0.5 | 1.2 | -8.632 | -9999 | -4.97 | -143 | 0.4 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.69
125 | 2008-07-06 | 40000 | -9999 | 155 | 0 | -73.9 | 0.04 | 0.5 | 1.2 | -8.593 | -9999 | -4.96 | -146.7 | 0.5 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.7
126 | 2008-07-06 | 50000 | -9999 | 153.4 | -0.1 | -85.5 | 0.04 | 0.5 | 1.2 | -8.62 | -9999 | -4.97 | -150.7 | 0.6 | 0 | 0 | 0.1 | 0.02 | 0.5 | 0.004 | 0 | 20.7
127 | 2008-07-06 | 60000 | -9999 | 152 | 0.1 | -87.4 | 0.04 | 0.5 | 1.3 | -8.594 | -9999 | -4.97 | -157.6 | 0.5 | 0 | -0.01 | 0.1 | 0.01 | 0.3 | 0.004 | 0.001 | 20.64
128 | 2008-07-06 | 70000 | -9999 | 150.7 | 0.2 | -105.2 | 0.04 | 0.5 | 1.2 | -8.585 | -9999 | -4.97 | -158.4 | 0.6 | 0 | -0.01 | 0.1 | 0.02 | 0.5 | 0.004 | 0.001 | 20.64
129 | 2008-07-06 | 80000 | -9999 | 149.3 | 0.2 | -106.6 | 0.04 | 0.5 | 1.2 | -8.591 | -9999 | -4.97 | -165.6 | 0.4 | 0 | 0 | 0.1 | 0.01 | 0.6 | 0.005 | 0 | 20.72
130 | 2008-07-06 | 90000 | -9999 | 148.4 | 0.2 | -88.8 | 0.04 | 0.5 | 1.2 | -8.583 | -9999 | -4.97 | -172.5 | 0.4 | 0 | 2.14 | 0.1 | 0.01 | 0.2 | 0.004 | 0.001 | 20.73
131 | 2008-07-06 | 100000 | -9999 | 147.2 | 0.2 | -94.5 | 0.04 | 0.5 | 1.2 | -8.564 | -9999 | -4.97 | -174 | 0.4 | 0 | 0 | 0.1 | 0.02 | 0.7 | 0.005 | 0.001 | 20.66
132 | 2008-07-06 | 110000 | -9999 | 145.7 | 0.1 | -111.1 | 0.04 | 0.5 | 1.2 | -8.619 | -9999 | -4.97 | -176.4 | 0.4 | 0 | -0.01 | 0.1 | 0.01 | 0.4 | 0.004 | 0.001 | 20.73
133 | 2008-07-06 | 120000 | -9999 | 144.7 | -0.2 | -84.7 | 0.04 | 0.5 | 1.2 | -8.621 | -9999 | -4.97 | -168.2 | 0.5 | 0 | 0 | 0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.72
134 | 2008-07-06 | 130000 | -9999 | 143.7 | -0.1 | -79.1 | 0.04 | 0.5 | 1.2 | -8.619 | -9999 | -4.97 | -161.2 | 0.4 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.003 | 0.001 | 20.64
135 | 2008-07-06 | 140000 | -9999 | 142.1 | 0.1 | -99.2 | 0.04 | 0.5 | 1.2 | -8.609 | -9999 | -4.97 | -159.3 | 0.5 | 0 | 0 | 0.1 | 0.02 | 0.4 | 0.004 | 0.001 | 20.72
136 | 2008-07-06 | 150000 | -9999 | 141.3 | -0.1 | -80.6 | 0.04 | 0.5 | 1.3 | -8.609 | -9999 | -4.97 | -160 | 0.7 | 0 | 0 | 0.2 | 0 | 0.1 | 0.003 | 0.001 | 20.72
137 | 2008-07-06 | 160000 | -9999 | 140.4 | 0 | -83.7 | 0.04 | 0.5 | 1.3 | -8.62 | -9999 | -4.97 | -152.7 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.71
138 | 2008-07-06 | 170000 | -9999 | 139 | 0.1 | -71.6 | 0.04 | 0.5 | 1.2 | -8.618 | -9999 | -4.97 | -146.7 | 0.6 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.004 | 0 | 20.7
139 | 2008-07-06 | 180000 | -9999 | 138.5 | 0.2 | -86 | 0.04 | 0.5 | 1.2 | -8.617 | -9999 | -4.97 | -142.4 | 0.6 | 0 | 0 | 0.1 | 0.02 | 0.4 | 0.004 | 0 | 20.69
140 | 2008-07-06 | 190000 | -9999 | 137 | 0.2 | -85.1 | 0.04 | 0.5 | 1.2 | -8.624 | -9999 | -4.97 | -141.3 | 0.6 | 0 | -0.01 | 0.1 | 0 | 0.1 | 0.003 | 0 | 20.69
141 | 2008-07-06 | 200000 | -9999 | 136.3 | 0.1 | -69.6 | 0.04 | 0.5 | 1.2 | -8.604 | -9999 | -4.97 | -140.2 | 0.7 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.69
142 | 2008-07-06 | 210000 | -9999 | 135 | 0.3 | -77.1 | 0.04 | 0.5 | 1.2 | -8.626 | -9999 | -4.97 | -142.6 | 0.8 | 0 | 0 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.69
143 | 2008-07-06 | 220000 | -9999 | 133.3 | 0.1 | -77.6 | 0.04 | 0.5 | 1.2 | -8.603 | -9999 | -4.96 | -145.8 | 0.8 | 0 | -0.01 | 0.1 | 0.01 | 0.5 | 0.004 | 0 | 20.7
144 | 2008-07-06 | 230000 | -9999 | 132.1 | 0.2 | -82.2 | 0.04 | 0.5 | 1.2 | -8.618 | -9999 | -4.96 | -149.1 | 0.8 | 0 | -0.01 | 0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.7
145 | 2008-07-07 | 0 | -9999 | 131.2 | 0.1 | -88.3 | 0.04 | 0.5 | 1.2 | -8.613 | -9999 | -4.97 | -152.3 | 0.8 | 0 | 0 | 0.1 | 0.02 | 0.5 | 0.004 | 0 | 20.71
146 | 2008-07-07 | 10000 | -9999 | 129.7 | 0.1 | -87 | 0.04 | 0.5 | 1.3 | -8.617 | -9999 | -4.97 | -158.5 | 0.8 | 0 | -0.01 | 0.1 | 0.02 | 0.5 | 0.004 | 0 | 20.64
147 | 2008-07-07 | 20000 | -9999 | 128.7 | -0.1 | -90.8 | 0.04 | 0.5 | 1.3 | -8.624 | -9999 | -4.97 | -162.9 | 0.8 | 0 | -0.01 | 0.1 | 0.02 | 0.5 | 0.004 | 0 | 20.72
148 | 2008-07-07 | 30000 | -9999 | 127.8 | -0.1 | -99.4 | 0.04 | 0.5 | 1.3 | -8.643 | -9999 | -4.97 | -163.4 | 0.7 | 0 | 0 | 0.1 | 0.02 | 0.3 | 0.004 | 0.001 | 20.72
149 | 2008-07-07 | 40000 | -9999 | 126.3 | -0.3 | -89.8 | 0.04 | 0.5 | 1.3 | -8.632 | -9999 | -4.97 | -168.2 | 0.8 | 0 | -0.01 | 0.1 | 0.02 | 0.5 | 0.005 | 0 | 20.72
150 | 2008-07-07 | 50000 | -9999 | 125.9 | -0.5 | -100.4 | 0.04 | 0.5 | 1.3 | -8.642 | -9999 | -4.97 | -175.2 | 0.6 | 0 | -0.01 | 0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.73
151 | 2008-07-07 | 60000 | -9999 | 124.3 | -0.1 | -106.2 | 0.04 | 0.5 | 1.3 | -8.647 | -9999 | -4.97 | -179.5 | 0.7 | 0 | 0 | 0.1 | 0.02 | 0.5 | 0.005 | 0.001 | 20.73
152 | 2008-07-07 | 70000 | -9999 | 123.9 | -0.2 | -120.8 | 0.04 | 0.5 | 1.3 | -8.619 | -9999 | -4.97 | -189.2 | 0.7 | 0 | 0 | 0.1 | 0.01 | 0.1 | 0.004 | 0.001 | 20.74
153 | 2008-07-07 | 80000 | -9999 | 122.5 | 12.6 | -67.2 | 0.04 | 0.5 | 1.3 | -8.623 | -9999 | -4.96 | -261.5 | 0.8 | 1.7 | -0.01 | 3.7 | 8 | 5.5 | 0.022 | 0.014 | 17.19
154 | 2008-07-07 | 90000 | -9999 | 122.6 | 1 | -134.5 | 0.04 | 0.5 | 1.3 | -8.603 | -9999 | -4.97 | -254.3 | 0.6 | 0.02 | 2.16 | 0.9 | 0.02 | 0.4 | 0.006 | 0.003 | 20.78
155 | 2008-07-07 | 100000 | -9999 | 121.6 | 0.4 | -127.8 | 0.04 | 0.5 | 1.3 | -8.626 | -9999 | -4.97 | -222.2 | 0.8 | 0.01 | -0.01 | 0.4 | 0.01 | 0.3 | 0.005 | 0.002 | 20.77
156 | 2008-07-07 | 110000 | -9999 | 120.9 | 0.1 | -127.6 | 0.04 | 0.5 | 1.3 | -8.63 | -9999 | -4.97 | -225.5 | 0.6 | 0.01 | 0 | 0.3 | 0.01 | 0.4 | 0.005 | 0.001 | 20.69
157 | 2008-07-07 | 120000 | -9999 | 120.8 | 0.2 | -111.7 | 0.04 | 0.5 | 1.3 | -8.628 | -9999 | -4.97 | -224 | 0.6 | 0.01 | 0 | 0.3 | 0.01 | 0.1 | 0.004 | 0.001 | 20.77
158 | 2008-07-07 | 130000 | -9999 | 119.5 | 0.9 | -111.3 | 0.04 | 0.5 | 1.3 | -8.613 | -9999 | -4.97 | -209.1 | 0.7 | 0.01 | -0.01 | 0.3 | 0.01 | 0.3 | 0.005 | 0.001 | 20.76
159 | 2008-07-07 | 140000 | -9999 | 118.9 | 1.2 | -119.2 | 0.24 | 0.5 | 1.2 | -8.583 | -9999 | -4.97 | -208.3 | 0.8 | 0.01 | 0 | 0.2 | 0.01 | 0.1 | 0.004 | 0.001 | 20.76
160 | 2008-07-07 | 150000 | -9999 | 118.9 | 1.2 | -108.9 | 0.18 | 0.5 | 1.2 | -8.609 | -9999 | -4.97 | -204.6 | 0.7 | 0 | 0 | 0.2 | 0.02 | 0.5 | 0.005 | 0.001 | 20.75
161 | 2008-07-07 | 160000 | -9999 | 118.8 | 1.2 | -108.2 | 0.04 | 0.5 | 1.2 | -8.601 | -9999 | -4.97 | -195 | 0.6 | 0.01 | 0 | 0.2 | 0.02 | 0.4 | 0.004 | 0.001 | 20.75
162 | 2008-07-07 | 170000 | -9999 | 118.8 | 1.3 | -107.3 | 0.04 | 0.5 | 1.2 | -8.61 | -9999 | -4.97 | -186.9 | 0.5 | 0.01 | -0.01 | 0.2 | 0.03 | 0.9 | 0.006 | 0.001 | 20.74
163 | 2008-07-07 | 180000 | -9999 | 118.5 | 1.2 | -100.5 | 0.04 | 0.5 | 1.3 | -8.592 | -9999 | -4.97 | -183.5 | 0.5 | 0 | -0.01 | 0.2 | 0.01 | 0.5 | 0.005 | 0.001 | 20.74
164 | 2008-07-07 | 190000 | -9999 | 117 | 1.3 | -114.3 | 0.04 | 0.5 | 1.2 | -8.592 | -9999 | -4.97 | -199.8 | 0.4 | 0.01 | 0 | 0.2 | 0.01 | 0.6 | 0.005 | 0.001 | 20.75
165 | 2008-07-07 | 200000 | -9999 | 117 | 1.6 | -111.5 | 0.04 | 0.5 | 1.3 | -8.599 | -9999 | -4.97 | -211.3 | 0.4 | 0.01 | -0.01 | 0.2 | 0 | 0.2 | 0.004 | 0.001 | 20.76
166 | 2008-07-07 | 210000 | -9999 | 115.7 | 1.4 | -137.2 | 0.04 | 0.5 | 1.3 | -8.612 | -9999 | -4.97 | -223.4 | 0.5 | 0 | -0.01 | 0.2 | 0.01 | 0.3 | 0.005 | 0.001 | 20.77
167 | 2008-07-07 | 220000 | -9999 | 115.1 | 1.5 | -130.9 | 0.04 | 0.5 | 1.3 | -8.585 | -9999 | -4.97 | -242.7 | 0.6 | 0.01 | -0.01 | 0.3 | 0.01 | 0.5 | 0.006 | 0.001 | 20.78
168 | 2008-07-07 | 230000 | -9999 | 114 | 1.2 | -132.2 | 0.04 | 0.5 | 1.3 | -8.576 | -9999 | -4.97 | -240.2 | 0.6 | 0 | -0.01 | 0.2 | 0.02 | 0.6 | 0.005 | 0.001 | 20.78
169 | 2008-07-08 | 0 | -9999 | 113.7 | 1.2 | -132.7 | 0.04 | 0.5 | 1.3 | -8.614 | -9999 | -4.97 | -251.1 | 0.8 | 0 | -0.01 | 0.2 | 0.01 | 0.6 | 0.006 | 0.001 | 20.78
170 | 2008-07-08 | 10000 | -9999 | 112.8 | 1.1 | -150 | 0.04 | 0.5 | 1.3 | -8.629 | -9999 | -4.97 | -263.3 | 0.7 | 0 | 0 | 0.2 | 0.02 | 0.7 | 0.006 | 0.001 | 20.79
171 | 2008-07-08 | 20000 | -9999 | 111.7 | 0.9 | -154.4 | 0.04 | 0.5 | 1.3 | -8.588 | -9999 | -4.97 | -269.6 | 0.8 | 0 | -0.01 | 0.2 | 0.02 | 0.8 | 0.007 | 0.001 | 20.79
172 | 2008-07-08 | 30000 | -9999 | 111.7 | 0.6 | -146.6 | 0.04 | 0.5 | 1.3 | -8.611 | -9999 | -4.97 | -282 | 0.8 | 0 | 0 | 0.3 | 0.02 | 0.7 | 0.007 | 0.001 | 20.79
173 | 2008-07-08 | 40000 | -9999 | 110.5 | 0.9 | -139.4 | 0.04 | 0.5 | 1.2 | -8.588 | -9999 | -4.97 | -273.4 | 0.8 | 0 | 0 | 0.2 | 0.01 | 0.6 | 0.007 | 0.001 | 20.79
174 | 2008-07-08 | 50000 | -9999 | 110.3 | 1.2 | -163.7 | 0.04 | 0.5 | 1.2 | -8.618 | -9999 | -4.96 | -280.1 | 0.7 | 0 | 0 | 0.2 | 0.02 | 0.8 | 0.007 | 0.001 | 20.72
175 | 2008-07-08 | 60000 | -9999 | 110.3 | 1.8 | -161.6 | 0.04 | 0.5 | 1.2 | -8.579 | -9999 | -4.97 | -292.3 | 0.7 | 0.01 | 0 | 0.4 | 0.02 | 0.8 | 0.007 | 0.001 | 20.72
176 | 2008-07-08 | 70000 | -9999 | 109.6 | 2 | -175 | 0.04 | 0.5 | 1.2 | -8.638 | -9999 | -4.97 | -299.5 | 0.8 | 0.01 | 0 | 0.5 | 0.01 | 0.3 | 0.007 | 0.002 | 20.8
177 | 2008-07-08 | 80000 | -9999 | 108.3 | 2.6 | -163.4 | 0.04 | 0.5 | 1.2 | -8.585 | -9999 | -4.97 | -295.2 | 0.8 | 0.01 | 0 | 0.4 | 0.01 | 0.3 | 0.006 | 0.002 | 20.8
178 | 2008-07-08 | 90000 | -9999 | 108.4 | 2.6 | -137.3 | 0.04 | 0.5 | 1.3 | -8.602 | -9999 | -4.97 | -270.1 | 0.7 | 0.01 | 2.14 | 0.4 | 0.01 | 0.3 | 0.006 | 0.002 | 20.79
179 | 2008-07-08 | 100000 | -9999 | 108.3 | 2.7 | -142.8 | 0.04 | 0.5 | 1.3 | -8.599 | -9999 | -4.97 | -247.2 | 0.8 | 0.01 | 0 | 0.4 | 0.01 | 0.3 | 0.006 | 0.001 | 20.7
180 | 2008-07-08 | 110000 | -9999 | 108.3 | 2.9 | -127.6 | 0.04 | 0.5 | 1.3 | -8.568 | -9999 | -4.97 | -220.7 | 0.8 | 0.01 | -0.01 | 0.3 | 0.02 | 0.6 | 0.005 | 0.001 | 20.76
181 | 2008-07-08 | 120000 | -9999 | 108.3 | 2.7 | -105.1 | 0.04 | 0.5 | 1.3 | -8.585 | -9999 | -4.96 | -209.6 | 0.7 | 0.01 | -0.01 | 0.2 | 0.02 | 0.6 | 0.006 | 0.001 | 20.76
182 | 2008-07-08 | 130000 | -9999 | 108.3 | 2 | -88.8 | 0.04 | 0.5 | 1.3 | -8.608 | -9999 | -4.97 | -191.1 | 0.7 | 0 | -0.01 | 0.2 | 0.01 | 0.4 | 0.004 | 0.001 | 20.74
183 | 2008-07-08 | 140000 | -9999 | 108.3 | 2.3 | -91.9 | 0.18 | 0.5 | 1.3 | -8.607 | -9999 | -4.97 | -177.8 | 0.7 | 0 | 0 | 0.2 | 0.02 | 0.5 | 0.004 | 0.001 | 20.73
184 | 2008-07-08 | 150000 | -9999 | 108.3 | 1.6 | -87.1 | 0.18 | 0.5 | 1.2 | -8.616 | -9999 | -4.96 | -167.1 | 0.6 | 0 | -0.01 | 0.1 | 0.02 | 0.3 | 0.004 | 0 | 20.72
185 | 2008-07-08 | 160000 | -9999 | 108.4 | 1 | -81.8 | 0.04 | 0.5 | 1.2 | -8.602 | -9999 | -4.97 | -156.5 | 0.4 | 0 | 0 | 0.1 | 0 | 0 | 0.003 | 0 | 20.71
186 | 2008-07-08 | 170000 | -9999 | 108.2 | 1 | -80.1 | 0.04 | 0.5 | 1.2 | -8.595 | -9999 | -4.97 | -145.6 | 0.4 | 0 | 0 | 0.2 | 0.01 | 0.2 | 0.003 | 0.001 | 20.7
187 | 2008-07-08 | 180000 | -9999 | 108.3 | 1 | -85 | 0.04 | 0.5 | 1.3 | -8.638 | -9999 | -4.97 | -140.8 | 0.3 | 0.01 | 0 | 0.2 | 0.01 | 0.3 | 0.003 | 0.001 | 20.69
188 | 2008-07-08 | 190000 | -9999 | 108.3 | 1 | -83.2 | 0.04 | 0.5 | 1.2 | -8.597 | -9999 | -4.97 | -141.8 | 0.3 | 0.01 | 0 | 0.2 | 0.02 | 0.3 | 0.003 | 0.001 | 20.69
189 | 2008-07-08 | 200000 | -9999 | 108.3 | 0.9 | -71.3 | 0.04 | 0.5 | 1.2 | -8.619 | -9999 | -4.97 | -141.8 | 0.1 | 0.01 | 0 | 0.2 | 0.01 | 0.4 | 0.004 | 0.001 | 20.69
190 | 2008-07-08 | 210000 | -9999 | 108.3 | 0.7 | -74.7 | 0.04 | 0.5 | 1.3 | -8.626 | -9999 | -4.97 | -141.5 | 0.2 | 0.01 | -0.01 | 0.2 | 0.01 | 0.3 | 0.003 | 0.001 | 20.69
191 | 2008-07-08 | 220000 | -9999 | 106.9 | 0.6 | -84.4 | 0.04 | 0.5 | 1.3 | -8.624 | -9999 | -4.97 | -145.6 | 0.3 | 0.01 | 0 | 0.2 | 0.01 | 0.2 | 0.003 | 0.001 | 20.7
192 | 2008-07-08 | 230000 | -9999 | 106.9 | 0.3 | -93 | 0.04 | 0.5 | 1.3 | -8.622 | -9999 | -4.97 | -145.3 | 0.2 | 0.01 | 0 | 0.2 | 0.01 | 0.4 | 0.004 | 0.001 | 20.7
193 | 2008-07-09 | 0 | -9999 | 105.3 | 0.2 | -81.6 | 0.04 | 0.5 | 1.3 | -8.627 | -9999 | -4.97 | -145 | 0.4 | 0.01 | 0 | 0.2 | 0.02 | 0.3 | 0.003 | 0.001 | 20.7
194 | 2008-07-09 | 10000 | -9999 | 104.8 | 0.1 | -76.4 | 0.04 | 0.5 | 1.3 | -8.584 | -9999 | -4.97 | -142.4 | 0.6 | 0.01 | -0.01 | 0.2 | 0.01 | 0.3 | 0.003 | 0.001 | 20.69
195 | 2008-07-09 | 20000 | -9999 | 104.9 | 0.1 | -84.3 | 0.04 | 0.5 | 1.3 | -8.609 | -9999 | -4.97 | -139.3 | 0.5 | 0.01 | -0.01 | 0.2 | 0.01 | 0.2 | 0.003 | 0.001 | 20.69
196 | 2008-07-09 | 30000 | -9999 | 342.7 | 23.9 | 75.5 | 5.92 | 15.4 | 15.9 | -8.644 | -9999 | -4.96 | -22.8 | 0.6 | 8.62 | 24.99 | 12.2 | 38.18 | 52.9 | 0.195 | 0.045 | 17.23
197 | 2008-07-09 | 40000 | -9999 | 600.4 | 18 | 6.8 | 6.88 | 18.1 | 18.5 | -8.604 | -9999 | -4.96 | -7.1 | 7.9 | 10.29 | 30.01 | 14.7 | 45.08 | 64.4 | 0.237 | 0.054 | 16.77
198 | 2008-07-09 | 50000 | -9999 | 588 | 19.6 | 9.4 | 6.91 | 19 | 19.3 | -8.605 | -9999 | -4.96 | -7 | 58.4 | 10.29 | 30.02 | 14.5 | 41.72 | 58.8 | 0.217 | 0.054 | 16.72
199 | 2008-07-09 | 60000 | -9999 | 586 | 20.6 | 9.3 | 6.91 | 19.3 | 19.6 | -8.613 | -9999 | -4.96 | -7 | 53 | 10.23 | 30.02 | 14.4 | 42.33 | 59.6 | 0.22 | 0.053 | 16.71
200 | 2008-07-09 | 70000 | -9999 | 595.9 | 25.5 | 53.2 | 7.35 | 20.4 | 20.8 | -8.593 | -9999 | -4.96 | -6.8 | 51.9 | 10.29 | 29.8 | 14.1 | 28.92 | 39.7 | 0.146 | 0.052 | 16.58
201 | 2008-07-09 | 80000 | -9999 | 618.7 | 8.7 | 25.1 | 15.68 | 112.2 | 124.9 | -8.605 | -9999 | -4.96 | -21.1 | 79.5 | 5.54 | 15.38 | 5.1 | 20.5 | 15.8 | 0.058 | 0.019 | 12.72
202 | 2008-07-09 | 90000 | -9999 | 625.2 | 0 | -2.3 | 16.25 | 119.3 | 154.8 | -8.639 | -9999 | -4.96 | -4.1 | 49.3 | 2.07 | 8.46 | 1.7 | 1.97 | 1.6 | 0.006 | 0.006 | 13.82
203 | 2008-07-09 | 100000 | -9999 | 627.9 | 0 | -2.4 | 16.82 | 126.4 | 195.7 | -8.622 | -9999 | -4.97 | -4.1 | 58.8 | 1.89 | 7.38 | 1.6 | 1.8 | 1.5 | 0.006 | 0.006 | 13.81
204 | 2008-07-09 | 110000 | -9999 | 651.7 | 0 | -2.2 | 20.92 | 168.3 | 252.7 | -8.622 | -9999 | -4.97 | -4 | 149.1 | 2.45 | 11.38 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.62
205 | 2008-07-09 | 120000 | -9999 | 657.4 | 0 | -2.2 | 20.65 | 166.1 | 251 | -2.595 | -9999 | -4.96 | -4 | 142.4 | 2.49 | 11.12 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.63
206 | 2008-07-09 | 130000 | -9999 | 656.8 | 0 | -2.6 | 20.48 | 164.8 | 249.3 | -8.607 | -9999 | -4.97 | -4 | 143.1 | 2.5 | 11.06 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.64
207 | 2008-07-09 | 140000 | -9999 | 674.5 | -0.1 | -2.2 | 20.35 | 163.3 | 256.2 | 179.582 | -9999 | -4.96 | -3.8 | 146.4 | 2.5 | 11.83 | 1.9 | 2.37 | 1.8 | 0.007 | 0.007 | 13.21
208 | 2008-07-09 | 150000 | -9999 | 739.3 | -0.2 | -1.8 | 20.39 | 162.8 | 276.9 | 463.2 | -9999 | -4.96 | -3.4 | 176.9 | 1.66 | 13.43 | 1.2 | 1.57 | 1.1 | 0.004 | 0.004 | 12.38
209 | 2008-07-09 | 160000 | -9999 | 739 | -0.2 | -1.7 | 20.52 | 163.3 | 278.7 | 463.2 | -9999 | -4.96 | -3.4 | 162.8 | 2.15 | 13.45 | 1.5 | 2.06 | 1.4 | 0.005 | 0.006 | 12.4
210 | 2008-07-09 | 170000 | -9999 | 742.8 | -0.2 | -1.6 | 21.25 | 171.1 | 289.3 | 463.2 | -9999 | -4.96 | -3.4 | 159 | 2.66 | 13.64 | 1.8 | 2.54 | 1.7 | 0.006 | 0.007 | 12.29
211 | 2008-07-09 | 180000 | -9999 | 723.9 | -0.1 | -1.9 | 21.59 | 174.9 | 286 | 463.2 | -9999 | -4.96 | -3.5 | 152.2 | 2.55 | 13.24 | 1.8 | 2.44 | 1.7 | 0.006 | 0.007 | 12.6
212 | 2008-07-09 | 190000 | -9999 | 743.6 | -0.1 | -1.8 | 20.86 | 166.2 | 284.2 | 340.033 | -9999 | -4.96 | -3.5 | 142 | 2.62 | 13.17 | 1.8 | 2.49 | 1.7 | 0.006 | 0.007 | 12.43
213 | 2008-07-09 | 200000 | -9999 | 593.1 | 13.7 | -30.2 | 5.19 | 33.2 | 55.3 | -8.605 | -9999 | -4.96 | -65.9 | 14.9 | 2.24 | 6.81 | 1.5 | 7.17 | 7.1 | 0.032 | 0.013 | 18
214 | 2008-07-09 | 210000 | -9999 | 456.1 | 2.6 | -79.1 | 0.04 | 0.5 | 1.3 | -8.561 | -9999 | -4.97 | -193 | 0.7 | -0.19 | 0.05 | -7.5 | -0.14 | -5.4 | 0 | 0 | 20.67
215 | 2008-07-09 | 220000 | -9999 | 429.6 | 1.5 | -117.2 | 0.04 | 0.5 | 1.2 | -8.583 | -9999 | -4.97 | -211.3 | 0.7 | -0.2 | 0 | -8.4 | -0.15 | -6.4 | 0 | 0 | 20.76
216 | 2008-07-09 | 230000 | -9999 | 422.8 | 1.3 | -120.2 | 0.04 | 0.5 | 1.2 | -8.646 | -9999 | -4.97 | -222.9 | 0.7 | -0.2 | -0.01 | -8.9 | -0.19 | -8.6 | 0 | 0 | 20.77
217 | 2008-07-10 | 0 | -9999 | 418.1 | 1.3 | -115.5 | 0.04 | 0.5 | 1.2 | -8.586 | -9999 | -4.97 | -235.7 | 0.8 | -0.2 | -0.01 | -9.5 | -0.18 | -8.6 | 0 | 0 | 20.77
218 | 2008-07-10 | 10000 | -9999 | 414.2 | 1.4 | -133.1 | 0.04 | 0.5 | 1.3 | -8.612 | -9999 | -4.97 | -256.5 | 0.7 | -0.2 | 0 | -10.3 | -0.18 | -9.3 | 0 | 0 | 20.78
219 | 2008-07-10 | 20000 | -9999 | 410.2 | 1.6 | -150.3 | 0.04 | 0.5 | 1.3 | -8.607 | -9999 | -4.97 | -271.1 | 0.6 | -0.2 | 0 | -11 | -0.19 | -10.2 | 0 | 0 | 20.71
220 | 2008-07-10 | 30000 | -9999 | 405.7 | 2 | -155.3 | 0.04 | 0.5 | 1.3 | -8.602 | -9999 | -4.97 | -272.3 | 0.6 | -0.2 | 0 | -11.1 | -0.19 | -10.4 | 0 | 0 | 20.79
221 | 2008-07-10 | 40000 | -9999 | 400.7 | 1.8 | -165.7 | 0.04 | 0.5 | 1.3 | -8.558 | -9999 | -4.97 | -287.5 | 0.6 | -0.2 | -0.02 | -11.8 | -0.19 | -11.1 | 0 | 0 | 20.79
222 | 2008-07-10 | 50000 | -9999 | 395.7 | 2.2 | -175.9 | 0.04 | 0.5 | 1.3 | -8.596 | -9999 | -4.97 | -326.4 | 0.5 | -0.2 | -0.03 | -13.3 | -0.19 | -12 | 0 | 0 | 20.81
223 | 2008-07-10 | 60000 | -9999 | 391.2 | 3 | -202.7 | 0.04 | 0.5 | 1.3 | -8.588 | -9999 | -4.97 | -397.9 | 0.6 | -0.2 | -0.03 | -16.4 | -0.18 | -14.9 | 0 | 0 | 20.82
224 | 2008-07-10 | 70000 | -9999 | 386.9 | 4.3 | -276.5 | 0.04 | 0.5 | 1.2 | -8.608 | -9999 | -4.97 | -495.3 | 0.6 | -0.2 | -0.03 | -20.3 | -0.18 | -18.3 | 0 | 0 | 20.84
225 | 2008-07-10 | 80000 | -9999 | 383.1 | 4.8 | -284.1 | 0.04 | 0.5 | 1.2 | -8.606 | -9999 | -4.96 | -590.1 | 0.4 | -0.2 | -0.03 | -24.3 | -0.18 | -22.2 | 0 | 0 | 20.84
226 | 2008-07-10 | 90000 | -9999 | 381.4 | 1.6 | -299 | 0.04 | 0.5 | 1.3 | -8.607 | -9999 | -4.97 | -655.9 | 0.5 | -0.2 | 2.09 | -26.9 | -0.19 | -25.5 | 0 | 0 | 20.85
227 | 2008-07-10 | 100000 | -9999 | 542.2 | 18.9 | 3.9 | 6.59 | 17.3 | 17.8 | -8.6 | -9999 | -4.96 | -21.2 | 0.5 | 9.85 | 28.31 | 14 | 42.68 | 61.6 | 0.229 | 0.054 | 17.01
228 | 2008-07-10 | 110000 | -9999 | 616.1 | 8.1 | 9.5 | 13.49 | 88.3 | 103.6 | -8.588 | -9999 | -4.96 | -4.7 | 52.7 | 4.86 | 17 | 5.2 | 21.8 | 23.4 | 0.086 | 0.019 | 14.55
229 | 2008-07-10 | 120000 | -9999 | 631.6 | 0 | -2.4 | 17.38 | 132.6 | 204.1 | -8.632 | -9999 | -4.96 | -4.2 | 58.3 | 1.73 | 7.15 | 1.5 | 1.65 | 1.4 | 0.005 | 0.005 | 13.89
230 | 2008-07-10 | 130000 | -9999 | 634.1 | 2.5 | -12.2 | 17.15 | 129.7 | 200.8 | -8.611 | -9999 | -4.97 | -72.2 | 48.8 | 3.34 | 7.69 | -0.7 | 9.49 | 2.1 | 0.014 | 0.007 | 12.29
231 | 2008-07-10 | 140000 | -9999 | 635.4 | 0 | -2.5 | 16.94 | 127.9 | 199.9 | -8.589 | -9999 | -4.96 | -4.2 | 44.7 | 2.62 | 7.36 | 2.2 | 2.5 | 2.1 | 0.008 | 0.008 | 13.9
232 | 2008-07-10 | 150000 | -9999 | 635.4 | 0 | -1.9 | 16.93 | 127.6 | 200.2 | -8.61 | -9999 | -4.96 | -4.2 | 45.3 | 2.55 | 6.87 | 2.1 | 2.43 | 2 | 0.008 | 0.008 | 13.89
233 | 2008-07-10 | 160000 | -9999 | 635.3 | 0 | -2.3 | 16.92 | 127.5 | 200 | -8.628 | -9999 | -4.96 | -4.2 | 48 | 2.4 | 6.86 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.9
234 | 2008-07-10 | 170000 | -9999 | 635.6 | 0 | -2.3 | 16.91 | 127.4 | 200.1 | -8.618 | -9999 | -4.97 | -4.2 | 49.9 | 2.4 | 6.99 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.9
235 | 2008-07-10 | 180000 | -9999 | 635.7 | 0 | -2 | 16.92 | 127.4 | 200 | -6.373 | -9999 | -4.96 | -4.2 | 49.3 | 2.38 | 6.92 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.9
236 | 2008-07-10 | 190000 | -9999 | 635.2 | 0 | -2.4 | 16.75 | 125.3 | 197.8 | -7.655 | -9999 | -4.96 | -4.2 | 50.3 | 2.4 | 7.03 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.89
237 | 2008-07-10 | 200000 | -9999 | 554.1 | 23.2 | -120.2 | 1.5 | 6.5 | 13.1 | -8.618 | -9999 | -4.96 | -259.9 | 2.8 | 2.04 | 5.48 | -3.6 | 7.9 | 3.7 | 0.039 | 0.016 | 19.71
238 | 2008-07-10 | 210000 | -9999 | 444.9 | 4.6 | -417.3 | 0.04 | 0.5 | 1.3 | -8.668 | -9999 | -4.97 | -782.7 | 0.4 | -0.19 | 0.03 | -30.5 | -0.16 | -24.3 | 0 | 0 | 20.86
239 | 2008-07-10 | 220000 | -9999 | 426.2 | 1.8 | -588.1 | 0.04 | 0.5 | 1.3 | -8.621 | -9999 | -4.97 | -987.9 | 0.5 | -0.2 | 0 | -39.6 | -0.18 | -36 | 7.918 | 0.005 | 20.8
240 | 2008-07-10 | 230000 | -9999 | 420.8 | 2.2 | -638.4 | 0.04 | 0.5 | 1.3 | -8.617 | -9999 | -4.97 | -1064.9 | 0.5 | -0.2 | 0 | -42.8 | -0.18 | -37.6 | 0.008 | 0.008 | 20.88
241 | 2008-07-11 | 0 | -9999 | 415.8 | 1.6 | -646.8 | 0.04 | 0.5 | 1.3 | -8.613 | -9999 | -4.97 | -1032.5 | 0.5 | -0.2 | 0 | -41.7 | -0.19 | -39.2 | 0.015 | 0.016 | 20.88
242 | 2008-07-11 | 10000 | -9999 | 412.2 | 1.5 | -456 | 0.04 | 0.5 | 1.3 | -8.628 | -9999 | -4.97 | -978.5 | 0.3 | -0.2 | -0.01 | -39.8 | -0.18 | -36.3 | 0.019 | 0.021 | 20.89
243 | 2008-07-11 | 20000 | -9999 | 408.1 | 1.8 | -696.5 | 0.04 | 0.5 | 1.3 | -8.604 | -9999 | -4.97 | -1160.8 | 0.4 | -0.2 | 0 | -47.2 | -0.2 | -46 | 3.176 | 0.014 | 20.89
244 | 2008-07-11 | 30000 | -9999 | 403.1 | 1.5 | -549.3 | 0.04 | 0.5 | 1.3 | -8.604 | -9999 | -4.97 | -978.6 | 0.4 | -0.2 | -0.03 | -40.3 | -0.19 | -36.7 | 7.938 | 0.028 | 20.89
245 | 2008-07-11 | 40000 | -9999 | 398.4 | 1 | -558.3 | 0.04 | 0.5 | 1.3 | -8.639 | -9999 | -4.97 | -959.9 | 0.4 | -0.2 | -0.03 | -39.2 | -0.19 | -36.2 | 6.356 | 0.031 | 20.89
246 | 2008-07-11 | 50000 | -9999 | 394 | 1.7 | -490.1 | 0.04 | 0.5 | 1.3 | -8.598 | -9999 | -4.97 | -753.1 | 0.4 | -0.2 | -0.03 | -30.8 | -0.19 | -30.9 | 9.534 | 0.047 | 20.9
247 | 2008-07-11 | 60000 | -9999 | 389.1 | 2.9 | -235.8 | 0.04 | 0.5 | 1.3 | -8.636 | -9999 | -4.97 | -485.7 | 0.4 | -0.2 | -0.02 | -19.7 | -0.18 | -17.9 | 3.228 | 0.075 | 20.83
248 | 2008-07-11 | 70000 | -9999 | 385.7 | 4.2 | -228.9 | 0.04 | 0.5 | 1.3 | -8.617 | -9999 | -4.97 | -574.4 | 0.4 | -0.2 | -0.03 | -23 | -0.19 | -23.1 | 0.067 | 0.074 | 20.91
249 | 2008-07-11 | 80000 | -9999 | 374.5 | 2.8 | -287.3 | 0.04 | 0.5 | 1.3 | -7.855 | -9999 | -4.97 | -509.6 | 0.5 | -0.2 | -0.04 | -20.3 | -0.18 | -18.7 | 0.067 | 0.079 | 20.91
250 | 2008-07-11 | 90000 | -9999 | 323.4 | 3.2 | -472.5 | 0.06 | 0.5 | 1.3 | -7.876 | -9999 | -4.97 | -861.9 | 0.5 | -0.2 | 2.07 | -34.5 | -0.18 | -31.7 | 0.046 | 0.054 | 20.9
251 | 2008-07-11 | 100000 | -9999 | 283.5 | 5.2 | -524.9 | 0.04 | 0.5 | 1.3 | -8.594 | -9999 | -4.97 | -995.4 | 0.5 | -0.2 | -0.04 | -40 | -0.18 | -37.9 | 0.019 | 0.026 | 20.89
252 | 2008-07-11 | 110000 | -9999 | 249 | 5.6 | -614.3 | 0.04 | 0.5 | 1.3 | -8.619 | -9999 | -4.97 | -1192.5 | 0.4 | -0.2 | -0.03 | -47.9 | -0.18 | -44.6 | 0.006 | 0.007 | 20.88
253 | 2008-07-11 | 120000 | -9999 | 232.3 | 2.4 | -594 | 0.04 | 0.5 | 1.3 | -8.617 | -9999 | -4.96 | -966.1 | 0.6 | -0.2 | -0.02 | -39.4 | -0.18 | -34.3 | 0.001 | 0.001 | 20.87
254 | 2008-07-11 | 130000 | -9999 | 223.7 | 1.2 | -433.4 | 0.04 | 0.5 | 1.3 | -8.64 | -9999 | -4.97 | -716.9 | 0.8 | -0.2 | -0.03 | -29.3 | -0.18 | -26.2 | 0.001 | 0.001 | 20.86
255 | 2008-07-11 | 140000 | -9999 | 216.4 | 0.9 | -270.4 | 0.18 | 0.5 | 1.3 | -8.631 | -9999 | -4.97 | -579.2 | 0.8 | -0.2 | -0.03 | -23.7 | -0.18 | -20.3 | 0 | 0 | 20.84
256 | 2008-07-11 | 150000 | -9999 | 211.2 | 0 | -282 | 0.16 | 0.5 | 1.3 | -2.248 | -9999 | -4.97 | -536 | 0.8 | -0.2 | -0.03 | -21.9 | -0.19 | -19.1 | 0 | 0 | 20.76
257 | 2008-07-11 | 160000 | -9999 | 206.8 | -0.1 | -229.5 | 0.05 | 0.5 | 1.3 | -8.624 | -9999 | -4.97 | -408.7 | 0.8 | -0.2 | -0.04 | -16.8 | -0.19 | -14.6 | 0 | 0 | 20.82
258 | 2008-07-11 | 170000 | -9999 | 203.1 | 0.4 | -191.5 | 0.04 | 0.5 | 1.3 | -6.15 | -9999 | -4.97 | -347.3 | 0.8 | -0.2 | -0.03 | -14.1 | -0.18 | -12.6 | 0 | 0 | 20.81
259 | 2008-07-11 | 180000 | -9999 | 201.2 | 1.3 | -169.3 | 0.04 | 0.5 | 1.3 | 4.176 | -9999 | -4.97 | -301.9 | 0.8 | -0.2 | -0.03 | -12.2 | -0.19 | -11.3 | 0 | 0 | 20.8
260 | 2008-07-11 | 190000 | -9999 | 199.6 | 2.7 | -200.5 | 0.04 | 0.5 | 1.2 | -8.609 | -9999 | -4.97 | -336.4 | 0.9 | -0.2 | -0.03 | -13.6 | -0.19 | -12.3 | 0 | 0 | 20.73
261 | 2008-07-11 | 200000 | -9999 | 197.6 | 3.1 | -189.8 | 0.04 | 0.5 | 1.2 | -4.41 | -9999 | -4.96 | -388 | 0.8 | -0.2 | -0.02 | -15.7 | -0.18 | -14.4 | 0 | 0 | 20.82
262 | 2008-07-11 | 210000 | -9999 | 195.8 | 3.6 | -291.7 | 0.04 | 0.5 | 1.2 | -8.601 | -9999 | -4.97 | -471.3 | 0.8 | -0.2 | -0.03 | -19.1 | -0.18 | -17.5 | 0 | 0 | 20.76
263 | 2008-07-11 | 220000 | -9999 | 193.7 | 4.4 | -296 | 0.04 | 0.5 | 1.2 | -7.853 | -9999 | -4.97 | -578.9 | 0.7 | -0.2 | -0.03 | -23.3 | -0.19 | -22.3 | 0 | 0 | 20.84
264 | 2008-07-11 | 230000 | -9999 | 192.1 | 6.7 | -339.6 | 0.04 | 0.5 | 1.2 | -8.592 | -9999 | -4.97 | -619.3 | 0.7 | -0.2 | -0.03 | -24.9 | -0.19 | -23.3 | 0 | 0 | 20.85
265 | 2008-07-12 | 0 | -9999 | 190.3 | 9.9 | -398.4 | 0.04 | 0.5 | 1.3 | -8.592 | -9999 | -4.97 | -615.8 | 0.6 | -0.2 | -0.03 | -24.7 | -0.19 | -24.4 | 0 | 0 | 20.85
266 | 2008-07-12 | 10000 | -9999 | 188.7 | 8.3 | -423.4 | 0.04 | 0.5 | 1.3 | -8.604 | -9999 | -4.97 | -630.1 | 0.7 | -0.2 | -0.04 | -25.5 | -0.18 | -22.9 | 0 | 0 | 20.77
267 | 2008-07-12 | 20000 | -9999 | 186.7 | 6 | -337.4 | 0.04 | 0.5 | 1.3 | -7.625 | -9999 | -4.97 | -638.3 | 0.7 | -0.2 | -0.03 | -25.8 | -0.19 | -23.7 | 0 | 0 | 20.77
268 | 2008-07-12 | 30000 | -9999 | 185 | 6.1 | -363.4 | 0.04 | 0.5 | 1.3 | -8.605 | -9999 | -4.97 | -653.4 | 0.6 | -0.2 | -0.04 | -26.2 | -0.19 | -25.4 | 0 | 0 | 20.85
269 | 2008-07-12 | 40000 | -9999 | 183.2 | 6.2 | -419.3 | 0.04 | 0.5 | 1.3 | -8.614 | -9999 | -4.96 | -678.9 | 0.6 | -0.2 | -0.03 | -27 | -0.17 | -23 | 0 | 0 | 20.85
270 | 2008-07-12 | 50000 | -9999 | 181.4 | 7.3 | -424.9 | 0.04 | 0.5 | 1.3 | -8.596 | -9999 | -4.97 | -798.3 | 0.8 | -0.2 | -0.03 | -32.4 | -0.19 | -29.2 | 0 | 0 | 20.86
271 | 2008-07-12 | 60000 | -9999 | 179.6 | 10 | -427.4 | 0.04 | 0.5 | 1.3 | -8.632 | -9999 | -4.97 | -783.6 | 0.7 | -0.2 | -0.03 | -31.2 | -0.18 | -28.2 | 0 | 0 | 20.86
272 | 2008-07-12 | 70000 | -9999 | 178.1 | 17.7 | -454.8 | 0.04 | 0.5 | 1.3 | -8.621 | -9999 | -4.97 | -900.7 | 0.9 | -0.2 | -0.03 | -35.5 | -0.15 | -27.4 | 0 | 0 | 20.86
273 | 2008-07-12 | 80000 | -9999 | 177.1 | 19.6 | -499.8 | 0.05 | 0.5 | 1.3 | -8.61 | -9999 | -4.96 | -982.1 | 0.9 | -0.19 | -0.02 | -37.4 | -0.14 | -27.3 | 7.916 | 0.002 | 20.87
274 | 2008-07-12 | 90000 | -9999 | 176 | 17.3 | -566.3 | 0.04 | 0.5 | 1.3 | -8.606 | -9999 | -4.97 | -997 | 0.8 | -0.19 | 2.11 | -38.9 | -0.14 | -27.1 | 0.002 | 0.002 | 20.87
275 | 2008-07-12 | 100000 | -9999 | 174.4 | 15.5 | -527.7 | 0.04 | 0.5 | 1.3 | -8.622 | -9999 | -4.97 | -908 | 0.6 | -0.2 | -0.03 | -36.4 | -0.19 | -34.7 | 0.001 | 0.001 | 20.86
276 | 2008-07-12 | 110000 | -9999 | 173.4 | 13.7 | -435 | 0.04 | 0.5 | 1.3 | -8.586 | -9999 | -4.97 | -859 | 0.7 | -0.2 | -0.03 | -34.7 | -0.18 | -30.7 | 0.001 | 0.001 | 20.86
277 | 2008-07-12 | 120000 | -9999 | 171.9 | 14.6 | -484.7 | 0.04 | 0.5 | 1.3 | -8.613 | -9999 | -4.97 | -841.1 | 1 | -0.2 | -0.03 | -33.9 | -0.2 | -34.8 | 0 | 0 | 20.86
278 | 2008-07-12 | 130000 | -9999 | 170.3 | 11.8 | -426.4 | 0.04 | 0.5 | 1.3 | -7.829 | -9999 | -4.97 | -721.4 | 0.8 | -0.2 | -0.03 | -29.3 | -0.18 | -28 | 0 | 0 | 20.85
279 | 2008-07-12 | 140000 | -9999 | 169.1 | 9.1 | -288.2 | 0.13 | 0.5 | 1.3 | -7.854 | -9999 | -4.97 | -560.4 | 0.9 | -0.2 | -0.03 | -23 | -0.19 | -21.6 | 0 | 0 | 20.77
280 | 2008-07-12 | 150000 | -9999 | 168.2 | 7.4 | -257.5 | 0.14 | 0.5 | 1.3 | -6.9 | -9999 | -4.97 | -471.1 | 1 | -0.2 | -0.03 | -19.4 | -0.18 | -18 | 0 | 0 | 20.76
281 | 2008-07-12 | 160000 | -9999 | 166.6 | 6.1 | -231 | 0.05 | 0.5 | 1.3 | -6.851 | -9999 | -4.97 | -419.2 | 1.1 | -0.2 | -0.03 | -17.1 | -0.18 | -15.6 | 0 | 0 | 20.83
282 | 2008-07-12 | 170000 | -9999 | 166.1 | 5.9 | -209.2 | 0.04 | 0.5 | 1.3 | -8.578 | -9999 | -4.97 | -377.7 | 1.1 | -0.2 | -0.04 | -15.3 | -0.18 | -13.9 | 0 | 0 | 20.74
283 | 2008-07-12 | 180000 | -9999 | 165.2 | 5.3 | -179.9 | 0.04 | 0.5 | 1.3 | -2.991 | -9999 | -4.97 | -358 | 1.1 | -0.2 | -0.04 | -14.5 | -0.18 | -13.1 | 0 | 0 | 20.81
284 | 2008-07-12 | 190000 | -9999 | 164.3 | 5.7 | -181.1 | 0.04 | 0.5 | 1.3 | -8.581 | -9999 | -4.97 | -354.1 | 0.9 | -0.2 | -0.03 | -14.3 | -0.18 | -13.3 | 0 | 0 | 20.81
285 | 2008-07-12 | 200000 | -9999 | 163.1 | 5.9 | -204.4 | 0.04 | 0.5 | 1.2 | -8.582 | -9999 | -4.97 | -373.2 | 0.9 | -0.2 | -0.03 | -15 | -0.18 | -13.3 | 0 | 0 | 20.82
286 | 2008-07-12 | 210000 | -9999 | 161.3 | 4.1 | -204.9 | 0.04 | 0.5 | 1.2 | -8.61 | -9999 | -4.97 | -379.9 | 0.9 | -0.2 | -0.03 | -15.4 | -0.18 | -13.9 | 0 | 0 | 20.82
287 | 2008-07-12 | 220000 | -9999 | 160 | 3.2 | -214.1 | 0.04 | 0.5 | 1.3 | -8.63 | -9999 | -4.97 | -388.5 | 0.7 | -0.2 | -0.03 | -15.7 | -0.18 | -14 | 0 | 0 | 20.82
288 | 2008-07-12 | 230000 | -9999 | 158.3 | 3.1 | -247.2 | 0.04 | 0.5 | 1.2 | -8.595 | -9999 | -4.97 | -409.8 | 0.8 | -0.2 | -0.03 | -16.6 | -0.18 | -14.9 | 0 | 0 | 20.82
289 | 2008-07-13 | 0 | -9999 | 157.3 | 2.9 | -203 | 0.04 | 0.5 | 1.3 | -8.647 | -9999 | -4.97 | -399.8 | 0.8 | -0.2 | -0.04 | -16.4 | -0.19 | -15.1 | 0 | 0 | 20.82
290 | 2008-07-13 | 10000 | -9999 | 156.2 | 2.1 | -186.1 | 0.04 | 0.5 | 1.2 | -8.613 | -9999 | -4.97 | -392.6 | 0.8 | -0.2 | -0.03 | -16.1 | -0.18 | -13.8 | 0 | 0 | 20.82
291 | 2008-07-13 | 20000 | -9999 | 154.7 | 1.8 | -227.8 | 0.04 | 0.5 | 1.3 | -8.622 | -9999 | -4.97 | -400 | 0.7 | -0.2 | -0.03 | -16.4 | -0.18 | -14.5 | 0 | 0 | 20.75
292 | 2008-07-13 | 30000 | -9999 | 153 | 2.1 | -207.2 | 0.04 | 0.5 | 1.3 | -8.62 | -9999 | -4.97 | -416.1 | 0.7 | -0.2 | -0.03 | -17.1 | -0.19 | -15.8 | 0 | 0 | 20.75
293 | 2008-07-13 | 40000 | -9999 | 151.7 | 1.5 | -229.9 | 0.04 | 0.5 | 1.3 | -8.643 | -9999 | -4.97 | -423.4 | 0.7 | -0.2 | -0.03 | -17.3 | -0.19 | -15.5 | 0 | 0 | 20.83
294 | 2008-07-13 | 50000 | -9999 | 150.5 | 2 | -223.2 | 0.04 | 0.5 | 1.3 | -8.648 | -9999 | -4.97 | -452.9 | 0.7 | -0.2 | -0.04 | -18.4 | -0.18 | -16.1 | 0 | 0 | 20.76
295 | 2008-07-13 | 60000 | -9999 | 149.1 | 2.9 | -292.9 | 0.04 | 0.5 | 1.3 | -8.604 | -9999 | -4.97 | -519.8 | 0.7 | -0.2 | -0.03 | -21.3 | -0.18 | -19.2 | 0 | 0 | 20.84
296 | 2008-07-13 | 70000 | -9999 | 148.3 | 3 | -273 | 0.04 | 0.5 | 1.3 | -8.627 | -9999 | -4.97 | -552.1 | 0.7 | -0.2 | -0.04 | -22.4 | -0.18 | -19.7 | 0 | 0 | 20.77
297 | 2008-07-13 | 80000 | -9999 | 147.3 | 3.2 | -315.2 | 0.04 | 0.5 | 1.3 | -8.612 | -9999 | -4.97 | -538.6 | 0.7 | -0.2 | -0.03 | -21.9 | -0.18 | -18.8 | 0 | 0 | 20.84
298 | 2008-07-13 | 90000 | -9999 | 146.3 | 2.7 | -277.4 | 0.04 | 0.5 | 1.3 | -8.638 | -9999 | -4.97 | -457.4 | 0.8 | -0.2 | 2.09 | -18.8 | -0.18 | -16.3 | 0 | 0 | 20.83
299 | 2008-07-13 | 100000 | -9999 | 145.7 | 2.9 | -218 | 0.04 | 0.5 | 1.3 | -8.636 | -9999 | -4.97 | -403.3 | 0.6 | -0.2 | -0.03 | -16.6 | -0.18 | -14.4 | 0 | 0 | 20.75
300 | 2008-07-13 | 110000 | -9999 | 144.9 | 2.4 | -181.1 | 0.04 | 0.5 | 1.3 | -8.638 | -9999 | -4.97 | -344.7 | 0.6 | -0.2 | -0.03 | -14.2 | -0.18 | -12.3 | 0 | 0 | 20.81
301 | 2008-07-13 | 120000 | -9999 | 143.8 | 2.2 | -217.5 | 0.04 | 0.5 | 1.3 | -8.598 | -9999 | -4.97 | -318 | 0.8 | -0.2 | -0.03 | -13 | -0.18 | -11.2 | 0 | 0 | 20.8
302 | 2008-07-13 | 130000 | -9999 | 142.8 | 1.4 | -134.9 | 0.05 | 0.5 | 1.3 | -8.621 | -9999 | -4.97 | -273.2 | 0.7 | -0.2 | -0.03 | -11.2 | -0.19 | -10.1 | 0 | 0 | 20.79
303 | 2008-07-13 | 140000 | -9999 | 142.1 | 1.1 | -141.6 | 0.26 | 0.5 | 1.3 | -8.599 | -9999 | -4.97 | -246.3 | 0.6 | -0.2 | -0.04 | -10 | -0.18 | -9.2 | 0 | 0 | 20.78
304 | 2008-07-13 | 150000 | -9999 | 141.5 | 1 | -117.2 | 0.15 | 0.5 | 1.3 | -8.624 | -9999 | -4.97 | -227.5 | 0.6 | -0.2 | -0.03 | -9.3 | -0.19 | -8.5 | 0 | 0 | 20.77
305 | 2008-07-13 | 160000 | -9999 | 140.5 | 0.9 | -127.2 | 0.05 | 0.5 | 1.3 | -8.605 | -9999 | -4.97 | -209.7 | 0.9 | -0.2 | -0.03 | -8.6 | -0.18 | -7.6 | 0 | 0 | 20.76
306 | 2008-07-13 | 170000 | -9999 | 140.4 | 0.7 | -104.6 | 0.04 | 0.5 | 1.3 | -8.64 | -9999 | -4.97 | -196.2 | -4.1 | -0.2 | -0.03 | -8 | -0.19 | -7.3 | 0 | 0 | 20.75
307 | 2008-07-13 | 180000 | -9999 | 140.1 | 0.7 | -98.3 | 0.04 | 0.5 | 1.3 | -8.63 | -9999 | -4.97 | -188.1 | -6.1 | -0.2 | -0.04 | -7.7 | -0.19 | -7.2 | 0 | 0 | 20.74
308 | 2008-07-13 | 190000 | -9999 | 138.7 | 0.6 | -123.7 | 0.04 | 0.5 | 1.3 | -8.592 | -9999 | -4.97 | -190.5 | -6 | -0.2 | -0.03 | -7.7 | -0.18 | -7 | 0 | 0 | 20.74
309 | 2008-07-13 | 200000 | -9999 | 138.5 | 0.5 | -112.3 | 0.04 | 0.5 | 1.3 | -8.63 | -9999 | -4.97 | -198.5 | -6 | -0.2 | -0.03 | -8.1 | -0.18 | -7 | 0 | 0 | 20.75
310 | 2008-07-13 | 210000 | -9999 | 136.9 | 0.5 | -121.4 | 0.04 | 0.5 | 1.3 | -8.634 | -9999 | -4.97 | -206.8 | -6.1 | -0.2 | -0.03 | -8.5 | -0.19 | -8.2 | 0 | 0 | 20.68
311 | 2008-07-13 | 220000 | -9999 | 135.7 | 0.8 | -117.5 | 0.04 | 0.5 | 1.3 | -8.656 | -9999 | -4.97 | -217.8 | -6 | -0.2 | -0.04 | -8.9 | -0.19 | -8.3 | 0 | 0 | 20.69
312 | 2008-07-13 | 230000 | -9999 | 134.5 | 1.5 | -134.4 | 0.04 | 0.5 | 1.3 | -8.616 | -9999 | -4.97 | -251.5 | -6 | -0.2 | -0.03 | -10.2 | -0.18 | -9.4 | 0 | 0 | 20.78
313 | 2008-07-14 | 0 | -9999 | 133.1 | 1.9 | -144.7 | 0.04 | 0.5 | 1.2 | -8.595 | -9999 | -4.97 | -277.9 | -6 | -0.2 | -0.04 | -11.2 | -0.18 | -10.1 | 0 | 0 | 20.79
314 | 2008-07-14 | 10000 | -9999 | 132.3 | 2.4 | -144.4 | 0.04 | 0.5 | 1.2 | -8.599 | -9999 | -4.97 | -285.6 | -6 | -0.2 | -0.03 | -11.6 | -0.18 | -10.2 | 0 | 0 | 20.79
315 | 2008-07-14 | 20000 | -9999 | 131.2 | 1.9 | -139.3 | 0.04 | 0.5 | 1.2 | -8.595 | -9999 | -4.97 | -291.6 | -6 | -0.2 | -0.03 | -12 | -0.18 | -10.8 | 0 | 0 | 20.72
316 | 2008-07-14 | 30000 | -9999 | 130 | 2 | -156.6 | 0.04 | 0.5 | 1.3 | -8.587 | -9999 | -4.97 | -275.9 | -6 | -0.2 | -0.04 | -11.3 | -0.18 | -10.1 | 0 | 0 | 20.79
317 | 2008-07-14 | 40000 | -9999 | 129.4 | 2.2 | -142.2 | 0.04 | 0.5 | 1.2 | -8.603 | -9999 | -4.97 | -281.7 | -6 | -0.2 | -0.03 | -11.5 | -0.18 | -10.7 | 0 | 0 | 20.79
318 | 2008-07-14 | 50000 | -9999 | 127.7 | 1.9 | -143.8 | 0.04 | 0.5 | 1.2 | -8.594 | -9999 | -4.97 | -278.5 | -6 | -0.2 | -0.03 | -11.4 | -0.18 | -10.1 | 0 | 0 | 20.79
319 | 2008-07-14 | 60000 | -9999 | 291.9 | 22.9 | 56.7 | 4.97 | 13.2 | 13.7 | -8.58 | -9999 | -4.96 | -80.3 | -6 | 7.17 | 20.86 | 7.4 | 31.38 | 41.5 | 0.164 | 0.039 | 17.9
320 | 2008-07-14 | 70000 | -9999 | 575.5 | 18.5 | 9.8 | 7.16 | 21.7 | 22 | -8.61 | -9999 | -4.96 | -6.9 | -6 | 10.29 | 30.01 | 14.3 | 50.7 | 70.7 | 0.261 | 0.053 | 16.66
321 | 2008-07-14 | 80000 | -9999 | 598.7 | 25.2 | 47.2 | 8.06 | 28.2 | 28.8 | -8.651 | -9999 | -4.96 | -6.2 | 4.2 | 10.29 | 30.02 | 13 | 39.8 | 50 | 0.184 | 0.048 | 16.21
322 | 2008-07-14 | 90000 | -9999 | 603.3 | 23.1 | 34.8 | 8.69 | 35.2 | 47 | -8.614 | -9999 | -4.96 | -5.7 | 0.6 | 10.29 | 27.34 | 11.9 | 44.71 | 51.2 | 0.189 | 0.044 | 15.75
323 | 2008-07-14 | 100000 | -9999 | 613 | 21.7 | 30.9 | 9.06 | 39.6 | 73.8 | -8.603 | -9999 | -4.96 | -5.5 | 0.7 | 10.29 | 30.02 | 11.3 | 51.05 | 55.9 | 0.206 | 0.042 | 15.53
324 | 2008-07-14 | 110000 | -9999 | 631.2 | 2.4 | 14.7 | 17.58 | 134.3 | 200.9 | -8.605 | -9999 | -4.96 | -20.8 | 59.4 | 4.45 | 9.36 | 2.5 | 12.84 | 6.3 | 0.025 | 0.011 | 12.18
325 | 2008-07-14 | 120000 | -9999 | 665 | 0.1 | -2.2 | 21.41 | 173.5 | 262.7 | 199.32 | -9999 | -4.96 | -3.9 | 146.4 | 2.66 | 11.31 | 2.1 | 2.54 | 2 | 0.007 | 0.008 | 13.42
326 | 2008-07-14 | 130000 | -9999 | 667 | 0 | -2.3 | 21.51 | 173.8 | 261.8 | 27.082 | -9999 | -4.97 | -4 | 139.4 | 2.5 | 10.86 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.5
327 | 2008-07-14 | 140000 | -9999 | 661 | 0 | -2.2 | 20.75 | 167.2 | 251.9 | -1.477 | -9999 | -4.96 | -4.1 | 129.7 | 2.49 | 9.94 | 2 | 2.38 | 1.9 | 0.007 | 0.008 | 13.7
328 | 2008-07-14 | 150000 | -9999 | 658.8 | 0 | -2.3 | 20.78 | 166.4 | 251.9 | -8.602 | -9999 | -4.96 | -4 | 140.4 | 2.46 | 10.79 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.62
329 | 2008-07-14 | 160000 | -9999 | 659.1 | 0 | -2.3 | 20.94 | 168.4 | 254.1 | -8.649 | -9999 | -4.96 | -4 | 138 | 2.5 | 10.74 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.56
330 | 2008-07-14 | 170000 | -9999 | 658.9 | 0 | -2.2 | 20.79 | 166.5 | 251.5 | -8.582 | -9999 | -4.96 | -4 | 139 | 2.51 | 10.73 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.58
331 | 2008-07-14 | 180000 | -9999 | 657.5 | 0 | -2.3 | 20.6 | 166 | 250.9 | -8.6 | -9999 | -4.96 | -4 | 138.6 | 2.49 | 10.84 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.59
332 | 2008-07-14 | 190000 | -9999 | 657.2 | 0 | -2.2 | 20.48 | 164.1 | 248.9 | -8.609 | -9999 | -4.97 | -4 | 136 | 2.44 | 10.67 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.59
333 | 2008-07-14 | 200000 | -9999 | 556.6 | 15.4 | -35.7 | 1.79 | 8.9 | 16.6 | -8.636 | -9999 | -4.97 | -82.9 | 25.5 | 1.41 | 5.11 | -1 | 5.49 | 3.7 | 0.022 | 0.007 | 19.42
334 | 2008-07-14 | 210000 | -9999 | 430.8 | 2.3 | -84.3 | 0.04 | 0.5 | 1.3 | -8.581 | -9999 | -4.97 | -150 | 0.6 | -0.19 | 0.05 | -5.8 | -0.14 | -4.4 | 0 | 0 | 20.7
335 | 2008-07-14 | 220000 | -9999 | 405.6 | 1.8 | -97.2 | 0.18 | 0.5 | 1.3 | -8.589 | -9999 | -4.97 | -162 | 0.7 | -0.2 | 0 | -6.4 | -0.15 | -5 | 0 | 0 | 20.72
336 | 2008-07-14 | 230000 | -9999 | 396.8 | 1.6 | -88.1 | 0.04 | 0.5 | 1.3 | -8.635 | -9999 | -4.97 | -171.9 | 0.7 | -0.2 | 0 | -6.9 | -0.16 | -5.7 | 0 | 0 | 20.73
337 | 2008-07-15 | 0 | -9999 | 395.6 | 1.4 | -106.9 | 0.04 | 0.5 | 1.3 | -8.61 | -9999 | -4.97 | -178.1 | 0.7 | -0.2 | 0 | -7.2 | -0.18 | -6.6 | 0 | 0 | 20.73
338 | 2008-07-15 | 10000 | -9999 | 395.6 | 1.2 | -91.3 | 0.04 | 0.5 | 1.3 | -8.614 | -9999 | -4.97 | -175 | 0.6 | -0.2 | 0 | -7.1 | -0.18 | -6.4 | 0 | 0 | 20.66
339 | 2008-07-15 | 20000 | -9999 | 393.2 | 1.2 | -94 | 0.04 | 0.5 | 1.3 | -8.631 | -9999 | -4.97 | -177.9 | 0.6 | -0.2 | 0 | -7.2 | -0.18 | -6.5 | 0 | 0 | 20.73
340 | 2008-07-15 | 30000 | -9999 | 388.9 | 1 | -96.6 | 0.04 | 0.5 | 1.3 | -8.619 | -9999 | -4.97 | -180.1 | 0.6 | -0.2 | 0 | -7.3 | -0.18 | -6.6 | 0 | 0 | 20.74
341 | 2008-07-15 | 40000 | -9999 | 384.7 | 1 | -77.9 | 0.04 | 0.5 | 1.3 | -8.626 | -9999 | -4.97 | -182.6 | 0.7 | -0.2 | -0.03 | -7.4 | -0.18 | -6.6 | 0 | 0 | 20.74
342 | 2008-07-15 | 50000 | -9999 | 380 | 1.1 | -107.7 | 0.04 | 0.5 | 1.3 | -8.62 | -9999 | -4.97 | -184.4 | 0.6 | -0.2 | -0.03 | -7.5 | -0.18 | -6.4 | 0 | 0 | 20.74
343 | 2008-07-15 | 60000 | -9999 | 375.2 | 1.5 | -91.5 | 0.04 | 0.5 | 1.3 | -8.598 | -9999 | -4.97 | -193.1 | 0.7 | -0.2 | -0.04 | -7.8 | -0.18 | -7 | 0 | 0 | 20.75
344 | 2008-07-15 | 70000 | -9999 | 370.5 | 2.1 | -121.4 | 0.04 | 0.5 | 1.3 | 234.896 | -9999 | -4.97 | -206 | 0.5 | -0.2 | -0.03 | -8.3 | -0.18 | -7.2 | 0 | 0 | 20.75
345 | 2008-07-15 | 80000 | -9999 | 366.8 | 1.9 | -117.2 | 0.04 | 0.5 | 1.3 | 281.439 | -9999 | -4.97 | -213.6 | 0.4 | -0.2 | -0.03 | -8.6 | -0.18 | -7.8 | 0 | 0 | 20.76
346 | 2008-07-15 | 90000 | -9999 | 365.3 | 0.8 | -110.8 | 0.06 | 0.5 | 1.3 | 262.391 | -9999 | -4.97 | -208.8 | 0.5 | -0.2 | 2.07 | -8.5 | -0.18 | -7.6 | 0 | 0 | 20.76
347 | 2008-07-15 | 100000 | -9999 | 540.6 | 20.9 | 12.6 | 6.73 | 19.7 | 20.2 | 258.805 | -9999 | -4.96 | -13.3 | 0.5 | 9.54 | 28.05 | 13 | 39.89 | 54 | 0.2 | 0.049 | 16.75
348 | 2008-07-15 | 110000 | -9999 | 615.7 | 16.1 | 11.5 | 11.52 | 65.6 | 97.8 | 300.091 | -9999 | -4.96 | -13.4 | 12.8 | 9.36 | 27.09 | 9.1 | 45.62 | 44.9 | 0.166 | 0.034 | 15.16
349 | 2008-07-15 | 120000 | -9999 | 650.5 | 2 | 21.7 | 21.4 | 173.3 | 258.7 | 192.467 | -9999 | -4.96 | -11.2 | 135.3 | 3.36 | 11.93 | 1.9 | 9.49 | 3.6 | 0.014 | 0.007 | 11.61
350 | 2008-07-15 | 130000 | -9999 | 650.2 | 0 | -2.1 | 21.33 | 173 | 258.3 | -0.955 | -9999 | -4.97 | -4 | 139.3 | 2.24 | 11.35 | 1.8 | 2.13 | 1.7 | 0.006 | 0.007 | 13.53
351 | 2008-07-15 | 140000 | -9999 | 663.2 | 0 | -2.2 | 21.33 | 172.5 | 258.8 | -0.989 | -9999 | -4.97 | -4 | 135.1 | 2.31 | 11.12 | 1.8 | 2.2 | 1.8 | 0.006 | 0.007 | 13.53
352 | 2008-07-15 | 150000 | -9999 | 663.8 | 0 | -2.3 | 21.33 | 172.6 | 259 | -1.001 | -9999 | -4.96 | -4 | 134.2 | 2.37 | 11.14 | 1.9 | 2.26 | 1.8 | 0.007 | 0.007 | 13.53
353 | 2008-07-15 | 160000 | -9999 | 662.9 | 0 | -2.3 | 21.32 | 172.1 | 257.3 | -0.961 | -9999 | -4.96 | -4 | 125.8 | 2.32 | 11.06 | 1.9 | 2.21 | 1.8 | 0.006 | 0.007 | 13.52
354 | 2008-07-15 | 170000 | -9999 | 662.7 | 0 | -2.2 | 21.32 | 172.6 | 258.8 | -1.006 | -9999 | -4.96 | -4 | 128.8 | 2.36 | 11.06 | 1.9 | 2.25 | 1.8 | 0.007 | 0.007 | 13.52
355 | 2008-07-15 | 180000 | -9999 | 663.4 | 0 | -2.2 | 21.39 | 173.8 | 260.3 | -1.016 | -9999 | -4.97 | -4 | 131.4 | 2.35 | 11.16 | 1.9 | 2.24 | 1.8 | 0.007 | 0.007 | 13.53
356 | 2008-07-15 | 190000 | -9999 | 664.3 | 0 | -2.3 | 21.46 | 174.5 | 260.8 | -1.001 | -9999 | -4.96 | -4 | 128.7 | 2.17 | 10.74 | 1.8 | 2.06 | 1.7 | 0.006 | 0.006 | 13.59
357 | 2008-07-15 | 200000 | -9999 | 666 | 0 | -2.1 | 21.39 | 174.1 | 260.1 | -1.029 | -9999 | -4.96 | -4.1 | 126.4 | 1.77 | 9.97 | 1.4 | 1.68 | 1.4 | 0.005 | 0.005 | 13.67
358 | 2008-07-15 | 210000 | -9999 | 668.1 | 0 | -2.3 | 21.66 | 176.8 | 264.2 | -0.998 | -9999 | -4.96 | -4 | 136.9 | 1.91 | 10.8 | 1.6 | 1.82 | 1.5 | 0.005 | 0.006 | 13.64
359 | 2008-07-15 | 220000 | -9999 | 668.8 | 0 | -2.2 | 21.65 | 177.1 | 264.2 | -0.967 | -9999 | -4.96 | -4.1 | 135.2 | 1.81 | 10.52 | 1.5 | 1.72 | 1.4 | 0.005 | 0.005 | 13.68
360 | 2008-07-15 | 230000 | -9999 | 668.7 | 0 | -2 | 21.44 | 175.1 | 262.3 | -0.985 | -9999 | -4.96 | -4.1 | 133.9 | 1.86 | 10.51 | 1.5 | 1.78 | 1.5 | 0.005 | 0.006 | 13.71
361 | 2008-07-16 | 0 | -9999 | 638 | 0.1 | -2.3 | 16.42 | 122.3 | 194.6 | -0.975 | -9999 | -4.96 | -4.1 | 83.5 | 0.84 | 7.28 | 0.7 | 0.8 | 0.7 | 0.002 | 0.003 | 13.83
362 | 2008-07-16 | 10000 | -9999 | 632.6 | 0.1 | -2.2 | 16.69 | 125.3 | 197.2 | -0.985 | -9999 | -4.96 | -4.1 | 77.1 | 1.72 | 7.1 | 1.4 | 1.63 | 1.4 | 0.005 | 0.005 | 13.83
363 | 2008-07-16 | 20000 | -9999 | 632.5 | 0.1 | -2.2 | 16.68 | 124.7 | 196.6 | -1.021 | -9999 | -4.96 | -4.1 | 66.1 | 2.17 | 7.11 | 1.8 | 2.07 | 1.7 | 0.006 | 0.007 | 13.83
364 | 2008-07-16 | 30000 | -9999 | 632.1 | 0.1 | -2.1 | 16.68 | 124.9 | 196.9 | -1.083 | -9999 | -4.96 | -4.2 | 68 | 2.22 | 7.11 | 1.9 | 2.11 | 1.8 | 0.007 | 0.007 | 13.85
365 | 2008-07-16 | 40000 | -9999 | 632 | 0.1 | -2.3 | 16.71 | 125.6 | 197.6 | -1.077 | -9999 | -4.96 | -4.2 | 69.7 | 2.1 | 7.15 | 1.8 | 2 | 1.7 | 0.006 | 0.007 | 13.86
366 | 2008-07-16 | 50000 | -9999 | 631.9 | 0.1 | -2.4 | 16.67 | 125.3 | 197.2 | -1.072 | -9999 | -4.96 | -4.2 | 75.5 | 2.02 | 7.23 | 1.7 | 1.91 | 1.6 | 0.006 | 0.006 | 13.87
367 | 2008-07-16 | 60000 | -9999 | 637.1 | 0.1 | -7.3 | 17.59 | 134.7 | 209.2 | -1.064 | -9999 | -4.96 | -7.5 | 80.8 | 1.91 | 7.09 | 1.5 | 1.82 | 1.5 | 0.006 | 0.006 | 13.96
368 | 2008-07-16 | 70000 | -9999 | 636.7 | 2.1 | 16.3 | 17.55 | 134.6 | 209.1 | -1.053 | -9999 | -4.96 | -78.3 | 76.8 | 3.35 | 7.87 | 0.7 | 9.69 | 3.2 | 26.923 | 6.339 | 12.17
369 | 2008-07-16 | 80000 | -9999 | 636.5 | 0.1 | -2.3 | 17.67 | 136.1 | 210.6 | -1.045 | -9999 | -4.96 | -4.2 | 80.2 | 2.16 | 7.06 | 1.8 | 2.11 | 1.8 | 0.007 | 0.007 | 13.89
370 | 2008-07-16 | 90000 | -9999 | 661 | 0 | -2.2 | 20.92 | 170.5 | 253 | -1.044 | -9999 | -4.96 | -4.2 | 105.6 | 1.59 | 8.67 | 1.3 | 1.54 | 1.3 | 0.005 | 0.005 | 13.96
371 | 2008-07-16 | 100000 | -9999 | 663 | 0 | -2.4 | 20.84 | 169.5 | 253 | -1.069 | -9999 | -4.96 | -4.2 | 92.7 | 1.96 | 7.79 | 1.7 | 1.9 | 1.6 | 0.006 | 0.006 | 13.96
372 | 2008-07-16 | 110000 | -9999 | 664 | 0 | -2.7 | 20.82 | 169.5 | 253 | -1.072 | -9999 | -4.96 | -4.2 | 96.6 | 1.37 | 7.74 | 1.2 | 1.32 | 1.1 | 0.004 | 0.004 | 13.97
373 | 2008-07-16 | 120000 | -9999 | 665.1 | 0 | -2.6 | 21.06 | 171.2 | 255.5 | -1.065 | -9999 | -4.96 | -4.2 | 91 | 2.06 | 8.26 | 1.7 | 2.01 | 1.7 | 0.006 | 0.007 | 13.95
374 | 2008-07-16 | 130000 | -9999 | 667.1 | 0 | -1.9 | 21.58 | 175.7 | 263.4 | -1.048 | -9999 | -4.96 | -4.1 | 124.3 | 2.42 | 10.91 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.74
375 | 2008-07-16 | 140000 | -9999 | 664.7 | 0 | -2 | 21.57 | 175.2 | 263.4 | -1.06 | -9999 | -4.96 | -4.1 | 133.5 | 2.43 | 11.59 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.69
376 | 2008-07-16 | 150000 | -9999 | 666.6 | 0 | -2.3 | 21.82 | 178 | 265.5 | -1.103 | -9999 | -4.96 | -4 | 131.1 | 2.47 | 11.53 | 2 | 2.41 | 1.9 | 0.007 | 0.007 | 13.63
377 | 2008-07-16 | 160000 | -9999 | 666 | 0 | -2.4 | 21.83 | 177.7 | 266 | -1.069 | -9999 | -4.96 | -4 | 129.2 | 2.48 | 11.41 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.62
378 | 2008-07-16 | 170000 | -9999 | 666.2 | 0 | -2.2 | 21.82 | 177.2 | 265.1 | -1.039 | -9999 | -4.96 | -4 | 127.5 | 2.48 | 11.34 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.62
379 | 2008-07-16 | 180000 | -9999 | 665.9 | 0 | -2.4 | 21.83 | 177.8 | 265.8 | -1.074 | -9999 | -4.97 | -4 | 127.7 | 2.48 | 11.33 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.62
380 | 2008-07-16 | 190000 | -9999 | 666.4 | 0 | -2.3 | 21.8 | 178 | 266.4 | -1.072 | -9999 | -4.96 | -4 | 128.9 | 2.48 | 11.39 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.62
381 | 2008-07-16 | 200000 | -9999 | 642.9 | 0 | -2.6 | 17.68 | 135.6 | 211.3 | -1.079 | -9999 | -4.96 | -4.2 | 52.5 | 2.2 | 6.8 | 1.8 | 2.15 | 1.8 | 0.007 | 0.007 | 13.85
382 | 2008-07-16 | 210000 | -9999 | 639.7 | 0 | -2.4 | 17.84 | 137.9 | 213.5 | -1.047 | -9999 | -4.96 | -4.2 | 54.7 | 2.41 | 6.89 | 2 | 2.35 | 2 | 0.007 | 0.007 | 13.86
383 | 2008-07-16 | 220000 | -9999 | 550.2 | 33.7 | -215.4 | 1.68 | 7.5 | 14.3 | -1.056 | -9999 | -4.96 | -372.3 | 53.2 | 1.73 | 5.63 | 2.7 | 4.64 | 5.3 | 22.184 | 0.01 | 19.65
384 | 2008-07-16 | 230000 | -9999 | 426.7 | 8.1 | -591.2 | 0.04 | 0.5 | 1.3 | -1.09 | -9999 | -4.97 | -1050.6 | 0.7 | 0 | 0.04 | -0.3 | 0.02 | 3.1 | 161.466 | 11.08 | 20.87
385 | 2008-07-17 | 0 | -9999 | 403.4 | 2.8 | -556.9 | 0.04 | 0.5 | 1.3 | -1.071 | -9999 | -4.97 | -1019.9 | 0.5 | 0 | -0.01 | -0.6 | 0.02 | 3.9 | 329.236 | 12.662 | 20.88
386 | 2008-07-17 | 10000 | -9999 | 394.5 | 1.9 | -529.2 | 0.04 | 0.5 | 1.3 | -1.072 | -9999 | -4.97 | -1047.1 | 0.7 | 0 | -0.02 | -1 | 0.01 | 2 | 104.489 | 9.497 | 20.88
387 | 2008-07-17 | 20000 | -9999 | 389.5 | 2.3 | -592.8 | 0.04 | 0.5 | 1.3 | -1.073 | -9999 | -4.97 | -1057.5 | 0.7 | 0 | -0.02 | -0.9 | 0.01 | 2.4 | 161.464 | 6.332 | 20.88
388 | 2008-07-17 | 30000 | -9999 | 392.5 | -0.3 | -536 | 0.04 | 0.5 | 1.3 | -1.031 | -9999 | -4.97 | -1070.6 | 0.7 | 0 | -0.03 | -0.8 | 0.01 | 3.3 | 93.408 | 0.001 | 20.88
389 | 2008-07-17 | 40000 | -9999 | 551.3 | 20.2 | -15.8 | 6.32 | 19 | 19.4 | -1.019 | -9999 | -4.96 | -114.1 | 0.4 | 8.33 | 25.68 | 11.5 | 33.56 | 45.9 | 6.503 | 0.043 | 17.18
390 | 2008-07-17 | 50000 | -9999 | 625.3 | 17.3 | 26 | 11 | 60.2 | 89.3 | -1.023 | -9999 | -4.96 | -5.3 | 41.1 | 8.32 | 25.6 | 9.4 | 39.75 | 44.3 | 0.163 | 0.035 | 15.27
391 | 2008-07-17 | 60000 | -9999 | 638.4 | 11.2 | -23.6 | 17.75 | 136.2 | 209.7 | -1.023 | -9999 | -4.96 | -65.4 | 52.6 | 2.19 | 7.25 | 1.7 | 2.14 | 2 | 23.749 | 4.754 | 13.9
392 | 2008-07-17 | 70000 | -9999 | 639.3 | 1.7 | 22.3 | 17.58 | 134.3 | 208.4 | -0.969 | -9999 | -4.96 | -7.2 | 51.7 | 3.38 | 7.83 | 2.4 | 9.78 | 4.1 | 0.015 | 0.009 | 12.24
393 | 2008-07-17 | 80000 | -9999 | 639.1 | 0.1 | -2.1 | 17.86 | 137 | 212.2 | -1.014 | -9999 | -4.96 | -4.2 | 54.4 | 2.39 | 6.9 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.87
394 | 2008-07-17 | 90000 | -9999 | 636 | 0.1 | -2.2 | 17.89 | 137.1 | 212.3 | -1.024 | -9999 | -4.96 | -4.2 | 56.6 | 2.41 | 7.97 | 2 | 2.34 | 2 | 0.007 | 0.007 | 13.87
395 | 2008-07-17 | 100000 | -9999 | 633.2 | 0.1 | -2.2 | 17.83 | 136.9 | 212 | -1.027 | -9999 | -4.97 | -4.2 | 57.7 | 2.39 | 7.07 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.87
396 | 2008-07-17 | 110000 | -9999 | 636.6 | 0 | -2.5 | 17.8 | 136.5 | 211.7 | -1.001 | -9999 | -4.97 | -4.2 | 57.4 | 2.4 | 7.06 | 2 | 2.33 | 2 | 0.007 | 0.007 | 13.88
397 | 2008-07-17 | 120000 | -9999 | 638 | 0 | -2.3 | 17.84 | 137.6 | 213.1 | -0.981 | -9999 | -4.96 | -4.2 | 57.8 | 2.37 | 7.11 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.87
398 | 2008-07-17 | 130000 | -9999 | 638.1 | 0 | -2.3 | 17.97 | 139 | 214.7 | -0.98 | -9999 | -4.97 | -4.2 | 56.1 | 2.42 | 6.86 | 2 | 2.36 | 2 | 0.007 | 0.007 | 13.86
399 | 2008-07-17 | 140000 | -9999 | 638.8 | 0 | -2.3 | 18.02 | 138.9 | 214.6 | -0.961 | -9999 | -4.96 | -4.2 | 55.9 | 2.4 | 6.76 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.86
400 | 2008-07-17 | 150000 | -9999 | 638.6 | 0 | -2.4 | 18.03 | 139.1 | 214.8 | -0.976 | -9999 | -4.96 | -4.2 | 56 | 2.4 | 6.74 | 2 | 2.34 | 2 | 0.007 | 0.007 | 13.85
401 | 2008-07-17 | 160000 | -9999 | 638.1 | 0 | -2.2 | 17.98 | 139.3 | 215 | -0.97 | -9999 | -4.96 | -4.2 | 55.7 | 2.4 | 6.66 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.85
402 | 2008-07-17 | 170000 | -9999 | 637.8 | 0 | -2.3 | 17.92 | 138.5 | 214 | -0.986 | -9999 | -4.96 | -4.2 | 55.2 | 2.42 | 6.64 | 2 | 2.35 | 2 | 0.007 | 0.007 | 13.85
403 | 2008-07-17 | 180000 | -9999 | 637.8 | 0 | -2 | 17.99 | 138.8 | 214.3 | -0.976 | -9999 | -4.96 | -4.1 | 55.5 | 2.4 | 6.65 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.84
404 | 2008-07-17 | 190000 | -9999 | 637.2 | 0 | -2.6 | 17.99 | 139.3 | 214.8 | -0.933 | -9999 | -4.96 | -4.1 | 55.3 | 2.41 | 6.7 | 2 | 2.35 | 2 | 0.007 | 0.007 | 13.83
405 | 2008-07-17 | 200000 | -9999 | 635.9 | 0 | -2.2 | 17.76 | 137.3 | 212.2 | -0.971 | -9999 | -4.96 | -4.1 | 52.3 | 2.41 | 6.68 | 2 | 2.35 | 2 | 0.007 | 0.007 | 13.83
406 | 2008-07-17 | 210000 | -9999 | 635.8 | 0.2 | -2.3 | 17.48 | 132.9 | 207 | -0.968 | -9999 | -4.96 | -4.1 | 50.4 | 2.61 | 7.34 | 2.2 | 4.07 | 3.4 | 0.013 | 0.008 | 13.83
407 | 2008-07-17 | 220000 | -9999 | 535.2 | 28.4 | -114.3 | 1.3 | 4.8 | 10 | -0.991 | -9999 | -4.97 | -206.4 | 3.3 | 2.01 | 5.7 | 4.3 | 7.47 | 10.7 | 0.042 | 0.016 | 19.81
408 | 2008-07-17 | 230000 | -9999 | 388.9 | 3.8 | -231.9 | 0.04 | 0.5 | 1.3 | -1.003 | -9999 | -4.97 | -468.8 | 0.6 | 0 | 0.07 | -0.1 | 0.01 | 0 | 0.01 | 0 | 20.83
409 | 2008-07-18 | 0 | -9999 | 335.4 | 2.9 | -325.9 | 0.04 | 0.5 | 1.3 | -0.994 | -9999 | -4.97 | -501.3 | 0.6 | 0 | 0 | -0.4 | 0.01 | 0.4 | 0.01 | 0 | 20.84
410 | 2008-07-18 | 10000 | -9999 | 298 | 2.6 | -237.5 | 0.04 | 0.5 | 1.3 | -1.011 | -9999 | -4.97 | -474.4 | 0.6 | 0 | 0.01 | -0.3 | 0.01 | 0.2 | 0.009 | 0 | 20.76
411 | 2008-07-18 | 20000 | -9999 | 270.8 | 1.7 | -241.4 | 0.04 | 0.5 | 1.3 | -0.998 | -9999 | -4.96 | -469.8 | 0.6 | 0 | -0.01 | -0.3 | 0.01 | 0.3 | 0.009 | 0 | 20.76
412 | 2008-07-18 | 30000 | -9999 | 256.5 | 0.9 | -255.5 | 0.04 | 0.5 | 1.3 | -0.998 | -9999 | -4.97 | -498.6 | 0.4 | 0 | -0.03 | -0.3 | 0.01 | 0.7 | 0.01 | 0 | 20.76
413 | 2008-07-18 | 40000 | -9999 | 251.8 | 0.2 | -259 | 0.04 | 0.5 | 1.3 | -0.97 | -9999 | -4.97 | -456.5 | 0.6 | 0 | -0.03 | -0.3 | 0.02 | 0.6 | 0.01 | 0 | 20.83
414 | 2008-07-18 | 50000 | -9999 | 248.2 | 0.6 | -265.8 | 0.04 | 0.5 | 1.3 | -0.963 | -9999 | -4.97 | -508.5 | 0.5 | 0 | -0.03 | -0.3 | 0.01 | 0.2 | 0.01 | 0 | 20.84
415 | 2008-07-18 | 60000 | -9999 | 243.8 | 2.2 | -357.2 | 0.04 | 0.5 | 1.3 | -1.032 | -9999 | -4.97 | -600.3 | 0.7 | 0 | -0.03 | -0.4 | 0.01 | 0.2 | 0.013 | 0 | 20.84
416 | 2008-07-18 | 70000 | -9999 | 239.6 | 4.4 | -476.8 | 0.04 | 0.5 | 1.3 | -1.042 | -9999 | -4.97 | -763.1 | 0.7 | 0 | -0.03 | -0.7 | 0.02 | 2.5 | 0.019 | 0 | 20.86
417 | 2008-07-18 | 80000 | -9999 | 235.6 | 6.1 | -539.2 | 0.04 | 0.5 | 1.3 | -1.076 | -9999 | -4.97 | -954.3 | 0.7 | 0 | -0.03 | -0.6 | 0.01 | 0.2 | 99.729 | 1.583 | 20.87
418 | 2008-07-18 | 90000 | -9999 | 232.6 | 6.2 | -558.7 | 0.04 | 0.5 | 1.3 | -1.057 | -9999 | -4.97 | -990.6 | 0.8 | 0 | 2.13 | -0.6 | 0.02 | 2 | 170.959 | 9.497 | 20.87
419 | 2008-07-18 | 100000 | -9999 | 229.6 | 7.6 | -644.3 | 0.04 | 0.5 | 1.3 | -1.077 | -9999 | -4.97 | -1154.5 | 0.6 | 0 | -0.03 | -0.8 | 0.01 | 1.5 | 102.908 | 3.166 | 20.87
420 | 2008-07-18 | 110000 | -9999 | 226.7 | 9.2 | -505.6 | 0.04 | 0.5 | 1.3 | -1.088 | -9999 | -4.97 | -1065.8 | 0.6 | 0 | -0.04 | -0.7 | 0.02 | 3 | 169.383 | 6.331 | 20.88
421 | 2008-07-18 | 120000 | -9999 | 224.1 | 8.3 | -536.5 | 0.04 | 0.5 | 1.3 | -1.075 | -9999 | -4.97 | -1050.6 | 0.7 | 0 | -0.03 | -0.9 | 0.01 | 2.2 | 226.358 | 0.001 | 20.88
422 | 2008-07-18 | 130000 | -9999 | 221 | 8.8 | -609.6 | 0.1 | 0.5 | 1.3 | -1.092 | -9999 | -4.97 | -1126.4 | 0.6 | 0 | -0.03 | -0.8 | 0.02 | 2.9 | 110.821 | 1.583 | 20.88
423 | 2008-07-18 | 140000 | -9999 | 218.7 | 8.6 | -494.1 | 0.14 | 0.5 | 1.3 | -1.078 | -9999 | -4.97 | -1045.3 | 0.6 | 0 | -0.03 | -0.7 | 0.02 | 3.8 | 147.223 | 1.584 | 20.87
424 | 2008-07-18 | 150000 | -9999 | 215.7 | 9.1 | -556.1 | 0.27 | 0.5 | 1.3 | -1.079 | -9999 | -4.97 | -1041.3 | 0.7 | 0 | -0.03 | -0.7 | 0.01 | 2 | 82.325 | 1.583 | 20.79
425 | 2008-07-18 | 160000 | -9999 | 211.9 | 7.3 | -474.3 | 0.2 | 0.5 | 1.3 | -1.096 | -9999 | -4.97 | -817.5 | 0.7 | 0 | -0.03 | -0.7 | 0.01 | 1.2 | 14.262 | 0 | 20.86
426 | 2008-07-18 | 170000 | -9999 | 208.5 | 6.5 | -387.8 | 0.19 | 0.5 | 1.3 | -1.072 | -9999 | -4.97 | -704.8 | 0.7 | 0 | -0.03 | -0.5 | 0.01 | 0 | 0.014 | 0 | 20.77
427 | 2008-07-18 | 180000 | -9999 | 205.2 | 4.8 | -272.3 | 0.04 | 0.5 | 1.2 | -1.085 | -9999 | -4.97 | -486.6 | 0.6 | 0 | -0.04 | -0.4 | 0.01 | 0.8 | 0.01 | 0 | 20.76
428 | 2008-07-18 | 190000 | -9999 | 202.4 | 5 | -283.5 | 0.04 | 0.5 | 1.3 | -1.086 | -9999 | -4.97 | -492.8 | 0.6 | 0 | -0.03 | -0.4 | 0.01 | 0.3 | 0.01 | 0 | 20.83
429 | 2008-07-18 | 200000 | -9999 | 199.6 | 4.6 | -248 | 0.04 | 0.5 | 1.3 | -1.073 | -9999 | -4.97 | -435.3 | 0.6 | 0 | -0.04 | -0.3 | 0.01 | 1.1 | 0.011 | 0 | 20.83
430 | 2008-07-18 | 210000 | -9999 | 196.5 | 4.3 | -216.6 | 0.04 | 0.5 | 1.2 | -1.08 | -9999 | -4.97 | -472.2 | 0.6 | 0 | -0.03 | -0.3 | 0.02 | 1.8 | 0.014 | 0 | 20.83
431 | 2008-07-18 | 220000 | -9999 | 193.6 | 4.6 | -266.8 | 0.04 | 0.5 | 1.3 | -1.085 | -9999 | -4.96 | -494.2 | 0.6 | 0 | -0.03 | -0.4 | 0.01 | 1.1 | 0.011 | 0 | 20.84
432 | 2008-07-18 | 230000 | -9999 | 190.6 | 5 | -305.1 | 0.04 | 0.5 | 1.3 | -1.076 | -9999 | -4.97 | -504.8 | 0.6 | 0 | -0.03 | -0.5 | 0.01 | 1.5 | 0.013 | 0 | 20.84
433 | 2008-07-19 | 0 | -9999 | 177.9 | 4.9 | -285.4 | 0.04 | 0.5 | 1.3 | -1.073 | -9999 | -4.97 | -497.2 | 0.7 | -0.01 | -0.04 | -0.6 | 0.01 | 0.6 | 0.01 | 0 | 20.83
434 | 2008-07-19 | 10000 | -9999 | 168 | 4.3 | -273.4 | 0.04 | 0.5 | 1.3 | -1.076 | -9999 | -4.97 | -443.4 | 0.6 | 0 | -0.03 | -0.4 | 0.01 | 0.3 | 0.009 | 0 | 20.75
435 | 2008-07-19 | 20000 | -9999 | 161.7 | 4.5 | -242 | 0.04 | 0.5 | 1.3 | -1.06 | -9999 | -4.97 | -447.5 | 0.6 | -0.01 | -0.03 | -0.6 | 0 | 0 | 0.008 | 0 | 20.83
436 | 2008-07-19 | 30000 | -9999 | 157.8 | 3.6 | -217 | 0.04 | 0.5 | 1.3 | -1.067 | -9999 | -4.96 | -437.7 | 0.7 | -0.01 | -0.04 | -0.6 | 0 | 0.5 | 0.009 | 0 | 20.83
437 | 2008-07-19 | 40000 | -9999 | 155.6 | 3.4 | -176.3 | 0.04 | 0.5 | 1.3 | -1.071 | -9999 | -4.97 | -393 | 0.7 | -0.01 | -0.02 | -0.5 | 0.01 | 0.7 | 0.009 | 0 | 20.82
438 | 2008-07-19 | 50000 | -9999 | 154 | 3.1 | -228.7 | 0.04 | 0.5 | 1.3 | -1.062 | -9999 | -4.97 | -363 | 0.7 | -0.01 | -0.03 | -0.5 | 0.01 | 0.9 | 0.008 | 0 | 20.82
439 | 2008-07-19 | 60000 | -9999 | 152.7 | 2.6 | -215.9 | 0.04 | 0.5 | 1.3 | -1.054 | -9999 | -4.97 | -374.1 | 0.6 | -0.01 | -0.03 | -0.5 | 0.01 | 0.6 | 0.009 | 0 | 20.82
440 | 2008-07-19 | 70000 | -9999 | 150.7 | 1.8 | -238.4 | 0.04 | 0.5 | 1.3 | -1.061 | -9999 | -4.97 | -387.2 | 0.7 | 0 | -0.03 | -0.4 | 0 | 0.2 | 0.007 | 0 | 20.82
441 | 2008-07-19 | 80000 | -9999 | 149.9 | 0.7 | -213.3 | 0.04 | 0.5 | 1.3 | -1.05 | -9999 | -4.97 | -367.8 | 0.8 | -0.01 | -0.03 | -0.4 | 0.01 | 0.3 | 0.007 | 0 | 20.82
442 | 2008-07-19 | 90000 | -9999 | 149.1 | 1.2 | -215.9 | 0.04 | 0.5 | 1.3 | -1.026 | -9999 | -4.97 | -358.6 | 0.4 | 0 | 2.15 | -0.3 | 0.01 | 0.3 | 0.007 | 0 | 20.81
443 | 2008-07-19 | 100000 | -9999 | 147.4 | 1 | -160.7 | 0.03 | 0.5 | 1.3 | -0.992 | -9999 | -4.97 | -312 | 0.5 | 0 | -0.03 | -0.2 | 0 | 0 | 0.006 | 0 | 20.8
444 | 2008-07-19 | 110000 | -9999 | 147.1 | 1 | -143.9 | 0.05 | 0.5 | 1.3 | -1.032 | -9999 | -4.97 | -267 | 0.4 | 0 | -0.03 | -0.2 | 0.01 | 0.5 | 0.007 | 0 | 20.79
445 | 2008-07-19 | 120000 | -9999 | 145.7 | 0.8 | -142.3 | 0.03 | 0.5 | 1.3 | -1.016 | -9999 | -4.97 | -245.8 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.005 | 0 | 20.78
446 | 2008-07-19 | 130000 | -9999 | 145.4 | 0.8 | -106.8 | 0.04 | 0.5 | 1.3 | -1.014 | -9999 | -4.97 | -212.8 | 0.5 | 0 | -0.03 | -0.2 | 0.01 | 0.1 | 0.004 | 0 | 20.76
447 | 2008-07-19 | 140000 | -9999 | 143.8 | 0.8 | -96.4 | 0.19 | 0.5 | 1.3 | -1.014 | -9999 | -4.97 | -190.6 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.4 | 0.005 | 0 | 20.74
448 | 2008-07-19 | 150000 | -9999 | 143.9 | 0.9 | -99.1 | 0.08 | 0.5 | 1.3 | -1.022 | -9999 | -4.97 | -179.4 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.004 | 0 | 20.73
449 | 2008-07-19 | 160000 | -9999 | 142.2 | 0.9 | -98 | 0.04 | 0.5 | 1.3 | -0.999 | -9999 | -4.97 | -167.4 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.1 | 0.004 | 0 | 20.72
450 | 2008-07-19 | 170000 | -9999 | 142.2 | 0.9 | -82.6 | 0.04 | 0.5 | 1.3 | -1.007 | -9999 | -4.97 | -158.6 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.71
451 | 2008-07-19 | 180000 | -9999 | 140.9 | 0.9 | -100.8 | 0.04 | 0.5 | 1.3 | -0.97 | -9999 | -4.97 | -155 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0 | 0.003 | 0 | 20.71
452 | 2008-07-19 | 190000 | -9999 | 140.5 | 0.9 | -81.4 | 0.04 | 0.5 | 1.3 | -1.013 | -9999 | -4.97 | -155.7 | 0.4 | 0 | -0.03 | -0.1 | 0 | -0.1 | 0.003 | 0 | 20.71
453 | 2008-07-19 | 200000 | -9999 | 138.6 | 0.7 | -92.8 | 0.04 | 0.5 | 1.3 | -0.996 | -9999 | -4.97 | -163.8 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.1 | 0.004 | 0 | 20.64
454 | 2008-07-19 | 210000 | -9999 | 137.6 | 0.7 | -90.4 | 0.04 | 0.5 | 1.3 | -1.02 | -9999 | -4.97 | -179.6 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.73
455 | 2008-07-19 | 220000 | -9999 | 136.4 | 0.4 | -106.7 | 0.04 | 0.5 | 1.3 | -0.985 | -9999 | -4.97 | -190 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0 | 0.004 | 0 | 20.74
456 | 2008-07-19 | 230000 | -9999 | 135 | 0.3 | -124.3 | 0.04 | 0.5 | 1.3 | -0.978 | -9999 | -4.97 | -195.8 | 0.4 | 0 | -0.03 | -0.1 | 0 | 0 | 0.004 | 0 | 20.75
457 | 2008-07-20 | 0 | -9999 | 133.7 | 0 | -100.6 | 0.04 | 0.5 | 1.3 | -1.012 | -9999 | -4.97 | -193.6 | 0.4 | 0 | -0.04 | -0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.75
458 | 2008-07-20 | 10000 | -9999 | 132.8 | 0.2 | -104.2 | 0.04 | 0.5 | 1.3 | -0.968 | -9999 | -4.97 | -199.2 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.4 | 0.005 | 0 | 20.75
459 | 2008-07-20 | 20000 | -9999 | 131.3 | 0 | -98.5 | 0.04 | 0.5 | 1.3 | -1.02 | -9999 | -4.97 | -210.7 | 0.4 | 0 | -0.03 | -0.1 | 0 | -0.1 | 0.004 | 0 | 20.68
460 | 2008-07-20 | 30000 | -9999 | 130.1 | 0.2 | -111.3 | 0.04 | 0.5 | 1.3 | -0.963 | -9999 | -4.97 | -215.6 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.6 | 0.006 | 0 | 20.76
461 | 2008-07-20 | 40000 | -9999 | 129.2 | 0.4 | -121.5 | 0.04 | 0.5 | 1.3 | -1.014 | -9999 | -4.97 | -220.3 | 0.4 | 0 | -0.03 | -0.2 | 0.01 | 0.3 | 0.005 | 0 | 20.69
462 | 2008-07-20 | 50000 | -9999 | 127.8 | 0.1 | -127.7 | 0.04 | 0.5 | 1.3 | -0.989 | -9999 | -4.97 | -232.7 | 0.4 | -0.01 | -0.03 | -0.2 | 0 | 0 | 0.004 | 0 | 20.77
463 | 2008-07-20 | 60000 | -9999 | 126.9 | 0.3 | -127.6 | 0.04 | 0.5 | 1.3 | -0.983 | -9999 | -4.97 | -233.1 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.4 | 0.005 | 0 | 20.77
464 | 2008-07-20 | 70000 | -9999 | 126.4 | 0.2 | -143.7 | 0.04 | 0.5 | 1.3 | -0.969 | -9999 | -4.97 | -238.1 | 0.3 | 0 | -0.03 | -0.2 | 0 | -0.1 | 0.004 | 0 | 20.78
465 | 2008-07-20 | 80000 | -9999 | 126.3 | 0.4 | -119.5 | 0.04 | 0.5 | 1.3 | -1.008 | -9999 | -4.97 | -242.4 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.1 | 0.005 | 0 | 20.78
466 | 2008-07-20 | 90000 | -9999 | 126.4 | 0.4 | -126 | 0.04 | 0.5 | 1.3 | -0.994 | -9999 | -4.96 | -236.3 | 0.5 | -0.01 | 2.1 | -0.3 | 0.01 | 0.2 | 0.005 | 0 | 20.77
467 | 2008-07-20 | 100000 | -9999 | 126.4 | 1.2 | -121.4 | 0.04 | 0.5 | 1.3 | -1.081 | -9999 | -4.97 | -232.2 | 0.5 | -0.01 | -0.03 | -0.2 | 0.02 | 0.6 | 0.005 | 0 | 20.7
468 | 2008-07-20 | 110000 | -9999 | 126.4 | 1.5 | -119.8 | 0.04 | 0.5 | 1.3 | -1.066 | -9999 | -4.97 | -228.1 | 0.5 | 0 | -0.04 | -0.2 | 0.01 | 0.3 | 0.005 | 0 | 20.77
469 | 2008-07-20 | 120000 | -9999 | 125.1 | 1.8 | -111.4 | 0.04 | 0.5 | 1.3 | -1.084 | -9999 | -4.97 | -214.8 | 0.5 | 0 | -0.03 | -0.2 | 0.01 | 0.3 | 0.005 | 0 | 20.76
470 | 2008-07-20 | 130000 | -9999 | 124.4 | 1.9 | -118.4 | 0.11 | 0.5 | 1.3 | -1.085 | -9999 | -4.97 | -195 | 0.5 | -0.01 | -0.04 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.75
471 | 2008-07-20 | 140000 | -9999 | 124.4 | 1.8 | -106.7 | 0.25 | 0.5 | 1.3 | -1.087 | -9999 | -4.97 | -182.6 | 0.5 | 0 | -0.03 | -0.2 | 0.01 | 0.2 | 0.004 | 0 | 20.74
472 | 2008-07-20 | 150000 | -9999 | 124.4 | 1.7 | -123 | 0.08 | 0.5 | 1.3 | -1.055 | -9999 | -4.97 | -172.3 | 0.5 | 0 | -0.03 | -0.2 | 0.01 | 0.2 | 0.004 | 0 | 20.73
473 | 2008-07-20 | 160000 | -9999 | 124.5 | 1.9 | -82.9 | 0.04 | 0.5 | 1.3 | -1.067 | -9999 | -4.97 | -163 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.72
474 | 2008-07-20 | 170000 | -9999 | 124 | 1.7 | -77.3 | 0.04 | 0.5 | 1.3 | -1.089 | -9999 | -4.97 | -160.2 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.64
475 | 2008-07-20 | 180000 | -9999 | 122.5 | 1.7 | -88.1 | 0.04 | 0.5 | 1.3 | -1.121 | -9999 | -4.97 | -154.8 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.71
476 | 2008-07-20 | 190000 | -9999 | 122.6 | 1.7 | -75.1 | 0.04 | 0.5 | 1.3 | -1.086 | -9999 | -4.97 | -162.4 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.72
477 | 2008-07-20 | 200000 | -9999 | 122.4 | 1.7 | -100.7 | 0.04 | 0.5 | 1.3 | -1.062 | -9999 | -4.97 | -175.3 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0 | 0.003 | 0 | 20.73
478 | 2008-07-20 | 210000 | -9999 | 121.5 | 1.5 | -94.3 | 0.04 | 0.5 | 1.3 | -1.079 | -9999 | -4.97 | -197.4 | 0.5 | 0 | -0.04 | -0.1 | 0.01 | 0.1 | 0.005 | 0 | 20.75
479 | 2008-07-20 | 220000 | -9999 | 120 | 1.4 | -140.9 | 0.04 | 0.5 | 1.3 | -1.079 | -9999 | -4.97 | -217.5 | 0.6 | 0 | -0.04 | -0.1 | 0 | 0 | 0.004 | 0 | 20.76
480 | 2008-07-20 | 230000 | -9999 | 119.1 | 1.4 | -105 | 0.04 | 0.5 | 1.3 | -1.032 | -9999 | -4.97 | -248.7 | 0.5 | 0 | -0.03 | -0.1 | 0 | 0 | 0.005 | 0 | 20.78
481 | 2008-07-21 | 0 | -9999 | 307.3 | 25.1 | 70.7 | 5.22 | 13.6 | 14.1 | -1.055 | -9999 | -4.96 | -62.6 | 0.5 | 7.78 | 22.44 | 11.4 | 34.4 | 49.3 | 0.183 | 0.042 | 17.72
482 | 2008-07-21 | 10000 | -9999 | 594.1 | 23.5 | 35.5 | 7.51 | 23.3 | 23.6 | -1.048 | -9999 | -4.96 | -6.7 | 0.4 | 10.29 | 30.02 | 13.9 | 43.83 | 59.5 | 0.219 | 0.051 | 16.52
483 | 2008-07-21 | 20000 | -9999 | 621.6 | 24.3 | 44.9 | 8.31 | 31 | 31.8 | -1.066 | -9999 | -4.96 | -6 | 17.9 | 10.29 | 29.96 | 12.5 | 41.09 | 49.5 | 0.183 | 0.046 | 16.02
484 | 2008-07-21 | 30000 | -9999 | 597.5 | 23 | 30.4 | 8.05 | 29.6 | 56.7 | -1.045 | -9999 | -4.96 | -6.3 | 21 | 10.29 | 30.02 | 13.1 | 43.93 | 55.4 | 0.204 | 0.048 | 16.17
485 | 2008-07-21 | 40000 | -9999 | 586.4 | 22.5 | 47.1 | 9.02 | 38.6 | 72.4 | -1.089 | -9999 | -4.96 | -5.7 | 36.9 | 10.29 | 30.02 | 11.8 | 45.18 | 50.7 | 0.187 | 0.043 | 15.71
486 | 2008-07-21 | 50000 | -9999 | 621.7 | 1.1 | -8.5 | 17.57 | 134 | 198.8 | -1.104 | -9999 | -4.96 | -25.9 | 85.1 | 2.19 | 8.74 | 1.6 | 3.24 | 2.6 | 0.01 | 0.006 | 13.53
487 | 2008-07-21 | 60000 | -9999 | 628.6 | 1.7 | 23.9 | 17.6 | 135 | 208.1 | -1.044 | -9999 | -4.96 | -5.3 | 98.2 | 1.55 | 7.75 | 0.8 | 7.83 | 2.6 | 0.009 | 0.003 | 12.5
488 | 2008-07-21 | 70000 | -9999 | 635.1 | 0.2 | -2.5 | 17.57 | 134.6 | 208.9 | -1.049 | -9999 | -4.96 | -4.1 | 50.9 | 2.14 | 6.74 | 1.8 | 2.07 | 1.7 | 0.006 | 0.007 | 13.8
489 | 2008-07-21 | 80000 | -9999 | 635.2 | 0.2 | -1.7 | 17.59 | 134.6 | 209.1 | -1.07 | -9999 | -4.96 | -4.1 | 52.4 | 2.42 | 6.86 | 2 | 2.35 | 2 | 0.007 | 0.007 | 13.81
490 | 2008-07-21 | 90000 | -9999 | 636.5 | 0.2 | -2.4 | 17.65 | 136.3 | 211.2 | -1.048 | -9999 | -4.96 | -4.1 | 53.6 | 2.41 | 7.78 | 2 | 2.35 | 2 | 0.007 | 0.007 | 13.8
491 | 2008-07-21 | 100000 | -9999 | 637.5 | 0.2 | -2.4 | 17.73 | 137.2 | 212.3 | -1.021 | -9999 | -4.97 | -4.1 | 53.4 | 2.42 | 6.78 | 2 | 2.36 | 2 | 0.007 | 0.007 | 13.8
492 | 2008-07-21 | 110000 | -9999 | 636.7 | 0.2 | -2.2 | 18.04 | 140.4 | 215.7 | -1.043 | -9999 | -4.96 | -4.1 | 60.2 | 2.51 | 7.09 | 2.1 | 2.44 | 2 | 0.007 | 0.007 | 13.79
493 | 2008-07-21 | 120000 | -9999 | 661.4 | 0.1 | -2.4 | 21.55 | 175.6 | 263.1 | -1.03 | -9999 | -4.96 | -4 | 132 | 2.45 | 11.44 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.59
494 | 2008-07-21 | 130000 | -9999 | 662.2 | 0.1 | -2.4 | 21.45 | 174.2 | 261.5 | -0.988 | -9999 | -4.97 | -4 | 128.7 | 2.49 | 11.35 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.59
495 | 2008-07-21 | 140000 | -9999 | 674.4 | 0.1 | -2.3 | 21.31 | 172.8 | 265.5 | 2.067 | -9999 | -4.96 | -3.9 | 127.8 | 2.66 | 11.69 | 2.1 | 2.59 | 2 | 0.007 | 0.007 | 13.3
496 | 2008-07-21 | 150000 | -9999 | 757.1 | -0.1 | -2 | 21.11 | 171.2 | 296.9 | 14.297 | -9999 | -4.96 | -3.3 | 166.9 | 3.14 | 14.82 | 2.1 | 3.07 | 2 | 0.007 | 0.008 | 11.99
497 | 2008-07-21 | 160000 | -9999 | 760.2 | -0.1 | -1.7 | 21.3 | 172.8 | 296.9 | 14.722 | -9999 | -4.96 | -3.3 | 169 | 3.04 | 14.68 | 2 | 2.96 | 1.9 | 0.007 | 0.007 | 11.91
498 | 2008-07-21 | 170000 | -9999 | 760.2 | -0.1 | -2.1 | 21.55 | 175.3 | 298.3 | 14.999 | -9999 | -4.97 | -3.2 | 169.3 | 3.08 | 14.69 | 2 | 3 | 2 | 0.007 | 0.007 | 11.87
499 | 2008-07-21 | 180000 | -9999 | 676.7 | 0 | -2.2 | 18.49 | 143.7 | 228.6 | 1.097 | -9999 | -4.97 | -3.9 | 88.9 | 2.4 | 9.37 | 1.9 | 2.34 | 1.9 | 0.007 | 0.007 | 13.42
500 | 2008-07-21 | 190000 | -9999 | 639.2 | 0.1 | -2.3 | 18 | 140 | 215.4 | -1.001 | -9999 | -4.96 | -4.1 | 53.6 | 2.35 | 6.62 | 1.9 | 2.29 | 1.9 | 0.007 | 0.007 | 13.77
501 | 2008-07-21 | 200000 | -9999 | 638.8 | 0.1 | -2.2 | 17.68 | 136.7 | 211.8 | -0.982 | -9999 | -4.96 | -4.1 | 51.7 | 2.45 | 6.67 | 2 | 2.39 | 2 | 0.007 | 0.007 | 13.79
502 | 2008-07-21 | 210000 | -9999 | 637.6 | 0.1 | -1.9 | 17.61 | 135.2 | 210.1 | -0.993 | -9999 | -4.96 | -4.1 | 53.3 | 2.42 | 6.81 | 2 | 2.35 | 2 | 0.007 | 0.007 | 13.8
503 | 2008-07-21 | 220000 | -9999 | 561.6 | 23 | -50.3 | 2.37 | 10.2 | 20.1 | -0.974 | -9999 | -4.96 | -122.8 | 18 | 3.04 | 8.23 | 5.7 | 9.81 | 13 | 0.05 | 0.021 | 19.18
504 | 2008-07-21 | 230000 | -9999 | 432 | 6.9 | -145 | 0.04 | 0.5 | 1.3 | -1.003 | -9999 | -4.97 | -304.5 | 1 | 0 | 0.12 | 0.2 | 0.01 | 0.4 | 0.007 | 0.001 | 20.8
505 | 2008-07-22 | 0 | -9999 | 406.3 | 5.5 | -166.3 | 0.04 | 0.5 | 1.3 | -1.019 | -9999 | -4.97 | -339.6 | 0.7 | 0 | 0 | -0.1 | 0 | -0.4 | 0.006 | 0 | 20.81
506 | 2008-07-22 | 10000 | -9999 | 397.2 | 5.7 | -181.7 | 0.04 | 0.5 | 1.3 | -1.004 | -9999 | -4.97 | -394.7 | 0.5 | 0 | 0 | -0.1 | 0.01 | 0.2 | 0.007 | 0 | 20.82
507 | 2008-07-22 | 20000 | -9999 | 389 | 5.9 | -238 | 0.04 | 0.5 | 1.3 | -0.991 | -9999 | -4.97 | -422.5 | 0.5 | 0 | 0 | -0.2 | 0.01 | 0 | 0.008 | 0 | 20.82
508 | 2008-07-22 | 30000 | -9999 | 388 | 4.1 | -225.9 | 0.04 | 0.5 | 1.3 | -1.005 | -9999 | -4.97 | -473.1 | 0.6 | 0 | -0.03 | -0.2 | 0 | -0.2 | 0.008 | 0 | 20.83
509 | 2008-07-22 | 40000 | -9999 | 560.4 | 21.7 | 2.6 | 6.37 | 18.7 | 19.1 | -0.995 | -9999 | -4.96 | -53.5 | 5.4 | 9.04 | 26.29 | 12.7 | 35.04 | 49 | 0.181 | 0.047 | 17.11
510 | 2008-07-22 | 50000 | -9999 | 625.6 | 12.1 | 7.4 | 12.36 | 75.3 | 117.3 | -0.997 | -9999 | -4.96 | -15.4 | 55.8 | 6.62 | 22.25 | 7 | 32.58 | 34.1 | 0.126 | 0.026 | 15
511 | 2008-07-22 | 60000 | -9999 | 636.5 | 2.3 | 24.6 | 17.76 | 136.6 | 210.6 | -0.982 | -9999 | -4.96 | -5.5 | 72.5 | 2.8 | 7.39 | 1.6 | 9.13 | 3.4 | 0.013 | 0.006 | 12
512 | 2008-07-22 | 70000 | -9999 | 639.5 | 0.3 | -2.3 | 17.73 | 136.8 | 212.2 | -0.986 | -9999 | -4.96 | -4.2 | 54.7 | 2.44 | 7.09 | 2 | 2.38 | 2 | 0.007 | 0.008 | 13.84
513 | 2008-07-22 | 80000 | -9999 | 639.7 | 0.3 | -2.2 | 17.76 | 137 | 212.3 | -0.989 | -9999 | -4.96 | -4.2 | 57.8 | 2.42 | 7.06 | 2 | 2.35 | 2 | 0.007 | 0.007 | 13.84
514 | 2008-07-22 | 90000 | -9999 | 639 | 0.3 | -2.5 | 17.64 | 135.7 | 210.7 | -0.982 | -9999 | -4.96 | -4.2 | 57.8 | 2.38 | 7.97 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.85
515 | 2008-07-22 | 100000 | -9999 | 640.5 | 0.3 | -2.4 | 18.4 | 142.9 | 219.4 | -0.966 | -9999 | -4.97 | -4.1 | 73.6 | 2.48 | 7.8 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.82
516 | 2008-07-22 | 110000 | -9999 | 668.4 | 0.3 | -2.3 | 22.03 | 179.5 | 268.5 | -0.955 | -9999 | -4.96 | -4 | 140.7 | 2.45 | 12.08 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.65
517 | 2008-07-22 | 120000 | -9999 | 668.7 | 0.2 | -2.4 | 21.87 | 179 | 268.1 | -0.97 | -9999 | -4.96 | -4 | 140.7 | 2.47 | 12.16 | 2 | 2.4 | 2 | 0.007 | 0.007 | 13.67
518 | 2008-07-22 | 130000 | -9999 | 680.2 | 0.2 | -1.9 | 21.83 | 178.5 | 271.1 | 1.457 | -9999 | -4.97 | -3.9 | 144.9 | 2.59 | 12.66 | 2 | 2.52 | 2 | 0.007 | 0.007 | 13.43
519 | 2008-07-22 | 140000 | -9999 | 710.1 | 0.1 | -2.1 | 21.83 | 177.8 | 275.2 | 6.255 | -9999 | -4.96 | -3.7 | 158.2 | 2.76 | 13.8 | 2 | 2.7 | 2 | 0.007 | 0.007 | 12.92
520 | 2008-07-22 | 150000 | -9999 | 721.9 | 0.1 | -1.8 | 21.76 | 177.1 | 279.3 | 7.434 | -9999 | -4.96 | -3.6 | 163.1 | 2.75 | 14.11 | 2 | 2.68 | 1.9 | 0.007 | 0.007 | 12.79
521 | 2008-07-22 | 160000 | -9999 | 716.9 | 0.1 | -2.1 | 21.73 | 177 | 276.5 | 6.753 | -9999 | -4.96 | -3.6 | 160.3 | 2.74 | 13.92 | 2 | 2.67 | 2 | 0.007 | 0.007 | 12.86
522 | 2008-07-22 | 170000 | -9999 | 718.6 | 0.1 | -2 | 21.68 | 177 | 278 | 7.391 | -9999 | -4.96 | -3.6 | 160.1 | 2.77 | 13.96 | 2 | 2.69 | 2 | 0.007 | 0.007 | 12.81
523 | 2008-07-22 | 180000 | -9999 | 721.2 | 0.1 | -1.9 | 21.81 | 177.5 | 279.3 | 7.676 | -9999 | -4.96 | -3.6 | 161 | 2.76 | 14.04 | 2 | 2.71 | 2 | 0.007 | 0.007 | 12.78
524 | 2008-07-22 | 190000 | -9999 | 701.9 | 0.1 | -2.1 | 21.82 | 178.3 | 277.3 | 3.121 | -9999 | -4.96 | -3.8 | 150.9 | 2.54 | 13.02 | 1.9 | 2.47 | 1.9 | 0.007 | 0.007 | 13.25
525 | 2008-07-22 | 200000 | -9999 | 641.6 | 0.2 | -2.2 | 17.23 | 131.2 | 206.3 | -1.053 | -9999 | -4.96 | -4.2 | 53.4 | 2.39 | 7.17 | 2 | 2.33 | 2 | 0.007 | 0.007 | 13.89
526 | 2008-07-22 | 210000 | -9999 | 637.3 | 0.2 | -2.1 | 17.33 | 132.4 | 206.8 | -1.056 | -9999 | -4.96 | -4.2 | 55.5 | 2.36 | 7.07 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.88
527 | 2008-07-22 | 220000 | -9999 | 549.4 | 49.9 | -185.8 | 1.58 | 6.8 | 13.5 | -1.037 | -9999 | -4.96 | -405.1 | 11.1 | 2.25 | 5.92 | 6 | 7.99 | 13.1 | 64.947 | 26.929 | 19.71
528 | 2008-07-22 | 230000 | -9999 | 427.6 | 27.3 | -293.2 | 0.04 | 0.5 | 1.3 | -1.044 | -9999 | -4.97 | -764.5 | 1.5 | 0 | 0.08 | 0.2 | 0.01 | 5.7 | 428.956 | 36.404 | 20.9
529 | 2008-07-23 | 0 | -9999 | 401.7 | 15 | -241.9 | 0.04 | 0.5 | 1.3 | -1.019 | -9999 | -4.96 | -504.5 | 0.6 | 0 | -0.01 | 0 | 0.02 | 2.5 | 669.517 | 17.411 | 20.91
530 | 2008-07-23 | 10000 | -9999 | 391.6 | 13.7 | -168 | 0.04 | 0.5 | 1.3 | -1.037 | -9999 | -4.97 | -478.8 | 0.6 | 0 | -0.01 | -0.2 | 0.01 | 0.7 | 683.758 | 4.75 | 20.91
531 | 2008-07-23 | 20000 | -9999 | 384 | 11.3 | -262.9 | 0.04 | 0.5 | 1.3 | -1.081 | -9999 | -4.97 | -461.1 | 0.8 | 0 | -0.01 | -0.1 | 0.01 | 2.6 | 587.216 | 14.246 | 20.91
532 | 2008-07-23 | 30000 | -9999 | 382.6 | 4.4 | -174.2 | 0.04 | 0.5 | 1.3 | -1.038 | -9999 | -4.97 | -217.1 | 0.9 | 0 | -0.03 | -0.1 | 0.01 | 1.3 | 473.254 | 9.499 | 20.92
533 | 2008-07-23 | 40000 | -9999 | 553.3 | 20.8 | 14.4 | 6.28 | 18.3 | 18.8 | -1.046 | -9999 | -4.96 | -38.9 | 2.9 | 8.87 | 25.76 | 12.6 | 38.52 | 55.2 | 76.176 | 4.795 | 17.25
534 | 2008-07-23 | 50000 | -9999 | 623.8 | 17.4 | 25.6 | 10.94 | 59.9 | 96.7 | -1.058 | -9999 | -4.96 | -5.2 | 59.5 | 8.71 | 26.15 | 9.5 | 41.31 | 44.4 | 0.164 | 0.035 | 15.2
535 | 2008-07-23 | 60000 | -9999 | 636.9 | 2.4 | 21.3 | 17.8 | 136.7 | 210.7 | -1.065 | -9999 | -4.96 | -11.4 | 78.7 | 2.58 | 8.44 | 1.6 | 8.94 | 3.4 | 0.013 | 0.006 | 12.28
536 | 2008-07-23 | 70000 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999
537 | 2008-07-23 | 80000 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999
538 | 2008-07-23 | 90000 | 1 | 712.3 | 0.2 | -1.9 | 22.12 | 182.1 | 278.6 | 0.26 | 1 | -4.96 | -3.7 | 150 | 2.6 | 12.6 | 1.9 | 2.53 | 1.9 | 0.007 | 0.007 | 13.02
539 | 2008-07-23 | 100000 | 1 | 693.6 | 0.3 | -2.1 | 21.81 | 178.5 | 274 | 0.085 | 1 | -4.96 | -4 | 132.8 | 2.39 | 11.67 | 1.9 | 2.33 | 1.9 | 0.007 | 0.007 | 13.52
540 | 2008-07-23 | 110000 | 1 | 690.7 | 0.3 | -2.3 | 21.79 | 177.9 | 273.1 | 0.059 | 1 | -4.96 | -4 | 143.9 | 2.42 | 12.31 | 1.9 | 2.36 | 1.9 | 0.007 | 0.007 | 13.53
541 | 2008-07-23 | 120000 | 0 | 569.8 | 51.3 | -215.9 | 2.09 | 11 | 19.9 | -0.047 | 0 | -4.96 | -355.6 | 4 | 1.76 | 5.38 | 3.5 | 7.46 | 12.4 | 167.823 | 49.077 | 19.53
542 | 2008-07-23 | 130000 | 0 | 450.3 | 16 | -49.2 | 0.08 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -178.8 | 1.2 | 1.46 | 0.03 | 0.6 | 6.72 | 4.9 | 626.788 | 77.556 | 17.72
543 | 2008-07-23 | 140000 | 0 | 430.7 | 36.9 | 66.6 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -342.9 | 1.7 | 2.38 | 2.09 | 5.5 | 13.65 | 11.7 | 289.693 | 120.308 | 13.57
544 | 2008-07-23 | 150000 | 0 | 424.5 | 195.8 | 112.4 | 0.08 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -123.6 | 1.9 | 2.11 | 0 | 13.6 | 8.29 | 15.2 | 0.056 | 0.05 | 14.12
545 | 2008-07-23 | 160000 | 0 | 419.5 | 89.1 | -143.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -301.2 | 1.3 | 0.05 | -0.01 | 2.5 | 0.05 | 2.1 | 0.013 | 0.01 | 20.72
546 | 2008-07-23 | 170000 | 0 | 415.3 | 49.4 | -177.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -300.8 | 1 | -0.02 | 0 | -1.2 | -0.01 | -1.2 | 0.004 | 0 | 20.8
547 | 2008-07-23 | 180000 | 0 | 411.5 | 43.8 | -152.7 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -276.3 | 1.1 | -0.03 | 0 | -1.6 | -0.02 | -1.6 | 0.003 | 0 | 20.79
548 | 2008-07-23 | 190000 | 0 | 406.4 | 41.2 | -168.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -271.3 | 1 | -0.03 | 0 | -1.8 | -0.02 | -1.2 | 0.003 | 0 | 20.79
549 | 2008-07-23 | 200000 | 0 | 401 | 39 | -148.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -265.6 | 1.2 | -0.04 | -0.01 | -2 | -0.02 | -1.3 | 0.003 | 0 | 20.79
550 | 2008-07-23 | 210000 | 0 | 395.7 | 40.1 | -158.9 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -286.6 | 1.2 | -0.04 | 0 | -2.4 | -0.02 | -1.6 | 0.003 | 0 | 20.79
551 | 2008-07-23 | 220000 | 0 | 390.7 | 40.9 | -171.7 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -309.7 | 1.4 | -0.04 | -0.02 | -2.6 | -0.02 | -0.9 | 0.005 | 0 | 20.8
552 | 2008-07-23 | 230000 | 0 | 386.6 | 41.3 | -184.9 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | -4.97 | -328.4 | 1.5 | -0.04 | -0.04 | -2.9 | -0.02 | -1.8 | 0.003 | 0 | 20.81
553 | 2008-07-24 | 0 | 0 | 382.3 | 38.7 | -182.5 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -326.7 | 1 | -0.04 | -0.03 | -2.9 | -0.02 | -1.4 | 0.004 | 0 | 20.81
554 | 2008-07-24 | 10000 | 0 | 377.6 | 36.8 | -185 | 0.04 | 0.5 | 1.2 | -0.046 | 0 | -4.97 | -324.5 | 1 | -0.04 | -0.03 | -2.9 | -0.02 | -1.3 | 0.004 | 0 | 20.81
555 | 2008-07-24 | 20000 | 0 | 366.4 | 33.9 | -167.7 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | -4.97 | -316.1 | 1.1 | -0.05 | -0.03 | -3 | -0.02 | -1.4 | 0.004 | 0 | 20.8
556 | 2008-07-24 | 30000 | 0 | 361.3 | 31.9 | -189.2 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -322.6 | 1.1 | -0.05 | -0.03 | -3.2 | -0.02 | -1.5 | 0.004 | 0 | 20.81
557 | 2008-07-24 | 40000 | 1 | 522.1 | 24.7 | -12.2 | 5.74 | 13 | 13.4 | -0.049 | 0 | -4.96 | -39.5 | 1.2 | 9.07 | 26.01 | 13.8 | 36.53 | 55.8 | 0.207 | 0.052 | 17.48
558 | 2008-07-24 | 50000 | 1 | 627.9 | 17.3 | 8.3 | 9.43 | 46 | 46.3 | -0.048 | 0 | -4.96 | -6.8 | 31.3 | 7.97 | 25.16 | 12.2 | 33.72 | 49.1 | 0.181 | 0.045 | 16.12
559 | 2008-07-24 | 60000 | 1 | 638.8 | 2.1 | 16.1 | 18.81 | 146.6 | 211.3 | -0.047 | 0 | -4.97 | -12.8 | 81.1 | 3.03 | 9.38 | 1.7 | 9.5 | 3.7 | 0.015 | 0.008 | 12.19
560 | 2008-07-24 | 70000 | 1 | 650.5 | 0.4 | -2.2 | 19.29 | 153.7 | 231.3 | -0.046 | 0 | -4.96 | -4.1 | 67.2 | 2.38 | 7.97 | 2 | 2.36 | 2 | 0.007 | 0.007 | 13.79
561 | 2008-07-24 | 80000 | 1 | 651.7 | 0.6 | -2.3 | 19.29 | 154.1 | 232.5 | -0.047 | 0 | -4.96 | -4.1 | 66.7 | 2.44 | 7.88 | 2 | 2.4 | 2 | 0.007 | 0.007 | 13.76
562 | 2008-07-24 | 90000 | 1 | 652.3 | 0.5 | -2.2 | 19.26 | 154.1 | 233 | -0.047 | 0 | -4.97 | -4.1 | 67.3 | 2.43 | 8.67 | 2 | 2.4 | 2 | 0.007 | 0.007 | 13.76
563 | 2008-07-24 | 100000 | 1 | 652.3 | 0.5 | -2.2 | 19.29 | 154.2 | 233.6 | -0.047 | 0 | -4.96 | -4.1 | 68.7 | 2.44 | 7.86 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.76
564 | 2008-07-24 | 110000 | 1 | 652.3 | 0.5 | -1.9 | 19.3 | 154.2 | 233.5 | -0.047 | 0 | -4.97 | -4.1 | 70.1 | 2.44 | 7.94 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.76
565 | 2008-07-24 | 120000 | 1 | 652.2 | 0.5 | -2.5 | 19.28 | 154 | 233.6 | -0.046 | 0 | -4.96 | -4.1 | 70.6 | 2.43 | 7.98 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.76
566 | 2008-07-24 | 130000 | 1 | 653.1 | 0.5 | -2.3 | 19.27 | 153.6 | 233.3 | -0.046 | 0 | -4.96 | -4.1 | 68.6 | 2.46 | 7.89 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.77
567 | 2008-07-24 | 140000 | 1 | 651.2 | 0.5 | -2.5 | 19.05 | 151.9 | 231.2 | -0.046 | 0 | -4.96 | -4.1 | 69.3 | 2.41 | 7.88 | 2 | 2.39 | 2 | 0.007 | 0.007 | 13.76
568 | 2008-07-24 | 150000 | 1 | 653.4 | 0.5 | -2.5 | 19.3 | 153.5 | 233.6 | -0.045 | 0 | -4.97 | -4.1 | 71.3 | 2.42 | 8.01 | 2 | 2.39 | 2 | 0.007 | 0.007 | 13.79
569 | 2008-07-24 | 160000 | 1 | 653.4 | 0.5 | -2.2 | 19.14 | 152.6 | 232.5 | -0.047 | 0 | -4.97 | -4.1 | 69.6 | 2.43 | 7.95 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.78
570 | 2008-07-24 | 170000 | 1 | 652.7 | 0.5 | -2.1 | 19.15 | 152.4 | 231.8 | -0.049 | 0 | -4.96 | -4.1 | 67.7 | 2.42 | 7.8 | 2 | 2.4 | 2 | 0.007 | 0.007 | 13.76
571 | 2008-07-24 | 180000 | 1 | 652.1 | 0.5 | -2.1 | 19.13 | 152.6 | 231.7 | -0.052 | 0 | -4.96 | -4.1 | 66.4 | 2.43 | 7.74 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.76
572 | 2008-07-24 | 190000 | 1 | 651.5 | 0.4 | -1.9 | 19.23 | 153.4 | 232.5 | -0.052 | 0 | -4.96 | -4.1 | 66.4 | 2.43 | 7.73 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.75
573 | 2008-07-24 | 200000 | 1 | 652 | 0.4 | -2.6 | 19.24 | 153.8 | 232.9 | -0.051 | 0 | -4.96 | -4.1 | 66.5 | 2.43 | 7.72 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.75
574 | 2008-07-24 | 210000 | 1 | 650.7 | 0.4 | -2.1 | 19.01 | 151.2 | 230 | -0.052 | 0 | -4.96 | -4.1 | 63.7 | 2.44 | 7.68 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.74
575 | 2008-07-24 | 220000 | 0 | 555.4 | 25.1 | -43.7 | 1.82 | 8.3 | 16.1 | -0.049 | 0 | -4.97 | -104.4 | 10.9 | 1.98 | 5.98 | 2.3 | 8.12 | 9 | 0.036 | 0.01 | 19.45
576 | 2008-07-24 | 230000 | 0 | 433.4 | 15.2 | -116.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -197.9 | 1.6 | -0.04 | 0.1 | -1.7 | -0.01 | -0.6 | 0.003 | 0 | 20.75
577 | 2008-07-25 | 0 | 0 | 414.3 | 14.1 | -122.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -212 | 1.7 | -0.05 | 0 | -2.1 | -0.01 | -0.5 | 0.004 | 0 | 20.68
578 | 2008-07-25 | 10000 | 0 | 410.3 | 13.7 | -123.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -222.8 | 1.5 | -0.05 | 0 | -2.3 | -0.03 | -1.4 | 0.003 | 0 | 20.69
579 | 2008-07-25 | 20000 | 0 | 405.4 | 13.9 | -120.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -237.3 | 1.3 | -0.05 | -0.02 | -2.4 | -0.04 | -1.6 | 0.002 | 0 | 20.7
580 | 2008-07-25 | 30000 | 0 | 401.2 | 13.7 | -142.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -252.2 | 1.2 | -0.05 | -0.02 | -2.6 | -0.04 | -2.3 | 0.002 | 0 | 20.78
581 | 2008-07-25 | 40000 | 0 | 397.4 | 12.8 | -136.5 | 0.04 | 0.5 | 1.2 | -0.051 | 0 | -4.97 | -251.2 | 1.3 | -0.05 | -0.03 | -2.6 | -0.05 | -2.4 | 0.002 | 0 | 20.71
582 | 2008-07-25 | 50000 | 0 | 392.9 | 13.2 | -152 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -281.6 | 1.2 | -0.05 | -0.03 | -3 | -0.05 | -2.7 | 0.002 | 0 | 20.79
583 | 2008-07-25 | 60000 | 0 | 388.1 | 13.8 | -182.3 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -4.97 | -310.6 | 0.6 | -0.05 | -0.03 | -3.2 | -0.04 | -2.4 | 0.003 | 0 | 20.8
584 | 2008-07-25 | 70000 | 0 | 383.7 | 15.2 | -160.6 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -352.3 | 0.6 | -0.05 | -0.03 | -3.7 | -0.05 | -3.3 | 0.002 | 0 | 20.81
585 | 2008-07-25 | 80000 | 0 | 379.2 | 14.6 | -201 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -360.3 | 0.7 | -0.05 | -0.04 | -3.8 | -0.04 | -3 | 0.003 | 0 | 20.81
586 | 2008-07-25 | 90000 | 0 | 374.5 | 13.7 | -220.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -367.1 | 0.9 | -0.05 | 2.1 | -4 | -0.05 | -3 | 0.003 | 0 | 20.82
587 | 2008-07-25 | 100000 | 0 | 370.3 | 13.6 | -209.7 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -366.2 | 1.1 | -0.05 | -0.03 | -3.8 | -0.04 | -3 | 0.003 | 0 | 20.82
588 | 2008-07-25 | 110000 | 0 | 365.8 | 13.6 | -233.7 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.96 | -383.3 | 1.4 | -0.05 | -0.03 | -4 | -0.04 | -3.1 | 0.003 | 0 | 20.82
589 | 2008-07-25 | 120000 | 0 | 360.9 | 11.3 | -195.7 | 0.13 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -342.8 | 1.3 | -0.05 | -0.03 | -3.7 | -0.04 | -2.8 | 0.003 | 0 | 20.73
590 | 2008-07-25 | 130000 | 0 | 356.5 | 9.1 | -170 | 0.09 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -281.4 | 0.8 | -0.05 | -0.03 | -3 | -0.04 | -2.4 | 0.002 | 0 | 20.72
591 | 2008-07-25 | 140000 | 0 | 351.9 | 8.6 | -143 | 0.26 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -260.8 | 0.6 | -0.05 | -0.03 | -2.8 | -0.04 | -2.1 | 0.002 | 0 | 20.78
592 | 2008-07-25 | 150000 | 0 | 349.1 | 8.3 | -123.1 | 0.05 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -239.9 | 0.6 | -0.05 | -0.03 | -2.6 | -0.05 | -2.2 | 0.002 | 0 | 20.77
593 | 2008-07-25 | 160000 | 0 | 344.6 | 8.5 | -119.6 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | -4.97 | -220.1 | 0.8 | -0.05 | -0.03 | -2.3 | -0.05 | -2.1 | 0.002 | 0 | 20.76
594 | 2008-07-25 | 170000 | 0 | 340.1 | 8 | -133.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -212.4 | 0.9 | -0.05 | -0.03 | -2.2 | -0.05 | -1.9 | 0.002 | 0 | 20.76
595 | 2008-07-25 | 180000 | 0 | 335.7 | 7.4 | -112.2 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -4.97 | -209.5 | 0.9 | -0.05 | -0.03 | -2.1 | -0.04 | -1.7 | 0.002 | 0 | 20.76
596 | 2008-07-25 | 190000 | 0 | 331.3 | 6.8 | -115.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -216.6 | 1 | -0.05 | -0.03 | -2.2 | -0.05 | -2 | 0.001 | 0 | 20.76
597 | 2008-07-25 | 200000 | 0 | 320.8 | 6.2 | -126.6 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -220 | 0.8 | -0.05 | -0.03 | -2.3 | -0.04 | -1.6 | 0.002 | 0 | 20.69
598 | 2008-07-25 | 210000 | 0 | 301.4 | 5.4 | -123.6 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -226.2 | 0.8 | -0.05 | -0.03 | -2.4 | -0.04 | -1.8 | 0.002 | 0 | 20.77
599 | 2008-07-25 | 220000 | 0 | 291 | 4.8 | -146.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -229.9 | 0.9 | -0.05 | -0.03 | -2.4 | -0.05 | -2.2 | 0.002 | 0 | 20.77
600 | 2008-07-25 | 230000 | 0 | 284.5 | 4.4 | -113.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -229.8 | 0.9 | -0.05 | -0.04 | -2.3 | -0.04 | -1.7 | 0.002 | 0 | 20.77
601 | 2008-07-26 | 0 | 0 | 280.6 | 4 | -130.7 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -228.2 | 1 | -0.05 | -0.03 | -2.4 | -0.05 | -2.2 | 0.002 | 0 | 20.77
602 | 2008-07-26 | 10000 | 0 | 277.8 | 3.8 | -121.3 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -227.9 | 0.9 | -0.05 | -0.03 | -2.5 | -0.04 | -1.9 | 0.002 | 0 | 20.77
603 | 2008-07-26 | 20000 | 0 | 275.3 | 3.1 | -140.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -227.5 | 0.8 | -0.05 | -0.03 | -2.4 | -0.04 | -1.7 | 0.002 | 0 | 20.77
604 | 2008-07-26 | 30000 | 0 | 273 | 3.5 | -120.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -230.4 | 0.9 | -0.05 | -0.03 | -2.3 | -0.04 | -2 | 0.002 | 0 | 20.77
605 | 2008-07-26 | 40000 | 0 | 270.6 | 2.9 | -128.4 | 0.04 | 0.5 | 1.2 | -0.046 | 0 | -4.97 | -224.3 | 0.9 | -0.05 | -0.03 | -2.3 | -0.04 | -2 | 0.001 | 0 | 20.69
606 | 2008-07-26 | 50000 | 0 | 267.3 | 2.9 | -133.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -232 | 0.8 | -0.05 | -0.03 | -2.4 | -0.03 | -1.7 | 0.002 | 0 | 20.77
607 | 2008-07-26 | 60000 | 0 | 264.6 | 3.9 | -127.1 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -246.4 | 0.8 | -0.05 | -0.03 | -2.4 | -0.03 | -1.2 | 0.003 | 0 | 20.78
608 | 2008-07-26 | 70000 | 0 | 262.2 | 5.3 | -120.9 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -244.5 | 0.8 | -0.04 | -0.03 | -2.2 | -0.02 | -1.1 | 0.003 | 0 | 20.78
609 | 2008-07-26 | 80000 | 0 | 259.9 | 5.3 | -154.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -249.2 | 0.8 | -0.04 | -0.03 | -2 | -0.02 | -1 | 0.003 | 0 | 20.78
610 | 2008-07-26 | 90000 | 0 | 257.3 | 5.8 | -139.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -239.9 | 0.9 | -0.04 | 2.15 | -1.8 | -0.01 | -0.8 | 0.003 | 0 | 20.77
611 | 2008-07-26 | 100000 | 0 | 254.9 | 5.1 | -126.1 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -228.5 | 1 | -0.04 | -0.04 | -1.9 | -0.02 | -1 | 0.003 | 0 | 20.77
612 | 2008-07-26 | 110000 | 0 | 252.7 | 3.7 | -111.7 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -221.1 | 0.9 | -0.05 | -0.03 | -2 | -0.01 | -0.6 | 0.003 | 0 | 20.69
613 | 2008-07-26 | 120000 | 0 | 250 | 3 | -113.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -209 | 0.9 | -0.05 | -0.04 | -2 | -0.01 | -0.6 | 0.003 | 0 | 20.76
614 | 2008-07-26 | 130000 | 0 | 247.8 | 2.5 | -109.3 | 0.05 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -200 | 0.9 | -0.05 | -0.04 | -2.1 | -0.05 | -2 | 0.001 | 0 | 20.75
615 | 2008-07-26 | 140000 | 0 | 245.6 | 2.7 | -105.4 | 0.05 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -192.6 | 1 | -0.05 | -0.03 | -2.1 | -0.05 | -1.8 | 0.001 | 0 | 20.75
616 | 2008-07-26 | 150000 | 0 | 243.2 | 2.8 | -101.6 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -192.7 | 1 | -0.05 | -0.04 | -2.1 | -0.05 | -1.8 | 0.002 | 0 | 20.74
617 | 2008-07-26 | 160000 | 0 | 241 | 3.2 | -92.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -190.8 | 1 | -0.05 | -0.04 | -2 | -0.04 | -1.6 | 0.001 | 0 | 20.74
618 | 2008-07-26 | 170000 | 0 | 238.9 | 3.1 | -106.6 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -184.7 | 1.1 | -0.05 | -0.03 | -2 | -0.05 | -1.8 | 0.001 | 0 | 20.74
619 | 2008-07-26 | 180000 | 0 | 236.3 | 3 | -114.7 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -185.3 | 1.1 | -0.05 | -0.03 | -2 | -0.05 | -2 | 0.001 | 0 | 20.74
620 | 2008-07-26 | 190000 | 0 | 233.6 | 2.9 | -95.1 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -185.6 | 0.9 | -0.05 | -0.03 | -2 | -0.05 | -1.7 | 0.001 | 0 | 20.74
621 | 2008-07-26 | 200000 | 0 | 230.9 | 2.6 | -119 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -184.5 | 0.9 | -0.06 | -0.03 | -2.1 | -0.05 | -1.9 | 0.001 | 0 | 20.66
622 | 2008-07-26 | 210000 | 0 | 228.3 | 2.8 | -94 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -189.3 | 0.9 | -0.05 | -0.04 | -2.1 | -0.04 | -1.9 | 0.002 | 0 | 20.74
623 | 2008-07-26 | 220000 | 0 | 226.2 | 3 | -111.4 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | -4.97 | -196.4 | 0.9 | -0.05 | -0.03 | -2.1 | -0.04 | -1.5 | 0.002 | 0 | 20.75
624 | 2008-07-26 | 230000 | 0 | 223.6 | 2.8 | -122.9 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | -4.97 | -194.7 | 0.9 | -0.05 | -0.04 | -2.1 | -0.05 | -1.9 | 0.001 | 0 | 20.75
625 | 2008-07-27 | 0 | 0 | 221.1 | 2.8 | -132 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -202.9 | 0.9 | -0.05 | -0.03 | -2.2 | -0.05 | -2.1 | 0.001 | 0 | 20.75
626 | 2008-07-27 | 10000 | 0 | 218.9 | 2.6 | -112 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -204.3 | 0.9 | -0.05 | -0.03 | -2.2 | -0.05 | -2 | 0.001 | 0 | 20.76
627 | 2008-07-27 | 20000 | 0 | 216.9 | 2.2 | -118.2 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -206.7 | 0.9 | -0.05 | -0.04 | -2.3 | -0.05 | -2.2 | 0.001 | 0 | 20.76
628 | 2008-07-27 | 30000 | 0 | 214.6 | 2.1 | -96 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -4.97 | -207.8 | 0.9 | -0.05 | -0.03 | -2.3 | -0.05 | -1.9 | 0.002 | 0 | 20.76
629 | 2008-07-27 | 40000 | 0 | 212.6 | 2.4 | -120.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -213.4 | 0.9 | -0.06 | -0.03 | -2.4 | -0.05 | -2.2 | 0.001 | 0 | 20.76
630 | 2008-07-27 | 50000 | 0 | 210.5 | 2.9 | -110.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -228.5 | 0.9 | -0.05 | -0.03 | -2.5 | -0.04 | -2 | 0.002 | 0 | 20.62
631 | 2008-07-27 | 60000 | 0 | 208.4 | 2.9 | -138.2 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.96 | -241.3 | 0.9 | -0.05 | -0.03 | -2.6 | -0.05 | -2.5 | 0.002 | 0 | 20.77
632 | 2008-07-27 | 70000 | 0 | 206.4 | 3.1 | -152.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -260.3 | 0.9 | -0.05 | -0.03 | -2.8 | -0.05 | -2.5 | 0.002 | 0 | 20.78
633 | 2008-07-27 | 80000 | 0 | 203.4 | 3.5 | -163.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -284.5 | 1 | -0.05 | -0.03 | -3.1 | -0.05 | -2.5 | 0.002 | 0 | 20.79
634 | 2008-07-27 | 90000 | 0 | 200.6 | 3.8 | -159.6 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -291.3 | 0.9 | -0.05 | 2.15 | -3.1 | -0.05 | -2.7 | 0.002 | 0 | 20.8
635 | 2008-07-27 | 100000 | 0 | 198 | 3.8 | -163.6 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -4.97 | -287.8 | 1 | -0.05 | -0.03 | -3.1 | -0.05 | -2.8 | 0.002 | 0 | 20.79
636 | 2008-07-27 | 110000 | 0 | 195.7 | 4.2 | -150.9 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | -4.96 | -286 | 1.1 | -0.05 | -0.03 | -3.1 | -0.06 | -3.2 | 0.002 | 0 | 20.79
637 | 2008-07-27 | 120000 | 0 | 195.2 | 4.8 | -151.9 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -293.1 | 1 | -0.05 | -0.03 | -3.2 | -0.05 | -2.5 | 0.002 | 0 | 20.72
638 | 2008-07-27 | 130000 | 0 | 194.4 | 4.5 | -170.2 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -302.6 | 1 | -0.05 | -0.03 | -3.3 | -0.05 | -2.9 | 0.002 | 0 | 20.72
639 | 2008-07-27 | 140000 | 0 | 192.5 | 5.4 | -172.2 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -4.97 | -314.4 | 0.9 | -0.05 | -0.04 | -3.4 | -0.05 | -2.7 | 0.002 | 0 | 20.8
640 | 2008-07-27 | 150000 | 0 | 190.1 | 4.8 | -184.9 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -4.97 | -293.7 | 0.9 | -0.05 | -0.03 | -3.2 | -0.05 | -2.7 | 0.002 | 0 | 20.8
641 | 2008-07-27 | 160000 | 0 | 187.6 | 4.7 | -157.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -287.5 | 1 | -0.05 | -0.03 | -3.1 | -0.04 | -2.1 | 0.002 | 0 | 20.79
642 | 2008-07-27 | 170000 | 0 | 185.3 | 5 | -123.2 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -4.97 | -278.5 | 1 | -0.05 | -0.03 | -3.1 | -0.04 | -2.3 | 0.002 | 0 | 20.79
643 | 2008-07-27 | 180000 | 0 | 183 | 4.6 | -146.1 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -264.3 | 0.9 | -0.05 | -0.03 | -2.9 | -0.05 | -2.4 | 0.002 | 0 | 20.79
644 | 2008-07-27 | 190000 | 0 | 180.8 | 4.8 | -153.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -265.1 | 1 | -0.05 | -0.03 | -2.9 | -0.05 | -2.5 | 0.001 | 0 | 20.79
645 | 2008-07-27 | 200000 | 0 | 178.5 | 5.1 | -172.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -289.1 | 1 | -0.05 | -0.03 | -3.2 | -0.05 | -2.9 | 0.001 | 0 | 20.79
646 | 2008-07-27 | 210000 | 0 | 176.5 | 5.7 | -155.6 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.96 | -305.5 | 0.9 | -0.05 | -0.04 | -3.2 | -0.04 | -2.2 | 0.004 | 0 | 20.73
647 | 2008-07-27 | 220000 | 0 | 174 | 5.3 | -163.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.96 | -321.9 | 0.9 | -0.05 | -0.03 | -3.5 | -0.05 | -3.2 | 0.002 | 0 | 20.81
648 | 2008-07-27 | 230000 | 0 | 171.7 | 4.5 | -174.1 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -318.1 | 0.9 | -0.05 | -0.03 | -3.4 | -0.05 | -3.1 | 0.002 | 0 | 20.8
649 | 2008-07-28 | 0 | 0 | 169.6 | 3.5 | -151.7 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -280.9 | 0.8 | -0.05 | -0.03 | -3.1 | -0.05 | -2.9 | 0.002 | 0 | 20.79
650 | 2008-07-28 | 10000 | 0 | 167.1 | 3 | -138.3 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -266.4 | 0.7 | -0.05 | -0.03 | -2.9 | -0.04 | -2.7 | 0.002 | 0 | 20.79
651 | 2008-07-28 | 20000 | 0 | 164.7 | 2.4 | -128.8 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -253.4 | 0.9 | -0.06 | -0.03 | -2.8 | -0.04 | -2.1 | 0.002 | 0 | 20.78
652 | 2008-07-28 | 30000 | 0 | 162.7 | 2.4 | -147.1 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -250.3 | 0.8 | -0.05 | -0.03 | -2.7 | -0.05 | -2.5 | 0.001 | 0 | 20.78
653 | 2008-07-28 | 40000 | 0 | 160.6 | 2.3 | -140.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -251.5 | 0.8 | -0.05 | -0.03 | -2.8 | -0.05 | -2.6 | 0.002 | 0 | 20.78
654 | 2008-07-28 | 50000 | 0 | 158.4 | 2.6 | -131 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -241.1 | 0.7 | -0.05 | -0.03 | -2.6 | -0.05 | -2.7 | 0.001 | 0 | 20.78
655 | 2008-07-28 | 60000 | 0 | 156.7 | 2.7 | -143.8 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -244.1 | 0.8 | -0.05 | -0.04 | -2.6 | -0.05 | -2.4 | 0.001 | 0 | 20.78
656 | 2008-07-28 | 70000 | 0 | 154.7 | 4.7 | -113.9 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | -4.97 | -233.7 | 0.8 | -0.05 | -0.03 | -2.3 | -0.02 | -1.1 | 0.003 | 0 | 20.77
657 | 2008-07-28 | 80000 | 0 | 153.4 | 4.1 | -107.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -217.2 | 0.6 | -0.05 | -0.03 | -2.2 | -0.04 | -1.7 | 0.002 | 0 | 20.76
658 | 2008-07-28 | 90000 | 0 | 151.8 | 3.4 | -120.4 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -213.4 | 0.6 | -0.05 | 2.16 | -2.2 | -0.05 | -2.1 | 0.001 | 0 | 20.69
659 | 2008-07-28 | 100000 | 0 | 150.5 | 3.8 | -123.1 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -200 | 0.7 | -0.05 | -0.03 | -1.9 | -0.02 | -0.7 | 0.003 | 0 | 20.75
660 | 2008-07-28 | 110000 | 0 | 149.1 | 4.4 | -102.6 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -184.9 | 0.7 | -0.03 | -0.01 | -1 | -0.03 | -1.1 | 0.001 | 0 | 20.67
661 | 2008-07-28 | 120000 | 0 | 147.3 | 4 | -99 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -174.3 | 0.7 | -0.02 | 0 | -0.5 | 0 | -0.2 | 0.003 | 0 | 20.73
662 | 2008-07-28 | 130000 | 0 | 146.2 | 3.2 | -85.4 | 0.09 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -165.7 | 0.7 | -0.03 | 0 | -1.2 | -0.01 | -0.4 | 0.002 | 0 | 20.72
663 | 2008-07-28 | 140000 | 0 | 145 | 2.6 | -88.3 | 0.26 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -156.8 | 0.7 | -0.05 | -0.02 | -1.5 | -0.03 | -0.8 | 0.002 | 0 | 20.71
664 | 2008-07-28 | 150000 | 0 | 143.8 | 2.3 | -85.2 | 0.08 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -149.9 | 0.8 | -0.05 | -0.03 | -1.5 | -0.05 | -1.5 | 0.001 | 0 | 20.7
665 | 2008-07-28 | 160000 | 0 | 142.7 | 9.9 | -16.6 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -119.8 | 0.7 | 1.68 | -0.03 | 0.9 | 8.11 | 3.8 | 0.018 | 0.007 | 17.16
666 | 2008-07-28 | 170000 | 0 | 141 | 7.3 | -77.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -135.3 | 0.6 | -0.02 | -0.03 | -0.6 | -0.01 | -0.3 | 0.002 | 0 | 20.68
667 | 2008-07-28 | 180000 | 0 | 139.7 | 16.7 | -63.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -119.3 | 0.8 | -0.03 | -0.03 | -0.8 | -0.02 | -0.5 | 0.002 | 0 | 20.65
668 | 2008-07-28 | 190000 | 0 | 139.4 | 16.4 | -78.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -122.1 | 0.7 | -0.04 | -0.03 | -0.9 | -0.02 | -0.5 | 0.002 | 0 | 20.66
669 | 2008-07-28 | 200000 | 0 | 138.7 | 16.1 | -78.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -129 | 0.6 | -0.04 | -0.03 | -1 | -0.02 | -0.5 | 0.002 | 0 | 20.67
670 | 2008-07-28 | 210000 | 0 | 136.3 | 16.2 | -70.5 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -138.7 | 0.6 | -0.04 | -0.03 | -1.1 | -0.01 | -0.4 | 0.002 | 0 | 20.61
671 | 2008-07-28 | 220000 | 0 | 134.4 | 16.1 | -77 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -150.5 | 0.6 | -0.04 | -0.03 | -1.3 | -0.02 | -0.4 | 0.002 | 0 | 20.7
672 | 2008-07-28 | 230000 | 0 | 132.7 | 15.3 | -81.3 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -150.9 | 0.6 | -0.04 | -0.03 | -1.3 | -0.02 | -0.6 | 0.002 | 0 | 20.7
673 | 2008-07-29 | 0 | 0 | 131.2 | 14.4 | -90.5 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -154.8 | 0.6 | -0.05 | -0.03 | -1.5 | -0.02 | -0.7 | 0.002 | 0 | 20.71
674 | 2008-07-29 | 10000 | 0 | 129.6 | 14.3 | -83 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -159.6 | 0.6 | -0.05 | -0.03 | -1.5 | -0.01 | -0.3 | 0.003 | 0 | 20.71
675 | 2008-07-29 | 20000 | 0 | 128.1 | 14.1 | -105.1 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.96 | -169.5 | 0.6 | -0.05 | -0.03 | -1.6 | -0.02 | -0.6 | 0.002 | 0 | 20.73
676 | 2008-07-29 | 30000 | 0 | 127.5 | 14.4 | -97.2 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -176.5 | 0.6 | -0.05 | -0.03 | -1.7 | -0.02 | -0.6 | 0.003 | 0 | 20.66
677 | 2008-07-29 | 40000 | 0 | 126.3 | 13.9 | -107.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -178.5 | 0.5 | -0.05 | -0.03 | -1.7 | -0.02 | -0.8 | 0.002 | 0 | 20.73
678 | 2008-07-29 | 50000 | 0 | 125.7 | 13.4 | -93.5 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -176.9 | 0.6 | -0.04 | -0.03 | -1.5 | -0.02 | -0.8 | 0.002 | 0 | 20.73
679 | 2008-07-29 | 60000 | 0 | 124.4 | 13.4 | -83.6 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.96 | -175.5 | 0.5 | -0.04 | -0.03 | -1.4 | -0.02 | -0.7 | 0.002 | 0 | 20.73
680 | 2008-07-29 | 70000 | 0 | 123.9 | 13.8 | -97.6 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.96 | -182 | 0.6 | -0.03 | -0.03 | -1.1 | -0.01 | -0.4 | 0.003 | 0 | 20.74
681 | 2008-07-29 | 80000 | 1 | 356.1 | 28.3 | 90.8 | 5.61 | 12 | 12.5 | -0.051 | 0 | -4.96 | -27.7 | 0.6 | 8.91 | 25.57 | 13.5 | 35.45 | 53.5 | 0.198 | 0.05 | 17.47
682 | 2008-07-29 | 90000 | 1 | 604 | 18.5 | 7.7 | 6.71 | 17.5 | 17.9 | -0.05 | 0 | -4.96 | -7.3 | 9 | 10.29 | 27.25 | 15 | 47.97 | 70.1 | 0.258 | 0.055 | 16.86
683 | 2008-07-29 | 100000 | 1 | 619.7 | 23.3 | 34.1 | 8.4 | 32.5 | 46.7 | -0.051 | 0 | -4.96 | -5.9 | 30.5 | 10.29 | 29.93 | 12.2 | 44.15 | 52.4 | 0.193 | 0.045 | 15.92
684 | 2008-07-29 | 110000 | 1 | 619 | 22.2 | 36.2 | 8.93 | 37.9 | 74.7 | -0.051 | 0 | -4.96 | -5.5 | 31.3 | 10.29 | 30.02 | 11.5 | 48.02 | 53.4 | 0.197 | 0.042 | 15.61
685 | 2008-07-29 | 120000 | 1 | 627 | 3 | 11.2 | 16.95 | 128 | 199.5 | -0.052 | 0 | -4.97 | -45.6 | 71.5 | 3.05 | 9.43 | 2.5 | 12.32 | 6.8 | 0.025 | 0.009 | 12.21
686 | 2008-07-29 | 130000 | 1 | 627.7 | 0.5 | -2.4 | 17.16 | 131 | 202.5 | -0.051 | 0 | -4.96 | -4.1 | 58.5 | 1.74 | 6.94 | 1.4 | 1.72 | 1.4 | 0.005 | 0.005 | 13.78
687 | 2008-07-29 | 140000 | 1 | 630.9 | 0.7 | -2.6 | 17.5 | 134.4 | 206.9 | -0.051 | 0 | -4.96 | -4.1 | 52.7 | 2.42 | 6.85 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.75
688 | 2008-07-29 | 150000 | 1 | 631.2 | 0.6 | -2 | 17.49 | 134.6 | 207.4 | -0.049 | 0 | -4.96 | -4.1 | 52.7 | 2.44 | 6.79 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.74
689 | 2008-07-29 | 160000 | 1 | 632.6 | 0.6 | -2.1 | 17.5 | 134.7 | 207.8 | -0.049 | 0 | -4.96 | -4.1 | 53 | 2.44 | 6.82 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.74
690 | 2008-07-29 | 170000 | 1 | 632.2 | 0.6 | -2.5 | 17.5 | 134.2 | 207.3 | -0.05 | 0 | -4.96 | -4.1 | 52.1 | 2.45 | 6.79 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.74
691 | 2008-07-29 | 180000 | 1 | 632.1 | 0.6 | -2.2 | 17.41 | 133.8 | 206.6 | -0.049 | 0 | -4.96 | -4.1 | 51 | 2.43 | 6.74 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.72
692 | 2008-07-29 | 190000 | 1 | 635 | 0.5 | -2.6 | 17.41 | 132.6 | 205.4 | -0.049 | 0 | -4.96 | -4.1 | 48.3 | 2.48 | 6.72 | 2 | 2.46 | 2 | 0.007 | 0.007 | 13.71
693 | 2008-07-29 | 200000 | 0 | 555.2 | 27.5 | -45.2 | 1.55 | 6.5 | 12.8 | -0.051 | 0 | -4.97 | -95.2 | 9.4 | 1.97 | 5.99 | 2.4 | 8.04 | 9.1 | 0.035 | 0.01 | 19.54
694 | 2008-07-29 | 210000 | 0 | 446.8 | 19.5 | -104 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -181.8 | 0.7 | -0.04 | 0.04 | -1.5 | -0.02 | -0.8 | 0.002 | 0 | 20.74
695 | 2008-07-29 | 220000 | 0 | 428 | 20.1 | -91.7 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -201.9 | 0.3 | -0.04 | 0 | -1.8 | -0.02 | -0.6 | 0.003 | 0 | 20.75
696 | 2008-07-29 | 230000 | 0 | 421.1 | 19.6 | -118.3 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -208.6 | 0.4 | -0.05 | 0 | -1.9 | -0.02 | -0.6 | 0.003 | 0 | 20.76
697 | 2008-07-30 | 0 | 0 | 415.8 | 19.8 | -136.4 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -224.2 | 0.5 | -0.05 | 0 | -2.1 | -0.01 | -0.3 | 0.004 | 0 | 20.77
698 | 2008-07-30 | 10000 | 0 | 409.9 | 20.8 | -139.9 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -243.2 | 0.5 | -0.05 | -0.01 | -2.3 | -0.01 | -0.5 | 0.004 | 0 | 20.78
699 | 2008-07-30 | 20000 | 0 | 405.5 | 22.5 | -141.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -280.7 | 0.5 | -0.05 | 0 | -2.7 | -0.02 | -1.2 | 0.004 | 0 | 20.79
700 | 2008-07-30 | 30000 | 0 | 400.6 | 21.1 | -161.3 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -282.5 | 0.5 | -0.05 | 0 | -2.9 | -0.02 | -1.2 | 0.004 | 0 | 20.79
701 | 2008-07-30 | 40000 | 0 | 395.1 | 21 | -137 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -300.4 | 0.5 | -0.05 | -0.01 | -3 | -0.03 | -1.6 | 0.003 | 0 | 20.8
702 | 2008-07-30 | 50000 | 0 | 390.1 | 21.8 | -167.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -326.1 | 0.6 | -0.05 | -0.01 | -3.3 | -0.03 | -1.5 | 0.004 | 0 | 20.81
703 | 2008-07-30 | 60000 | 0 | 385.1 | 22.1 | -174.7 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -327.7 | 0.5 | -0.05 | -0.03 | -3.2 | -0.02 | -1.5 | 0.004 | 0 | 20.81
704 | 2008-07-30 | 70000 | 0 | 379.7 | 24.3 | -205.9 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -391.7 | 0.7 | -0.05 | -0.02 | -3.8 | -0.02 | -2.1 | 0.005 | 0 | 20.82
705 | 2008-07-30 | 80000 | 0 | 374.8 | 25.3 | -261.4 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | -4.97 | -451.3 | 0.6 | -0.05 | -0.03 | -4.6 | -0.03 | -2.9 | 0.005 | 0 | 20.83
706 | 2008-07-30 | 90000 | 0 | 369.7 | 24 | -243.6 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | -4.97 | -483.4 | 0.7 | -0.05 | 2.11 | -4.9 | -0.04 | -3.9 | 0.004 | 0 | 20.83
707 | 2008-07-30 | 100000 | 1 | 525.8 | 21.9 | -3.1 | 6.15 | 15.3 | 15.8 | -0.047 | 0 | -4.96 | -36.4 | 0.6 | 9.3 | 26.98 | 13.6 | 42.12 | 62 | 0.23 | 0.051 | 17.23
708 | 2008-07-30 | 110000 | 1 | 619.1 | 15.9 | 20.1 | 11.2 | 62.5 | 96.4 | -0.049 | 0 | -4.96 | -5.1 | 33.1 | 8.64 | 25.18 | 9.2 | 41.71 | 44.3 | 0.163 | 0.034 | 15.03
709 | 2008-07-30 | 120000 | 1 | 630.4 | 2.2 | 26.2 | 17.54 | 134.3 | 207.7 | -0.049 | 0 | -4.97 | -5.7 | 60.1 | 3.22 | 8.49 | 2.1 | 9.7 | 4 | 38 | 28.497 | 12.27
710 | 2008-07-30 | 130000 | 1 | 637.9 | 0.5 | -2.1 | 17.58 | 134.3 | 208.2 | -0.047 | 0 | -4.96 | -4.2 | 52.9 | 2.41 | 7.07 | 2 | 2.4 | 2 | 0.007 | 0.007 | 13.85
711 | 2008-07-30 | 140000 | 1 | 638.2 | 0.6 | -2.3 | 17.42 | 133.3 | 207.9 | -0.048 | 0 | -4.96 | -4.1 | 54.6 | 2.41 | 7.12 | 2 | 2.38 | 2 | 0.007 | 0.007 | 13.83
712 | 2008-07-30 | 150000 | 1 | 639 | 0.6 | -2.4 | 17.45 | 133.5 | 208.8 | -0.047 | 0 | -4.96 | -4.1 | 55.4 | 2.43 | 7.15 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.82
713 | 2008-07-30 | 160000 | 1 | 638.4 | 0.6 | -2.3 | 17.41 | 132.4 | 207.2 | -0.048 | 0 | -4.96 | -4.1 | 55.6 | 2.39 | 7.13 | 2 | 2.37 | 2 | 0.007 | 0.007 | 13.82
714 | 2008-07-30 | 170000 | 1 | 638.8 | 0.6 | -2.2 | 17.43 | 133 | 208.1 | -0.048 | 0 | -4.96 | -4.1 | 55.9 | 2.42 | 7.14 | 2 | 2.4 | 2 | 0.007 | 0.007 | 13.81
715 | 2008-07-30 | 180000 | 1 | 637.9 | 0.5 | -2.5 | 17.41 | 132.8 | 207.8 | -0.047 | 0 | -4.96 | -4.1 | 55.4 | 2.41 | 7.07 | 2 | 2.4 | 2 | 0.007 | 0.007 | 13.8
716 | 2008-07-30 | 190000 | 1 | 638 | 0.5 | -2.3 | 17.25 | 131.4 | 206.1 | -0.048 | 0 | -4.96 | -4.1 | 54.6 | 2.45 | 7.16 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.79
717 | 2008-07-30 | 200000 | 0 | 557.5 | 23.8 | -33.7 | 1.45 | 5.9 | 12 | -0.048 | 0 | -4.97 | -83.9 | 9.1 | 1.89 | 5.86 | 2.4 | 8.28 | 9.3 | 0.036 | 0.01 | 19.58
718 | 2008-07-30 | 210000 | 0 | 449.7 | 15.8 | -79.8 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -145.2 | 0.7 | -0.04 | 0.05 | -1.1 | -0.02 | -0.7 | 0.002 | 0 | 20.7
719 | 2008-07-30 | 220000 | 0 | 431.1 | 14.7 | -87.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -147.5 | 0.6 | -0.04 | 0 | -1.2 | -0.02 | -0.8 | 0.002 | 0 | 20.7
720 | 2008-07-30 | 230000 | 0 | 424 | 14 | -88.1 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -149.7 | 0.6 | -0.04 | 0 | -1.3 | -0.02 | -0.5 | 0.002 | 0 | 20.7
721 | 2008-07-31 | 0 | 0 | 418.7 | 13.1 | -90.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -152.1 | 0.5 | -0.05 | -0.01 | -1.4 | -0.02 | -0.7 | 0.002 | 0 | 20.71
722 | 2008-07-31 | 10000 | 0 | 413.2 | 12.6 | -82.4 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -149.3 | 0.6 | -0.05 | 0 | -1.5 | -0.02 | -0.6 | 0.002 | 0 | 20.7
723 | 2008-07-31 | 20000 | 0 | 408 | 11.9 | -85.4 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -148.8 | 0.6 | -0.05 | 0 | -1.4 | -0.02 | -0.7 | 0.002 | 0 | 20.7
724 | 2008-07-31 | 30000 | 0 | 407.1 | 10.8 | -90.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -146.8 | 0.7 | -0.04 | 0 | -1.3 | -0.03 | -0.8 | 0.002 | 0 | 20.7
725 | 2008-07-31 | 40000 | 1 | 557.5 | 21.5 | 6.4 | 6.09 | 15.8 | 16.2 | -0.049 | 0 | -4.96 | -19 | 1.3 | 9 | 26.7 | 12.8 | 41.42 | 58.9 | 0.217 | 0.048 | 17.16
726 | 2008-07-31 | 50000 | 1 | 615.4 | 17.6 | 23.5 | 10.73 | 57.3 | 87.9 | -0.051 | 0 | -4.96 | -5.2 | 35.7 | 9.31 | 27.13 | 9.9 | 47.3 | 50.1 | 0.185 | 0.037 | 15.14
727 | 2008-07-31 | 60000 | 1 | 638.3 | 3.2 | 8.9 | 19.64 | 158.7 | 237.7 | -0.049 | 0 | -4.96 | -31 | 80.6 | 3.34 | 9.43 | 2.3 | 9.69 | 4.1 | 0.015 | 0.008 | 12.15
728 | 2008-07-31 | 70000 | 1 | 639.4 | 0.5 | -2.3 | 19.53 | 156.7 | 235.7 | -0.051 | 0 | -4.97 | -4.1 | 70.8 | 2.44 | 8.11 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.71
729 | 2008-07-31 | 80000 | 1 | 642.5 | 0.6 | -2.2 | 19.3 | 154.7 | 233 | -0.05 | 0 | -4.96 | -4.1 | 68.6 | 2.46 | 7.99 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.69
730 | 2008-07-31 | 90000 | 1 | 651.1 | 0.6 | -2.5 | 19.2 | 153.3 | 232 | -0.049 | 0 | -4.96 | -4.1 | 65.5 | 2.47 | 8.69 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.68
731 | 2008-07-31 | 100000 | 1 | 650.2 | 0.6 | -2.1 | 19.45 | 155 | 234.9 | -0.049 | 0 | -4.96 | -4.1 | 82.4 | 2.56 | 8.81 | 2.1 | 2.54 | 2.1 | 0.008 | 0.008 | 13.65
732 | 2008-07-31 | 110000 | 1 | 666.2 | 0.5 | -2.1 | 21.8 | 177.8 | 266.5 | -0.034 | 0 | -4.96 | -3.9 | 133.4 | 2.54 | 12.19 | 2 | 2.51 | 2 | 0.007 | 0.007 | 13.43
733 | 2008-07-31 | 120000 | 1 | 664.3 | 0.5 | -2 | 21.69 | 177.1 | 264.7 | -0.052 | 0 | -4.97 | -3.9 | 128.4 | 2.53 | 11.99 | 2 | 2.51 | 2 | 0.007 | 0.007 | 13.45
734 | 2008-07-31 | 130000 | 1 | 663.8 | 0.5 | -2.3 | 21.55 | 176.6 | 263.9 | -0.05 | 0 | -4.96 | -3.9 | 126.5 | 2.54 | 13.51 | 2 | 2.53 | 2 | 0.007 | 0.007 | 13.45
735 | 2008-07-31 | 140000 | 1 | 663.2 | 0.5 | -2 | 21.54 | 175.7 | 262.9 | -0.05 | 0 | -4.96 | -3.9 | 124.6 | 2.54 | 11.74 | 2 | 2.52 | 2 | 0.007 | 0.007 | 13.44
736 | 2008-07-31 | 150000 | 1 | 662.2 | 0.5 | -2.2 | 21.54 | 175.3 | 262.1 | -0.051 | 0 | -4.96 | -3.9 | 123.2 | 2.55 | 11.67 | 2 | 2.52 | 2 | 0.007 | 0.007 | 13.44
737 | 2008-07-31 | 160000 | 1 | 663.1 | 0.5 | -1.9 | 21.45 | 174.8 | 262.2 | -0.05 | 0 | -4.96 | -3.9 | 123 | 2.51 | 11.58 | 2 | 2.49 | 2 | 0.007 | 0.007 | 13.45
738 | 2008-07-31 | 170000 | 1 | 652.2 | 0.4 | -2.3 | 19.12 | 152.6 | 231.5 | -0.049 | 0 | -4.96 | -4.1 | 61.8 | 2.43 | 7.52 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.67
739 | 2008-07-31 | 180000 | 1 | 646.7 | 0.4 | -2.2 | 18.74 | 148 | 226 | -0.049 | 0 | -4.96 | -4.1 | 61.4 | 2.47 | 7.42 | 2 | 2.46 | 2 | 0.007 | 0.007 | 13.67
740 | 2008-07-31 | 190000 | 1 | 647.2 | 0.4 | -2.2 | 18.94 | 150.4 | 228.6 | -0.05 | 0 | -4.96 | -4 | 65.3 | 2.45 | 7.51 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.66
741 | 2008-07-31 | 200000 | 1 | 649.5 | 0.4 | -2.3 | 19.19 | 153.2 | 232.3 | -0.049 | 0 | -4.96 | -4.1 | 66.7 | 2.47 | 7.62 | 2 | 2.46 | 2 | 0.007 | 0.007 | 13.67
742 | 2008-07-31 | 210000 | 1 | 652.3 | 0.4 | -1.9 | 19.18 | 153.2 | 232.7 | -0.049 | 0 | -4.96 | -4.1 | 66.1 | 2.45 | 7.62 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.68
743 | 2008-07-31 | 220000 | 1 | 640 | 0.3 | -2.5 | 17.4 | 134 | 208.6 | -0.05 | 0 | -4.96 | -4.1 | 52 | 2.5 | 6.85 | 2 | 2.48 | 2 | 0.008 | 0.007 | 13.71
744 | 2008-07-31 | 230000 | 1 | 638.7 | 0.3 | -2.1 | 17.49 | 134.5 | 208.9 | -0.048 | 0 | -4.96 | -4.1 | 56.1 | 2.42 | 6.97 | 2 | 2.38 | 2 | 0.007 | 0.007 | 13.7
745 | / | /
[7 empty] | July Total MW-hr |  | 41648.5
Excluding non-op hours
Used gas use column to confirm operation


## August CEMS data
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-01
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 12.5 | 0.3 | 1.1 | 7.17 | 0.3 | 0.3 | 0.7 | 647.6 | 149.6
1 | 2 | 2 | 12.5 | 0.2 | 0.8 | 7.16 | 0.3 | 0.3 | 0.7 | 647.2 | 149.1
2 | 2 | 2 | 12.5 | 0.2 | 0.8 | 7.16 | 0.3 | 0.3 | 0.7 | 648 | 149.9
3 | 2 | 2 | 12.5 | 0.2 | 0.8 | 7.15 | 0.2 | 0.3 | 0.5 | 648.4 | 149.8
4 | 2 | 2 | 12.5 | 0.2 | 0.8 | 7.14 | 0.3 | 0.3 | 0.7 | 648 | 149.4
5 | 2 | 2 | 10.9 | 0 | 0 | 7.14 | 0.3 | 0.3 | 0.5 | 648 | 149.4
6 | 2 | 2 | 12.7 | 0.5 | 1.7 | 7.13 | 0.3 | 0.3 | 0.7 | 648.4 | 152.2
7 | 1.9 | 2 | 12.5 | 0.6 | 2.4 | 7.13 | 0.5 | 0.3 | 1.2 | 665 | 176.1
8 | 2 | 2 | 12.5 | 0.6 | 2.2 | 7.12 | 0.4 | 0.3 | 1 | 666.2 | 176.4
9 | 2 | 2 | 12.5 | 0.5 | 2.1 | 7.12 | 0.4 | 0.3 | 1 | 665.8 | 175.6
10 | 2 | 2 | 12.5 | 0.5 | 2 | 7.11 | 0.4 | 0.3 | 1 | 665.8 | 175.8
11 | 1.9 | 2 | 12.5 | 0.5 | 1.9 | 7.11 | 0.4 | 0.3 | 1 | 665.8 | 175.9
12 | 2 | 2 | 12.5 | 0.5 | 1.8 | 7.11 | 0.4 | 0.3 | 1 | 664.6 | 175.7
13 | 2 | 2 | 12.5 | 0.4 | 1.7 | 7.1 | 0.5 | 0.3 | 1.2 | 664.2 | 175.7
14 | 1.9 | 2 | 12 | 0.4 | 1.6 | 7.1 | 0.4 | 0.3 | 0.9 | 661.1 | 168.1
15 | 1.7 | 2 | 10.4 | 0.4 | 1.6 | 7.09 | 0.4 | 0.3 | 1 | 663 | 170.1
16 | 2.1 | 2 | 13.9 | 0.4 | 1.5 | 7.09 | 0.3 | 0.3 | 0.8 | 664.2 | 169.9
17 | 2 | 2 | 12.5 | 0.4 | 1.5 | 7.08 | 0.5 | 0.3 | 1.2 | 664.2 | 175.7
18 | 1.9 | 2 | 12.4 | 0.4 | 1.4 | 7.08 | 0.4 | 0.3 | 1 | 663.8 | 174.2
19 | 2 | 2 | 12.5 | 0.3 | 1.1 | 7.07 | 0.2 | 0.3 | 0.5 | 648.4 | 148.7
20 | 2 | 2 | 11 | 0.3 | 1.1 | 7.07 | 0.3 | 0.3 | 0.7 | 647.2 | 149.6
21 | 2 | 2 | 11 | 0.3 | 1 | 7.06 | 0.3 | 0.3 | 0.7 | 647.2 | 149.6
22 | 2 | 2 | 11 | 0.3 | 1 | 7.06 | 0.3 | 0.3 | 0.7 | 648 | 150.1
23 | 2 | 2 | 11 | 0.3 | 0.9 | 7.05 | 0.3 | 0.4 | 0.7 | 647.2 | 149.6
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-02
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 10.9 | 0.3 | 0.8 | 7.05 | 0.3 | 0.4 | 0.7 | 647.2 | 149.4
1 | 2 | 2 | 11 | 0.2 | 0.8 | 7.04 | 0.3 | 0.4 | 0.7 | 647.6 | 149.5
2 | 2 | 2 | 11 | 0.2 | 0.8 | 7.04 | 0.3 | 0.4 | 0.7 | 647.6 | 149.9
3 | 2 | 2 | 11 | 0.2 | 0.7 | 7.03 | 0.3 | 0.4 | 0.7 | 647.6 | 149.6
4 | 2 | 2 | 11 | 0.2 | 0.7 | 7.03 | 0.3 | 0.4 | 0.7 | 647.2 | 149.6
5 | 1.9 | 2 | 11 | 0 | 0 | 7.02 | 0.3 | 0.4 | 0.5 | 646.5 | 149.3
6 | 2 | 2 | 11 | 0.4 | 1.2 | 7.02 | 0.3 | 0.4 | 0.7 | 647.2 | 149.6
7 | 2 | 2 | 12.6 | 0.6 | 2.1 | 7.01 | 0.3 | 0.3 | 0.7 | 646.5 | 150.5
8 | 2 | 2 | 14.3 | 0.6 | 2.4 | 7.01 | 0.4 | 0.3 | 1 | 665.8 | 177.3
9 | 2 | 2 | 12.5 | 0.6 | 2.2 | 7 | 0.4 | 0.3 | 1 | 667.8 | 176
10 | 2 | 2 | 14.3 | 0.5 | 2.1 | 7 | 0.4 | 0.3 | 1 | 667.4 | 176.1
11 | 2 | 2 | 12.5 | 0.5 | 2 | 6.99 | 0.4 | 0.3 | 1 | 667 | 175.8
12 | 2 | 2 | 14.3 | 0.5 | 1.9 | 6.99 | 0.4 | 0.3 | 1 | 666.2 | 176.2
13 | 2 | 2 | 12.5 | 0.5 | 1.9 | 6.98 | 0.4 | 0.3 | 1 | 665.4 | 175.9
14 | 2 | 2 | 14.3 | 0.5 | 1.8 | 6.98 | 0.4 | 0.3 | 1 | 664.6 | 175.7
15 | 2 | 2 | 14.3 | 0.4 | 1.7 | 6.97 | 0.4 | 0.3 | 1 | 663.8 | 175.7
16 | 1.9 | 2 | 12.5 | 0.4 | 1.6 | 6.97 | 0.4 | 0.3 | 1 | 663.8 | 176.1
17 | 2 | 2 | 14.3 | 0.4 | 1.6 | 6.96 | 0.4 | 0.3 | 1 | 665.4 | 175.7
18 | 2 | 2 | 12.4 | 0.4 | 1.5 | 6.96 | 0.4 | 0.3 | 1 | 665.4 | 175
19 | 2 | 2 | 11 | 0.4 | 1.2 | 6.95 | 0.2 | 0.3 | 0.5 | 648 | 149.4
20 | 2 | 2 | 11 | 0.4 | 1.2 | 6.95 | 0.2 | 0.3 | 0.5 | 646.9 | 149.9
21 | 2 | 2 | 11 | 0.3 | 1.2 | 6.94 | 0.2 | 0.3 | 0.5 | 646.5 | 149.6
22 | 2 | 2 | 11 | 0.3 | 1.1 | 6.94 | 0.2 | 0.3 | 0.5 | 647.6 | 150.3
23 | 2 | 2 | 11 | 0.3 | 1.1 | 6.93 | 0.2 | 0.3 | 0.5 | 647.6 | 150.3
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-03
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11 | 0.3 | 1 | 6.93 | 0.2 | 0.3 | 0.5 | 647.2 | 149.7
1 | 2 | 2 | 11 | 0.3 | 1 | 6.92 | 0.3 | 0.3 | 0.7 | 647.6 | 150.1
2 | 2 | 2 | 11 | 0.3 | 0.9 | 6.92 | 0.3 | 0.3 | 0.7 | 647.6 | 150.2
3 | 2 | 2 | 11 | 0.3 | 0.9 | 6.91 | 0.2 | 0.3 | 0.5 | 647.6 | 149.9
4 | 2 | 2 | 11 | 0.2 | 0.8 | 6.91 | 0.2 | 0.3 | 0.5 | 647.6 | 149.7
5 | 2 | 2 | 11 | 0 | 0 | 6.9 | 0.3 | 0.3 | 0.5 | 647.2 | 149.8
6 | 2 | 2 | 10.9 | 0.6 | 2 | 6.9 | 0.2 | 0.3 | 0.5 | 647.6 | 150.1
7 | 2 | 2 | 10.9 | 0.6 | 2.1 | 6.9 | 0.2 | 0.3 | 0.5 | 646.5 | 149
8 | 2 | 2 | 11 | 0.6 | 2.1 | 6.89 | 0.2 | 0.3 | 0.5 | 646.5 | 149.6
9 | 2 | 2 | 11 | 0.6 | 1.9 | 6.89 | 0.2 | 0.3 | 0.5 | 647.2 | 149.3
10 | 2 | 2 | 11 | 0.5 | 1.9 | 6.88 | 0.2 | 0.3 | 0.5 | 646.9 | 149.6
11 | 2 | 2 | 12.7 | 0.5 | 1.8 | 6.88 | 0.3 | 0.3 | 0.7 | 647.6 | 151.5
12 | 2 | 2 | 12.7 | 0.5 | 2 | 6.87 | 0.5 | 0.3 | 1.2 | 667.8 | 177.5
13 | 1.9 | 2 | 12.4 | 0.4 | 1.7 | 6.87 | 0.5 | 0.3 | 1.3 | 686.7 | 173.7
14 | 1.9 | 2 | 12.4 | 0.4 | 1.7 | 6.86 | 0.5 | 0.3 | 1.2 | 667.4 | 174.7
15 | 1.8 | 2 | 12.4 | 0.4 | 1.7 | 6.86 | 0.5 | 0.3 | 1.2 | 665.4 | 175
16 | 2 | 2 | 12.4 | 0.4 | 1.7 | 6.85 | 0.5 | 0.3 | 1.2 | 665.8 | 174.4
17 | 2 | 2 | 12.5 | 0.4 | 1.6 | 6.85 | 0.5 | 0.3 | 1.2 | 664.6 | 175.7
18 | 2 | 2 | 12.5 | 0.4 | 1.5 | 6.85 | 0.5 | 0.3 | 1.2 | 663.4 | 176.4
19 | 2 | 2 | 10.8 | 0.4 | 1.2 | 6.84 | 0.2 | 0.3 | 0.5 | 648.4 | 147
20 | 2 | 2 | 11 | 0.4 | 1.2 | 6.84 | 0.3 | 0.3 | 0.7 | 647.2 | 150.6
21 | 2 | 2 | 12.5 | 0.3 | 1.1 | 6.83 | 0.3 | 0.3 | 0.7 | 647.6 | 150.2
22 | 2 | 2 | 10.9 | 0.3 | 1.1 | 6.83 | 0.3 | 0.3 | 0.7 | 647.2 | 149.6
23 | 2 | 2 | 12.5 | 0.3 | 1 | 6.82 | 0.3 | 0.3 | 0.7 | 647.6 | 149.8
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-04
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 12.5 | 0.3 | 1 | 6.82 | 0.3 | 0.3 | 0.7 | 646.9 | 149.5
1 | 2 | 2 | 12.5 | 0.3 | 0.9 | 6.81 | 0.3 | 0.3 | 0.7 | 646.9 | 149.6
2 | 2 | 2 | 12.5 | 0.3 | 0.9 | 6.81 | 0.3 | 0.3 | 0.7 | 646.5 | 149.1
3 | 2 | 2 | 12.5 | 0.3 | 0.8 | 6.8 | 0.3 | 0.3 | 0.7 | 646.5 | 149.5
4 | 2 | 2 | 11 | 0.2 | 0.8 | 6.8 | 0.3 | 0.3 | 0.7 | 647.6 | 150.5
5 | 2 | 2 | 11 | 0 | 0 | 6.79 | 0.3 | 0.3 | 0.5 | 647.6 | 149.8
6 | 2 | 2 | 12.5 | 0.6 | 2 | 6.79 | 0.3 | 0.3 | 0.7 | 648 | 150.6
7 | 2 | 2 | 12.5 | 0.6 | 2.1 | 6.79 | 0.3 | 0.3 | 0.7 | 648 | 149.8
8 | 2 | 2 | 12.5 | 0.6 | 2 | 6.78 | 0.3 | 0.3 | 0.7 | 647.2 | 149.6
9 | 2 | 2 | 12.6 | 0.6 | 1.9 | 6.78 | 0.3 | 0.4 | 0.7 | 647.6 | 151.1
10 | 2 | 2 | 11.9 | 0.5 | 2 | 6.77 | 0.3 | 0.4 | 0.8 | 662.2 | 166.1
11 | 2.1 | 2 | 13.7 | 0.5 | 1.9 | 6.77 | 0.4 | 0.4 | 0.9 | 667 | 165.9
12 | 2 | 2 | 12.4 | 0.3 | 1.1 | 6.76 | 0.7 | 0.4 | 1.8 | 741.6 | 172.1
13 | 2 | 2 | 12.3 | 0.3 | 1 | 6.76 | 0.7 | 0.4 | 1.8 | 745.5 | 171
14 | 2 | 2 | 12.3 | 0.3 | 1 | 6.75 | 0.7 | 0.4 | 1.8 | 746.7 | 170.1
15 | 1.9 | 2 | 11.9 | 0.5 | 1.7 | 6.75 | 0.3 | 0.4 | 0.8 | 674.1 | 164.3
16 | 2 | 2 | 11.9 | 0.5 | 1.7 | 6.75 | 0.3 | 0.4 | 0.8 | 663.8 | 165.3
17 | 2 | 2 | 13.6 | 0.4 | 1.6 | 6.74 | 0.3 | 0.4 | 0.8 | 665.4 | 165.8
18 | 2 | 2 | 12 | 0.4 | 1.6 | 6.74 | 0.3 | 0.4 | 0.8 | 663.4 | 165.9
19 | 1.9 | 2 | 11.9 | 0.4 | 1.5 | 6.73 | 0.3 | 0.4 | 0.7 | 663 | 164.9
20 | 2 | 2 | 11.9 | 0.4 | 1.4 | 6.73 | 0.3 | 0.4 | 0.8 | 661.5 | 164.1
21 | 2 | 2 | 12.5 | 0.4 | 1.2 | 6.72 | 0.2 | 0.4 | 0.5 | 649.6 | 149
22 | 2 | 2 | 12.6 | 0.4 | 1.2 | 6.72 | 0.2 | 0.3 | 0.5 | 648 | 149.5
23 | 2 | 2 | 12.5 | 0.3 | 1.2 | 6.71 | 0.3 | 0.3 | 0.7 | 648.4 | 149.5
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-05
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 12.5 | 0.3 | 1.1 | 6.71 | 0.3 | 0.3 | 0.7 | 648.4 | 149.2
1 | 2 | 2 | 12.5 | 0.3 | 1 | 6.7 | 0.2 | 0.3 | 0.5 | 648.4 | 149.5
2 | 2 | 2 | 12.5 | 0.3 | 1 | 6.7 | 0.3 | 0.3 | 0.7 | 648.4 | 150.2
3 | 2 | 2 | 12.5 | 0.3 | 1 | 6.7 | 0.3 | 0.3 | 0.7 | 648.4 | 149.8
4 | 2 | 2 | 12.6 | 0.3 | 0.9 | 6.69 | 0.3 | 0.3 | 0.7 | 648.8 | 150.4
5 | 2 | 2 | 11 | 0 | 0 | 6.69 | 0.3 | 0.3 | 0.5 | 648.8 | 150.1
6 | 2 | 2 | 11 | 0.4 | 1.3 | 6.68 | 0.2 | 0.3 | 0.5 | 647.6 | 149.2
7 | 2 | 2 | 11 | 0.6 | 2.2 | 6.68 | 0.3 | 0.3 | 0.7 | 648.4 | 150.2
8 | 2 | 2 | 11 | 0.6 | 2.1 | 6.67 | 0.2 | 0.3 | 0.5 | 647.6 | 149.2
9 | 2 | 2 | 11 | 0.6 | 2 | 6.67 | 0.2 | 0.3 | 0.5 | 648.8 | 150
10 | 2 | 2 | 11 | 0.5 | 1.9 | 6.67 | 0.2 | 0.3 | 0.5 | 648.4 | 149.5
11 | 2 | 2 | 11.1 | 0.5 | 1.8 | 6.66 | 0.2 | 0.3 | 0.5 | 650.8 | 151.2
12 | 2 | 2 | 11.1 | 0.5 | 1.8 | 6.66 | 0.2 | 0.3 | 0.5 | 651.2 | 150.8
13 | 2 | 2 | 11.2 | 0.5 | 1.7 | 6.65 | 0.2 | 0.3 | 0.5 | 653.2 | 151.5
14 | 2 | 2 | 11.1 | 0.5 | 1.7 | 6.65 | 0.3 | 0.3 | 0.7 | 653.2 | 150.8
15 | 2 | 2 | 10.8 | 0.5 | 1.7 | 6.64 | 0.2 | 0.3 | 0.5 | 652 | 145 |  |  | 15:30 | 15:30
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-06
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 56.4 | 2 | 109.8 | 19.7 | 23.3 | 6.65 | 0 | 0.3 | 0 | 537.5 | 17.2WS | 3:04
4 | 41.4 | 2 | 139.6 | 22.3 | 45.6 | 6.66 | 0 | 0.3 | 0 | 615.7 | 60.4WS |  | 4:55 |  |  | ET 1:51
5 | 1.8 | 2 | 10.3 | 0 | 0 | 6.66 | 0.1 | 0.2 | 0.2 | 636.2 | 136.5
6 | 2.1 | 2 | 11.7 | 0 | 0 | 6.65 | 0.3 | 0.2 | 0.5 | 635.4 | 135.6
7 | 2 | 2 | 11 | 0.7 | 2.4 | 6.65 | 0.2 | 0.2 | 0.5 | 647.6 | 150.3
8 | 2 | 2 | 11.1 | 0.7 | 2.3 | 6.65 | 0.2 | 0.2 | 0.5 | 649.6 | 151.2
9 | 2 | 2 | 11 | 0.6 | 2.2 | 6.64 | 0.2 | 0.2 | 0.5 | 647.6 | 150.1
10 | 2 | 2 | 11 | 0.6 | 2.1 | 6.64 | 0.2 | 0.2 | 0.5 | 648 | 149.9
11 | 2 | 2 | 11.1 | 0.6 | 2 | 6.63 | 0.2 | 0.2 | 0.5 | 649.6 | 151.1
12 | 2 | 2 | 11.1 | 0.6 | 1.9 | 6.63 | 0.2 | 0.2 | 0.5 | 649.6 | 151.3
13 | 2.1 | 2 | 12.8 | 0.5 | 1.9 | 6.63 | 0.2 | 0.2 | 0.5 | 650.4 | 152.2
14 | 2 | 2 | 11.8 | 0.5 | 2 | 6.62 | 0.3 | 0.2 | 0.8 | 660.3 | 162.5
15 | 2.1 | 2 | 12.4 | 0.5 | 1.8 | 6.62 | 0.2 | 0.2 | 0.5 | 646.9 | 146.9
16 | 2 | 2 | 11.9 | 0.5 | 2 | 6.61 | 0.4 | 0.2 | 0.9 | 658.3 | 165.3
17 | 2 | 2 | 11.9 | 0.5 | 1.9 | 6.61 | 0.3 | 0.2 | 0.8 | 659.5 | 165
18 | 2 | 2 | 11.9 | 0.5 | 1.8 | 6.6 | 0.3 | 0.2 | 0.8 | 660.3 | 165.1
19 | 1.9 | 2 | 11.9 | 0.4 | 1.6 | 6.6 | 0.3 | 0.2 | 0.8 | 663.8 | 166.4
20 | 1.9 | 2 | 11.9 | 0.4 | 1.5 | 6.6 | 0.3 | 0.2 | 0.6 | 663.8 | 165.8
21 | 2 | 2 | 11 | 0.4 | 1.2 | 6.59 | 0.2 | 0.2 | 0.5 | 649.6 | 149.5
22 | 2 | 2 | 11 | 0.4 | 1.2 | 6.59 | 0.2 | 0.2 | 0.5 | 647.2 | 150.2
23 | 2 | 2 | 11 | 0.3 | 1.1 | 6.58 | 0.2 | 0.2 | 0.5 | 647.2 | 150.3
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-07
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11 | 0.3 | 1.1 | 6.58 | 0.2 | 0.2 | 0.5 | 646.9 | 149.9
1 | 2 | 2 | 11 | 0.3 | 1.1 | 6.57 | 0.2 | 0.2 | 0.5 | 647.2 | 150.1
2 | 2 | 2 | 11 | 0.3 | 1 | 6.57 | 0.2 | 0.2 | 0.5 | 647.6 | 150.8
3 | 2 | 2 | 11 | 0.3 | 1 | 6.57 | 0.2 | 0.2 | 0.5 | 647.6 | 150.3
4 | 2 | 2 | 11 | 0.3 | 1 | 6.56 | 0.2 | 0.2 | 0.5 | 646.9 | 149.8
5 | 1.8 | 2 | 11.1 | 0 | 0 | 6.56 | 0.4 | 0.2 | 0.9 | 648.4 | 151.7
6 | 1.9 | 2 | 11.1 | 0 | 0 | 6.55 | 0.3 | 0.2 | 0.5 | 647.6 | 152.2
7 | 2 | 2 | 14.3 | 0.8 | 3.2 | 6.55 | 0.4 | 0.3 | 1 | 663.4 | 175.8
8 | 2 | 2 | 12.5 | 0.7 | 2.9 | 6.55 | 0.3 | 0.3 | 0.8 | 665.4 | 174.5
9 | 2 | 2 | 14.2 | 0.7 | 2.8 | 6.54 | 0.4 | 0.3 | 1 | 665.8 | 174.4
10 | 2 | 2 | 12.4 | 0.7 | 2.6 | 6.54 | 0.4 | 0.3 | 1 | 664.2 | 174.9
11 | 2 | 2 | 12.4 | 0.6 | 2.5 | 6.53 | 0.4 | 0.3 | 1 | 663 | 174.5
12 | 2 | 2 | 12.5 | 0.6 | 2.4 | 6.53 | 0.5 | 0.3 | 1.2 | 663.4 | 174.7
13 | 2 | 2 | 12.4 | 0.6 | 2.3 | 6.53 | 0.5 | 0.3 | 1.2 | 663 | 174.2
14 | 2 | 2 | 11 | 0.6 | 1.9 | 6.52 | 0.2 | 0.3 | 0.5 | 650 | 149.5
15 | 2 | 2 | 11.1 | 0.6 | 2 | 6.52 | 0.2 | 0.3 | 0.5 | 648.8 | 151.5
16 | 2 | 2 | 11.1 | 0.6 | 1.9 | 6.51 | 0.2 | 0.3 | 0.5 | 650 | 151.2
17 | 2 | 2 | 11.1 | 0.5 | 1.8 | 6.51 | 0.2 | 0.3 | 0.5 | 648.8 | 151.1
18 | 2 | 2 | 12.7 | 0.5 | 1.8 | 6.5 | 0.3 | 0.3 | 0.7 | 649.6 | 153
19 | 2 | 2 | 12.4 | 0.5 | 1.9 | 6.5 | 0.5 | 0.3 | 1.2 | 661.8 | 173.6
20 | 1.9 | 2 | 12.3 | 0.4 | 1.6 | 6.5 | 0.4 | 0.3 | 1 | 663.4 | 173.2
21 | 2 | 2 | 12.3 | 0.4 | 1.5 | 6.49 | 0.3 | 0.3 | 0.8 | 665 | 173.4
22 | 2 | 2 | 14.1 | 0.4 | 1.4 | 6.49 | 0.3 | 0.3 | 0.8 | 665.8 | 173
23 | 1.9 | 2 | 12.3 | 0.3 | 1.3 | 6.48 | 0.4 | 0.3 | 1 | 665.4 | 172.9
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-08
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 12.4 | 0.3 | 1.3 | 6.48 | 0.4 | 0.3 | 1 | 666.6 | 173.6
1 | 2.1 | 2 | 12.6 | 0.3 | 1 | 6.48 | 0.2 | 0.3 | 0.5 | 650.4 | 151
2 | 2 | 2 | 11.1 | 0.3 | 1 | 6.47 | 0.3 | 0.3 | 0.7 | 648 | 151.6
3 | 2 | 2 | 11.1 | 0.3 | 1 | 6.47 | 0.3 | 0.3 | 0.7 | 648.4 | 151.5
4 | 2 | 2 | 11.1 | 0.3 | 1 | 6.46 | 0.3 | 0.3 | 0.7 | 648.4 | 151.6
5 | 1.8 | 2 | 11.1 | 0 | 0 | 6.46 | 0.4 | 0.3 | 0.9 | 648.8 | 151.8
6 | 1.9 | 2 | 12.4 | 0 | 0 | 6.46 | 0.5 | 0.3 | 1.2 | 661.1 | 174.4
7 | 2 | 2 | 12.4 | 0.8 | 3.1 | 6.45 | 0.4 | 0.3 | 1 | 666.6 | 174.6
8 | 2 | 2 | 14.2 | 0.8 | 3 | 6.45 | 0.4 | 0.4 | 1 | 667.4 | 174.7
9 | 2 | 2 | 14.2 | 0.7 | 2.8 | 6.44 | 0.4 | 0.4 | 1 | 667.4 | 174.6
10 | 2 | 2 | 12.4 | 0.7 | 2.7 | 6.44 | 0.4 | 0.4 | 1 | 667.4 | 174.1
11 | 2 | 2 | 14.2 | 0.7 | 2.6 | 6.44 | 0.4 | 0.4 | 1 | 666.6 | 174.2
12 | 2 | 2 | 14.2 | 0.6 | 2.4 | 6.43 | 0.4 | 0.3 | 1 | 666.2 | 174.3
13 | 2 | 2 | 14.1 | 0.6 | 2.4 | 6.43 | 0.4 | 0.3 | 1 | 665.4 | 172.3
14 | 2 | 2 | 12.4 | 0.6 | 2.3 | 6.42 | 0.5 | 0.4 | 1.2 | 664.2 | 173.3
15 | 1.9 | 2 | 12.4 | 0.6 | 2.3 | 6.42 | 0.5 | 0.4 | 1.2 | 663.8 | 173.6
16 | 2 | 2 | 12.3 | 0.6 | 2.2 | 6.42 | 0.5 | 0.4 | 1.1 | 669 | 172.3
17 | 2 | 2 | 12.5 | 0.5 | 2.1 | 6.41 | 0.5 | 0.4 | 1.2 | 666.6 | 174.8
18 | 2 | 2 | 12.5 | 0.5 | 2 | 6.41 | 0.5 | 0.4 | 1.2 | 664.2 | 176
19 | 2 | 2 | 12.5 | 0.5 | 1.9 | 6.4 | 0.5 | 0.4 | 1.2 | 666.2 | 176.4
20 | 2 | 2 | 12.5 | 0.4 | 1.7 | 6.4 | 0.5 | 0.4 | 1.2 | 665.8 | 176.1
21 | 1.9 | 2 | 11 | 0.4 | 1.4 | 6.4 | 0.2 | 0.4 | 0.5 | 649.6 | 149.8
22 | 2 | 2 | 11 | 0.4 | 1.4 | 6.39 | 0.2 | 0.4 | 0.5 | 649.2 | 150.6 |  |  | 22:59
23 | 37.5 | 2 | 81.1 | 20.8 | 27.4 | 6.4 | 0 | 0.4 | 0 | 635.8 | 32.8SD |  |  |  | 23:16
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-09
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 0 | 2 | 0 | 1 | 0.1 | 6.4 | 0 | 0.4 | 0 | 468.1 | 0.4HS
4 | 48.4 | 2 | 139.2 | 22.8 | 40 | 6.41 | 0 | 0.4 | 0 | 578.6 | 45.9HS | 4:02 | 4:58 |  |  | ET 0:56
5 | 1.7 | 2 | 10.2 | 0.3 | 1.3 | 6.41 | 0.3 | 0.4 | 0.8 | 644.9 | 164.6
6 | 1.8 | 2 | 11 | 0 | 0 | 6.4 | 0.3 | 0.4 | 0.6 | 650 | 150.5
7 | 2 | 2 | 11.1 | 0.6 | 2.2 | 6.4 | 0.3 | 0.4 | 0.7 | 649.2 | 150.9
8 | 2 | 2 | 11.1 | 0.9 | 3 | 6.39 | 0.3 | 0.4 | 0.7 | 650.4 | 151.2
9 | 2 | 2 | 11 | 0.8 | 2.9 | 6.39 | 0.2 | 0.4 | 0.5 | 649.2 | 150.6
10 | 2 | 2 | 11.1 | 0.8 | 2.8 | 6.39 | 0.2 | 0.4 | 0.5 | 649.6 | 150.8
11 | 2 | 2 | 11.1 | 0.8 | 2.6 | 6.38 | 0.2 | 0.4 | 0.5 | 650.4 | 151.2
12 | 2 | 2 | 11 | 0.7 | 2.5 | 6.38 | 0.2 | 0.4 | 0.5 | 649.6 | 150.4
13 | 2 | 2 | 11.1 | 0.7 | 2.4 | 6.38 | 0.3 | 0.4 | 0.7 | 649.2 | 151
14 | 2 | 2 | 11 | 0.7 | 2.4 | 6.37 | 0.3 | 0.3 | 0.5 | 649.2 | 150.6
15 | 2 | 2 | 11 | 0.6 | 2.2 | 6.37 | 0.3 | 0.3 | 0.5 | 648.4 | 150.5
16 | 2 | 2 | 11 | 0.6 | 2.2 | 6.36 | 0.3 | 0.3 | 0.5 | 648.8 | 150.8
17 | 2 | 2 | 11.1 | 0.6 | 2 | 6.36 | 0.3 | 0.3 | 0.5 | 647.6 | 151
18 | 2 | 2 | 11.1 | 0.6 | 1.9 | 6.36 | 0.3 | 0.3 | 0.5 | 648.4 | 151.7
19 | 2 | 2 | 11.1 | 0.5 | 1.8 | 6.35 | 0.3 | 0.3 | 0.5 | 648 | 150.8
20 | 2 | 2 | 11 | 0.5 | 1.7 | 6.35 | 0.3 | 0.3 | 0.5 | 648 | 149.7
21 | 1.9 | 2 | 9.5 | 0.5 | 1.5 | 6.35 | 0.3 | 0.3 | 0.5 | 632.6 | 120.7
22 | 2 | 2 | 9.6 | 0.5 | 1.6 | 6.34 | 0.3 | 0.3 | 0.5 | 629.9 | 123
23 | 1.9 | 2 | 11.1 | 0.5 | 1.6 | 6.34 | 0.3 | 0.3 | 0.5 | 649.6 | 153.1
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-10
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11.1 | 0.4 | 1.4 | 6.33 | 0.3 | 0.3 | 0.5 | 650.4 | 151.3
1 | 2 | 2 | 11 | 0.4 | 1.4 | 6.33 | 0.3 | 0.3 | 0.5 | 650.4 | 150.2
2 | 2 | 2 | 11 | 0.4 | 1.3 | 6.33 | 0.3 | 0.3 | 0.5 | 650 | 150.4
3 | 2 | 2 | 11.1 | 0.4 | 1.2 | 6.32 | 0.3 | 0.3 | 0.5 | 650.4 | 151
4 | 2 | 2 | 11.1 | 0.4 | 1.2 | 6.32 | 0.3 | 0.3 | 0.5 | 651.2 | 151.9
5 | 2 | 2 | 11 | 0.3 | 1.2 | 6.31 | 0.3 | 0.3 | 0.5 | 650.4 | 150.6
6 | 2 | 2 | 11.1 | 0.3 | 1.2 | 6.31 | 0.3 | 0.3 | 0.5 | 651.6 | 151.1
7 | 2 | 2 | 11 | 0.3 | 1.1 | 6.31 | 0.3 | 0.3 | 0.5 | 650.4 | 151
8 | 1.9 | 2 | 11.1 | 0 | 0 | 6.3 | 0.3 | 0.3 | 0.6 | 651.2 | 151.2
9 | 2 | 2 | 11 | 0.7 | 2.3 | 6.3 | 0.3 | 0.3 | 0.5 | 649.6 | 150.1
10 | 2 | 2 | 11 | 0.9 | 3.1 | 6.3 | 0.3 | 0.3 | 0.5 | 650 | 150.4
11 | 2 | 2 | 11.1 | 0.9 | 3 | 6.29 | 0.3 | 0.3 | 0.5 | 651.2 | 151.3
12 | 2 | 2 | 11.1 | 0.8 | 3 | 6.29 | 0.3 | 0.3 | 0.5 | 650.4 | 151.5
13 | 2 | 2 | 11.1 | 0.8 | 2.7 | 6.28 | 0.3 | 0.3 | 0.5 | 650.4 | 151.1
14 | 2 | 2 | 11.1 | 0.8 | 2.6 | 6.28 | 0.3 | 0.3 | 0.5 | 650 | 151.1
15 | 2 | 2 | 11.1 | 0.7 | 2.5 | 6.28 | 0.3 | 0.3 | 0.5 | 650 | 150.9
16 | 2 | 2 | 11 | 0.7 | 2.4 | 6.27 | 0.3 | 0.3 | 0.5 | 649.2 | 149.9
17 | 2 | 2 | 11.1 | 0.7 | 2.3 | 6.27 | 0.3 | 0.3 | 0.5 | 650.4 | 151.8
18 | 2 | 2 | 11.1 | 0.6 | 2.2 | 6.27 | 0.3 | 0.3 | 0.5 | 650.8 | 151.3
19 | 2 | 2 | 11.1 | 0.6 | 2.1 | 6.26 | 0.3 | 0.3 | 0.5 | 650 | 151.6
20 | 2 | 2 | 11.1 | 0.6 | 1.9 | 6.26 | 0.3 | 0.3 | 0.5 | 649.6 | 151.2
21 | 2 | 2 | 11 | 0.5 | 1.8 | 6.26 | 0.3 | 0.3 | 0.5 | 649.6 | 150.6
22 | 2 | 2 | 11.1 | 0.5 | 1.8 | 6.25 | 0.2 | 0.3 | 0.5 | 649.2 | 151.5
23 | 2 | 2 | 11 | 0.5 | 1.7 | 6.25 | 0.3 | 0.3 | 0.7 | 649.2 | 150.6
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-11
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11 | 0.5 | 1.7 | 6.24 | 0.3 | 0.3 | 0.5 | 648.8 | 150.6
1 | 2 | 2 | 11.1 | 0.5 | 1.6 | 6.24 | 0.3 | 0.3 | 0.5 | 648.8 | 151.2
2 | 2 | 2 | 11 | 0.4 | 1.5 | 6.24 | 0.2 | 0.3 | 0.5 | 649.6 | 150.4
3 | 2 | 2 | 11 | 0.4 | 1.5 | 6.23 | 0.2 | 0.3 | 0.5 | 649.2 | 150.3
4 | 2 | 2 | 11.1 | 0.4 | 1.4 | 6.23 | 0.2 | 0.3 | 0.5 | 650.8 | 152
5 | 2 | 2 | 11 | 0.4 | 1.3 | 6.23 | 0.2 | 0.3 | 0.5 | 651.2 | 150.8
6 | 2 | 2 | 11 | 0.4 | 1.3 | 6.22 | 0.2 | 0.3 | 0.5 | 649.2 | 150.1
7 | 2 | 2 | 11 | 0 | 0 | 6.22 | 0.3 | 0.3 | 0.6 | 649.6 | 150.2
8 | 2.1 | 2 | 12.7 | 0.3 | 1.1 | 6.21 | 0.3 | 0.3 | 0.7 | 649.6 | 151.5
9 | 2 | 2 | 12.5 | 0.8 | 3.2 | 6.21 | 0.5 | 0.3 | 1.2 | 664.2 | 174.2
10 | 2.1 | 2 | 14.1 | 0.7 | 2.9 | 6.21 | 0.5 | 0.3 | 1.2 | 664.2 | 172.6
11 | 1.9 | 2 | 12.4 | 0.7 | 2.8 | 6.2 | 0.5 | 0.3 | 1.2 | 664.6 | 173.6
12 | 2 | 2 | 12.4 | 0.7 | 2.6 | 6.2 | 0.5 | 0.3 | 1.2 | 665 | 173.2
13 | 2.1 | 2 | 14.2 | 0.6 | 2.5 | 6.2 | 0.5 | 0.3 | 1.2 | 665.4 | 173.4
14 | 2 | 2 | 12.5 | 0.6 | 2.4 | 6.19 | 0.5 | 0.3 | 1.2 | 664.6 | 173.8
15 | 2 | 2 | 14.2 | 0.5 | 2.1 | 6.19 | 0.5 | 0.3 | 1.3 | 695.8 | 173
16 | 2 | 2 | 14.2 | 0.5 | 2 | 6.19 | 0.5 | 0.3 | 1.3 | 697.8 | 172.4
17 | 2 | 2 | 12.4 | 0.5 | 1.9 | 6.18 | 0.5 | 0.4 | 1.3 | 697.4 | 172.3
18 | 2 | 2 | 12.4 | 0.4 | 1.7 | 6.18 | 0.5 | 0.4 | 1.3 | 698.2 | 172.3
19 | 2 | 2 | 14.2 | 0.4 | 1.6 | 6.18 | 0.5 | 0.4 | 1.3 | 694.6 | 172.9
20 | 2 | 2 | 12.3 | 0.4 | 1.5 | 6.17 | 0.5 | 0.4 | 1.3 | 691.8 | 172
21 | 2 | 2 | 12.5 | 0.4 | 1.2 | 6.17 | 0.2 | 0.4 | 0.5 | 652.4 | 150
22 | 2 | 2 | 12.5 | 0.4 | 1.2 | 6.16 | 0.2 | 0.4 | 0.5 | 648.8 | 149.1
23 | 36.1 | 2 | 76 | 23.4 | 29.9 | 6.18 | 0 | 0.4 | 0 | 635.4 | 31.3SD |  |  | 23:02 | 23:19
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-12
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 45.2 | 2 | 97.9 | 47.1 | 62.3 | 6.2 | 0 | 0.4 | 0 | 583.7 | 23.1HS | 3:08
4 | 40.8 | 2 | 138.2 | 21.2 | 43.8 | 6.21 | 0 | 0.4 | 0 | 612.1 | 61.6HS |  | 4:59 |  |  | ET 1:51
5 | 1.8 | 2 | 12.1 | 0.2 | 0.9 | 6.21 | 0.2 | 0.4 | 0.6 | 657.1 | 169
6 | 2 | 2 | 12.1 | 0.2 | 0.6 | 6.2 | 0.2 | 0.4 | 0.6 | 667.8 | 168.3
7 | 2 | 2 | 11.9 | 0.1 | 0.5 | 6.2 | 0.2 | 0.4 | 0.6 | 666.6 | 166.8
8 | 1.9 | 2 | 11.9 | 0 | 0 | 6.2 | 0.3 | 0.4 | 0.6 | 666.2 | 166.3
9 | 2 | 2 | 12 | 0.5 | 1.9 | 6.19 | 0.2 | 0.4 | 0.6 | 667 | 167.1
10 | 2.1 | 2 | 13.7 | 0.8 | 3 | 6.19 | 0.2 | 0.4 | 0.6 | 667.4 | 167.9
11 | 2.1 | 2 | 14.2 | 0.6 | 2.3 | 6.18 | 0.7 | 0.4 | 1.6 | 707.2 | 173.7
12 | 2 | 2 | 12.4 | 0.5 | 2.1 | 6.18 | 0.7 | 0.4 | 1.6 | 721.1 | 172.9
13 | 2 | 2 | 14.1 | 0.4 | 1.7 | 6.18 | 0.7 | 0.4 | 1.7 | 730.1 | 171.2
14 | 2 | 2 | 12.3 | 0.4 | 1.5 | 6.17 | 0.8 | 0.4 | 1.8 | 736.1 | 169.4
15 | 1.9 | 2 | 12.2 | 0.4 | 1.4 | 6.17 | 0.8 | 0.4 | 1.8 | 736.4 | 168.8
16 | 2.1 | 2 | 14.1 | 0.3 | 1.3 | 6.17 | 1.4 | 0.5 | 3.3 | 735.3 | 172.7
17 | 1.4 | 2 | 8.8 | 0.3 | 1.2 | 6.16 | 1.2 | 0.5 | 3 | 736.4 | 172.7
18 | 1.7 | 2 | 10.3 | 0.4 | 1.5 | 6.16 | 0.6 | 0.5 | 1.4 | 696.2 | 166.5
19 | 2 | 2 | 12.5 | 0.4 | 1.6 | 6.16 | 0.5 | 0.5 | 1.1 | 675.7 | 175.5
20 | 1.9 | 1.9 | 12.3 | 0.3 | 1.2 | 6.15 | 0.5 | 0.5 | 1.1 | 699 | 171.7
21 | 2 | 1.9 | 12.6 | 0.3 | 1.1 | 6.15 | 0.2 | 0.5 | 0.5 | 652.8 | 149.9
22 | 2 | 1.9 | 11.1 | 0.3 | 1.1 | 6.14 | 0.3 | 0.5 | 0.7 | 652.4 | 151.6
23 | 2 | 1.9 | 12.1 | 0.3 | 1.1 | 6.14 | 0.2 | 0.5 | 0.6 | 665.8 | 169.1
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-13
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 1.9 | 12.1 | 0.3 | 1 | 6.14 | 0.2 | 0.5 | 0.6 | 667.4 | 169.2
1 | 2 | 1.9 | 12.1 | 0.2 | 0.8 | 6.13 | 0.2 | 0.5 | 0.6 | 667.4 | 169.7
2 | 2 | 2 | 12.1 | 0.2 | 0.8 | 6.13 | 0.2 | 0.5 | 0.6 | 666.2 | 169.2
3 | 2 | 2 | 12.2 | 0.2 | 0.8 | 6.13 | 0.2 | 0.5 | 0.6 | 667 | 169.9
4 | 2 | 2 | 12.1 | 0.2 | 0.7 | 6.12 | 0.3 | 0.5 | 0.6 | 667.4 | 169.6
5 | 2 | 2 | 12 | 0.2 | 0.6 | 6.12 | 0.2 | 0.5 | 0.6 | 665.8 | 167.9
6 | 2.2 | 2 | 13.8 | 0.2 | 0.6 | 6.12 | 0.3 | 0.5 | 0.8 | 666.2 | 168.9
7 | 1.9 | 2 | 12.6 | 0 | 0 | 6.11 | 0.4 | 0.5 | 1 | 669.3 | 177
8 | 2 | 2 | 14.3 | 0.3 | 1 | 6.11 | 0.5 | 0.5 | 1.3 | 700.9 | 175
9 | 2 | 2 | 12.5 | 0.7 | 2.6 | 6.1 | 0.7 | 0.5 | 1.6 | 710 | 174.4
10 | 1.8 | 2 | 12.4 | 0.6 | 2.3 | 6.1 | 0.7 | 0.5 | 1.7 | 718.7 | 172
11 | 1.8 | 1.9 | 12.3 | 0.5 | 2 | 6.1 | 0.7 | 0.5 | 1.7 | 723 | 170.3
12 | 1.8 | 1.9 | 12.3 | 0.5 | 1.9 | 6.09 | 0.7 | 0.5 | 1.7 | 719.5 | 170.3
13 | 1.7 | 1.9 | 10.4 | 0.4 | 1.6 | 6.09 | 0.9 | 0.5 | 2.1 | 742.4 | 165.5
14 | 1.7 | 1.9 | 10.7 | 0.4 | 1.7 | 6.09 | 0.8 | 0.5 | 1.8 | 734.9 | 171.2
15 | 1.8 | 1.9 | 10.6 | 0.4 | 1.7 | 6.08 | 1 | 0.5 | 2.5 | 732.9 | 173.9
16 | 2.1 | 1.9 | 14.1 | 0.4 | 1.5 | 6.08 | 1.1 | 0.5 | 2.6 | 736.8 | 176
17 | 1.8 | 1.9 | 12 | 0.3 | 1.2 | 6.08 | 1.1 | 0.5 | 2.6 | 755.4 | 165.4
18 | 3.5 | 2 | 22.5 | 0.3 | 1.1 | 6.07 | 1.5 | 0.6 | 3.6 | 755.8 | 167.1
19 | 1.9 | 2 | 12.7 | 0.3 | 1.1 | 6.07 | 1.4 | 0.6 | 3.4 | 767.2 | 181.9
20 | 2.1 | 2 | 14.8 | 0.3 | 1.1 | 6.07 | 1.3 | 0.6 | 3.3 | 766.8 | 187.1
21 | 1.6 | 2 | 10.1 | 0.3 | 1.3 | 6.06 | 0.8 | 0.7 | 1.8 | 684.3 | 163
22 | 1.6 | 2 | 10.3 | 0.4 | 1.4 | 6.06 | 0.5 | 0.7 | 1.2 | 665 | 168.6
23 | 1.6 | 2 | 9.4 | 0.3 | 1.1 | 6.06 | 0.5 | 0.7 | 1 | 652.8 | 148.7
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-14
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 12.6 | 0.3 | 1.1 | 6.05 | 0.3 | 0.7 | 0.7 | 651.6 | 150.9
1 | 2 | 2 | 12.7 | 0.3 | 1 | 6.05 | 0.4 | 0.7 | 0.9 | 650.4 | 151.1
2 | 2 | 2 | 12.6 | 0.3 | 1 | 6.04 | 0.4 | 0.7 | 0.9 | 650.8 | 151.5
3 | 2 | 2 | 11.2 | 0.3 | 1 | 6.04 | 0.4 | 0.7 | 0.9 | 654 | 154.7
4 | 2 | 2 | 12.7 | 0.2 | 0.8 | 6.04 | 0.4 | 0.7 | 0.9 | 652 | 151.5
5 | 2 | 2 | 12.2 | 0.2 | 0.8 | 6.03 | 0.4 | 0.7 | 1 | 663.8 | 169.6
6 | 2 | 1.9 | 12.1 | 0.2 | 0.6 | 6.03 | 0.4 | 0.7 | 1 | 667.8 | 168.3
7 | 2 | 2 | 12 | 0.1 | 0.5 | 6.03 | 0.4 | 0.7 | 1 | 667 | 166.5
8 | 1.9 | 1.9 | 12 | 0 | 0 | 6.02 | 0.3 | 0.7 | 0.8 | 665.4 | 166.4
9 | 1.9 | 1.9 | 12.1 | 0.6 | 2.2 | 6.02 | 0.5 | 0.7 | 1.1 | 662.6 | 166.5
10 | 1.8 | 1.9 | 12 | 0.8 | 3 | 6.02 | 0.5 | 0.7 | 1.1 | 661.5 | 166.2
11 | 2 | 2 | 12.2 | 0.7 | 2.9 | 6.01 | 0.5 | 0.7 | 1.1 | 668.6 | 168
12 | 2.1 | 2 | 14 | 0.5 | 2 | 6.01 | 0.7 | 0.7 | 1.6 | 738.8 | 168.8
13 | 2 | 2 | 12.2 | 0.5 | 1.8 | 6.01 | 0.7 | 0.7 | 1.8 | 745.9 | 168.2
14 | 2 | 2 | 12.2 | 0.4 | 1.7 | 6 | 0.8 | 0.7 | 1.9 | 748.3 | 167.6
15 | 2 | 2 | 12.2 | 0.4 | 1.7 | 6 | 0.8 | 0.7 | 1.9 | 750.3 | 166.6
16 | 2 | 2 | 12.2 | 0.4 | 1.5 | 6 | 0.8 | 0.7 | 1.9 | 751.8 | 166.2
17 | 2 | 2 | 12.2 | 0.4 | 1.5 | 5.99 | 0.8 | 0.6 | 1.9 | 751.4 | 167.1
18 | 2 | 1.9 | 12.2 | 0.4 | 1.3 | 5.99 | 0.8 | 0.6 | 1.9 | 748.7 | 167.6
19 | 2 | 1.9 | 12.3 | 0.3 | 1.2 | 5.99 | 0.7 | 0.6 | 1.8 | 745.9 | 169.1
20 | 2 | 1.9 | 12.4 | 0.2 | 0.9 | 5.98 | 0.8 | 0.6 | 1.9 | 756.2 | 170.7
21 | 1.9 | 2 | 12.4 | 0.4 | 1.4 | 5.98 | 0.6 | 0.6 | 1.4 | 704.9 | 172.1
22 | 2 | 2 | 12.4 | 0.3 | 1.2 | 5.98 | 0.6 | 0.6 | 1.4 | 699.3 | 173
23 | 2 | 2 | 12 | 0.3 | 1.2 | 5.97 | 0.4 | 0.6 | 1 | 667.8 | 166.9
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-15
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 13.8 | 0.3 | 1.2 | 5.97 | 0.4 | 0.6 | 1 | 664.2 | 167.5
1 | 2 | 2 | 13.8 | 0.3 | 1 | 5.97 | 0.4 | 0.6 | 1 | 664.2 | 167.7
2 | 2 | 2 | 13.8 | 0.3 | 0.9 | 5.96 | 0.4 | 0.6 | 1 | 666.2 | 168
3 | 2 | 2 | 12.1 | 0.2 | 0.8 | 5.96 | 0.4 | 0.6 | 1 | 666.2 | 167.8
4 | 2 | 2 | 13.8 | 0.2 | 0.7 | 5.95 | 0.4 | 0.6 | 1 | 666.6 | 168.2
5 | 2 | 2 | 12 | 0.2 | 0.6 | 5.95 | 0.4 | 0.6 | 1 | 666.6 | 167.3
6 | 2 | 2 | 12 | 0.2 | 0.6 | 5.95 | 0.4 | 0.6 | 1 | 666.6 | 167.8
7 | 2.2 | 2 | 13.8 | 0.2 | 0.6 | 5.94 | 0.4 | 0.6 | 0.9 | 670.5 | 167.3
8 | 1.9 | 2 | 12.5 | 0 | 0 | 5.94 | 0.8 | 0.6 | 1.9 | 744.3 | 173.5
9 | 2 | 2 | 12.5 | 0.3 | 1.3 | 5.94 | 0.8 | 0.6 | 2 | 748.7 | 172.3
10 | 2 | 2 | 12.3 | 0.5 | 2 | 5.93 | 0.8 | 0.6 | 1.9 | 752.2 | 170.6
11 | 2 | 2 | 12.3 | 0.5 | 1.9 | 5.93 | 0.9 | 0.6 | 2 | 755.8 | 169.5
12 | 2 | 2 | 12.2 | 0.5 | 1.8 | 5.93 | 0.9 | 0.6 | 2 | 757.8 | 168.2
13 | 2 | 2 | 12.2 | 0.4 | 1.7 | 5.92 | 0.8 | 0.6 | 2 | 760.1 | 167.4
14 | 2 | 2 | 12.2 | 0.4 | 1.6 | 5.92 | 0.8 | 0.6 | 2 | 761.7 | 166.5
15 | 2 | 2 | 12.2 | 0.4 | 1.5 | 5.92 | 0.9 | 0.6 | 2.1 | 761.7 | 166.5
16 | 2 | 2 | 12.2 | 0.4 | 1.4 | 5.91 | 0.8 | 0.6 | 2 | 761.7 | 166.5
17 | 2 | 2 | 12.2 | 0.3 | 1.3 | 5.91 | 0.8 | 0.6 | 2 | 760.9 | 167.3
18 | 2 | 2 | 12.2 | 0.3 | 1.2 | 5.91 | 0.8 | 0.6 | 2 | 758.2 | 167.9
19 | 2 | 2 | 12.3 | 0.3 | 1 | 5.9 | 0.9 | 0.7 | 2 | 757.4 | 169.3
20 | 2 | 2 | 12.3 | 0.2 | 0.9 | 5.9 | 0.8 | 0.7 | 1.9 | 753.4 | 170.9
21 | 2 | 2 | 12.5 | 0.2 | 0.8 | 5.9 | 0.8 | 0.7 | 1.9 | 750.7 | 172.1
22 | 2 | 2 | 12.5 | 0.2 | 0.7 | 5.89 | 0.8 | 0.7 | 2 | 747.5 | 173.1
23 | 1.9 | 2 | 11.8 | 0.3 | 1.2 | 5.89 | 0.4 | 0.7 | 0.9 | 670.5 | 164.1
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-16
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11.9 | 0.3 | 1.2 | 5.89 | 0.4 | 0.7 | 0.9 | 665.4 | 166.2
1 | 2 | 2 | 11.9 | 0.3 | 1.2 | 5.88 | 0.4 | 0.7 | 0.9 | 665.4 | 166.2
2 | 2 | 2 | 11.9 | 0.3 | 1 | 5.88 | 0.4 | 0.7 | 1 | 665.4 | 166.9
3 | 2 | 2 | 11.9 | 0.3 | 1 | 5.88 | 0.4 | 0.7 | 1 | 665.8 | 166.8
4 | 2 | 2 | 11.9 | 0.2 | 0.9 | 5.87 | 0.3 | 0.7 | 0.8 | 664.6 | 166.1
5 | 2 | 2 | 12 | 0.2 | 0.8 | 5.87 | 0.3 | 0.7 | 0.8 | 665.4 | 168
6 | 1.9 | 2 | 12 | 0 | 0 | 5.87 | 0.3 | 0.7 | 0.8 | 665.4 | 168.3
7 | 2 | 2 | 13.7 | 0.8 | 2.9 | 5.86 | 0.4 | 0.7 | 1 | 665.4 | 167.2
8 | 2 | 2 | 12 | 0.8 | 3.1 | 5.86 | 0.4 | 0.6 | 0.9 | 665.4 | 167.3
9 | 2 | 2 | 12 | 0.8 | 2.9 | 5.86 | 0.4 | 0.6 | 0.9 | 662.2 | 167.2
10 | 2 | 2 | 12 | 0.7 | 2.8 | 5.85 | 0.5 | 0.6 | 1.1 | 660.3 | 166.7
11 | 2 | 2 | 12.1 | 0.7 | 2.7 | 5.85 | 0.5 | 0.6 | 1.1 | 660.7 | 168
12 | 2 | 2 | 12.1 | 0.7 | 2.5 | 5.85 | 0.5 | 0.6 | 1.1 | 661.1 | 166.9
13 | 2 | 2 | 12 | 0.7 | 2.5 | 5.85 | 0.5 | 0.6 | 1.1 | 661.1 | 165.9
14 | 2 | 2 | 11.9 | 0.7 | 2.4 | 5.84 | 0.5 | 0.6 | 1.1 | 660.3 | 165.2
15 | 2 | 2 | 11.9 | 0.6 | 2.4 | 5.84 | 0.4 | 0.5 | 0.9 | 658.7 | 165.1
16 | 2 | 2 | 11.9 | 0.6 | 2.3 | 5.84 | 0.5 | 0.5 | 1.1 | 658.7 | 165.2
17 | 2 | 2 | 11.9 | 0.6 | 2.2 | 5.83 | 0.5 | 0.5 | 1.1 | 658.7 | 165.8
18 | 2 | 2 | 12.1 | 0.5 | 2 | 5.83 | 0.5 | 0.5 | 1.1 | 659.9 | 167.3
19 | 2 | 2 | 12 | 0.5 | 1.8 | 5.83 | 0.4 | 0.5 | 0.9 | 661.5 | 167.8
20 | 2 | 2 | 12 | 0.4 | 1.6 | 5.82 | 0.4 | 0.5 | 0.9 | 662.2 | 167.3
21 | 2 | 2 | 12.1 | 0.4 | 1.5 | 5.82 | 0.4 | 0.4 | 0.9 | 662.6 | 167.9
22 | 2 | 2 | 12 | 0.4 | 1.3 | 5.82 | 0.4 | 0.4 | 0.9 | 664.2 | 166.8
23 | 2 | 2 | 11 | 0.3 | 1.2 | 5.81 | 0.3 | 0.4 | 0.7 | 652.4 | 151.1
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-17
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11 | 0.3 | 1.1 | 5.81 | 0.4 | 0.4 | 0.9 | 650 | 151
1 | 2 | 2 | 11.1 | 0.3 | 1 | 5.81 | 0.4 | 0.4 | 0.9 | 651.6 | 151.9
2 | 2 | 2 | 11.1 | 0.3 | 0.9 | 5.8 | 0.4 | 0.4 | 0.9 | 650.4 | 151.7
3 | 2 | 2 | 11.1 | 0.2 | 0.8 | 5.8 | 0.3 | 0.4 | 0.7 | 652 | 152.3
4 | 2 | 2 | 11.1 | 0.2 | 0.7 | 5.8 | 0.3 | 0.4 | 0.7 | 652 | 152.1
5 | 2 | 2 | 11.1 | 0.2 | 0.7 | 5.79 | 0.4 | 0.4 | 0.9 | 652 | 152
6 | 1.9 | 2 | 11.1 | 0 | 0 | 5.79 | 0.3 | 0.4 | 0.7 | 651.6 | 152.2
7 | 2 | 2 | 11 | 0.7 | 2.4 | 5.79 | 0.4 | 0.4 | 0.9 | 649.6 | 151.3
8 | 2 | 2 | 11.1 | 0.9 | 3 | 5.79 | 0.4 | 0.4 | 0.9 | 650 | 151.8
9 | 2 | 2 | 11.1 | 0.8 | 2.7 | 5.78 | 0.4 | 0.4 | 0.9 | 650.8 | 151.9
10 | 2 | 2 | 11.1 | 0.8 | 2.6 | 5.78 | 0.4 | 0.4 | 0.9 | 650.4 | 151.9
11 | 2 | 2 | 12 | 0.7 | 2.7 | 5.78 | 0.5 | 0.4 | 1.1 | 659.5 | 167.3
12 | 2 | 2 | 12 | 0.7 | 2.6 | 5.77 | 0.4 | 0.4 | 0.9 | 659.5 | 166.5
13 | 2 | 2 | 12 | 0.7 | 2.5 | 5.77 | 0.5 | 0.4 | 1.1 | 659.1 | 166.3
14 | 2 | 2 | 12 | 0.6 | 2.4 | 5.77 | 0.4 | 0.4 | 0.9 | 660.7 | 166.6
15 | 2 | 2 | 12.1 | 0.6 | 2.3 | 5.76 | 0.4 | 0.4 | 0.9 | 661.8 | 167.5
16 | 2 | 2 | 13.7 | 0.5 | 2.1 | 5.76 | 0.4 | 0.4 | 1 | 663.4 | 167.6
17 | 2 | 2 | 13.7 | 0.5 | 1.9 | 5.76 | 0.4 | 0.4 | 1 | 663.8 | 167.3
18 | 2 | 2 | 13.7 | 0.5 | 1.8 | 5.76 | 0.4 | 0.4 | 1 | 665.4 | 167.3
19 | 2 | 2 | 13.7 | 0.5 | 1.7 | 5.75 | 0.3 | 0.4 | 0.8 | 665.4 | 167.2
20 | 2 | 2 | 13.7 | 0.4 | 1.6 | 5.75 | 0.4 | 0.4 | 1 | 665.8 | 166.7
21 | 2 | 2 | 12 | 0.4 | 1.5 | 5.75 | 0.4 | 0.4 | 0.9 | 663.8 | 167.6
22 | 2 | 2 | 13.8 | 0.4 | 1.4 | 5.74 | 0.4 | 0.4 | 1 | 664.2 | 168.1
23 | 2 | 2 | 12.3 | 0.4 | 1.3 | 5.74 | 0.5 | 0.4 | 1.1 | 663.8 | 171.1
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-18
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11 | 0.3 | 1.2 | 5.74 | 0.4 | 0.4 | 0.9 | 650 | 150.8
1 | 2 | 2 | 11.1 | 0.3 | 1.1 | 5.73 | 0.4 | 0.4 | 0.9 | 649.2 | 151.6
2 | 2 | 2 | 11.1 | 0.3 | 1.1 | 5.73 | 0.4 | 0.4 | 0.9 | 649.6 | 151.5
3 | 2 | 2 | 11 | 0.3 | 1 | 5.73 | 0.4 | 0.4 | 0.9 | 649.6 | 150.9
4 | 2 | 2 | 11.1 | 0.3 | 0.9 | 5.72 | 0.4 | 0.4 | 0.9 | 650.8 | 152
5 | 2 | 2 | 11.2 | 0.3 | 0.9 | 5.72 | 0.4 | 0.4 | 0.9 | 651.6 | 154
6 | 1.9 | 2 | 12.4 | 0 | 0 | 5.72 | 0.5 | 0.4 | 1.2 | 662.2 | 174.4
7 | 2 | 2 | 12.4 | 0.7 | 2.9 | 5.71 | 0.5 | 0.4 | 1.2 | 663.4 | 174.4
8 | 2 | 2 | 12.3 | 0.9 | 3.3 | 5.71 | 0.4 | 0.4 | 1 | 664.2 | 172.6
9 | 2 | 2 | 12.4 | 0.8 | 3.2 | 5.71 | 0.5 | 0.4 | 1.2 | 663.8 | 174
10 | 2 | 2 | 12.4 | 0.8 | 3 | 5.71 | 0.5 | 0.4 | 1.1 | 663 | 173.9
11 | 2 | 2 | 12.4 | 0.7 | 2.8 | 5.7 | 0.5 | 0.4 | 1.1 | 663 | 173.3
12 | 2 | 2 | 12.5 | 0.7 | 2.7 | 5.7 | 0.5 | 0.4 | 1.1 | 663.8 | 174.7
13 | 2 | 2 | 12.4 | 0.6 | 2.5 | 5.7 | 0.5 | 0.4 | 1.1 | 663.8 | 173.5
14 | 2 | 2 | 11.1 | 0.6 | 2.1 | 5.69 | 0.3 | 0.4 | 0.7 | 651.2 | 151.4
15 | 2 | 2 | 12.4 | 0.6 | 2.3 | 5.69 | 0.5 | 0.4 | 1.1 | 661.5 | 173.5
16 | 2 | 2 | 12.3 | 0.5 | 2.1 | 5.69 | 0.4 | 0.4 | 1 | 662.6 | 172.2
17 | 2 | 2 | 11.1 | 0.5 | 1.7 | 5.69 | 0.3 | 0.4 | 0.7 | 651.2 | 150.8
18 | 2 | 2 | 11.1 | 0.5 | 1.7 | 5.68 | 0.4 | 0.4 | 0.9 | 650 | 151.6
19 | 2 | 2 | 11.1 | 0.5 | 1.6 | 5.68 | 0.4 | 0.4 | 0.9 | 650 | 152.1
20 | 2 | 2 | 11.2 | 0.5 | 1.6 | 5.68 | 0.4 | 0.4 | 0.9 | 651.6 | 154.2
21 | 2 | 2 | 12.4 | 0.4 | 1.7 | 5.67 | 0.5 | 0.4 | 1.2 | 663.8 | 173.6
22 | 2 | 2 | 11 | 0.4 | 1.3 | 5.67 | 0.3 | 0.4 | 0.7 | 652.4 | 151.2
23 | 2 | 2 | 11 | 0.4 | 1.3 | 5.67 | 0.3 | 0.4 | 0.7 | 648.4 | 149.1
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-19
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11 | 0.4 | 1.2 | 5.66 | 0.3 | 0.4 | 0.7 | 649.2 | 149.7
1 | 2 | 2 | 11 | 0.3 | 1.1 | 5.66 | 0.3 | 0.4 | 0.7 | 649.2 | 149.1
2 | 2 | 2 | 11 | 0.3 | 1.1 | 5.66 | 0.4 | 0.4 | 0.9 | 649.6 | 149.7
3 | 2 | 2 | 11 | 0.3 | 1 | 5.66 | 0.4 | 0.4 | 0.9 | 649.6 | 150.1
4 | 2 | 2 | 11 | 0.3 | 1 | 5.65 | 0.4 | 0.4 | 0.9 | 649.6 | 150.2
5 | 2 | 2 | 11.1 | 0.3 | 0.9 | 5.65 | 0.4 | 0.4 | 0.9 | 651.6 | 152.3
6 | 1.8 | 2 | 11.1 | 0 | 0 | 5.65 | 0.3 | 0.4 | 0.7 | 652 | 151.8
7 | 2 | 2 | 11.1 | 0.8 | 2.8 | 5.64 | 0.4 | 0.4 | 0.9 | 652 | 152.7
8 | 2 | 2 | 11.1 | 0.9 | 3.2 | 5.64 | 0.4 | 0.4 | 0.9 | 651.6 | 151.6
9 | 2 | 2 | 11.2 | 0.9 | 3 | 5.64 | 0.4 | 0.4 | 0.9 | 652 | 152.7
10 | 2 | 2 | 11.1 | 0.8 | 2.8 | 5.64 | 0.4 | 0.4 | 0.9 | 652 | 152.2
11 | 2 | 2 | 11.1 | 0.8 | 2.7 | 5.63 | 0.4 | 0.4 | 0.9 | 652.8 | 152.9
12 | 2 | 2 | 12.7 | 0.7 | 2.6 | 5.63 | 0.4 | 0.4 | 0.9 | 652.4 | 152.3
13 | 2 | 2 | 12.7 | 0.7 | 2.5 | 5.63 | 0.4 | 0.4 | 0.9 | 652.4 | 152.5
14 | 2 | 2 | 12.7 | 0.7 | 2.4 | 5.62 | 0.4 | 0.4 | 0.9 | 652.4 | 151.8
15 | 2 | 2 | 11.1 | 0.6 | 2.2 | 5.62 | 0.4 | 0.4 | 0.9 | 652 | 151.7
16 | 2 | 2 | 11.1 | 0.6 | 2.1 | 5.62 | 0.3 | 0.4 | 0.7 | 652.8 | 152.3
17 | 2 | 2 | 11.2 | 0.6 | 2 | 5.62 | 0.4 | 0.4 | 0.9 | 653.2 | 153.6
18 | 2 | 2 | 11.1 | 0.5 | 1.8 | 5.61 | 0.3 | 0.4 | 0.7 | 652.8 | 151.8
19 | 2 | 2 | 11.1 | 0.5 | 1.8 | 5.61 | 0.3 | 0.4 | 0.7 | 651.2 | 152.2
20 | 2 | 2 | 11.1 | 0.5 | 1.7 | 5.61 | 0.3 | 0.4 | 0.7 | 652 | 151.8
21 | 2 | 2 | 10.9 | 0.5 | 1.5 | 5.6 | 0.3 | 0.4 | 0.7 | 650 | 150.1
22 | 2 | 2 | 10.9 | 0.4 | 1.4 | 5.6 | 0.3 | 0.4 | 0.7 | 649.2 | 150
23 | 2 | 2 | 11.1 | 0.4 | 1.3 | 5.6 | 0.3 | 0.4 | 0.7 | 652.8 | 153.8
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-20
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11.1 | 0.4 | 1.3 | 5.6 | 0.4 | 0.4 | 0.9 | 653.2 | 153.8
1 | 2 | 2 | 11.1 | 0.4 | 1.2 | 5.59 | 0.3 | 0.4 | 0.7 | 654 | 153.8
2 | 2 | 2 | 11.1 | 0.4 | 1.2 | 5.59 | 0.3 | 0.4 | 0.7 | 654 | 153.7
3 | 2 | 2 | 11.2 | 0.3 | 1.2 | 5.59 | 0.3 | 0.4 | 0.7 | 654.7 | 154.5
4 | 2 | 2 | 11.2 | 0.3 | 1.1 | 5.58 | 0.3 | 0.4 | 0.7 | 654 | 154
5 | 2 | 2 | 11.2 | 0.3 | 1 | 5.58 | 0.3 | 0.3 | 0.7 | 653.6 | 154.4
6 | 1.9 | 2 | 11.2 | 0 | 0 | 5.58 | 0.3 | 0.3 | 0.7 | 653.2 | 154.2
7 | 2 | 2 | 11.1 | 0.8 | 2.8 | 5.57 | 0.3 | 0.3 | 0.7 | 652.4 | 153.5
8 | 2 | 2 | 11.2 | 0.9 | 3.2 | 5.57 | 0.4 | 0.3 | 0.9 | 654 | 154.6
9 | 2 | 2 | 11.2 | 0.9 | 3.1 | 5.57 | 0.4 | 0.3 | 0.9 | 654 | 154.1
10 | 2 | 2 | 11.2 | 0.8 | 2.9 | 5.57 | 0.3 | 0.3 | 0.7 | 653.2 | 153.6
11 | 2 | 2 | 11.2 | 0.8 | 2.8 | 5.56 | 0.3 | 0.3 | 0.7 | 653.2 | 153.6
12 | 2 | 2 | 11.3 | 0.8 | 2.7 | 5.56 | 0.3 | 0.3 | 0.7 | 655.1 | 154.8
13 | 2 | 2 | 11.2 | 0.7 | 2.6 | 5.56 | 0.3 | 0.3 | 0.7 | 653.6 | 153.3
14 | 2 | 2 | 11.1 | 0.7 | 2.4 | 5.56 | 0.4 | 0.3 | 0.9 | 653.2 | 153.3
15 | 2 | 2 | 11.1 | 0.6 | 2.2 | 5.55 | 0.4 | 0.3 | 0.9 | 652.4 | 153.5
16 | 2 | 2 | 11.2 | 0.6 | 2.1 | 5.55 | 0.4 | 0.3 | 0.9 | 653.6 | 154.6
17 | 2 | 2 | 11.1 | 0.6 | 2 | 5.55 | 0.4 | 0.3 | 0.9 | 652.8 | 152.9
18 | 2 | 2 | 11.1 | 0.6 | 1.9 | 5.54 | 0.4 | 0.3 | 0.9 | 652 | 152.9
19 | 2 | 2 | 11.1 | 0.5 | 1.7 | 5.54 | 0.4 | 0.3 | 0.9 | 652.4 | 153.5
20 | 2 | 2 | 11.2 | 0.5 | 1.6 | 5.54 | 0.4 | 0.3 | 0.9 | 653.2 | 154.7
21 | 2 | 2 | 11.1 | 0.4 | 1.5 | 5.54 | 0.4 | 0.3 | 0.9 | 653.2 | 153.5
22 | 2 | 2 | 11 | 0.4 | 1.4 | 5.53 | 0.4 | 0.4 | 0.9 | 652 | 150.8
23 | 36.4 | 2 | 75.7 | 27 | 34.1 | 5.55 | 0 | 0.4 | 0 | 634.6 | 28.5SD |  |  | 23:03 | 23:19
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-21
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 54.4 | 2 | 108.2 | 17.6 | 21.3 | 5.55 | 0 | 0.4 | 0 | 576.6 | 18.4HS | 3:01
4 | 32.5 | 2 | 114.3 | 22.2 | 47.3 | 5.56 | 0 | 0.4 | 0 | 618.8 | 66.3HS |  | 4:50 |  |  | ET 1:49
5 | 2 | 2 | 11.3 | 0.3 | 1.1 | 5.56 | 0.3 | 0.4 | 0.7 | 652 | 155
6 | 2 | 2 | 11.1 | 0 | 0 | 5.56 | 0.3 | 0.4 | 0.7 | 652.8 | 153.1
7 | 2 | 2 | 11.2 | 0.7 | 2.5 | 5.55 | 0.4 | 0.4 | 0.9 | 653.6 | 153.9
8 | 1.7 | 2 | 9.6 | 0.9 | 3.2 | 5.55 | 0.4 | 0.4 | 0.9 | 653.6 | 153.6
9 | 1.3 | 2 | 8 | 0.9 | 3.1 | 5.55 | 0.6 | 0.4 | 1.2 | 653.6 | 153.7
10 | 1 | 1.9 | 6.4 | 0.8 | 2.9 | 5.54 | 0.7 | 0.4 | 1.4 | 652.4 | 153.6
11 | 0.7 | 1.8 | 4.8 | 0.8 | 2.8 | 5.54 | 0.8 | 0.4 | 1.8 | 652.4 | 153.9
12 | 0.6 | 1.8 | 3.2 | 0.7 | 2.6 | 5.54 | 1 | 0.4 | 2.1 | 652.4 | 153.5
13 | 1.2 | 1.7 | 7.9 | 0.7 | 2.5 | 5.54 | 0.5 | 0.5 | 1.1 | 652.4 | 152.9
14 | 1.6 | 1.7 | 9.5 | 0.6 | 2.2 | 5.53 | 0.5 | 0.5 | 1.1 | 652.4 | 152.8
15 | 1.9 | 1.7 | 11.2 | 0.2 | 0.8 | 5.53 | 0.4 | 0.5 | 0.9 | 652.8 | 153.9
16 | 2 | 1.7 | 11.2 | 0.7 | 2.5 | 5.53 | 0.4 | 0.5 | 0.9 | 652.4 | 153.4
17 | 2.1 | 1.7 | 12.2 | 0.7 | 2.4 | 5.53 | 0.3 | 0.5 | 0.7 | 644.9 | 144.1
18 | 2 | 1.7 | 11 | 0.7 | 2.4 | 5.52 | 0.4 | 0.5 | 0.9 | 647.6 | 150.2
19 | 2 | 1.7 | 11.2 | 0.6 | 2.2 | 5.52 | 0.4 | 0.5 | 0.9 | 652 | 154.2
20 | 2 | 1.7 | 11.1 | 0.6 | 2 | 5.52 | 0.3 | 0.5 | 0.7 | 651.6 | 151.5
21 | 36.8 | 1.7 | 79.4 | 29.4 | 38.7 | 5.53 | 0 | 0.5 | 0 | 635 | 31.3SD |  |  | 21:05 | 21:18
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-22
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-23
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | 59.3X | 1.7 | 112.2 | 73.1X | 84.3 | 5.57 | 0 | 0.5 | 0 | 396.2 | 15.5CS | 22:00
23 | 54.4X | 1.7 | 120.8 | 26.3X | 35.6 | 5.58 | 0 | 0.5 | 0 | 620 | 22.2CS
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-24
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 29.8X | 1.7 | 105.3 | 14.0X | 29.9 | 5.58 | 0 | 0.5 | 0 | 617.6 | 67.3CS |  | 0:42 |  |  | ET 2:42 | Shortest yet maybe.
1 | 1.8X | 1.6 | 11.4 | 0.2X | 0.8 | 5.58 | 0.4 | 0.5 | 0.9 | 639.4 | 156.1
2 | 1.5X | 1.6 | 7.8 | 0.0X | 0 | 5.58 | 0 | 0.4 | 0 | 639.7 | 149.1
3 | 15.4 | 1.6 | 74.3 | 9.6 | 28 | 5.58 | 0 | 0.4 | 0 | 634.6 | 117.0CS |  |  | 3:50 | 4:00
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-25
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | 55.5 | 1.6 | 106.5 | 43.6 | 50.7 | 5.6 | 0 | 0.4 | 0 | 487.4 | 15.8WS | 2:00
3 | 44.4 | 1.6 | 110.3 | 43.5 | 65.5 | 5.62 | 0 | 0.5 | 0 | 620 | 29.3WS
4 | 38.8 | 1.6 | 129.2 | 21 | 42.4 | 5.63 | 0 | 0.5 | 0 | 616.9 | 59.1WS |  | 4:52 |  |  | ET 2:52
5 | 1.6X | 1.6 | 9.8 | 0.0X | 0 | 5.63 | 0.3 | 0.5 | 0.7 | 637 | 158.1
6 | 1.9 | 1.6 | 11.2 | 0.4 | 1.4 | 5.62 | 0.4 | 0.5 | 0.9 | 639 | 153.3
7 | 1.9 | 1.6 | 11.2 | 0.9 | 3.3 | 5.62 | 0.3 | 0.4 | 0.7 | 640.9 | 153
8 | 1.9 | 1.7 | 11.2 | 0.9 | 3.2 | 5.62 | 0.4 | 0.4 | 0.9 | 643.7 | 153.6
9 | 1.9 | 1.7 | 11.2 | 0.9 | 3.1 | 5.62 | 0.4 | 0.4 | 0.9 | 644.9 | 153.5
10 | 2 | 1.8 | 11.4 | 0.8 | 3 | 5.61 | 0.5 | 0.4 | 1.1 | 645.7 | 156.9
11 | 1.9 | 1.9 | 12.6 | 0.8 | 3.1 | 5.61 | 0.5 | 0.4 | 1.2 | 662.2 | 176.2
12 | 1.9 | 1.9 | 12.5 | 0.7 | 2.8 | 5.61 | 0.6 | 0.4 | 1.4 | 662.2 | 175.2
13 | 1.9 | 1.9 | 12.6 | 0.7 | 2.7 | 5.61 | 0.5 | 0.4 | 1.2 | 662.2 | 176.4
14 | 1.9 | 1.9 | 12.5 | 0.7 | 2.7 | 5.6 | 0.5 | 0.4 | 1.2 | 660.3 | 175.5
15 | 1.9 | 1.9 | 12.5 | 0.6 | 2.5 | 5.6 | 0.4 | 0.4 | 1 | 659.1 | 175.6
16 | 2 | 1.9 | 10 | 0.6 | 2 | 5.6 | 0.3 | 0.4 | 0.6 | 657.9 | 131.1
17 | 1.9 | 1.9 | 9.8 | 0.6 | 2 | 5.6 | 0.3 | 0.4 | 0.6 | 647.2 | 127.7
18 | 1.9 | 1.9 | 9.4 | 0.6 | 1.9 | 5.59 | 0.3 | 0.4 | 0.6 | 643.3 | 118.9
19 | 1.9 | 1.9 | 11.4 | 0.6 | 2.1 | 5.59 | 0.5 | 0.4 | 1.1 | 656.7 | 153.9
20 | 1.9 | 1.9 | 10.9 | 0.5 | 1.5 | 5.59 | 0.4 | 0.4 | 0.9 | 650.8 | 147.7
21 | 2 | 1.9 | 11.2 | 0.5 | 1.7 | 5.58 | 0.4 | 0.4 | 0.9 | 644.1 | 154.2
22 | 2 | 1.9 | 11.2 | 0.4 | 1.5 | 5.58 | 0.4 | 0.4 | 0.9 | 644.5 | 153.9
23 | 2 | 1.9 | 11.2 | 0.4 | 1.5 | 5.58 | 0.3 | 0.4 | 0.7 | 644.5 | 154.6
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-26
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 1.9 | 11.1 | 0.4 | 1.4 | 5.58 | 0.4 | 0.4 | 0.9 | 644.5 | 153.1
1 | 2 | 1.9 | 11.1 | 0.4 | 1.4 | 5.57 | 0.3 | 0.4 | 0.7 | 644.5 | 153
2 | 2 | 1.9 | 11.2 | 0.4 | 1.3 | 5.57 | 0.3 | 0.4 | 0.7 | 644.1 | 154
3 | 2 | 1.9 | 11.1 | 0.4 | 1.3 | 5.57 | 0.3 | 0.4 | 0.7 | 643.3 | 153
4 | 2 | 1.9 | 11.2 | 0.4 | 1.2 | 5.56 | 0.4 | 0.4 | 0.9 | 643.7 | 153.8
5 | 1.9 | 1.9 | 11.2 | 0 | 0 | 5.56 | 0.4 | 0.4 | 0.9 | 643.7 | 153.9
6 | 2 | 1.9 | 11.2 | 0.5 | 1.6 | 5.56 | 0.4 | 0.4 | 0.9 | 647.6 | 153.6
7 | 2 | 2 | 11.2 | 1 | 3.4 | 5.56 | 0.4 | 0.4 | 0.9 | 651.6 | 154.2
8 | 2 | 2 | 11.2 | 0.9 | 3.3 | 5.55 | 0.3 | 0.4 | 0.7 | 653.2 | 154.2
9 | 2 | 2 | 11.2 | 0.9 | 3.2 | 5.55 | 0.4 | 0.4 | 0.9 | 653.2 | 154.1
10 | 2 | 2 | 11.2 | 0.8 | 3 | 5.55 | 0.4 | 0.4 | 0.9 | 652.4 | 152.6
11 | 2 | 2 | 11.2 | 0.8 | 2.8 | 5.55 | 0.4 | 0.4 | 0.9 | 651.6 | 153.1
12 | 2 | 2 | 11.2 | 0.8 | 2.7 | 5.54 | 0.4 | 0.4 | 0.9 | 652 | 153.3
13 | 2 | 2 | 11.2 | 0.7 | 2.6 | 5.54 | 0.4 | 0.4 | 0.9 | 652.8 | 153.7
14 | 2 | 2 | 11.2 | 0.7 | 2.5 | 5.54 | 0.4 | 0.4 | 0.9 | 649.6 | 153.4
15 | 2 | 2 | 11.2 | 0.7 | 2.5 | 5.54 | 0.4 | 0.4 | 0.9 | 652.8 | 152.6
16 | 2 | 2 | 11.1 | 0.7 | 2.4 | 5.53 | 0.4 | 0.4 | 0.9 | 651.6 | 152.6
17 | 2 | 2 | 11.1 | 0.7 | 2.3 | 5.53 | 0.4 | 0.4 | 0.9 | 651.6 | 152.6
18 | 2 | 2 | 11.2 | 0.6 | 2.2 | 5.53 | 0.4 | 0.4 | 0.9 | 651.6 | 153.4
19 | 2 | 2 | 11.2 | 0.6 | 2 | 5.53 | 0.4 | 0.4 | 0.9 | 652 | 153.9
20 | 2 | 2 | 11.2 | 0.5 | 1.9 | 5.52 | 0.4 | 0.4 | 0.9 | 653.2 | 153.9
21 | 2 | 2 | 11.1 | 0.5 | 1.8 | 5.52 | 0.4 | 0.4 | 0.9 | 651.6 | 153.3
22 | 2 | 2 | 12.6 | 0.5 | 1.7 | 5.52 | 0.3 | 0.4 | 0.7 | 652 | 150.1
23 | 44.8 | 2 | 86.7 | 0 | 40 | 5.51 | 0 | 0.4 | 0 | 632.6 | 24.6SD |  |  | 23:05 | 23:20
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-27
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 52.8 | 2 | 108.4 | 0 | 29.7 | 5.51 | 0 | 0.4 | 0 | 558.4 | 19.9HS | 3:10
4 | 32.3 | 2 | 121.1 | 0 | 36.4 | 5.51 | 0 | 0.4 | 0 | 610.9 | 74.0HS |  | 4:45 |  |  | ET 1:35
5 | 1.9 | 2 | 11.4 | 0 | 0 | 5.51 | 0.3 | 0.4 | 0.7 | 639.4 | 156.5
6 | 2 | 2 | 12.8 | 0.5 | 1.9 | 5.5 | 0.4 | 0.4 | 0.9 | 645.7 | 153.6
7 | 2 | 2 | 12.8 | 0 | 0 | 5.5 | 0.4 | 0.4 | 0.9 | 653.6 | 153.7
8 | 2 | 2 | 11.2 | 0 | 0 | 5.5 | 0.3 | 0.4 | 0.8 | 653.6 | 153.3
9 | 1.9I | 2 | 11.2 | 0.1I | 0.1 | 5.49 | 0 | 0.4 | 0 | 653.6 | 153.5
10 | 2.0I | 2 | 11.2 | 0.3I | 0.9 | 5.49 | 0 | 0.3 | 0 | 652.4 | 153.1
11 | 2.1 | 2 | 12.8 | 0.2 | 0.6 | 5.49 | 0.3 | 0.3 | 0.7 | 652.8 | 154
12 | 1.7 | 2 | 9.3 | 0.1 | 0.1 | 5.49 | 0.3 | 0.3 | 0.7 | 648.8 | 148.1
13 | 2 | 2 | 11.2 | 0 | 0.1 | 5.48 | 0.3 | 0.3 | 0.7 | 652.4 | 154.5
14 | 2.1 | 2 | 12.8 | 0 | 0.1 | 5.48 | 0.3 | 0.3 | 0.7 | 652.4 | 153.7
15 | 2 | 2 | 11.2 | 0 | 0.1 | 5.48 | 0.3 | 0.3 | 0.7 | 652.4 | 153.5
16 | 1.9 | 2 | 11.1 | 0 | 0.1 | 5.47 | 0.3 | 0.3 | 0.7 | 651.6 | 153.1
17 | 2 | 2 | 11.2 | 0 | 0.1 | 5.47 | 0.3 | 0.3 | 0.7 | 650.8 | 153.3
18 | 2.1 | 2 | 12.8 | 0 | 0.1 | 5.47 | 0.3 | 0.3 | 0.7 | 652 | 153.3
19 | 2.1 | 2 | 12.8 | 0 | 0.1 | 5.47 | 0.3 | 0.3 | 0.7 | 652.4 | 154
20 | 2.1 | 2 | 12.6 | 0.1 | 0.1 | 5.46 | 0.3 | 0.3 | 0.7 | 653.6 | 150.9
21 | 44.5 | 2 | 87.7 | 0 | 42.7 | 5.46 | 0 | 0.3 | 0 | 634.2 | 25.7SD |  |  | 21:05 | 21:19
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-28
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | 61 | 2 | 125.1 | 0 | 21.7 | 5.46 | 0 | 0.3 | 0 | 556.5 | 19.9HS | 4:08
5 | 37.5 | 2 | 136.5 | 0 | 47.6 | 5.45 | 0 | 0.3 | 0 | 612.9 | 70.1HS |  | 5:47 |  |  | ET 1:39
6 | 1.8 | 2 | 9.2 | 0 | 0 | 5.45 | 0.3 | 0.3 | 0.6 | 636.6 | 145.5
7 | 1.9 | 2 | 10.7 | 0.1 | 0.4 | 5.45 | 0.3 | 0.3 | 0.7 | 638.6 | 144.7
8 | 1.9 | 2 | 10.7 | 0.1 | 0.3 | 5.45 | 0.3 | 0.3 | 0.7 | 642.9 | 144.3
9 | 1.9 | 2 | 10.7 | 0.1 | 0.3 | 5.44 | 0.3 | 0.3 | 0.7 | 645.3 | 144.3
10 | 1.9 | 2 | 10.7 | 0.1 | 0.2 | 5.44 | 0.3 | 0.3 | 0.7 | 645.3 | 144.4
11 | 1.9 | 2 | 10.7 | 0.1 | 0.2 | 5.44 | 0.3 | 0.3 | 0.7 | 645.3 | 144.6
12 | 1.9 | 2 | 10.7 | 0.1 | 0.2 | 5.43 | 0.3 | 0.3 | 0.7 | 645.7 | 144.1
13 | 1.9 | 2 | 10.8 | 0.1 | 0.2 | 5.43 | 0.3 | 0.3 | 0.7 | 646.5 | 145
14 | 2 | 2 | 10.8 | 0.1 | 0.2 | 5.43 | 0.3 | 0.3 | 0.7 | 646.1 | 144.6
15 | 1.9 | 2 | 10.7 | 0.1 | 0.2 | 5.43 | 0.3 | 0.3 | 0.7 | 645.7 | 144.9
16 | 1.9 | 2 | 10.8 | 0.1 | 0.2 | 5.42 | 0.3 | 0.3 | 0.7 | 645.3 | 144.9
17 | 1.9 | 1.9 | 10.7 | 0.1 | 0.2 | 5.42 | 0.3 | 0.3 | 0.7 | 644.9 | 144.3
18 | 1.9 | 2 | 10.7 | 0.1 | 0.2 | 5.42 | 0.3 | 0.3 | 0.7 | 644.9 | 144.7
19 | 2 | 2 | 10.8 | 0.1 | 0.2 | 5.41 | 0.3 | 0.3 | 0.7 | 645.3 | 145.3
20 | 2 | 1.9 | 10.6 | 0.1 | 0.3 | 5.41 | 0.3 | 0.3 | 0.7 | 645.7 | 142.2
21 | 43 | 1.9 | 81 | 0 | 44.9 | 5.41 | 0 | 0.3 | 0 | 631.1 | 23.8SD |  |  | 22:05 | 22:18
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-29
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 58.1 | 1.9 | 118.4 | 0 | 24.1 | 5.41 | 0 | 0.3 | 0 | 552.9 | 20.3HS | 3:08
4 | 34.1 | 1.9 | 126.3 | 0 | 41.3 | 5.4 | 0 | 0.3 | 0 | 610.9 | 72.6HS |  | 4:44 |  |  | ET 1:36
5 | 1.8 | 1.9 | 11.4 | 0 | 0 | 5.4 | 0.3 | 0.3 | 0.6 | 640.9 | 156.4
6 | 2 | 1.9 | 11.2 | 0.1 | 0.4 | 5.4 | 0.3 | 0.3 | 0.7 | 644.9 | 154.6
7 | 2 | 1.9 | 11.3 | 0.1 | 0.2 | 5.39 | 0.3 | 0.3 | 0.7 | 654 | 155.6
8 | 2 | 1.9 | 11.3 | 0.1 | 0.2 | 5.39 | 0.4 | 0.3 | 0.9 | 655.1 | 155.7
9 | 2.1 | 1.9 | 14.2 | 0 | 0 | 5.39 | 0.6 | 0.3 | 1.4 | 706.8 | 173.5
10 | 2 | 1.9 | 12.4 | 0 | 0 | 5.39 | 0.6 | 0.3 | 1.5 | 714.3 | 172.6
11 | 2 | 1.9 | 12.4 | 0 | 0 | 5.38 | 0.6 | 0.3 | 1.4 | 715.1 | 172.3
12 | 2 | 1.9 | 12.4 | 0 | 0 | 5.38 | 0.6 | 0.4 | 1.4 | 714.7 | 172.3
13 | 2 | 2 | 12.4 | 0 | 0 | 5.38 | 0.6 | 0.4 | 1.4 | 713.6 | 172.9
14 | 2 | 2 | 14.2 | 0 | 0 | 5.37 | 0.6 | 0.4 | 1.5 | 711.2 | 173.4
15 | 2 | 2 | 14.2 | 0 | 0 | 5.37 | 0.6 | 0.4 | 1.5 | 710.8 | 173.5
16 | 2 | 2 | 12.4 | 0 | 0 | 5.37 | 0.6 | 0.4 | 1.5 | 709.6 | 172.9
17 | 2 | 2 | 11.1 | 0 | 0 | 5.37 | 0.3 | 0.4 | 0.7 | 657.5 | 152.4
18 | 2 | 2 | 11.3 | 0 | 0.1 | 5.36 | 0.3 | 0.4 | 0.7 | 653.6 | 154.5
19 | 2 | 2 | 11.2 | 0 | 0.1 | 5.36 | 0.4 | 0.4 | 0.9 | 654 | 155.1
20 | 2 | 2 | 11.1 | 0 | 0.1 | 5.36 | 0.3 | 0.4 | 0.7 | 652.8 | 151.9
21 | 41 | 2 | 82.1 | 0 | 34.2 | 5.36 | 0 | 0.4 | 0 | 635 | 27.9SD |  |  | 21:06 | 21:18
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-30
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-08-31
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
[7 empty] | Sum NH3 (lbs): |  | 514.9
Note on D618: LINERRO: Excess emission reported as incident 2008-02

## August CEMS Raw data
This data is raw hourly CEMs database data which may include invalid data such as values obtained during calibration checks.
Aug | 2008
GT MW
Record# | DATE | TIME | BOILER11 | CATTMP12 | CO_COR13 | CO_HCOR14 | GAS15 | GEN16 | GEN27 | HGAS18 | HGASON19 | NH3110 | NH3COR111 | NH3FLO112 | NOX113 | NOX1I14 | NOXCOR115 | NOXH116 | NOXHCOR117 | NOXHRT118 | NOXRT119 | OXY120
1 | 2008-08-01 | 0 | 1 | 648.2 | 0.3 | -2.3 | 18.86 | 148.9 | 227.4 | -0.05 | 0 | -4.96 | -4.1 | 63.3 | 2.46 | 7.43 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.67
2 | 2008-08-01 | 10000 | 1 | 647.8 | 0.3 | -2.1 | 18.87 | 149.6 | 227.9 | -0.05 | 0 | -4.96 | -4.1 | 64.6 | 2.46 | 7.45 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.68
3 | 2008-08-01 | 20000 | 1 | 647.5 | 0.3 | -2.6 | 18.88 | 149.1 | 227.4 | -0.05 | 0 | -4.96 | -4.1 | 64 | 2.46 | 7.41 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.68
4 | 2008-08-01 | 30000 | 1 | 648.4 | 0.3 | -2.5 | 18.9 | 149.9 | 228.2 | -0.049 | 0 | -4.96 | -4.1 | 64.2 | 2.45 | 7.4 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.68
5 | 2008-08-01 | 40000 | 1 | 648.5 | 0.3 | -2.8 | 18.9 | 149.9 | 227.9 | -0.051 | 0 | -4.96 | -4.1 | 62.4 | 2.46 | 7.29 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.67
6 | 2008-08-01 | 50000 | 1 | 648 | 0.2 | -2.3 | 18.85 | 149.5 | 227.3 | -0.05 | 0 | -4.96 | -4 | 61.9 | 2.47 | 7.24 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.67
7 | 2008-08-01 | 60000 | 1 | 648.4 | 2.5 | 12.5 | 18.88 | 149.4 | 227.2 | -0.048 | 0 | -4.96 | -21.7 | 61.9 | 3.49 | 8.15 | 2 | 9.79 | 3.8 | 0.015 | 0.008 | 12.11
8 | 2008-08-01 | 70000 | 1 | 648.7 | 0.5 | -2.3 | 19.14 | 152.1 | 230.3 | -0.049 | 0 | -4.96 | -4.1 | 66.1 | 2.49 | 7.53 | 2 | 2.48 | 2 | 0.007 | 0.007 | 13.66
9 | 2008-08-01 | 80000 | 1 | 665.3 | 0.6 | -1.8 | 21.56 | 176.1 | 263.2 | -0.05 | 0 | -4.96 | -4 | 122.4 | 2.45 | 11.21 | 2 | 2.44 | 1.9 | 0.007 | 0.007 | 13.52
10 | 2008-08-01 | 90000 | 1 | 666.5 | 0.6 | -2.2 | 21.58 | 176.4 | 262.6 | -0.048 | 0 | -4.96 | -4 | 117.6 | 2.52 | 11.15 | 2 | 2.49 | 2 | 0.007 | 0.007 | 13.54
11 | 2008-08-01 | 100000 | 1 | 666.1 | 0.5 | -2.3 | 21.52 | 175.6 | 262.6 | -0.049 | 0 | -4.96 | -4 | 112.6 | 2.47 | 10.68 | 2 | 2.46 | 2 | 0.007 | 0.007 | 13.58
12 | 2008-08-01 | 110000 | 1 | 666.1 | 0.5 | -2.3 | 21.51 | 175.8 | 262.9 | -0.048 | 0 | -4.96 | -4 | 116.1 | 2.52 | 10.87 | 2 | 2.5 | 2 | 0.007 | 0.008 | 13.58
13 | 2008-08-01 | 120000 | 1 | 666.2 | 0.5 | -2.3 | 21.48 | 175.9 | 263.2 | -0.046 | 0 | -4.97 | -4 | 117.8 | 2.44 | 11.03 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.59
14 | 2008-08-01 | 130000 | 1 | 664.9 | 0.5 | -2.3 | 21.53 | 175.7 | 263.4 | -0.048 | 0 | -4.96 | -4 | 123.9 | 2.52 | 11.45 | 2 | 2.51 | 2 | 0.007 | 0.007 | 13.56
15 | 2008-08-01 | 140000 | 1 | 664.4 | 0.4 | -2 | 21.54 | 175.7 | 263.7 | -0.047 | 0 | -4.96 | -4 | 129 | 2.53 | 11.66 | 2 | 2.51 | 2 | 0.007 | 0.007 | 13.53
16 | 2008-08-01 | 150000 | 1 | 661.2 | 0.4 | -2.3 | 20.67 | 168.1 | 253.3 | -0.048 | 0 | -4.96 | -4 | 109.4 | 2.32 | 10.23 | 1.9 | 2.31 | 1.9 | 0.007 | 0.007 | 13.63
17 | 2008-08-01 | 160000 | 1 | 663.2 | 0.4 | -2.4 | 20.96 | 170.1 | 255 | -0.047 | 0 | -4.96 | -4.1 | 105.7 | 2.14 | 9.33 | 1.7 | 2.12 | 1.7 | 0.006 | 0.006 | 13.72
18 | 2008-08-01 | 170000 | 1 | 664.4 | 0.4 | -2.2 | 20.92 | 169.9 | 254.4 | -0.047 | 0 | -4.96 | -4.1 | 90.7 | 2.45 | 8.86 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.76
19 | 2008-08-01 | 180000 | 1 | 664.6 | 0.4 | -2.3 | 21.53 | 175.7 | 263.6 | -0.05 | 0 | -4.97 | -4 | 128.7 | 2.49 | 11.49 | 2 | 2.47 | 2 | 0.007 | 0.007 | 13.58
20 | 2008-08-01 | 190000 | 1 | 664.2 | 0.4 | -2.2 | 21.41 | 174.4 | 261.8 | -0.049 | 0 | -4.96 | -4 | 119.8 | 2.42 | 10.94 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.62
21 | 2008-08-01 | 200000 | 1 | 648.5 | 0.3 | -2 | 18.84 | 148.7 | 227.1 | -0.047 | 0 | -4.96 | -4.1 | 62.4 | 2.46 | 7.41 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.73
22 | 2008-08-01 | 210000 | 1 | 647.3 | 0.3 | -2 | 18.91 | 149.6 | 227.8 | -0.048 | 0 | -4.96 | -4.1 | 65 | 2.45 | 7.45 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.72
23 | 2008-08-01 | 220000 | 1 | 647.4 | 0.3 | -2.1 | 18.89 | 149.6 | 227.8 | -0.048 | 0 | -4.97 | -4.1 | 65.9 | 2.44 | 7.46 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.72
24 | 2008-08-01 | 230000 | 1 | 648.2 | 0.3 | -2.1 | 18.9 | 150.1 | 228.4 | -0.047 | 0 | -4.96 | -4.1 | 66.6 | 2.45 | 7.52 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.73
25 | 2008-08-02 | 0 | 1 | 647.6 | 0.3 | -2.1 | 18.89 | 149.7 | 227.8 | -0.047 | 0 | -4.96 | -4.1 | 66.6 | 2.44 | 7.54 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.74
26 | 2008-08-02 | 10000 | 1 | 647.5 | 0.3 | -2.4 | 18.88 | 149.4 | 227.5 | -0.047 | 0 | -4.96 | -4.1 | 66.5 | 2.45 | 7.54 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.73
27 | 2008-08-02 | 20000 | 1 | 647.9 | 0.2 | -2.5 | 18.9 | 149.5 | 227.7 | -0.046 | 0 | -4.96 | -4.1 | 66.7 | 2.44 | 7.56 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.74
28 | 2008-08-02 | 30000 | 1 | 647.9 | 0.2 | -2.2 | 18.9 | 150 | 228.2 | -0.047 | 0 | -4.97 | -4.1 | 67 | 2.44 | 7.56 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.74
29 | 2008-08-02 | 40000 | 1 | 647.7 | 0.2 | -2.5 | 18.9 | 149.7 | 227.8 | -0.048 | 0 | -4.96 | -4.1 | 66.3 | 2.44 | 7.52 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.74
30 | 2008-08-02 | 50000 | 1 | 647.5 | 0.2 | -2.2 | 18.9 | 149.6 | 227.8 | -0.049 | 0 | -4.96 | -4.1 | 66.4 | 2.44 | 7.52 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.75
31 | 2008-08-02 | 60000 | 1 | 646.8 | 5.6 | -1.8 | 18.91 | 149.4 | 227.5 | -0.047 | 0 | -4.96 | -70.7 | 66.1 | 3.46 | 6.9 | 1.7 | 9.8 | 3.3 | 6.347 | 0.009 | 12.18
32 | 2008-08-02 | 70000 | 1 | 647.3 | 0.4 | -2.2 | 18.9 | 149.7 | 227.9 | -0.048 | 0 | -4.96 | -4.1 | 66.6 | 2.43 | 8.87 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.77
33 | 2008-08-02 | 80000 | 1 | 646.8 | 0.6 | -2.3 | 19.05 | 150.5 | 228.9 | -0.048 | 0 | -4.96 | -4.1 | 67.9 | 2.47 | 7.53 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.73
34 | 2008-08-02 | 90000 | 1 | 665.9 | 0.6 | -2.4 | 21.63 | 177.3 | 264.3 | -0.049 | 0 | -4.96 | -4.1 | 118.2 | 2.45 | 11.12 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.67
35 | 2008-08-02 | 100000 | 1 | 667.8 | 0.6 | -2.3 | 21.54 | 176.1 | 263.1 | -0.05 | 0 | -4.96 | -4.1 | 111.5 | 2.42 | 10.24 | 2 | 2.4 | 2 | 0.007 | 0.007 | 13.71
36 | 2008-08-02 | 110000 | 1 | 667.8 | 0.5 | -2.5 | 21.54 | 176.1 | 263.4 | -0.051 | 0 | -4.96 | -4.1 | 113.6 | 2.47 | 10.43 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.71
37 | 2008-08-02 | 120000 | 1 | 667.1 | 0.5 | -2.4 | 21.54 | 175.9 | 263.4 | -0.051 | 0 | -4.96 | -4.1 | 117.2 | 2.45 | 10.7 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.7
38 | 2008-08-02 | 130000 | 1 | 666.3 | 0.5 | -2.4 | 21.59 | 176.2 | 263.9 | -0.049 | 0 | -4.97 | -4.1 | 122.2 | 2.5 | 11.03 | 2 | 2.48 | 2 | 0.007 | 0.008 | 13.68
39 | 2008-08-02 | 140000 | 1 | 665.8 | 0.5 | -2.6 | 21.59 | 175.9 | 263.3 | -0.051 | 0 | -4.96 | -4.1 | 120.4 | 2.44 | 10.96 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.68
40 | 2008-08-02 | 150000 | 1 | 664.7 | 0.5 | -2.3 | 21.54 | 175.7 | 263.5 | -0.049 | 0 | -4.96 | -4.1 | 125.1 | 2.47 | 11.29 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.67
41 | 2008-08-02 | 160000 | 1 | 663.8 | 0.4 | -2.4 | 21.54 | 175.7 | 263.4 | -0.05 | 0 | -4.96 | -4.1 | 124.3 | 2.47 | 11.47 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.67
42 | 2008-08-02 | 170000 | 1 | 664.1 | 0.4 | -2.3 | 21.54 | 176.2 | 263.9 | -0.052 | 0 | -4.96 | -4 | 125.6 | 2.45 | 11.55 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.65
43 | 2008-08-02 | 180000 | 1 | 665.4 | 0.4 | -2 | 21.52 | 175.7 | 263 | -0.049 | 0 | -4.96 | -4.1 | 119.5 | 2.51 | 11.1 | 2 | 2.49 | 2 | 0.007 | 0.008 | 13.68
44 | 2008-08-02 | 190000 | 1 | 665.5 | 0.4 | -2.3 | 21.42 | 175.1 | 262.6 | -0.048 | 0 | -4.96 | -4 | 119.3 | 2.39 | 11.11 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.67
45 | 2008-08-02 | 200000 | 1 | 648.4 | 0.4 | -1.8 | 18.88 | 149.4 | 228 | -0.049 | 0 | -4.96 | -4.1 | 62.8 | 2.43 | 7.55 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.76
46 | 2008-08-02 | 210000 | 1 | 647 | 0.4 | -2.5 | 18.94 | 149.9 | 228.2 | -0.048 | 0 | -4.96 | -4.1 | 65.3 | 2.44 | 7.57 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.75
47 | 2008-08-02 | 220000 | 1 | 646.6 | 0.3 | -2.2 | 18.9 | 149.6 | 227.7 | -0.049 | 0 | -4.96 | -4.1 | 65.5 | 2.44 | 7.66 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.75
48 | 2008-08-02 | 230000 | 1 | 647.7 | 0.3 | -2.5 | 18.92 | 150.3 | 228.6 | -0.049 | 0 | -4.96 | -4.1 | 65.9 | 2.44 | 7.57 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.74
49 | 2008-08-03 | 0 | 1 | 647.9 | 0.3 | -2.3 | 18.91 | 150.3 | 228.4 | -0.047 | 0 | -4.96 | -4.1 | 66.1 | 2.44 | 7.65 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.74
50 | 2008-08-03 | 10000 | 1 | 647.4 | 0.3 | -2.3 | 18.9 | 149.7 | 227.8 | -0.049 | 0 | -4.96 | -4.1 | 65.8 | 2.44 | 7.58 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.74
51 | 2008-08-03 | 20000 | 1 | 647.8 | 0.3 | -2.4 | 18.9 | 150.2 | 228.3 | -0.049 | 0 | -4.96 | -4.1 | 66.3 | 2.44 | 7.61 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.74
52 | 2008-08-03 | 30000 | 1 | 648 | 0.3 | -2.2 | 18.9 | 150.2 | 228.2 | -0.051 | 0 | -4.96 | -4.1 | 66.6 | 2.44 | 7.65 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.74
53 | 2008-08-03 | 40000 | 1 | 647.8 | 0.3 | -2.2 | 18.9 | 150 | 227.9 | -0.05 | 0 | -4.96 | -4.1 | 66.5 | 2.44 | 7.78 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.75
54 | 2008-08-03 | 50000 | 1 | 647.7 | 0.2 | -2.3 | 18.9 | 149.7 | 227.6 | -0.05 | 0 | -4.96 | -4.1 | 66.5 | 2.44 | 7.76 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.75
55 | 2008-08-03 | 60000 | 1 | 647.3 | 5.2 | -10.9 | 18.9 | 149.9 | 227.6 | -0.049 | 0 | -4.96 | -74.4 | 67.5 | 3.4 | 8.5 | 1.6 | 9.67 | 3.9 | 7.929 | 0.008 | 12.2
56 | 2008-08-03 | 70000 | 1 | 647.6 | 0.6 | -2.5 | 18.88 | 150.1 | 228.2 | -0.047 | 0 | -4.96 | -4.1 | 66.6 | 2.45 | 7.75 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.74
57 | 2008-08-03 | 80000 | 1 | 646.6 | 0.6 | -2.4 | 18.86 | 149 | 226.9 | -0.05 | 0 | -4.96 | -4.1 | 65.3 | 2.44 | 7.7 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.73
58 | 2008-08-03 | 90000 | 1 | 646.7 | 0.6 | -2 | 18.9 | 149.6 | 227.6 | -0.048 | 0 | -4.96 | -4.1 | 65.8 | 2.44 | 8.51 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.73
59 | 2008-08-03 | 100000 | 1 | 647.3 | 0.6 | -2.5 | 18.9 | 149.3 | 227.5 | -0.047 | 0 | -4.96 | -4.1 | 65 | 2.45 | 7.69 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.73
60 | 2008-08-03 | 110000 | 1 | 647.2 | 0.5 | -2.3 | 18.92 | 149.6 | 227.9 | -0.049 | 0 | -4.96 | -4.1 | 64.7 | 2.45 | 7.52 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.72
61 | 2008-08-03 | 120000 | 1 | 647.6 | 0.5 | -2.2 | 19.12 | 151.4 | 230.2 | -0.047 | 0 | -4.96 | -4.1 | 70.5 | 2.54 | 7.84 | 2.1 | 2.52 | 2.1 | 0.008 | 0.007 | 13.71
62 | 2008-08-03 | 130000 | 1 | 668 | 0.5 | -2.1 | 21.79 | 177.5 | 267.5 | 0.006 | 0 | -4.96 | -3.9 | 133 | 2.53 | 11.99 | 2 | 2.52 | 2 | 0.007 | 0.007 | 13.4
63 | 2008-08-03 | 140000 | 1 | 686.8 | 0.4 | -2.3 | 21.35 | 173.8 | 267.8 | 0.058 | 1 | -4.96 | -3.9 | 128.4 | 2.54 | 11.65 | 2 | 2.52 | 2 | 0.007 | 0.007 | 13.33
64 | 2008-08-03 | 150000 | 1 | 667.5 | 0.5 | -2.3 | 21.42 | 174.7 | 262 | -0.046 | 0 | -4.96 | -4 | 120.7 | 2.4 | 10.91 | 1.9 | 2.38 | 1.9 | 0.007 | 0.007 | 13.55
65 | 2008-08-03 | 160000 | 1 | 665.7 | 0.4 | -2.6 | 21.43 | 175 | 262.4 | -0.047 | 0 | -4.96 | -4 | 126 | 2.34 | 11.03 | 1.9 | 2.33 | 1.9 | 0.007 | 0.007 | 13.54
66 | 2008-08-03 | 170000 | 1 | 665.8 | 0.4 | -2.4 | 21.39 | 174.4 | 261.3 | -0.047 | 0 | -4.97 | -4 | 117.4 | 2.45 | 10.74 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.56
67 | 2008-08-03 | 180000 | 1 | 664.8 | 0.4 | -2.4 | 21.54 | 175.8 | 263.5 | -0.047 | 0 | -4.97 | -3.9 | 130.2 | 2.51 | 11.7 | 2 | 2.49 | 2 | 0.007 | 0.007 | 13.47
68 | 2008-08-03 | 190000 | 1 | 663.8 | 0.4 | -2.3 | 21.53 | 176.5 | 263.9 | -0.047 | 0 | -4.96 | -3.9 | 128.9 | 2.48 | 11.66 | 2 | 2.47 | 2 | 0.007 | 0.007 | 13.49
69 | 2008-08-03 | 200000 | 1 | 648.6 | 0.4 | -2.2 | 18.65 | 147.1 | 225.1 | -0.046 | 0 | -4.96 | -4.1 | 59.1 | 2.43 | 7.15 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.7
70 | 2008-08-03 | 210000 | 1 | 647.3 | 0.4 | -2 | 18.97 | 150.7 | 228.7 | -0.047 | 0 | -4.96 | -4.1 | 64.3 | 2.43 | 7.32 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.72
71 | 2008-08-03 | 220000 | 1 | 647.8 | 0.3 | -2.4 | 18.88 | 150.2 | 228.4 | -0.047 | 0 | -4.97 | -4.1 | 63.9 | 2.46 | 7.33 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.71
72 | 2008-08-03 | 230000 | 1 | 647.4 | 0.3 | -2 | 18.88 | 149.7 | 227.7 | -0.046 | 0 | -4.96 | -4.1 | 64.4 | 2.45 | 7.35 | 2 | 2.42 | 2 | 0.007 | 0.007 | 13.71
73 | 2008-08-04 | 0 | 1 | 647.7 | 0.3 | -2.4 | 18.85 | 149.8 | 227.8 | -0.047 | 0 | -4.96 | -4.1 | 64.2 | 2.45 | 7.35 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.71
74 | 2008-08-04 | 10000 | 1 | 646.9 | 0.3 | -2.1 | 18.87 | 149.6 | 227.4 | -0.048 | 0 | -4.96 | -4.1 | 64.4 | 2.46 | 7.37 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.71
75 | 2008-08-04 | 20000 | 1 | 647 | 0.3 | -2.3 | 18.9 | 149.6 | 227.4 | -0.048 | 0 | -4.96 | -4.1 | 64.9 | 2.46 | 7.38 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.71
76 | 2008-08-04 | 30000 | 1 | 646.6 | 0.3 | -2 | 18.9 | 149.1 | 226.9 | -0.047 | 0 | -4.96 | -4.1 | 64.5 | 2.46 | 7.36 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.7
77 | 2008-08-04 | 40000 | 1 | 646.7 | 0.3 | -2.4 | 18.91 | 149.5 | 227.3 | -0.046 | 0 | -4.96 | -4.1 | 64.9 | 2.46 | 7.41 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.71
78 | 2008-08-04 | 50000 | 1 | 647.7 | 0.2 | -2.1 | 18.95 | 150.5 | 228.7 | -0.047 | 0 | -4.97 | -4.1 | 65.9 | 2.44 | 7.43 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.71
79 | 2008-08-04 | 60000 | 1 | 647.8 | 3 | -9.4 | 18.9 | 149.8 | 227.8 | -0.048 | 0 | -4.96 | -41 | 65.2 | 3.47 | 14.7 | 2 | 9.85 | 4 | 15.843 | 0.008 | 12.12
80 | 2008-08-04 | 70000 | 1 | 648.2 | 0.6 | -2.6 | 18.91 | 150.6 | 228.8 | -0.048 | 0 | -4.96 | -4.1 | 65.8 | 2.45 | 7.42 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.69
81 | 2008-08-04 | 80000 | 1 | 648.1 | 0.6 | -2.3 | 18.91 | 149.8 | 227.9 | -0.048 | 0 | -4.96 | -4.1 | 65 | 2.46 | 7.41 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.69
82 | 2008-08-04 | 90000 | 1 | 647.4 | 0.6 | -2.3 | 18.91 | 149.6 | 227.8 | -0.048 | 0 | -4.96 | -4.1 | 64.8 | 2.46 | 8.25 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.69
83 | 2008-08-04 | 100000 | 1 | 647.6 | 0.6 | -1.9 | 19.02 | 151.1 | 229.4 | -0.047 | 0 | -4.96 | -4.1 | 66 | 2.46 | 7.38 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.69
84 | 2008-08-04 | 110000 | 1 | 662.3 | 0.5 | -2.6 | 20.57 | 166.1 | 248.7 | -0.048 | 0 | -4.96 | -4.1 | 74.2 | 2.4 | 7.67 | 2 | 2.38 | 2 | 0.007 | 0.007 | 13.79
85 | 2008-08-04 | 120000 | 1 | 667 | 0.5 | -2.2 | 20.58 | 166 | 251.5 | 0.02 | 0 | -4.96 | -4 | 90.2 | 2.64 | 9.07 | 2.1 | 2.62 | 2.1 | 0.008 | 0.008 | 13.55
86 | 2008-08-04 | 130000 | 1 | 741.7 | 0.3 | -1.7 | 21.32 | 172.2 | 289.7 | 0.515 | 1 | -4.96 | -3.4 | 146.8 | 3 | 13.7 | 2 | 2.98 | 2 | 0.007 | 0.007 | 12.23
87 | 2008-08-04 | 140000 | 1 | 745.9 | 0.3 | -2 | 21.17 | 171.1 | 288.4 | 0.497 | 1 | -4.96 | -3.4 | 145.8 | 2.95 | 13.54 | 2 | 2.94 | 2 | 0.007 | 0.007 | 12.25
88 | 2008-08-04 | 150000 | 1 | 747 | 0.3 | -1.9 | 21.06 | 170.2 | 287.9 | 0.493 | 1 | -4.96 | -3.4 | 145 | 2.93 | 13.43 | 2 | 2.91 | 2 | 0.007 | 0.007 | 12.24
89 | 2008-08-04 | 160000 | 1 | 674.6 | 0.5 | -2.2 | 20.43 | 164.3 | 248.8 | -0.049 | 0 | -4.96 | -4.1 | 79.2 | 2.32 | 8.13 | 1.9 | 2.3 | 1.9 | 0.007 | 0.007 | 13.66
90 | 2008-08-04 | 170000 | 1 | 664 | 0.5 | -1.9 | 20.56 | 165.3 | 248.5 | -0.051 | 0 | -4.96 | -4 | 80.1 | 2.44 | 8.31 | 2 | 2.41 | 2 | 0.007 | 0.007 | 13.66
91 | 2008-08-04 | 180000 | 1 | 665.6 | 0.4 | -2.1 | 20.6 | 165.8 | 248.9 | -0.051 | 0 | -4.96 | -4.1 | 79.5 | 2.5 | 8.26 | 2 | 2.48 | 2 | 0.007 | 0.007 | 13.67
92 | 2008-08-04 | 190000 | 1 | 663.5 | 0.4 | -2.3 | 20.63 | 165.9 | 249 | -0.052 | 0 | -4.96 | -4 | 81.9 | 2.47 | 8.42 | 2 | 2.46 | 2 | 0.007 | 0.007 | 13.64
93 | 2008-08-04 | 200000 | 1 | 663.2 | 0.4 | -2.4 | 20.54 | 164.9 | 247.8 | -0.051 | 0 | -4.96 | -4 | 84.2 | 2.45 | 8.53 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.65
94 | 2008-08-04 | 210000 | 1 | 661.5 | 0.4 | -2.3 | 20.45 | 164.1 | 247.7 | -0.05 | 0 | -4.96 | -4 | 91.8 | 2.41 | 9.12 | 2 | 2.4 | 1.9 | 0.007 | 0.007 | 13.65
95 | 2008-08-04 | 220000 | 1 | 649.7 | 0.4 | -2.1 | 18.85 | 149 | 227 | -0.051 | 0 | -4.96 | -4.1 | 62.5 | 2.51 | 7.41 | 2.1 | 2.5 | 2 | 0.008 | 0.008 | 13.68
96 | 2008-08-04 | 230000 | 1 | 648.4 | 0.4 | -2.1 | 18.95 | 149.5 | 227.6 | -0.05 | 0 | -4.96 | -4.1 | 63.8 | 2.46 | 7.39 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.68
97 | 2008-08-05 | 0 | 1 | 648.6 | 0.3 | -2.2 | 18.92 | 149.5 | 227.6 | -0.049 | 0 | -4.96 | -4.1 | 63.3 | 2.46 | 7.34 | 2 | 2.44 | 2 | 0.007 | 0.007 | 13.67
98 | 2008-08-05 | 10000 | 1 | 648.6 | 0.3 | -2.4 | 18.84 | 149.3 | 227.2 | -0.05 | 0 | -4.96 | -4.1 | 62.6 | 2.47 | 7.3 | 2 | 2.46 | 2 | 0.007 | 0.007 | 13.67
99 | 2008-08-05 | 20000 | 1 | 648.6 | 0.3 | -2.2 | 18.87 | 149.5 | 227.4 | -0.05 | 0 | -4.96 | -4.1 | 62.5 | 2.47 | 7.26 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.66
100 | 2008-08-05 | 30000 | 1 | 648.5 | 0.3 | -2 | 18.95 | 150.2 | 228.1 | -0.05 | 0 | -4.97 | -4 | 63 | 2.45 | 7.26 | 2 | 2.43 | 2 | 0.007 | 0.007 | 13.66
101 | 2008-08-05 | 40000 | 1 | 648.5 | 0.3 | -2.2 | 18.9 | 149.8 | 227.7 | -0.049 | 0 | -4.96 | -4 | 63 | 2.47 | 7.26 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.66
102 | 2008-08-05 | 50000 | 1 | 648.9 | 0.3 | -2.6 | 18.99 | 150.5 | 228.5 | -0.05 | 0 | -4.96 | -4 | 63.5 | 2.46 | 7.29 | 2 | 2.45 | 2 | 0.007 | 0.007 | 13.66
103 | 2008-08-05 | 60000 | 1 | 649 | 2.7 | 12.2 | 18.95 | 150.1 | 228.2 | -0.05 | 0 | -4.96 | -23.3 | 63.6 | 3.5 | 8.16 | 2 | 9.68 | 3.9 | 0.016 | 0.009 | 12.13
104 | 2008-08-05 | 70000 | 1 | 647.8 | 0.4 | -2.2 | 18.9 | 149.2 | 227 | -0.049 | 0 | -4.96 | -4.1 | 64.1 | 2.42 | 7.27 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.79
105 | 2008-08-05 | 80000 | 1 | 648.5 | 0.6 | -2.3 | 18.99 | 150.3 | 228.4 | -0.051 | 0 | -4.96 | -4.1 | 65.4 | 2.43 | 7.35 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.76
106 | 2008-08-05 | 90000 | 1 | 647.7 | 0.6 | -2.1 | 18.93 | 149.3 | 227.3 | -0.05 | 0 | -4.96 | -4.1 | 66.1 | 2.43 | 8.37 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.78
107 | 2008-08-05 | 100000 | 1 | 648.9 | 0.6 | -2.4 | 18.99 | 150 | 228.5 | -0.051 | 0 | -4.96 | -4.1 | 67 | 2.43 | 7.69 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.8
108 | 2008-08-05 | 110000 | 1 | 648.6 | 0.5 | -2.6 | 18.96 | 149.5 | 228 | -0.05 | 0 | -4.96 | -4.1 | 67 | 2.41 | 7.67 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.81
109 | 2008-08-05 | 120000 | 1 | 650.8 | 0.5 | -2.3 | 19.13 | 151.2 | 230.3 | -0.05 | 0 | -4.96 | -4.1 | 67.9 | 2.41 | 7.73 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.82
110 | 2008-08-05 | 130000 | 1 | 651.4 | 0.5 | -2.4 | 19.1 | 150.9 | 230 | -0.048 | 0 | -4.96 | -4.1 | 68.5 | 2.41 | 7.77 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.83
111 | 2008-08-05 | 140000 | 1 | 653.3 | 0.5 | -2.8 | 19.24 | 151.6 | 231 | -0.049 | 0 | -4.96 | -4.2 | 69.1 | 2.42 | 7.76 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.85
112 | 2008-08-05 | 150000 | 1 | 653.5 | 0.5 | -2.2 | 19.17 | 150.8 | 230.1 | -0.05 | 0 | -4.97 | -4.2 | 68.3 | 2.4 | 7.65 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.84
113 | 2008-08-05 | 160000 | 0 | 613.9 | 18.9 | -56.7 | 9.09 | 70.7 | 109.4 | -0.047 | 0 | -4.97 | -102.7 | 34 | 1.37 | 4.14 | 0.8 | 1.55 | 1.4 | 0.008 | 0.005 | 17.28
114 | 2008-08-05 | 170000 | 0 | 462.9 | 22.7 | -98.7 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -214.1 | 0.5 | -0.05 | 0.02 | -2 | -0.01 | -0.5 | 0.004 | 0 | 20.76
115 | 2008-08-05 | 180000 | 0 | 425.3 | 23.8 | -101.4 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -218.6 | 0.5 | -0.05 | -0.01 | -2 | -0.02 | -1.2 | 0.002 | 0 | 20.76
116 | 2008-08-05 | 190000 | 0 | 414.7 | 24.8 | -145.6 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -247.1 | 0.6 | -0.05 | -0.04 | -2.4 | -0.02 | -1.1 | 0.003 | 0 | 20.78
117 | 2008-08-05 | 200000 | 0 | 407.5 | 27.6 | -169.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -297.2 | 0.7 | -0.05 | -0.03 | -2.9 | -0.02 | -1.1 | 0.004 | 0 | 20.8
118 | 2008-08-05 | 210000 | 0 | 401.7 | 31.7 | -196.9 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -368.3 | 0.8 | -0.05 | -0.04 | -3.8 | -0.02 | -1.2 | 0.005 | 0 | 20.82
119 | 2008-08-05 | 220000 | 0 | 396.6 | 35.6 | -230.8 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -452.6 | 0.6 | -0.05 | -0.03 | -4.7 | -0.02 | -2.2 | 0.005 | 0 | 20.83
120 | 2008-08-05 | 230000 | 0 | 390.7 | 41.1 | -257.3 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -4.97 | -556.2 | 0.6 | -0.05 | -0.04 | -5.9 | -0.02 | -2.8 | 0.006 | 0 | 20.84
121 | 2008-08-06 | 0 | 0 | 384.7 | 45.9 | -344.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -670.9 | 0.6 | -0.05 | -0.03 | -7.3 | -0.03 | -4.3 | 0.007 | 0 | 20.85
122 | 2008-08-06 | 10000 | 0 | 379.3 | 50.7 | -359.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -782.8 | 0.6 | -0.05 | -0.03 | -8.5 | -0.04 | -6.5 | 0.007 | 0 | 20.86
123 | 2008-08-06 | 20000 | 0 | 374 | 53.6 | -473.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -870.7 | 0.7 | -0.05 | -0.03 | -9.4 | -0.05 | -7.9 | 17.416 | 0 | 20.86
124 | 2008-08-06 | 30000 | 0 | 371.4 | 54 | -513.3 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -4.97 | -1016.4 | 0.7 | -0.06 | -0.03 | -11.4 | -0.05 | -9.5 | 25.331 | 0.001 | 20.87
125 | 2008-08-06 | 40000 | 1 | 527.6 | 26.5 | -36.9 | 5.92 | 16 | 16.4 | -0.049 | 0 | -4.96 | -131.7 | 0.6 | 8.71 | 25.38 | 11.3 | 33.63 | 47.8 | 0.179 | 0.047 | 17.35
126 | 2008-08-06 | 50000 | 1 | 615.7 | 17.4 | 24.6 | 10.99 | 60.2 | 89.2 | -0.048 | 0 | -4.96 | -5.1 | 49.1 | 8.89 | 26.51 | 9.5 | 40.81 | 43.1 | 0.159 | 0.035 | 15.11
127 | 2008-08-06 | 60000 | 1 | 636.2 | 1.5 | 24 | 17.72 | 136.5 | 209.6 | -0.049 | 0 | -4.96 | -5.5 | 49.6 | 3.35 | 7.37 | 2 | 9.27 | 3.6 | 0.014 | 0.008 | 12.13
128 | 2008-08-06 | 70000 | 1 | 638.8 | 1.5 | -1.8 | 17.62 | 135.6 | 209.7 | -0.048 | 0 | -4.96 | -6.9 | 56.4 | 2.4 | 7.03 | 2.2 | 2.33 | 2.1 | 0.008 | 0.008 | 13.96
129 | 2008-08-06 | 80000 | 1 | 647.8 | 0.7 | -2.3 | 19 | 150.3 | 227.3 | -0.049 | 0 | -4.96 | -4.1 | 64.9 | 2.38 | 7.61 | 2 | 2.21 | 1.8 | 0.007 | 0.007 | 13.78
130 | 2008-08-06 | 90000 | 1 | 649.8 | 0.7 | -2 | 19.1 | 151.2 | 228.8 | -0.048 | 0 | -4.97 | -4.1 | 67.3 | 2.44 | 8.36 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.79
131 | 2008-08-06 | 100000 | 1 | 647.9 | 0.6 | -2.4 | 18.98 | 150.2 | 228.3 | -0.049 | 0 | -4.96 | -4.1 | 66 | 2.43 | 7.54 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.79
132 | 2008-08-06 | 110000 | 1 | 648.1 | 0.6 | -2.3 | 18.96 | 150 | 228.1 | -0.048 | 0 | -4.96 | -4.1 | 66.1 | 2.42 | 7.53 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.79
133 | 2008-08-06 | 120000 | 1 | 649.6 | 0.6 | -2 | 19.1 | 151.1 | 229.7 | -0.049 | 0 | -4.96 | -4.1 | 67.1 | 2.42 | 7.63 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.8
134 | 2008-08-06 | 130000 | 1 | 649.9 | 0.6 | -2.3 | 19.08 | 151.4 | 229.9 | -0.047 | 0 | -4.97 | -4.1 | 67.7 | 2.41 | 7.65 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.81
135 | 2008-08-06 | 140000 | 1 | 650.8 | 0.5 | -2.3 | 19.24 | 152.2 | 230.9 | -0.046 | 0 | -4.96 | -4.1 | 69.7 | 2.48 | 7.85 | 2.1 | 2.31 | 1.9 | 0.007 | 0.007 | 13.8
136 | 2008-08-06 | 150000 | 1 | 660.3 | 0.5 | -2.3 | 20.32 | 162.6 | 246 | -0.049 | 0 | -4.97 | -4.1 | 93.8 | 2.36 | 9.41 | 2 | 2.19 | 1.8 | 0.007 | 0.007 | 13.76
137 | 2008-08-06 | 160000 | 1 | 646.9 | 0.5 | -2.5 | 18.7 | 146.9 | 224.2 | -0.05 | 0 | -4.96 | -4.1 | 65.4 | 2.52 | 7.64 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.78
138 | 2008-08-06 | 170000 | 1 | 658.4 | 0.5 | -2.3 | 20.55 | 165.3 | 249.6 | -0.05 | 0 | -4.96 | -4 | 114.4 | 2.46 | 10.96 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.65
139 | 2008-08-06 | 180000 | 1 | 659.7 | 0.5 | -2.3 | 20.53 | 165 | 248.8 | -0.052 | 0 | -4.97 | -4.1 | 103.2 | 2.41 | 10.18 | 2 | 2.25 | 1.8 | 0.007 | 0.007 | 13.7
140 | 2008-08-06 | 190000 | 1 | 660.6 | 0.5 | -2.2 | 20.46 | 165.1 | 248.2 | -0.05 | 0 | -4.96 | -4.1 | 88.8 | 2.36 | 9.07 | 2 | 2.2 | 1.8 | 0.007 | 0.007 | 13.8
141 | 2008-08-06 | 200000 | 1 | 664.2 | 0.4 | -2.4 | 20.56 | 166.4 | 248.8 | -0.053 | 0 | -4.97 | -4.2 | 81.4 | 2.35 | 8.14 | 2 | 2.18 | 1.8 | 0.007 | 0.007 | 13.87
142 | 2008-08-06 | 210000 | 1 | 664 | 0.4 | -2.6 | 20.44 | 165.9 | 247.8 | -0.051 | 0 | -4.96 | -4.2 | 70.8 | 2.33 | 7.74 | 2 | 2.17 | 1.8 | 0.007 | 0.007 | 13.89
143 | 2008-08-06 | 220000 | 1 | 650.1 | 0.4 | -2.4 | 18.92 | 149.5 | 227.6 | -0.05 | 0 | -4.96 | -4.1 | 65.2 | 2.36 | 7.56 | 2 | 2.19 | 1.8 | 0.007 | 0.007 | 13.8
144 | 2008-08-06 | 230000 | 1 | 647.3 | 0.4 | -2.5 | 18.96 | 150.2 | 227.9 | -0.052 | 0 | -4.97 | -4.1 | 65.8 | 2.41 | 7.56 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.8
145 | 2008-08-07 | 0 | 1 | 647.5 | 0.3 | -2.5 | 18.93 | 150.3 | 228.2 | -0.051 | 0 | -4.96 | -4.1 | 65.9 | 2.42 | 7.57 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.8
146 | 2008-08-07 | 10000 | 1 | 647.2 | 0.3 | -1.8 | 18.94 | 149.9 | 227.7 | -0.049 | 0 | -4.96 | -4.1 | 64.6 | 2.42 | 7.54 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.8
147 | 2008-08-07 | 20000 | 1 | 647.4 | 0.3 | -2.2 | 18.92 | 150.1 | 227.8 | -0.05 | 0 | -4.96 | -4.1 | 64.8 | 2.43 | 7.57 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.8
148 | 2008-08-07 | 30000 | 1 | 647.9 | 0.3 | -2.2 | 18.95 | 150.8 | 228.7 | -0.049 | 0 | -4.96 | -4.1 | 65 | 2.42 | 7.6 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.79
149 | 2008-08-07 | 40000 | 1 | 647.6 | 0.3 | -2.4 | 18.96 | 150.3 | 228.3 | -0.05 | 0 | -4.96 | -4.1 | 64.7 | 2.43 | 7.48 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.79
150 | 2008-08-07 | 50000 | 1 | 647.1 | 0.3 | -2.4 | 18.96 | 149.8 | 227.6 | -0.05 | 0 | -4.96 | -4.1 | 64.3 | 2.42 | 7.46 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.79
151 | 2008-08-07 | 60000 | 1 | 648.7 | 1.5 | 23.3 | 19.1 | 151.7 | 229.8 | -0.049 | 0 | -4.96 | -4.4 | 76.5 | 3.28 | 8.28 | 1.9 | 9.2 | 3.5 | 0.014 | 0.008 | 12.12
152 | 2008-08-07 | 70000 | 1 | 647.9 | 1.5 | -3.2 | 19.19 | 152.1 | 230.3 | -0.048 | 0 | -4.96 | -6.4 | 65.8 | 2.27 | 7.56 | 1.9 | 2.19 | 1.9 | 0.007 | 0.007 | 13.92
153 | 2008-08-07 | 80000 | 1 | 663.8 | 0.8 | -2.2 | 21.59 | 175.8 | 262.2 | -0.052 | 0 | -4.96 | -4 | 121.4 | 2.46 | 11.12 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.66
154 | 2008-08-07 | 90000 | 1 | 665.7 | 0.7 | -2.3 | 21.48 | 174.5 | 260.7 | -0.051 | 0 | -4.96 | -4.1 | 111.1 | 2.41 | 10.9 | 2 | 2.24 | 1.8 | 0.007 | 0.007 | 13.7
155 | 2008-08-07 | 100000 | 1 | 665.9 | 0.7 | -2.3 | 21.41 | 174.5 | 260.8 | -0.05 | 0 | -4.96 | -4.1 | 114.6 | 2.54 | 10.78 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.68
156 | 2008-08-07 | 110000 | 1 | 664.6 | 0.7 | -2.4 | 21.47 | 174.9 | 261.6 | -0.051 | 0 | -4.96 | -4 | 121.4 | 2.46 | 11.34 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.65
157 | 2008-08-07 | 120000 | 1 | 663.4 | 0.7 | -2.1 | 21.47 | 174.5 | 261.3 | -0.05 | 0 | -4.96 | -4 | 125.2 | 2.53 | 11.67 | 2 | 2.35 | 1.9 | 0.007 | 0.008 | 13.62
158 | 2008-08-07 | 130000 | 1 | 663.7 | 0.6 | -2.3 | 21.51 | 174.7 | 262.1 | -0.041 | 0 | -4.96 | -4 | 129.4 | 2.49 | 11.96 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.55
159 | 2008-08-07 | 140000 | 1 | 663.2 | 0.6 | -2.4 | 21.45 | 174.2 | 260.9 | -0.052 | 0 | -4.96 | -4 | 127.5 | 2.5 | 11.82 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.54
160 | 2008-08-07 | 150000 | 1 | 650.1 | 0.6 | -2 | 18.95 | 149.6 | 227.8 | -0.05 | 0 | -4.96 | -4.1 | 65.8 | 2.37 | 7.74 | 1.9 | 2.21 | 1.8 | 0.007 | 0.007 | 13.73
161 | 2008-08-07 | 160000 | 1 | 649.1 | 0.6 | -2.3 | 19.12 | 151.5 | 229.9 | -0.049 | 0 | -4.96 | -4.1 | 67.5 | 2.41 | 7.74 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.78
162 | 2008-08-07 | 170000 | 1 | 650.1 | 0.6 | -2 | 19.12 | 151.2 | 229.8 | -0.048 | 0 | -4.96 | -4.1 | 66.2 | 2.43 | 7.64 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.77
163 | 2008-08-07 | 180000 | 1 | 649.2 | 0.5 | -2.5 | 19.07 | 151.1 | 229.3 | -0.049 | 0 | -4.96 | -4.1 | 64.8 | 2.43 | 7.52 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.75
164 | 2008-08-07 | 190000 | 1 | 649.6 | 0.5 | -2.6 | 19.19 | 152.9 | 231.3 | -0.047 | 0 | -4.96 | -4.1 | 68.3 | 2.49 | 7.65 | 2 | 2.31 | 1.9 | 0.007 | 0.008 | 13.74
165 | 2008-08-07 | 200000 | 1 | 662.2 | 0.5 | -2.4 | 21.34 | 173.6 | 260 | -0.048 | 0 | -4.97 | -4 | 125.6 | 2.49 | 11.58 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.57
166 | 2008-08-07 | 210000 | 1 | 663.7 | 0.4 | -2.1 | 21.27 | 173.2 | 259.1 | -0.049 | 0 | -4.97 | -4 | 112.6 | 2.41 | 10.65 | 2 | 2.24 | 1.8 | 0.007 | 0.007 | 13.65
167 | 2008-08-07 | 220000 | 1 | 665.1 | 0.4 | -2.4 | 21.28 | 173.4 | 259.1 | -0.047 | 0 | -4.96 | -4.1 | 107.4 | 2.41 | 10.27 | 2 | 2.24 | 1.8 | 0.007 | 0.007 | 13.68
168 | 2008-08-07 | 230000 | 1 | 666.1 | 0.4 | -2.7 | 21.31 | 173.1 | 258.3 | -0.048 | 0 | -4.96 | -4.1 | 101.9 | 2.47 | 9.88 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.71
169 | 2008-08-08 | 0 | 1 | 665.7 | 0.3 | -2.3 | 21.25 | 172.9 | 258.1 | -0.05 | 0 | -4.96 | -4.1 | 103.3 | 2.31 | 9.73 | 1.9 | 2.13 | 1.8 | 0.006 | 0.007 | 13.73
170 | 2008-08-08 | 10000 | 1 | 666.6 | 0.3 | -2 | 21.32 | 173.7 | 259.6 | -0.049 | 0 | -4.96 | -4.1 | 109.7 | 2.37 | 10.24 | 1.9 | 2.2 | 1.8 | 0.007 | 0.007 | 13.7
171 | 2008-08-08 | 20000 | 1 | 650.6 | 0.3 | -2 | 18.98 | 151 | 229.4 | -0.047 | 0 | -4.96 | -4.1 | 64.7 | 2.45 | 7.48 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.76
172 | 2008-08-08 | 30000 | 1 | 648.2 | 0.3 | -1.8 | 19.07 | 151.7 | 229.9 | -0.047 | 0 | -4.96 | -4.1 | 67.5 | 2.43 | 7.5 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.76
173 | 2008-08-08 | 40000 | 1 | 648.6 | 0.3 | -2.6 | 19.06 | 151.5 | 229.6 | -0.047 | 0 | -4.96 | -4.1 | 67.8 | 2.43 | 7.5 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.76
174 | 2008-08-08 | 50000 | 1 | 648.8 | 0.3 | -2.3 | 19.1 | 151.6 | 229.8 | -0.047 | 0 | -4.96 | -4.1 | 67.8 | 2.44 | 7.51 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.76
175 | 2008-08-08 | 60000 | 1 | 649.1 | 3 | -27.8 | 19.1 | 151.8 | 230 | -0.047 | 0 | -4.96 | -58.5 | 76.7 | 3.4 | 8.29 | 1.7 | 9.36 | 4 | 0.016 | 0.009 | 12.08
176 | 2008-08-08 | 70000 | 1 | 661.4 | 1.3 | -1.9 | 21.43 | 174.3 | 260.3 | -0.048 | 0 | -4.97 | -5.1 | 128.6 | 2.28 | 11.3 | 1.9 | 2.21 | 1.9 | 0.007 | 0.007 | 13.73
177 | 2008-08-08 | 80000 | 1 | 666.6 | 0.8 | -2.4 | 21.41 | 174.6 | 260.7 | -0.048 | 0 | -4.97 | -4.1 | 109.6 | 2.4 | 10.19 | 2 | 2.23 | 1.8 | 0.007 | 0.007 | 13.7
178 | 2008-08-08 | 90000 | 1 | 667.4 | 0.8 | -2.3 | 21.4 | 174.8 | 261 | -0.049 | 0 | -4.96 | -4.1 | 111.4 | 2.5 | 10.79 | 2 | 2.33 | 1.9 | 0.007 | 0.008 | 13.7
179 | 2008-08-08 | 100000 | 1 | 667.4 | 0.7 | -2.2 | 21.45 | 174.6 | 261.1 | -0.049 | 0 | -4.96 | -4.1 | 112.6 | 2.47 | 10.39 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.69
180 | 2008-08-08 | 110000 | 1 | 667.6 | 0.7 | -2.1 | 21.4 | 174.2 | 260.6 | -0.048 | 0 | -4.96 | -4.1 | 112.7 | 2.41 | 10.38 | 2 | 2.25 | 1.8 | 0.007 | 0.007 | 13.69
181 | 2008-08-08 | 120000 | 1 | 666.9 | 0.7 | -2.1 | 21.37 | 174.2 | 259.8 | -0.049 | 0 | -4.96 | -4.1 | 115 | 2.49 | 10.57 | 2 | 2.31 | 1.9 | 0.007 | 0.008 | 13.68
182 | 2008-08-08 | 130000 | 1 | 666.5 | 0.6 | -2.2 | 21.37 | 174.3 | 261 | -0.048 | 0 | -4.96 | -4 | 119.1 | 2.47 | 10.88 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.66
183 | 2008-08-08 | 140000 | 1 | 665.5 | 0.6 | -2.2 | 21.29 | 172.3 | 257.6 | -0.048 | 0 | -4.96 | -4.1 | 114.5 | 2.49 | 10.61 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.68
184 | 2008-08-08 | 150000 | 1 | 664.3 | 0.6 | -2.1 | 21.35 | 173.4 | 260.9 | -0.048 | 0 | -4.96 | -4 | 136.6 | 2.54 | 12.15 | 2 | 2.36 | 1.9 | 0.007 | 0.008 | 13.59
185 | 2008-08-08 | 160000 | 1 | 663.9 | 0.6 | -2.2 | 21.39 | 173.6 | 260.8 | -0.048 | 0 | -4.96 | -4 | 129.1 | 2.44 | 11.6 | 2 | 2.27 | 1.8 | 0.007 | 0.007 | 13.57
186 | 2008-08-08 | 170000 | 1 | 669.1 | 0.6 | -2.3 | 21.24 | 172.3 | 260 | -0.006 | 0 | -4.96 | -4 | 119.1 | 2.55 | 11.1 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.49
187 | 2008-08-08 | 180000 | 1 | 667 | 0.5 | -2.3 | 21.5 | 174.9 | 262.1 | -0.046 | 0 | -4.96 | -4 | 123 | 2.49 | 11.21 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.59
188 | 2008-08-08 | 190000 | 1 | 664.4 | 0.5 | -2.1 | 21.57 | 176.1 | 263.4 | -0.048 | 0 | -4.96 | -4 | 130.5 | 2.5 | 11.74 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.56
189 | 2008-08-08 | 200000 | 1 | 666.5 | 0.5 | -1.9 | 21.64 | 176.4 | 263.7 | -0.052 | 0 | -4.97 | -4 | 128.4 | 2.46 | 11.58 | 2 | 2.29 | 1.8 | 0.007 | 0.007 | 13.58
190 | 2008-08-08 | 210000 | 1 | 666 | 0.4 | -2.2 | 21.63 | 176.2 | 263.6 | -0.052 | 0 | -4.96 | -4 | 127.4 | 2.46 | 11.46 | 2 | 2.29 | 1.8 | 0.007 | 0.007 | 13.6
191 | 2008-08-08 | 220000 | 1 | 650 | 0.4 | -2.2 | 18.91 | 149.8 | 228 | -0.048 | 0 | -4.96 | -4.1 | 63.1 | 2.3 | 7.34 | 1.9 | 2.13 | 1.8 | 0.007 | 0.007 | 13.77
192 | 2008-08-08 | 230000 | 1 | 649.6 | 0.4 | -2.2 | 19.03 | 150.8 | 229.1 | -0.051 | 0 | -4.96 | -4.1 | 64.1 | 2.43 | 7.4 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.78
193 | 2008-08-09 | 0 | 0 | 560.2 | 44.7 | -125.3 | 1.6 | 7.7 | 14 | -0.05 | 0 | -4.96 | -287.8 | 3.3 | 1.63 | 4.78 | 0.2 | 6.44 | 6.8 | 0.032 | 0.009 | 19.68
194 | 2008-08-09 | 10000 | 0 | 450.6 | 59.7 | -421.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -701.7 | 0.6 | -0.05 | 0.02 | -7.4 | -0.02 | -3.1 | 0.009 | 0 | 20.78
195 | 2008-08-09 | 20000 | 0 | 426.8 | 67.2 | -454.5 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -4.97 | -779.3 | 0.6 | -0.05 | -0.03 | -8.6 | -0.02 | -2.8 | 63.32 | 0 | 20.86
196 | 2008-08-09 | 30000 | 0 | 418.7 | 70.7 | -436.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -4.97 | -852.1 | 0.6 | -0.05 | -0.04 | -9.2 | -0.05 | -7 | 15.835 | 0 | 20.86
197 | 2008-08-09 | 40000 | 0 | 420.6 | 71.9 | -563.5 | 0.05 | 0.5 | 1.2 | -0.051 | 0 | -4.97 | -969 | 0.7 | -0.05 | -0.04 | -10.3 | -0.05 | -7.9 | 34.826 | 0.001 | 20.79
198 | 2008-08-09 | 50000 | 1 | 578.2 | 19.6 | 3.4 | 9.4 | 45.7 | 46.3 | -0.051 | 0 | -4.96 | -23.4 | 17.2 | 9.14 | 26.7 | 10.2 | 43.55 | 47.2 | 0.175 | 0.038 | 15.64
199 | 2008-08-09 | 60000 | 1 | 644.9 | 0.4 | -2.4 | 20.44 | 164.5 | 238.3 | -0.051 | 0 | -4.96 | -4.1 | 97.9 | 2.12 | 9.67 | 1.8 | 1.97 | 1.6 | 0.006 | 0.007 | 13.81
200 | 2008-08-09 | 70000 | 1 | 650.3 | 2.9 | 22.4 | 19.05 | 150.5 | 228.4 | -0.05 | 0 | -4.96 | -15.4 | 68.1 | 3.27 | 8.31 | 2 | 9.26 | 3.7 | 0.014 | 0.008 | 12.25
201 | 2008-08-09 | 80000 | 1 | 649.5 | 0.6 | -2.4 | 19.11 | 150.9 | 229.2 | -0.051 | 0 | -4.96 | -4.1 | 66.1 | 2.42 | 7.42 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.82
202 | 2008-08-09 | 90000 | 1 | 650.5 | 0.9 | -2.2 | 19.06 | 151.3 | 229.8 | -0.051 | 0 | -4.96 | -4.1 | 68 | 2.42 | 8.39 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.83
203 | 2008-08-09 | 100000 | 1 | 649.5 | 0.8 | -2.4 | 19.05 | 150.6 | 229.3 | -0.05 | 0 | -4.96 | -4.1 | 67.7 | 2.4 | 7.56 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.83
204 | 2008-08-09 | 110000 | 1 | 649.7 | 0.8 | -2.6 | 19.1 | 150.9 | 229.5 | -0.05 | 0 | -4.96 | -4.1 | 66.5 | 2.41 | 7.53 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.83
205 | 2008-08-09 | 120000 | 1 | 650.8 | 0.8 | -2.1 | 19.11 | 151.3 | 229.9 | -0.05 | 0 | -4.96 | -4.1 | 66.4 | 2.41 | 7.51 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.84
206 | 2008-08-09 | 130000 | 1 | 649.9 | 0.7 | -2.2 | 19.03 | 150.4 | 228.8 | -0.049 | 0 | -4.96 | -4.2 | 66.4 | 2.41 | 7.52 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.84
207 | 2008-08-09 | 140000 | 1 | 649.3 | 0.7 | -2.5 | 19.07 | 151 | 229.6 | -0.05 | 0 | -4.96 | -4.2 | 68.1 | 2.4 | 7.65 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.85
208 | 2008-08-09 | 150000 | 1 | 649.4 | 0.7 | -2.2 | 19.01 | 150.7 | 229.2 | -0.05 | 0 | -4.96 | -4.2 | 68.1 | 2.4 | 7.65 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.86
209 | 2008-08-09 | 160000 | 1 | 648.6 | 0.6 | -2.4 | 19.02 | 150.6 | 229.1 | -0.049 | 0 | -4.96 | -4.2 | 68.3 | 2.39 | 7.65 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.87
210 | 2008-08-09 | 170000 | 1 | 648.8 | 0.6 | -2.7 | 19.03 | 150.8 | 229.3 | -0.05 | 0 | -4.96 | -4.2 | 67.7 | 2.39 | 7.61 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.87
211 | 2008-08-09 | 180000 | 1 | 648 | 0.6 | -2.3 | 19.06 | 151 | 229.4 | -0.05 | 0 | -4.96 | -4.2 | 67.2 | 2.39 | 7.53 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.87
212 | 2008-08-09 | 190000 | 1 | 648.8 | 0.6 | -2.3 | 19.14 | 151.7 | 230.3 | -0.051 | 0 | -4.96 | -4.2 | 67.4 | 2.4 | 7.58 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.87
213 | 2008-08-09 | 200000 | 1 | 648.2 | 0.5 | -2.1 | 19.07 | 150.8 | 229.3 | -0.049 | 0 | -4.96 | -4.2 | 66.7 | 2.39 | 7.53 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.88
214 | 2008-08-09 | 210000 | 1 | 648.2 | 0.5 | -2.4 | 18.99 | 149.8 | 228.2 | -0.049 | 0 | -4.96 | -4.2 | 64.9 | 2.41 | 7.5 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.89
215 | 2008-08-09 | 220000 | 1 | 632.8 | 0.5 | -2.5 | 16.36 | 120.7 | 191.8 | -0.049 | 0 | -4.96 | -4.2 | 54.8 | 2.34 | 7.52 | 2 | 2.17 | 1.8 | 0.007 | 0.007 | 13.93
216 | 2008-08-09 | 230000 | 1 | 630.2 | 0.5 | -2.1 | 16.49 | 122.9 | 194 | -0.048 | 0 | -4.97 | -4.2 | 54.1 | 2.39 | 7.44 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.92
217 | 2008-08-10 | 0 | 1 | 649.9 | 0.5 | -2.2 | 19.21 | 153.1 | 231.5 | -0.048 | 0 | -4.97 | -4.2 | 69.8 | 2.29 | 7.55 | 1.9 | 2.13 | 1.8 | 0.007 | 0.007 | 13.86
218 | 2008-08-10 | 10000 | 1 | 650.6 | 0.4 | -2.3 | 19.11 | 151.3 | 229.9 | -0.047 | 0 | -4.96 | -4.2 | 66.7 | 2.4 | 7.46 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.86
219 | 2008-08-10 | 20000 | 1 | 650.4 | 0.4 | -2.6 | 18.96 | 150.2 | 228.4 | -0.048 | 0 | -4.96 | -4.2 | 65.9 | 2.4 | 7.42 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.86
220 | 2008-08-10 | 30000 | 1 | 650 | 0.4 | -2.3 | 18.97 | 150.4 | 228.7 | -0.048 | 0 | -4.96 | -4.2 | 66.1 | 2.41 | 7.42 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.86
221 | 2008-08-10 | 40000 | 1 | 650.7 | 0.4 | -2.3 | 19.06 | 151 | 229.4 | -0.048 | 0 | -4.97 | -4.2 | 66.6 | 2.39 | 7.45 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.86
222 | 2008-08-10 | 50000 | 1 | 651.5 | 0.3 | -2.2 | 19.15 | 151.9 | 230.5 | -0.048 | 0 | -4.96 | -4.2 | 66.9 | 2.4 | 7.49 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.86
223 | 2008-08-10 | 60000 | 1 | 650.6 | 0.3 | -2.3 | 19.01 | 150.7 | 229.1 | -0.047 | 0 | -4.96 | -4.2 | 66.3 | 2.41 | 7.45 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.86
224 | 2008-08-10 | 70000 | 1 | 651.7 | 0.3 | -2.7 | 19.09 | 151.2 | 229.7 | -0.047 | 0 | -4.96 | -4.2 | 66.8 | 2.39 | 7.48 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.87
225 | 2008-08-10 | 80000 | 1 | 650.7 | 0.3 | -1.9 | 19.04 | 151 | 229.4 | -0.048 | 0 | -4.96 | -4.2 | 66.8 | 2.39 | 7.46 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.88
226 | 2008-08-10 | 90000 | 1 | 651.6 | 2.7 | 24.7 | 19.06 | 151.2 | 230 | -0.046 | 0 | -4.96 | -6.1 | 68.1 | 3.37 | 8.3 | 2 | 9.42 | 3.8 | 0.014 | 0.008 | 12.32
227 | 2008-08-10 | 100000 | 1 | 649.8 | 0.7 | -2 | 18.97 | 150.1 | 228.7 | -0.047 | 0 | -4.96 | -4.2 | 67 | 2.39 | 7.49 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.9
228 | 2008-08-10 | 110000 | 1 | 650.4 | 0.9 | -1.9 | 18.99 | 150.4 | 229.2 | -0.047 | 0 | -4.96 | -4.2 | 68 | 2.39 | 7.56 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.9
229 | 2008-08-10 | 120000 | 1 | 651.4 | 0.9 | -2.3 | 19.13 | 151.3 | 230.4 | -0.047 | 0 | -4.96 | -4.2 | 68.8 | 2.39 | 7.63 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.91
230 | 2008-08-10 | 130000 | 1 | 650.6 | 0.8 | -2.1 | 19.14 | 151.6 | 230.6 | -0.046 | 0 | -4.96 | -4.2 | 69.6 | 2.38 | 7.67 | 2 | 2.21 | 1.9 | 0.007 | 0.007 | 13.91
231 | 2008-08-10 | 140000 | 1 | 650.5 | 0.8 | -2.1 | 19.11 | 151.1 | 230.2 | -0.048 | 0 | -4.96 | -4.2 | 69.3 | 2.4 | 7.68 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.9
232 | 2008-08-10 | 150000 | 1 | 650.1 | 0.8 | -2.3 | 19.1 | 151.1 | 230.2 | -0.046 | 0 | -4.97 | -4.2 | 69.8 | 2.37 | 7.71 | 2 | 2.21 | 1.9 | 0.007 | 0.007 | 13.91
233 | 2008-08-10 | 160000 | 1 | 650.2 | 0.7 | -2.5 | 19.12 | 151 | 230 | -0.047 | 0 | -4.96 | -4.2 | 69 | 2.39 | 7.66 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.9
234 | 2008-08-10 | 170000 | 1 | 649.4 | 0.7 | -2.4 | 18.96 | 150 | 228.7 | -0.046 | 0 | -4.96 | -4.2 | 68.2 | 2.39 | 7.62 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.89
235 | 2008-08-10 | 180000 | 1 | 650.7 | 0.7 | -2.7 | 19.13 | 151.9 | 230.8 | -0.047 | 0 | -4.96 | -4.2 | 69.6 | 2.38 | 7.68 | 2 | 2.21 | 1.9 | 0.007 | 0.007 | 13.89
236 | 2008-08-10 | 190000 | 1 | 651.1 | 0.6 | -2.3 | 19.14 | 151.4 | 230.3 | -0.047 | 0 | -4.96 | -4.2 | 68 | 2.4 | 7.58 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.88
237 | 2008-08-10 | 200000 | 1 | 650.1 | 0.6 | -2.6 | 19.1 | 151.7 | 230.3 | -0.047 | 0 | -4.96 | -4.2 | 67 | 2.39 | 7.49 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.87
238 | 2008-08-10 | 210000 | 1 | 650 | 0.6 | -2.4 | 19.06 | 151.2 | 229.7 | -0.047 | 0 | -4.96 | -4.2 | 65.7 | 2.4 | 7.42 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.87
239 | 2008-08-10 | 220000 | 1 | 649.6 | 0.5 | -2.4 | 19.03 | 150.7 | 229 | -0.048 | 0 | -4.96 | -4.2 | 65.5 | 2.4 | 7.38 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.86
240 | 2008-08-10 | 230000 | 1 | 649.6 | 0.5 | -2.2 | 19.12 | 151.5 | 229.8 | -0.05 | 0 | -4.96 | -4.2 | 65.6 | 2.4 | 7.39 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.85
241 | 2008-08-11 | 0 | 1 | 649.3 | 0.5 | -2.4 | 19.02 | 150.7 | 229 | -0.053 | 0 | -4.96 | -4.2 | 65.1 | 2.4 | 7.35 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.85
242 | 2008-08-11 | 10000 | 1 | 648.9 | 0.5 | -2 | 19.01 | 150.6 | 228.8 | -0.051 | 0 | -4.96 | -4.2 | 64.7 | 2.41 | 7.35 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.85
243 | 2008-08-11 | 20000 | 1 | 649.2 | 0.5 | -2.4 | 19.06 | 151.2 | 229.5 | -0.052 | 0 | -4.96 | -4.2 | 65.7 | 2.39 | 7.36 | 2 | 2.22 | 1.8 | 0.007 | 0.007 | 13.85
244 | 2008-08-11 | 30000 | 1 | 649.7 | 0.5 | -2.4 | 18.97 | 150.4 | 228.7 | -0.052 | 0 | -4.96 | -4.2 | 64.4 | 2.41 | 7.32 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.85
245 | 2008-08-11 | 40000 | 1 | 649.5 | 0.4 | -2.1 | 18.95 | 150.3 | 228.4 | -0.051 | 0 | -4.96 | -4.2 | 64.4 | 2.41 | 7.32 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.85
246 | 2008-08-11 | 50000 | 1 | 651.2 | 0.4 | -2.1 | 19.12 | 152 | 230.3 | -0.051 | 0 | -4.96 | -4.2 | 64.9 | 2.39 | 7.35 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.85
247 | 2008-08-11 | 60000 | 1 | 651.3 | 0.4 | -2.5 | 19.05 | 150.8 | 229 | -0.052 | 0 | -4.96 | -4.2 | 64.4 | 2.41 | 7.29 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.85
248 | 2008-08-11 | 70000 | 1 | 649.4 | 0.4 | -2.2 | 19 | 150.1 | 228 | -0.052 | 0 | -4.96 | -4.2 | 63.8 | 2.41 | 7.25 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.85
249 | 2008-08-11 | 80000 | 1 | 649.7 | 2.3 | 23.7 | 19.04 | 150.2 | 228.4 | -0.05 | 0 | -4.96 | -5.7 | 62.9 | 3.48 | 8.2 | 2.2 | 9.56 | 3.8 | 0.015 | 0.008 | 12.24
250 | 2008-08-11 | 90000 | 1 | 649.8 | 0.3 | -2.3 | 19.14 | 151.5 | 229.8 | -0.052 | 0 | -4.96 | -4.1 | 66.5 | 2.47 | 8.38 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.78
251 | 2008-08-11 | 100000 | 1 | 664.5 | 0.8 | -2.1 | 21.49 | 174.2 | 261.3 | -0.051 | 0 | -4.96 | -4 | 131 | 2.47 | 11.51 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.59
252 | 2008-08-11 | 110000 | 1 | 664.4 | 0.7 | -2.6 | 21.32 | 172.7 | 259.6 | -0.051 | 0 | -4.96 | -4 | 128.9 | 2.57 | 11.68 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.61
253 | 2008-08-11 | 120000 | 1 | 664.7 | 0.7 | -2.2 | 21.42 | 173.7 | 260.4 | -0.051 | 0 | -4.96 | -4 | 122.9 | 2.43 | 11.15 | 2 | 2.27 | 1.8 | 0.007 | 0.007 | 13.59
254 | 2008-08-11 | 130000 | 1 | 665.1 | 0.7 | -1.9 | 21.4 | 173.2 | 259.6 | -0.051 | 0 | -4.96 | -4 | 117.8 | 2.46 | 10.81 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.59
255 | 2008-08-11 | 140000 | 1 | 665.5 | 0.6 | -2.1 | 21.45 | 173.4 | 259.8 | -0.052 | 0 | -4.96 | -4 | 120.9 | 2.55 | 11.12 | 2.1 | 2.4 | 1.9 | 0.007 | 0.008 | 13.56
256 | 2008-08-11 | 150000 | 1 | 664.7 | 0.6 | -2.2 | 21.49 | 173.9 | 260.9 | -0.051 | 0 | -4.96 | -4 | 130.1 | 2.54 | 11.75 | 2 | 2.39 | 1.9 | 0.007 | 0.008 | 13.5
257 | 2008-08-11 | 160000 | 1 | 695.8 | 0.5 | -1.9 | 21.34 | 173 | 270.6 | 0.151 | 1 | -4.96 | -3.7 | 131.3 | 2.69 | 12.15 | 2 | 2.53 | 1.9 | 0.007 | 0.007 | 13.06
258 | 2008-08-11 | 170000 | 1 | 697.8 | 0.5 | -1.9 | 21.33 | 172.5 | 268.1 | 0.177 | 1 | -4.96 | -3.7 | 130.1 | 2.67 | 12.1 | 2 | 2.52 | 1.9 | 0.007 | 0.007 | 13.06
259 | 2008-08-11 | 180000 | 1 | 697.4 | 0.5 | -2 | 21.33 | 172.3 | 270.1 | 0.176 | 1 | -4.96 | -3.7 | 129.3 | 2.68 | 12.05 | 2 | 2.52 | 1.9 | 0.007 | 0.007 | 13.04
260 | 2008-08-11 | 190000 | 1 | 698.2 | 0.5 | -2.4 | 21.33 | 172.3 | 270.5 | 0.189 | 1 | -4.96 | -3.7 | 129.4 | 2.69 | 12.07 | 2 | 2.52 | 1.9 | 0.007 | 0.007 | 13.01
261 | 2008-08-11 | 200000 | 1 | 694.8 | 0.4 | -2.3 | 21.33 | 172.9 | 269.5 | 0.173 | 1 | -4.96 | -3.8 | 128.6 | 2.66 | 11.97 | 2 | 2.49 | 1.9 | 0.007 | 0.007 | 13.09
262 | 2008-08-11 | 210000 | 1 | 692.1 | 0.4 | -1.9 | 21.2 | 172.1 | 267.6 | 0.121 | 1 | -4.96 | -3.8 | 126.7 | 2.56 | 11.7 | 1.9 | 2.39 | 1.8 | 0.007 | 0.007 | 13.17
263 | 2008-08-11 | 220000 | 1 | 652.5 | 0.4 | -2.4 | 18.93 | 150 | 228 | -0.048 | 0 | -4.97 | -4.1 | 59.9 | 2.45 | 7.15 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.68
264 | 2008-08-11 | 230000 | 1 | 648.9 | 0.4 | -2.2 | 18.87 | 149.2 | 227 | -0.049 | 0 | -4.96 | -4.1 | 61.6 | 2.46 | 7.24 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.69
265 | 2008-08-12 | 0 | 0 | 560.7 | 23.3 | -46.7 | 1.53 | 7.3 | 13.2 | -0.049 | 0 | -4.96 | -110 | 2.7 | 1.68 | 4.67 | 2.6 | 6.27 | 7.3 | 0.029 | 0.01 | 19.6
266 | 2008-08-12 | 10000 | 0 | 450.2 | 11.4 | -109.6 | 0.34 | 1.4 | 2 | -0.048 | 0 | -4.97 | -193.3 | 0.9 | 0 | 0.02 | -0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.75
267 | 2008-08-12 | 20000 | 0 | 429.4 | 11.2 | -97.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -4.97 | -184.3 | 0.9 | 0 | -0.02 | -0.2 | 0.01 | 0.3 | 0.004 | 0 | 20.74
268 | 2008-08-12 | 30000 | 0 | 426.8 | 9.3 | -105.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -187.7 | 0.8 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.74
269 | 2008-08-12 | 40000 | 1 | 580.7 | 22.4 | 32.4 | 6.88 | 22.4 | 22.6 | -0.048 | 0 | -4.96 | -21.1 | 4.6 | 9.18 | 26.83 | 11.7 | 32.55 | 41.1 | 0.152 | 0.043 | 16.65
270 | 2008-08-12 | 50000 | 1 | 612.3 | 16.3 | 22.8 | 11.1 | 61.3 | 96.6 | -0.048 | 0 | -4.96 | -4.9 | 62.3 | 8.96 | 26.49 | 9 | 42.35 | 42.4 | 0.156 | 0.033 | 14.83
271 | 2008-08-12 | 60000 | 1 | 657.4 | 0.2 | -2.2 | 20.89 | 169 | 251.6 | -0.047 | 0 | -4.97 | -4.1 | 85.9 | 2.21 | 8.7 | 1.8 | 2.06 | 1.7 | 0.006 | 0.007 | 13.77
272 | 2008-08-12 | 70000 | 1 | 667.9 | 0.2 | -2.2 | 20.8 | 168.4 | 251.8 | -0.047 | 0 | -4.96 | -4.1 | 77.4 | 2.4 | 7.98 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.81
273 | 2008-08-12 | 80000 | 1 | 666.9 | 0.1 | -2.3 | 20.55 | 166.8 | 249.3 | -0.047 | 0 | -4.97 | -4.1 | 73.4 | 2.42 | 7.72 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.82
274 | 2008-08-12 | 90000 | 1 | 666.2 | 6.7 | -7.7 | 20.56 | 166.4 | 248.4 | -0.049 | 0 | -4.97 | -79.8 | 73.1 | 3.41 | 8.43 | 2.2 | 9.47 | 4.1 | 0.016 | 1.591 | 12.23
275 | 2008-08-12 | 100000 | 1 | 667.2 | 0.5 | -2.1 | 20.61 | 167.1 | 249.5 | -0.048 | 0 | -4.96 | -4.1 | 73.6 | 2.4 | 7.7 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.83
276 | 2008-08-12 | 110000 | 1 | 667.7 | 0.8 | -1.9 | 20.73 | 167.9 | 250.3 | -0.048 | 0 | -4.96 | -4.1 | 76 | 2.54 | 7.97 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.81
277 | 2008-08-12 | 120000 | 1 | 707.3 | 0.6 | -1.9 | 21.4 | 173.8 | 276.6 | 0.306 | 1 | -4.96 | -3.6 | 143.6 | 2.87 | 13.32 | 2.1 | 2.7 | 2 | 0.007 | 0.008 | 12.8
278 | 2008-08-12 | 130000 | 1 | 721.4 | 0.5 | -1.9 | 21.33 | 172.9 | 277.5 | 0.278 | 1 | -4.96 | -3.6 | 144.2 | 2.69 | 13.14 | 2 | 2.53 | 1.8 | 0.007 | 0.007 | 12.83
279 | 2008-08-12 | 140000 | 1 | 730.4 | 0.4 | -1.7 | 21.2 | 171.3 | 280.8 | 0.43 | 1 | -4.96 | -3.5 | 149.2 | 2.92 | 13.92 | 2 | 2.74 | 1.9 | 0.007 | 0.007 | 12.51
280 | 2008-08-12 | 150000 | 1 | 736.2 | 0.4 | -1.9 | 21.04 | 169.4 | 278.6 | 0.494 | 1 | -4.96 | -3.4 | 153.7 | 2.93 | 14.24 | 2 | 2.75 | 1.9 | 0.007 | 0.007 | 12.38
281 | 2008-08-12 | 160000 | 1 | 736.6 | 0.4 | -2 | 20.98 | 168.8 | 277.3 | 0.505 | 1 | -4.96 | -3.4 | 155.4 | 2.94 | 14.31 | 2 | 2.76 | 1.9 | 0.007 | 0.007 | 12.37
282 | 2008-08-12 | 170000 | 1 | 735.6 | 0.3 | -1.9 | 21.19 | 172.8 | 280.8 | 0.517 | 1 | -4.96 | -3.4 | 237.7 | 3.23 | 18.69 | 2.2 | 3.1 | 2.1 | 0.008 | 0.008 | 12.27
283 | 2008-08-12 | 180000 | 1 | 736.7 | 0.3 | -1.9 | 21.22 | 172.8 | 280.9 | 0.527 | 1 | -4.96 | -3.4 | 220.2 | 2.01 | 16.54 | 1.4 | 1.89 | 1.3 | 0.005 | 0.005 | 12.27
284 | 2008-08-12 | 190000 | 1 | 696.7 | 0.4 | -1.9 | 20.63 | 166.5 | 261.9 | 0.121 | 0 | -4.96 | -3.8 | 128.3 | 2.18 | 11.35 | 1.7 | 2.05 | 1.6 | 0.006 | 0.006 | 13.23
285 | 2008-08-12 | 200000 | 1 | 675.6 | 0.4 | -2.3 | 21.55 | 175.5 | 266.7 | 0.067 | 0 | -4.96 | -3.9 | 129 | 2.63 | 12.13 | 2 | 2.47 | 1.9 | 0.007 | 0.007 | 13.29
286 | 2008-08-12 | 210000 | 1 | 699.4 | 0.3 | -1.9 | 21.14 | 171.8 | 268.5 | 0.12 | 1 | -4.96 | -3.8 | 124.1 | 2.47 | 11.71 | 1.9 | 2.31 | 1.8 | 0.007 | 0.007 | 13.2
287 | 2008-08-12 | 220000 | 1 | 653.2 | 0.3 | -2.1 | 18.97 | 149.9 | 227.8 | -0.047 | 0 | -4.96 | -4.1 | 61.8 | 2.48 | 7.37 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.7
288 | 2008-08-12 | 230000 | 1 | 652.5 | 0.3 | -2.5 | 19.08 | 151.6 | 229.6 | -0.048 | 0 | -4.96 | -4.1 | 65.2 | 2.44 | 7.43 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.72
289 | 2008-08-13 | 0 | 1 | 666.1 | 0.3 | -2.5 | 20.84 | 169.1 | 252.4 | -0.047 | 0 | -4.96 | -4.1 | 77.2 | 2.37 | 8.04 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.81
290 | 2008-08-13 | 10000 | 1 | 667.3 | 0.3 | -2.4 | 20.83 | 169.2 | 252.4 | -0.049 | 0 | -4.96 | -4.1 | 75.4 | 2.41 | 7.84 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.83
291 | 2008-08-13 | 20000 | 1 | 667.7 | 0.2 | -2.5 | 20.94 | 169.8 | 253.4 | -0.05 | 0 | -4.96 | -4.1 | 77.9 | 2.41 | 8.04 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.82
292 | 2008-08-13 | 30000 | 1 | 666.5 | 0.2 | -1.8 | 20.89 | 169.3 | 252.3 | -0.049 | 0 | -4.96 | -4.2 | 73.8 | 2.42 | 7.77 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.84
293 | 2008-08-13 | 40000 | 1 | 667.4 | 0.2 | -2.5 | 20.97 | 170 | 253.6 | -0.049 | 0 | -4.96 | -4.2 | 76.9 | 2.39 | 7.91 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.84
294 | 2008-08-13 | 50000 | 1 | 667.6 | 0.2 | -2.1 | 20.88 | 169.6 | 253 | -0.051 | 0 | -4.96 | -4.2 | 73.8 | 2.4 | 7.73 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.86
295 | 2008-08-13 | 60000 | 1 | 666.2 | 0.2 | -2.3 | 20.72 | 167.9 | 250.4 | -0.051 | 0 | -4.96 | -4.2 | 72.4 | 2.41 | 7.71 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.84
296 | 2008-08-13 | 70000 | 1 | 666.3 | 0.2 | -2.3 | 20.77 | 168.9 | 251.6 | -0.049 | 0 | -4.96 | -4.1 | 76 | 2.55 | 8.77 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.83
297 | 2008-08-13 | 80000 | 1 | 669.6 | 2.6 | 5.1 | 21.75 | 177 | 264.9 | -0.032 | 0 | -4.96 | -28.8 | 133.6 | 3.48 | 12.04 | 2.2 | 9.52 | 4.1 | 7.929 | 0.008 | 12.03
298 | 2008-08-13 | 90000 | 1 | 701.1 | 0.3 | -2 | 21.54 | 175 | 274.5 | 0.205 | 1 | -4.96 | -3.7 | 141.6 | 2.71 | 12.99 | 2 | 2.55 | 1.9 | 0.007 | 0.007 | 13.08
299 | 2008-08-13 | 100000 | 1 | 710 | 0.7 | -2 | 21.51 | 174.4 | 273.7 | 0.28 | 1 | -4.96 | -3.7 | 146.5 | 2.75 | 13.16 | 2 | 2.57 | 1.9 | 0.007 | 0.007 | 12.87
300 | 2008-08-13 | 110000 | 1 | 719.1 | 0.6 | -2 | 21.3 | 172.1 | 273.9 | 0.335 | 1 | -4.96 | -3.6 | 151.5 | 2.5 | 13.21 | 1.8 | 2.35 | 1.7 | 0.006 | 0.007 | 12.74
301 | 2008-08-13 | 120000 | 1 | 723.3 | 0.5 | -1.9 | 21.11 | 170.3 | 275.2 | 0.368 | 1 | -4.96 | -3.5 | 151 | 2.53 | 13.33 | 1.8 | 2.37 | 1.7 | 0.006 | 0.007 | 12.65
302 | 2008-08-13 | 130000 | 1 | 719.5 | 0.5 | -2 | 21.12 | 170.3 | 274.5 | 0.369 | 1 | -4.96 | -3.5 | 146.7 | 2.6 | 13.14 | 1.9 | 2.45 | 1.7 | 0.006 | 0.007 | 12.64
303 | 2008-08-13 | 140000 | 1 | 742.5 | 0.4 | -1.9 | 20.69 | 165.5 | 278 | 0.548 | 1 | -4.96 | -3.4 | 165.6 | 2.66 | 14.39 | 1.8 | 2.5 | 1.7 | 0.006 | 0.007 | 12.24
304 | 2008-08-13 | 150000 | 1 | 735.1 | 0.4 | -1.9 | 21.31 | 171.2 | 279.4 | 0.458 | 1 | -4.96 | -3.4 | 159.8 | 2.72 | 13.96 | 1.9 | 2.56 | 1.8 | 0.006 | 0.007 | 12.39
305 | 2008-08-13 | 160000 | 1 | 733.3 | 0.4 | -1.6 | 21.26 | 173.9 | 279.7 | 0.475 | 1 | -4.96 | -3.4 | 199.1 | 2.82 | 16.7 | 1.9 | 2.65 | 1.8 | 0.007 | 0.007 | 12.24
306 | 2008-08-13 | 170000 | 1 | 737.1 | 0.4 | -1.7 | 21.18 | 176 | 281.8 | 0.537 | 1 | -4.96 | -3.3 | 202.4 | 3.07 | 17.84 | 2 | 2.88 | 1.9 | 0.007 | 0.007 | 12
307 | 2008-08-13 | 180000 | 1 | 755.7 | 0.3 | -1.9 | 20.52 | 165.5 | 284.9 | 0.692 | 1 | -4.96 | -3.3 | 186.2 | 2.81 | 15.98 | 1.8 | 2.71 | 1.8 | 0.007 | 0.007 | 11.89
308 | 2008-08-13 | 190000 | 1 | 755.9 | 0.3 | -1.8 | 20.71 | 167.1 | 286.5 | 0.681 | 1 | -4.96 | -3.3 | 253.1 | 4.92 | 22.76 | 3.2 | 5.4 | 3.5 | 0.013 | 0.012 | 11.91
309 | 2008-08-13 | 200000 | 1 | 767.4 | 0.3 | -1.6 | 21.69 | 181.9 | 302.2 | 0.796 | 1 | -4.96 | -3.1 | 247.6 | 3.07 | 20.71 | 1.9 | 2.89 | 1.8 | 0.007 | 0.007 | 11.38
310 | 2008-08-13 | 210000 | 1 | 766.9 | 0.3 | -1.9 | 22.18 | 187.1 | 306.1 | 0.745 | 1 | -4.97 | -3.1 | 240.8 | 3.34 | 19.95 | 2.1 | 3.14 | 2 | 0.007 | 0.008 | 11.49
311 | 2008-08-13 | 220000 | 1 | 684.8 | 0.4 | -1.9 | 20.24 | 163.1 | 250.6 | 0.021 | 0 | -4.96 | -3.9 | 166.8 | 2.04 | 13.76 | 1.6 | 1.92 | 1.5 | 0.005 | 0.006 | 13.41
312 | 2008-08-13 | 230000 | 1 | 665.1 | 0.4 | -2.4 | 20.82 | 168.6 | 253 | -0.05 | 0 | -4.96 | -4 | 112.2 | 1.96 | 9.72 | 1.6 | 1.85 | 1.5 | 0.006 | 0.006 | 13.66
313 | 2008-08-14 | 0 | 1 | 652.8 | 0.3 | -2.2 | 18.91 | 148.8 | 227.7 | -0.049 | 0 | -4.96 | -4.1 | 99.3 | 1.98 | 9.43 | 1.6 | 1.86 | 1.5 | 0.006 | 0.006 | 13.69
314 | 2008-08-14 | 10000 | 1 | 651.7 | 0.3 | -2.3 | 19.09 | 150.9 | 229.4 | -0.049 | 0 | -4.96 | -4.1 | 84 | 2.47 | 9.18 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.71
315 | 2008-08-14 | 20000 | 1 | 650.7 | 0.3 | -2.3 | 19.09 | 151.1 | 229.4 | -0.051 | 0 | -4.96 | -4.1 | 86.4 | 2.45 | 9.19 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.7
316 | 2008-08-14 | 30000 | 1 | 651.2 | 0.3 | -2.2 | 19.08 | 151.5 | 229.7 | -0.05 | 0 | -4.96 | -4.1 | 86.8 | 2.47 | 9.22 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.69
317 | 2008-08-14 | 40000 | 1 | 654.3 | 0.3 | -2.5 | 19.4 | 154.8 | 233.8 | -0.049 | 0 | -4.96 | -4.1 | 89.5 | 2.45 | 9.29 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.7
318 | 2008-08-14 | 50000 | 1 | 652.2 | 0.2 | -2.2 | 19.12 | 151.6 | 229.8 | -0.048 | 0 | -4.96 | -4.1 | 87.5 | 2.46 | 9.23 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.68
319 | 2008-08-14 | 60000 | 1 | 664 | 0.2 | -2.5 | 20.95 | 169.6 | 253.2 | -0.048 | 0 | -4.97 | -4.1 | 103.7 | 2.41 | 9.68 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.71
320 | 2008-08-14 | 70000 | 1 | 668 | 0.2 | -2.4 | 20.86 | 168.3 | 251.7 | -0.048 | 0 | -4.96 | -4.1 | 100.2 | 2.44 | 9.45 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.77
321 | 2008-08-14 | 80000 | 1 | 667.1 | 0.2 | -2.3 | 20.68 | 166.6 | 249.9 | -0.047 | 0 | -4.96 | -4.1 | 100.2 | 2.44 | 9.49 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.79
322 | 2008-08-14 | 90000 | 1 | 665.5 | 2.9 | -1.2 | 20.67 | 166.4 | 250.6 | -0.046 | 0 | -4.96 | -51.1 | 102.5 | 3.47 | 10.22 | 2.1 | 9.48 | 3.9 | 0.015 | 0.008 | 12.17
323 | 2008-08-14 | 100000 | 1 | 662.7 | 0.6 | -2.2 | 20.83 | 166.6 | 251.7 | -0.046 | 0 | -4.97 | -4 | 118.9 | 2.43 | 10.57 | 2 | 2.28 | 1.8 | 0.007 | 0.007 | 13.62
324 | 2008-08-14 | 110000 | 1 | 661.8 | 0.8 | -2.2 | 20.72 | 166.2 | 251.6 | -0.048 | 0 | -4.96 | -4 | 121 | 2.3 | 10.94 | 1.8 | 2.16 | 1.7 | 0.006 | 0.007 | 13.55
325 | 2008-08-14 | 120000 | 1 | 668.5 | 0.8 | -2.2 | 20.9 | 168.1 | 255.4 | 0.035 | 0 | -4.96 | -3.9 | 110.8 | 2.53 | 10.51 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.36
326 | 2008-08-14 | 130000 | 1 | 739.1 | 0.5 | -1.7 | 21.05 | 168.8 | 282.9 | 0.461 | 1 | -4.96 | -3.4 | 139.2 | 2.96 | 13.09 | 2 | 2.78 | 1.9 | 0.007 | 0.007 | 12.3
327 | 2008-08-14 | 140000 | 1 | 746.3 | 0.5 | -2 | 20.92 | 168.2 | 284.7 | 0.529 | 1 | -4.97 | -3.4 | 142.8 | 3 | 13.35 | 2 | 2.81 | 1.9 | 0.007 | 0.007 | 12.18
328 | 2008-08-14 | 150000 | 1 | 748.5 | 0.5 | -2 | 20.85 | 167.6 | 284.6 | 0.53 | 1 | -4.96 | -3.3 | 143.8 | 2.99 | 13.39 | 2 | 2.82 | 1.9 | 0.007 | 0.007 | 12.13
329 | 2008-08-14 | 160000 | 1 | 750.4 | 0.4 | -1.9 | 20.84 | 166.7 | 283.6 | 0.555 | 1 | -4.96 | -3.3 | 143.7 | 3.02 | 13.42 | 2 | 2.84 | 1.9 | 0.007 | 0.007 | 12.06
330 | 2008-08-14 | 170000 | 1 | 752 | 0.4 | -2 | 20.79 | 166.2 | 285.1 | 0.573 | 1 | -4.96 | -3.3 | 143.5 | 3.03 | 13.43 | 2 | 2.84 | 1.9 | 0.007 | 0.007 | 12.02
331 | 2008-08-14 | 180000 | 1 | 751.5 | 0.4 | -1.5 | 20.84 | 167.2 | 285.7 | 0.563 | 1 | -4.96 | -3.3 | 144.9 | 3.01 | 13.45 | 2 | 2.83 | 1.9 | 0.007 | 0.007 | 12.06
332 | 2008-08-14 | 190000 | 1 | 748.8 | 0.4 | -1.6 | 20.85 | 167.7 | 285.3 | 0.546 | 1 | -4.96 | -3.3 | 142.9 | 3 | 13.35 | 2 | 2.82 | 1.9 | 0.007 | 0.007 | 12.08
333 | 2008-08-14 | 200000 | 1 | 746.1 | 0.3 | -1.8 | 21.04 | 169.2 | 285.9 | 0.546 | 1 | -4.96 | -3.3 | 143.1 | 3.01 | 13.36 | 2 | 2.83 | 1.9 | 0.007 | 0.007 | 12.13
334 | 2008-08-14 | 210000 | 1 | 756.5 | 0.2 | -2 | 21.18 | 170.7 | 293.1 | 0.608 | 1 | -4.96 | -3.3 | 154.2 | 3.02 | 14.01 | 2 | 2.84 | 1.9 | 0.007 | 0.007 | 11.99
335 | 2008-08-14 | 220000 | 1 | 705.4 | 0.4 | -2.1 | 21.33 | 172.2 | 271 | 0.2 | 1 | -4.96 | -3.7 | 130.7 | 2.64 | 11.99 | 2 | 2.48 | 1.8 | 0.007 | 0.007 | 12.98
336 | 2008-08-14 | 230000 | 1 | 699.4 | 0.3 | -2.4 | 21.32 | 173.1 | 271.2 | 0.188 | 1 | -4.96 | -3.7 | 132 | 2.67 | 12.06 | 2 | 2.51 | 1.9 | 0.007 | 0.007 | 13.01
337 | 2008-08-15 | 0 | 1 | 668 | 0.3 | -2.1 | 20.69 | 166.9 | 250.3 | -0.046 | 0 | -4.96 | -4.1 | 98.3 | 2.41 | 9.42 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.68
338 | 2008-08-15 | 10000 | 1 | 664.3 | 0.3 | -2.2 | 20.79 | 167.6 | 251.2 | -0.047 | 0 | -4.96 | -4.1 | 102 | 2.47 | 9.64 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.67
339 | 2008-08-15 | 20000 | 1 | 664.3 | 0.3 | -2.3 | 20.84 | 167.7 | 251.3 | -0.046 | 0 | -4.96 | -4.1 | 101 | 2.45 | 9.58 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.67
340 | 2008-08-15 | 30000 | 1 | 666.6 | 0.3 | -2.2 | 20.84 | 168 | 251.5 | -0.048 | 0 | -4.96 | -4.1 | 100.9 | 2.45 | 9.54 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.69
341 | 2008-08-15 | 40000 | 1 | 666.6 | 0.2 | -2.3 | 20.78 | 167.8 | 250.8 | -0.048 | 0 | -4.96 | -4.1 | 98.6 | 2.45 | 9.42 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.71
342 | 2008-08-15 | 50000 | 1 | 667 | 0.2 | -2.1 | 20.78 | 168.2 | 251.6 | -0.047 | 0 | -4.96 | -4.1 | 100.1 | 2.46 | 9.5 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.7
343 | 2008-08-15 | 60000 | 1 | 666.7 | 0.2 | -2.1 | 20.68 | 167.3 | 249.9 | -0.047 | 0 | -4.96 | -4.1 | 98.2 | 2.45 | 9.33 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.75
344 | 2008-08-15 | 70000 | 1 | 666.9 | 0.2 | -2.1 | 20.74 | 167.8 | 250.9 | -0.051 | 0 | -4.96 | -4.1 | 99 | 2.43 | 9.4 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
345 | 2008-08-15 | 80000 | 1 | 670.4 | 0.2 | -2.3 | 20.67 | 167.3 | 253.3 | 0.051 | 0 | -4.96 | -4 | 103.7 | 2.65 | 10.09 | 2.1 | 2.5 | 2 | 0.007 | 0.008 | 13.52
346 | 2008-08-15 | 90000 | 1 | 744.4 | 2.6 | 10.7 | 21.38 | 173.6 | 292.1 | 0.542 | 1 | -4.96 | -41.5 | 157.2 | 3.77 | 13.66 | 2 | 9.8 | 3.8 | 0.015 | 0.007 | 11.05
347 | 2008-08-15 | 100000 | 1 | 749 | 0.3 | -1.9 | 21.33 | 172.3 | 292.4 | 0.572 | 1 | -4.96 | -3.3 | 154.1 | 3.01 | 14.09 | 2 | 2.83 | 1.9 | 0.007 | 0.007 | 12.12
348 | 2008-08-15 | 110000 | 1 | 752.3 | 0.5 | -1.8 | 21.13 | 170.6 | 292.4 | 0.611 | 1 | -4.96 | -3.3 | 153.9 | 3.03 | 14.13 | 2 | 2.85 | 1.9 | 0.007 | 0.007 | 12
349 | 2008-08-15 | 120000 | 1 | 756.1 | 0.5 | -1.8 | 21.06 | 169.6 | 292.9 | 0.636 | 1 | -4.96 | -3.3 | 153.4 | 3.07 | 14.15 | 2 | 2.89 | 1.9 | 0.007 | 0.007 | 11.92
350 | 2008-08-15 | 130000 | 1 | 758.1 | 0.5 | -2.1 | 20.91 | 168.2 | 291.8 | 0.657 | 1 | -4.96 | -3.2 | 150.5 | 3.08 | 14.03 | 2 | 2.9 | 1.9 | 0.007 | 0.007 | 11.86
351 | 2008-08-15 | 140000 | 1 | 760.5 | 0.4 | -1.6 | 20.83 | 167.4 | 292.6 | 0.697 | 1 | -4.96 | -3.2 | 150.9 | 3.13 | 14.16 | 2 | 2.95 | 1.9 | 0.007 | 0.007 | 11.76
352 | 2008-08-15 | 150000 | 1 | 761.9 | 0.4 | -1.6 | 20.83 | 166.6 | 292.7 | 0.708 | 1 | -4.96 | -3.2 | 151.4 | 3.14 | 14.21 | 2 | 2.96 | 1.9 | 0.007 | 0.007 | 11.69
353 | 2008-08-15 | 160000 | 1 | 762 | 0.4 | -1.7 | 20.81 | 166.5 | 292.4 | 0.711 | 1 | -4.96 | -3.2 | 152.7 | 3.07 | 14.18 | 2 | 2.89 | 1.9 | 0.007 | 0.007 | 11.71
354 | 2008-08-15 | 170000 | 1 | 761.8 | 0.4 | -1.7 | 20.83 | 166.6 | 292.6 | 0.708 | 1 | -4.96 | -3.2 | 151.3 | 3.13 | 14.16 | 2 | 2.95 | 1.9 | 0.007 | 0.007 | 11.7
355 | 2008-08-15 | 180000 | 1 | 761.3 | 0.3 | -1.8 | 20.83 | 167.3 | 293.1 | 0.704 | 1 | -4.96 | -3.2 | 151.7 | 3.12 | 14.17 | 2 | 2.93 | 1.9 | 0.007 | 0.007 | 11.73
356 | 2008-08-15 | 190000 | 1 | 758.5 | 0.3 | -1.6 | 20.83 | 167.9 | 292.2 | 0.67 | 1 | -4.96 | -3.2 | 150.8 | 3.1 | 14.05 | 2 | 2.91 | 1.9 | 0.007 | 0.007 | 11.8
357 | 2008-08-15 | 200000 | 1 | 757.6 | 0.3 | -2 | 20.99 | 169.4 | 293.2 | 0.651 | 1 | -4.96 | -3.2 | 152.8 | 3.08 | 14.12 | 2 | 2.89 | 1.9 | 0.007 | 0.007 | 11.87
358 | 2008-08-15 | 210000 | 1 | 753.8 | 0.2 | -1.5 | 21.08 | 170.9 | 292.9 | 0.595 | 1 | -4.96 | -3.3 | 153.6 | 3.03 | 14.06 | 2 | 2.86 | 1.9 | 0.007 | 0.007 | 12
359 | 2008-08-15 | 220000 | 1 | 750.9 | 0.2 | -1.8 | 21.31 | 172.2 | 292.7 | 0.569 | 1 | -4.96 | -3.3 | 154.5 | 3 | 14.05 | 2 | 2.82 | 1.9 | 0.007 | 0.007 | 12.09
360 | 2008-08-15 | 230000 | 1 | 747.8 | 0.2 | -1.8 | 21.33 | 173.2 | 291.7 | 0.504 | 1 | -4.96 | -3.4 | 155.1 | 2.91 | 13.88 | 2 | 2.74 | 1.9 | 0.007 | 0.007 | 12.22
361 | 2008-08-16 | 0 | 1 | 670.9 | 0.3 | -2.4 | 20.3 | 164.1 | 246.7 | -0.048 | 0 | -4.96 | -4.1 | 93.8 | 2.34 | 9.15 | 1.9 | 2.2 | 1.8 | 0.007 | 0.007 | 13.71
362 | 2008-08-16 | 10000 | 1 | 665.5 | 0.3 | -2.8 | 20.53 | 166.3 | 248.9 | -0.048 | 0 | -4.96 | -4.1 | 97 | 2.45 | 9.31 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.72
363 | 2008-08-16 | 20000 | 1 | 665.5 | 0.3 | -2.3 | 20.53 | 166.2 | 248.5 | -0.048 | 0 | -4.96 | -4.1 | 95.9 | 2.44 | 9.24 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
364 | 2008-08-16 | 30000 | 1 | 665.7 | 0.3 | -1.9 | 20.58 | 167 | 249.5 | -0.049 | 0 | -4.96 | -4.1 | 97 | 2.44 | 9.3 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.73
365 | 2008-08-16 | 40000 | 1 | 666 | 0.3 | -2.3 | 20.56 | 166.8 | 249 | -0.05 | 0 | -4.96 | -4.1 | 96 | 2.44 | 9.22 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.75
366 | 2008-08-16 | 50000 | 1 | 664.7 | 0.2 | -2.1 | 20.49 | 166.1 | 247.9 | -0.05 | 0 | -4.96 | -4.1 | 95.1 | 2.44 | 9.4 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.73
367 | 2008-08-16 | 60000 | 1 | 665.5 | 0.4 | -3.2 | 20.76 | 168 | 250.8 | -0.05 | 0 | -4.96 | -5.8 | 97.8 | 2.38 | 9.59 | 2 | 2.23 | 1.8 | 0.007 | 0.007 | 13.86
368 | 2008-08-16 | 70000 | 1 | 665.7 | 2.1 | 18 | 20.77 | 168.3 | 251.2 | -0.051 | 0 | -4.96 | -18.4 | 100.4 | 3.47 | 10.05 | 2 | 9.5 | 3.7 | 0.014 | 0.008 | 11.98
369 | 2008-08-16 | 80000 | 1 | 665.7 | 0.8 | -2.4 | 20.69 | 167.2 | 249.8 | -0.049 | 0 | -4.96 | -4.1 | 96.7 | 2.45 | 9.48 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.72
370 | 2008-08-16 | 90000 | 1 | 665.4 | 0.8 | -2.2 | 20.74 | 167.4 | 250.5 | -0.049 | 0 | -4.96 | -4 | 98.9 | 2.48 | 10.21 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.65
371 | 2008-08-16 | 100000 | 1 | 662.5 | 0.8 | -2.1 | 20.77 | 167.2 | 251.5 | -0.049 | 0 | -4.96 | -4 | 105.2 | 2.53 | 10.24 | 2 | 2.37 | 1.9 | 0.007 | 0.008 | 13.55
372 | 2008-08-16 | 110000 | 1 | 660.3 | 0.7 | -2.5 | 20.75 | 166.7 | 251.7 | -0.047 | 0 | -4.96 | -3.9 | 118.9 | 2.55 | 11.34 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.44
373 | 2008-08-16 | 120000 | 1 | 660.9 | 0.7 | -2.1 | 20.85 | 168 | 252.8 | -0.048 | 0 | -4.96 | -3.9 | 114.2 | 2.54 | 11.02 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.37
374 | 2008-08-16 | 130000 | 1 | 661.1 | 0.7 | -2.2 | 20.83 | 166.9 | 251.3 | -0.048 | 0 | -4.96 | -3.9 | 109.7 | 2.57 | 10.83 | 2 | 2.41 | 1.9 | 0.007 | 0.007 | 13.35
375 | 2008-08-16 | 140000 | 1 | 661.3 | 0.7 | -2.3 | 20.67 | 166 | 249.9 | -0.046 | 0 | -4.96 | -3.9 | 108.7 | 2.58 | 10.76 | 2 | 2.42 | 1.9 | 0.007 | 0.007 | 13.34
376 | 2008-08-16 | 150000 | 1 | 660.4 | 0.7 | -2.1 | 20.56 | 165.2 | 248.8 | -0.048 | 0 | -4.97 | -3.9 | 108.7 | 2.57 | 10.71 | 2 | 2.4 | 1.9 | 0.007 | 0.007 | 13.33
377 | 2008-08-16 | 160000 | 1 | 659 | 0.6 | -2.3 | 20.56 | 165.2 | 248.6 | -0.047 | 0 | -4.97 | -3.9 | 105.4 | 2.58 | 10.58 | 2 | 2.42 | 1.9 | 0.007 | 0.007 | 13.33
378 | 2008-08-16 | 170000 | 1 | 659.1 | 0.6 | -2.1 | 20.56 | 165.2 | 248.8 | -0.047 | 0 | -4.96 | -3.9 | 106 | 2.58 | 10.55 | 2 | 2.41 | 1.9 | 0.007 | 0.007 | 13.33
379 | 2008-08-16 | 180000 | 1 | 658.9 | 0.6 | -2.2 | 20.58 | 165.8 | 249.5 | -0.047 | 0 | -4.96 | -3.9 | 107.1 | 2.58 | 10.65 | 2 | 2.42 | 1.9 | 0.007 | 0.007 | 13.32
380 | 2008-08-16 | 190000 | 1 | 660.1 | 0.5 | -2 | 20.81 | 167.3 | 251.4 | -0.048 | 0 | -4.96 | -3.9 | 109.8 | 2.58 | 10.82 | 2 | 2.42 | 1.9 | 0.007 | 0.007 | 13.33
381 | 2008-08-16 | 200000 | 1 | 661.7 | 0.5 | -2.1 | 20.74 | 167.8 | 251.8 | -0.046 | 0 | -4.96 | -3.9 | 105.6 | 2.53 | 10.42 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.4
382 | 2008-08-16 | 210000 | 1 | 662.3 | 0.4 | -2.1 | 20.69 | 167.3 | 250.8 | -0.047 | 0 | -4.97 | -4 | 99.6 | 2.55 | 9.9 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.48
383 | 2008-08-16 | 220000 | 1 | 662.7 | 0.4 | -2.3 | 20.8 | 168 | 251.6 | -0.048 | 0 | -4.97 | -4 | 99.5 | 2.49 | 9.85 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.5
384 | 2008-08-16 | 230000 | 1 | 664.3 | 0.4 | -2.2 | 20.62 | 166.9 | 250 | -0.047 | 0 | -4.97 | -4 | 96.9 | 2.48 | 9.62 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.57
385 | 2008-08-17 | 0 | 1 | 652.7 | 0.3 | -2.4 | 19 | 151.2 | 229.1 | -0.046 | 0 | -4.96 | -4 | 85.1 | 2.54 | 9.29 | 2.1 | 2.39 | 1.9 | 0.007 | 0.007 | 13.58
386 | 2008-08-17 | 10000 | 1 | 650.2 | 0.3 | -2.1 | 19 | 151 | 228.7 | -0.05 | 0 | -4.96 | -4 | 86.9 | 2.49 | 9.41 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.6
387 | 2008-08-17 | 20000 | 1 | 651.6 | 0.3 | -2 | 19.11 | 152 | 230 | -0.048 | 0 | -4.96 | -4 | 87.6 | 2.48 | 9.39 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.62
388 | 2008-08-17 | 30000 | 1 | 650.8 | 0.3 | -2 | 19.07 | 151.7 | 229.5 | -0.048 | 0 | -4.97 | -4 | 86 | 2.48 | 9.33 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.58
389 | 2008-08-17 | 40000 | 1 | 652.3 | 0.2 | -2 | 19.13 | 152.4 | 230.3 | -0.047 | 0 | -4.96 | -4 | 85.8 | 2.5 | 9.35 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.58
390 | 2008-08-17 | 50000 | 1 | 652.4 | 0.2 | -2.2 | 19.11 | 152.1 | 230.1 | -0.048 | 0 | -4.97 | -4 | 85.5 | 2.5 | 9.31 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.57
391 | 2008-08-17 | 60000 | 1 | 652 | 0.2 | -1.8 | 19.09 | 152 | 230 | -0.048 | 0 | -4.96 | -4 | 87 | 2.5 | 9.33 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.58
392 | 2008-08-17 | 70000 | 1 | 651.8 | 1.9 | 19.3 | 19.1 | 152.2 | 230.1 | -0.047 | 0 | -4.96 | -13.4 | 90.3 | 3.37 | 9.81 | 2 | 9.36 | 3.6 | 0.014 | 0.007 | 12.04
393 | 2008-08-17 | 80000 | 1 | 650 | 0.7 | -2 | 19.05 | 151.3 | 229.2 | -0.048 | 0 | -4.96 | -4 | 86 | 2.52 | 9.33 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.58
394 | 2008-08-17 | 90000 | 1 | 650.1 | 0.9 | -2.4 | 19.08 | 151.8 | 229.6 | -0.045 | 0 | -4.96 | -4 | 87.1 | 2.48 | 10.02 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.58
395 | 2008-08-17 | 100000 | 1 | 650.9 | 0.8 | -2.2 | 19.13 | 152 | 230.1 | -0.048 | 0 | -4.96 | -4 | 86.6 | 2.49 | 9.31 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.6
396 | 2008-08-17 | 110000 | 1 | 650.4 | 0.8 | -2.4 | 19.16 | 151.9 | 230.2 | -0.054 | 0 | -4.96 | -4 | 85.7 | 2.48 | 9.22 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.61
397 | 2008-08-17 | 120000 | 1 | 659.6 | 0.7 | -1.9 | 20.77 | 167.4 | 251.8 | -0.051 | 0 | -4.96 | -3.9 | 116.2 | 2.54 | 11.05 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.45
398 | 2008-08-17 | 130000 | 1 | 659.6 | 0.7 | -2.4 | 20.72 | 166.5 | 250.9 | -0.051 | 0 | -4.96 | -3.9 | 112.6 | 2.46 | 10.96 | 2 | 2.3 | 1.8 | 0.007 | 0.007 | 13.47
399 | 2008-08-17 | 140000 | 1 | 659.4 | 0.7 | -2.3 | 20.67 | 166.3 | 250.6 | -0.05 | 0 | -4.96 | -3.9 | 112.3 | 2.5 | 10.83 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.48
400 | 2008-08-17 | 150000 | 1 | 660.9 | 0.6 | -1.9 | 20.61 | 166.6 | 250.3 | -0.05 | 0 | -4.96 | -4 | 102.2 | 2.5 | 10.09 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.57
401 | 2008-08-17 | 160000 | 1 | 662.1 | 0.6 | -2.3 | 20.79 | 167.5 | 250.8 | -0.051 | 0 | -4.96 | -4 | 101.3 | 2.47 | 9.95 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.61
402 | 2008-08-17 | 170000 | 1 | 663.5 | 0.5 | -2.4 | 20.72 | 167.6 | 250.6 | -0.051 | 0 | -4.96 | -4.1 | 99.8 | 2.47 | 9.8 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.67
403 | 2008-08-17 | 180000 | 1 | 663.8 | 0.5 | -1.7 | 20.68 | 167.4 | 250.3 | -0.05 | 0 | -4.96 | -4.1 | 99.6 | 2.47 | 9.77 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.69
404 | 2008-08-17 | 190000 | 1 | 665.5 | 0.5 | -2.3 | 20.69 | 167.4 | 250.4 | -0.051 | 0 | -4.96 | -4.1 | 99.8 | 2.46 | 9.79 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.67
405 | 2008-08-17 | 200000 | 1 | 665.4 | 0.4 | -2.1 | 20.7 | 167.3 | 250.3 | -0.05 | 0 | -4.96 | -4 | 99 | 2.47 | 9.76 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.66
406 | 2008-08-17 | 210000 | 1 | 666 | 0.4 | -2.3 | 20.64 | 166.7 | 249.4 | -0.05 | 0 | -4.96 | -4.1 | 97.5 | 2.46 | 9.61 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.69
407 | 2008-08-17 | 220000 | 1 | 663.9 | 0.4 | -2.3 | 20.71 | 167.6 | 250.3 | -0.049 | 0 | -4.96 | -4 | 101.6 | 2.47 | 9.92 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.64
408 | 2008-08-17 | 230000 | 1 | 664.3 | 0.4 | -2.4 | 20.76 | 168.1 | 250.6 | -0.049 | 0 | -4.96 | -4.1 | 98.8 | 2.51 | 9.52 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.69
409 | 2008-08-18 | 0 | 1 | 664.2 | 0.4 | -2 | 21.14 | 171.2 | 257 | -0.05 | 0 | -4.96 | -4 | 115.1 | 2.47 | 10.68 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.53
410 | 2008-08-18 | 10000 | 1 | 650.1 | 0.3 | -2 | 18.99 | 150.8 | 228.5 | -0.049 | 0 | -4.96 | -4 | 86.4 | 2.51 | 9.31 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.62
411 | 2008-08-18 | 20000 | 1 | 649.6 | 0.3 | -2.4 | 19.12 | 151.6 | 229.6 | -0.05 | 0 | -4.96 | -4 | 87.6 | 2.48 | 9.29 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.64
412 | 2008-08-18 | 30000 | 1 | 649.8 | 0.3 | -2.2 | 19.1 | 151.5 | 229.5 | -0.05 | 0 | -4.96 | -4 | 87.8 | 2.47 | 9.31 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.64
413 | 2008-08-18 | 40000 | 1 | 649.9 | 0.3 | -2.3 | 19.02 | 151 | 229 | -0.05 | 0 | -4.97 | -4 | 86.9 | 2.48 | 9.35 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.63
414 | 2008-08-18 | 50000 | 1 | 651 | 0.3 | -2.1 | 19.07 | 152 | 228.7 | -0.049 | 0 | -4.97 | -4 | 87.5 | 2.48 | 9.41 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.61
415 | 2008-08-18 | 60000 | 1 | 652 | 0.3 | -2 | 19.26 | 154 | 232.3 | -0.048 | 0 | -4.96 | -4 | 89.9 | 2.51 | 9.52 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.62
416 | 2008-08-18 | 70000 | 1 | 662.6 | 2.1 | 17.3 | 21.36 | 174.4 | 261.1 | -0.049 | 0 | -4.96 | -16.6 | 133.6 | 3.41 | 11.92 | 2 | 9.38 | 3.6 | 0.014 | 0.007 | 11.95
417 | 2008-08-18 | 80000 | 1 | 663.7 | 0.7 | -2.1 | 21.36 | 174.5 | 261.5 | -0.051 | 0 | -4.96 | -3.9 | 126.6 | 2.53 | 11.8 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.47
418 | 2008-08-18 | 90000 | 1 | 664.2 | 0.9 | -2.3 | 21.26 | 172.7 | 258.5 | -0.051 | 0 | -4.96 | -4 | 115 | 2.51 | 11.31 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.52
419 | 2008-08-18 | 100000 | 1 | 664.1 | 0.8 | -2.2 | 21.44 | 174.1 | 260.9 | -0.05 | 0 | -4.96 | -3.9 | 128.6 | 2.52 | 11.9 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.46
420 | 2008-08-18 | 110000 | 1 | 663.3 | 0.8 | -2.1 | 21.4 | 173.9 | 260.9 | -0.05 | 0 | -4.96 | -3.9 | 129.4 | 2.54 | 12.02 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.45
421 | 2008-08-18 | 120000 | 1 | 663.3 | 0.7 | -2.3 | 21.36 | 173.3 | 260 | -0.049 | 0 | -4.96 | -3.9 | 124.1 | 2.51 | 11.63 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.45
422 | 2008-08-18 | 130000 | 1 | 664 | 0.7 | -2.3 | 21.54 | 174.8 | 261.5 | -0.05 | 0 | -4.96 | -3.9 | 123.6 | 2.55 | 11.58 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.42
423 | 2008-08-18 | 140000 | 1 | 664 | 0.6 | -2.6 | 21.43 | 173.6 | 260.2 | -0.049 | 0 | -4.96 | -3.9 | 121.5 | 2.49 | 11.43 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.44
424 | 2008-08-18 | 150000 | 1 | 651.5 | 0.6 | -2.3 | 19.14 | 151.4 | 229.3 | -0.048 | 0 | -4.96 | -4 | 84.2 | 2.51 | 9.24 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.63
425 | 2008-08-18 | 160000 | 1 | 661.8 | 0.6 | -2.5 | 21.43 | 173.5 | 259.9 | -0.049 | 0 | -4.96 | -3.9 | 127 | 2.51 | 11.68 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.44
426 | 2008-08-18 | 170000 | 1 | 662.9 | 0.5 | -2.2 | 21.28 | 172.3 | 258.9 | -0.049 | 0 | -4.97 | -3.9 | 122.8 | 2.49 | 11.57 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.46
427 | 2008-08-18 | 180000 | 1 | 651.3 | 0.5 | -2.5 | 19.07 | 150.8 | 228.7 | -0.049 | 0 | -4.96 | -4 | 84.4 | 2.51 | 9.31 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.64
428 | 2008-08-18 | 190000 | 1 | 650 | 0.5 | -2.4 | 19.08 | 151.6 | 229.5 | -0.049 | 0 | -4.96 | -4 | 86.1 | 2.47 | 9.31 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.63
429 | 2008-08-18 | 200000 | 1 | 650.3 | 0.5 | -2.3 | 19.12 | 152.1 | 230.2 | -0.047 | 0 | -4.96 | -4 | 86.2 | 2.48 | 9.31 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.63
430 | 2008-08-18 | 210000 | 1 | 651.9 | 0.5 | -2.2 | 19.36 | 154.2 | 232.6 | -0.048 | 0 | -4.96 | -4 | 90.2 | 2.53 | 9.51 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.62
431 | 2008-08-18 | 220000 | 1 | 663.9 | 0.4 | -2 | 21.42 | 173.6 | 260.6 | -0.049 | 0 | -4.96 | -3.9 | 125.8 | 2.46 | 11.63 | 1.9 | 2.3 | 1.8 | 0.007 | 0.007 | 13.46
432 | 2008-08-18 | 230000 | 1 | 652.6 | 0.4 | -2.1 | 19.04 | 151.2 | 229.4 | -0.049 | 0 | -4.96 | -4 | 85.5 | 2.5 | 9.39 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.64
433 | 2008-08-19 | 0 | 1 | 648.8 | 0.4 | -2 | 18.9 | 149.1 | 226.6 | -0.047 | 0 | -4.96 | -4 | 84.5 | 2.48 | 9.28 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.63
434 | 2008-08-19 | 10000 | 1 | 649.5 | 0.4 | -2.1 | 18.91 | 149.7 | 227.3 | -0.048 | 0 | -4.97 | -4 | 83.8 | 2.48 | 9.2 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.63
435 | 2008-08-19 | 20000 | 1 | 649.5 | 0.3 | -2.2 | 18.9 | 149.2 | 226.6 | -0.048 | 0 | -4.96 | -4 | 84.1 | 2.48 | 9.22 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.63
436 | 2008-08-19 | 30000 | 1 | 649.6 | 0.3 | -2.3 | 18.9 | 149.7 | 227.3 | -0.048 | 0 | -4.96 | -4 | 85.5 | 2.48 | 9.31 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.64
437 | 2008-08-19 | 40000 | 1 | 649.7 | 0.3 | -2.1 | 18.91 | 150.1 | 227.8 | -0.049 | 0 | -4.97 | -4 | 86 | 2.47 | 9.25 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.64
438 | 2008-08-19 | 50000 | 1 | 650 | 0.3 | -2 | 18.93 | 150.2 | 227.8 | -0.048 | 0 | -4.96 | -4 | 85 | 2.47 | 9.15 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.63
439 | 2008-08-19 | 60000 | 1 | 651.8 | 0.3 | -2.4 | 19.12 | 152.4 | 230.4 | -0.048 | 0 | -4.96 | -4 | 86.4 | 2.47 | 9.17 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.63
440 | 2008-08-19 | 70000 | 1 | 652.3 | 2.3 | 19.6 | 19.14 | 151.8 | 229.8 | -0.046 | 0 | -4.96 | -20.4 | 87.7 | 3.41 | 9.66 | 2.1 | 9.37 | 3.7 | 0.014 | 0.008 | 12.08
441 | 2008-08-19 | 80000 | 1 | 652.2 | 0.8 | -2.2 | 19.19 | 152.7 | 230.9 | -0.046 | 0 | -4.96 | -4 | 86.3 | 2.48 | 9.15 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.64
442 | 2008-08-19 | 90000 | 1 | 651.7 | 0.9 | -2.2 | 19.11 | 151.6 | 229.6 | -0.045 | 0 | -4.97 | -4 | 85.6 | 2.48 | 9.73 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.64
443 | 2008-08-19 | 100000 | 1 | 652.1 | 0.9 | -2.2 | 19.25 | 152.7 | 231 | -0.046 | 0 | -4.96 | -4 | 86.5 | 2.47 | 9.14 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.64
444 | 2008-08-19 | 110000 | 1 | 652.2 | 0.8 | -2.1 | 19.19 | 152.3 | 230.5 | -0.049 | 0 | -4.97 | -4 | 85.7 | 2.48 | 9.1 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.65
445 | 2008-08-19 | 120000 | 1 | 652.9 | 0.8 | -2.4 | 19.21 | 152.9 | 231.2 | -0.047 | 0 | -4.97 | -4 | 86.1 | 2.47 | 9.1 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.65
446 | 2008-08-19 | 130000 | 1 | 652.6 | 0.7 | -2 | 19.13 | 152.3 | 230.6 | -0.047 | 0 | -4.96 | -4 | 86 | 2.48 | 9.12 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.66
447 | 2008-08-19 | 140000 | 1 | 652.5 | 0.7 | -2 | 19.19 | 152.5 | 230.8 | -0.051 | 0 | -4.97 | -4 | 87.9 | 2.46 | 9.2 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.66
448 | 2008-08-19 | 150000 | 1 | 652.5 | 0.7 | -2.2 | 19.16 | 151.8 | 230.2 | -0.051 | 0 | -4.96 | -4 | 88.4 | 2.47 | 9.29 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.66
449 | 2008-08-19 | 160000 | 1 | 652 | 0.7 | -2.6 | 19.11 | 151.7 | 229.8 | -0.05 | 0 | -4.96 | -4 | 86.3 | 2.46 | 9.27 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.65
450 | 2008-08-19 | 170000 | 1 | 653.1 | 0.6 | -2.3 | 19.15 | 152.3 | 230.3 | -0.05 | 0 | -4.96 | -4 | 84.7 | 2.48 | 9.2 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.62
451 | 2008-08-19 | 180000 | 1 | 653.6 | 0.6 | -2.6 | 19.24 | 153.6 | 231.8 | -0.05 | 0 | -4.96 | -4 | 86.7 | 2.47 | 9.3 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.63
452 | 2008-08-19 | 190000 | 1 | 652.8 | 0.5 | -2.1 | 19.12 | 151.8 | 229.6 | -0.049 | 0 | -4.97 | -4 | 83.9 | 2.5 | 9.19 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.59
453 | 2008-08-19 | 200000 | 1 | 651.3 | 0.5 | -2.4 | 19.13 | 152.3 | 229.9 | -0.052 | 0 | -4.96 | -4 | 84.3 | 2.49 | 9.21 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.58
454 | 2008-08-19 | 210000 | 1 | 652.1 | 0.5 | -2.3 | 19.06 | 151.8 | 229.5 | -0.05 | 0 | -4.96 | -4 | 83.8 | 2.5 | 9.2 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.58
455 | 2008-08-19 | 220000 | 1 | 650.2 | 0.5 | -2 | 18.87 | 150.1 | 227.3 | -0.048 | 0 | -4.96 | -4 | 82.5 | 2.5 | 9.14 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.57
456 | 2008-08-19 | 230000 | 1 | 649.4 | 0.4 | -2.2 | 18.8 | 150 | 227.1 | -0.049 | 0 | -4.97 | -4 | 83.1 | 2.5 | 9.16 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.56
457 | 2008-08-20 | 0 | 1 | 653.1 | 0.4 | -2.3 | 19.13 | 153.8 | 231.9 | -0.049 | 0 | -4.96 | -4 | 85 | 2.49 | 9.27 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.58
458 | 2008-08-20 | 10000 | 1 | 653.4 | 0.4 | -2 | 19.13 | 153.8 | 232 | -0.049 | 0 | -4.96 | -4 | 85.5 | 2.49 | 9.22 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.58
459 | 2008-08-20 | 20000 | 1 | 654 | 0.4 | -2 | 19.21 | 153.8 | 231.9 | -0.049 | 0 | -4.96 | -4 | 85.2 | 2.5 | 9.21 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.58
460 | 2008-08-20 | 30000 | 1 | 654.1 | 0.4 | -2.2 | 19.19 | 153.7 | 231.9 | -0.048 | 0 | -4.96 | -4 | 85.6 | 2.5 | 9.21 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.58
461 | 2008-08-20 | 40000 | 1 | 655.1 | 0.3 | -2.7 | 19.34 | 154.5 | 232.9 | -0.05 | 0 | -4.96 | -4 | 85.6 | 2.49 | 9.19 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.59
462 | 2008-08-20 | 50000 | 1 | 654.1 | 0.3 | -2.1 | 19.27 | 154.1 | 232.2 | -0.049 | 0 | -4.97 | -4 | 85.6 | 2.49 | 9.21 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.58
463 | 2008-08-20 | 60000 | 1 | 653.9 | 0.4 | -2 | 19.31 | 154.4 | 232.7 | -0.049 | 0 | -4.96 | -4 | 86.8 | 2.48 | 9.31 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.61
464 | 2008-08-20 | 70000 | 1 | 653.2 | 1.8 | 19.7 | 19.32 | 154.2 | 232.6 | -0.049 | 0 | -4.96 | -12.2 | 88 | 3.49 | 9.86 | 2 | 9.44 | 3.7 | 0.014 | 0.008 | 12.03
465 | 2008-08-20 | 80000 | 1 | 652.7 | 0.8 | -2.2 | 19.21 | 153.5 | 231.7 | -0.048 | 0 | -4.96 | -4 | 87.4 | 2.49 | 9.46 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.59
466 | 2008-08-20 | 90000 | 1 | 654.1 | 0.9 | -2.3 | 19.38 | 154.6 | 233 | -0.05 | 0 | -4.97 | -4 | 89.7 | 2.51 | 9.94 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.59
467 | 2008-08-20 | 100000 | 1 | 654.1 | 0.9 | -2 | 19.31 | 154.1 | 232.6 | -0.05 | 0 | -4.97 | -4 | 88.7 | 2.48 | 9.38 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.59
468 | 2008-08-20 | 110000 | 1 | 653.3 | 0.8 | -2.4 | 19.32 | 153.7 | 231.9 | -0.049 | 0 | -4.96 | -4 | 85.3 | 2.49 | 9.27 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.58
469 | 2008-08-20 | 120000 | 1 | 653.5 | 0.8 | -1.9 | 19.24 | 153.7 | 231.8 | -0.048 | 0 | -4.96 | -4 | 84.7 | 2.48 | 9.24 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.59
470 | 2008-08-20 | 130000 | 1 | 655.3 | 0.8 | -2.4 | 19.44 | 154.8 | 233.3 | -0.05 | 0 | -4.96 | -4 | 83.8 | 2.49 | 9.09 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.59
471 | 2008-08-20 | 140000 | 1 | 653.9 | 0.7 | -2.2 | 19.31 | 153.4 | 231.5 | -0.049 | 0 | -4.96 | -4 | 82.2 | 2.5 | 8.97 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.56
472 | 2008-08-20 | 150000 | 1 | 653.3 | 0.7 | -2.2 | 19.22 | 153.3 | 231.2 | -0.049 | 0 | -4.96 | -4 | 82.1 | 2.51 | 8.94 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.55
473 | 2008-08-20 | 160000 | 1 | 652.5 | 0.6 | -2.2 | 19.22 | 153.6 | 231.6 | -0.048 | 0 | -4.97 | -4 | 85.4 | 2.51 | 9.02 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.57
474 | 2008-08-20 | 170000 | 1 | 653.7 | 0.6 | -2.2 | 19.37 | 154.6 | 233.3 | -0.048 | 0 | -4.96 | -4 | 88.6 | 2.5 | 9.2 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.59
475 | 2008-08-20 | 180000 | 1 | 653.1 | 0.6 | -1.8 | 19.2 | 152.9 | 231.3 | -0.047 | 0 | -4.97 | -4 | 88 | 2.5 | 9.23 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.59
476 | 2008-08-20 | 190000 | 1 | 652.4 | 0.6 | -2 | 19.17 | 152.9 | 231.2 | -0.046 | 0 | -4.96 | -4 | 89.5 | 2.48 | 9.3 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.6
477 | 2008-08-20 | 200000 | 1 | 652.7 | 0.5 | -1.9 | 19.2 | 153.5 | 232.1 | -0.047 | 0 | -4.97 | -4 | 90.1 | 2.49 | 9.37 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.61
478 | 2008-08-20 | 210000 | 1 | 653.2 | 0.5 | -2.1 | 19.31 | 154.7 | 233.4 | -0.047 | 0 | -4.97 | -4 | 90.6 | 2.48 | 9.36 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.61
479 | 2008-08-20 | 220000 | 1 | 653.4 | 0.4 | -2.2 | 19.21 | 153.5 | 231.9 | -0.046 | 0 | -4.96 | -4 | 89.7 | 2.5 | 9.38 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.6
480 | 2008-08-20 | 230000 | 1 | 652.3 | 0.4 | -2.3 | 19.01 | 151 | 229.1 | -0.047 | 0 | -4.96 | -4 | 87.5 | 2.49 | 9.46 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.61
481 | 2008-08-21 | 0 | 0 | 555.3 | 18.7 | -20.7 | 1.76 | 7.7 | 15.3 | -0.046 | 0 | -4.97 | -4 | 22.1 | 2.03 | 6.23 | 2.8 | 7.38 | 8.4 | 0.031 | 0.01 | 19.31
482 | 2008-08-21 | 10000 | 0 | 432.6 | 7.3 | -49.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -4 | 0.6 | 0 | 0.1 | -0.1 | 0.02 | 0.3 | 0.002 | 0 | 20.59
483 | 2008-08-21 | 20000 | 0 | 408.6 | 7.6 | -49.5 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -4 | 0.5 | 0 | -0.01 | 0 | 0.02 | 0.3 | 0.003 | 0 | 20.6
484 | 2008-08-21 | 30000 | 0 | 406.4 | 6.7 | -49 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -4.97 | -4 | 0.6 | -0.01 | -0.02 | -0.1 | 0.01 | 0.3 | 0.002 | 0 | 20.61
485 | 2008-08-21 | 40000 | 1 | 574.3 | 20.5 | 10.8 | 6.4 | 18 | 18.4 | -0.047 | 0 | -4.96 | -4 | 5.9 | 9.06 | 27.27 | 12.2 | 37.08 | 49.8 | 0.183 | 0.045 | 16.83
486 | 2008-08-21 | 50000 | 1 | 619.1 | 15.1 | 25.6 | 11.47 | 66 | 103.4 | -0.047 | 0 | -4.96 | -4 | 61.5 | 8.44 | 25.17 | 8.7 | 33.74 | 34.5 | 0.127 | 0.032 | 14.82
487 | 2008-08-21 | 60000 | 1 | 652 | 0.3 | -2.5 | 19.44 | 155.1 | 233.7 | -0.048 | 0 | -4.97 | -4 | 95.5 | 2.38 | 10.3 | 1.9 | 2.23 | 1.8 | 0.007 | 0.007 | 13.65
488 | 2008-08-21 | 70000 | 1 | 653.1 | 2.3 | 20 | 19.23 | 153.1 | 231.6 | -0.046 | 0 | -4.96 | -4 | 90.7 | 3.47 | 9.72 | 2 | 9.42 | 3.7 | 0.014 | 0.007 | 12.11
489 | 2008-08-21 | 80000 | 1 | 653.8 | 0.7 | -2 | 19.32 | 154 | 232.5 | -0.046 | 0 | -4.96 | -4 | 91.9 | 2.46 | 9.71 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.65
490 | 2008-08-21 | 90000 | 1 | 653.7 | 0.9 | -2.4 | 19.28 | 153.7 | 232.2 | -0.047 | 0 | -4.97 | -4 | 101.8 | 2.08 | 10.26 | 1.7 | 1.95 | 1.6 | 0.006 | 0.006 | 13.66
491 | 2008-08-21 | 100000 | 1 | 653.7 | 0.9 | -2.3 | 19.32 | 153.7 | 232.5 | -0.047 | 0 | -4.97 | -4 | 113.7 | 1.57 | 9.88 | 1.3 | 1.46 | 1.2 | 0.004 | 0.005 | 13.68
492 | 2008-08-21 | 110000 | 1 | 652.5 | 0.8 | -2 | 19.31 | 153.6 | 232.5 | -0.048 | 0 | -4.96 | -4 | 125.2 | 1.18 | 9.9 | 1 | 1.11 | 0.9 | 0.003 | 0.004 | 13.7
493 | 2008-08-21 | 120000 | 1 | 652.8 | 0.8 | -2 | 19.33 | 153.9 | 232.9 | -0.046 | 0 | -4.97 | -4 | 137.3 | 0.88 | 9.82 | 0.7 | 0.82 | 0.7 | 0.003 | 0.003 | 13.71
494 | 2008-08-21 | 130000 | 1 | 652.6 | 0.8 | -2.1 | 19.28 | 153.5 | 232.2 | -0.047 | 0 | -4.97 | -4 | 148.5 | 0.69 | 9.72 | 0.6 | 0.64 | 0.5 | 0.002 | 0.002 | 13.71
495 | 2008-08-21 | 140000 | 1 | 652.5 | 0.7 | -2.3 | 19.17 | 152.9 | 231.7 | -0.046 | 0 | -4.96 | -4 | 106.6 | 1.52 | 9.73 | 1.3 | 1.43 | 1.2 | 0.004 | 0.005 | 13.72
496 | 2008-08-21 | 150000 | 1 | 652.6 | 1 | -1.8 | 19.18 | 152.8 | 231.7 | -0.046 | 0 | -4.96 | -4 | 96.5 | 2.6 | 9.72 | 1.9 | 2.44 | 1.7 | 0.006 | 0.007 | 12.94
497 | 2008-08-21 | 160000 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999
498 | 2008-08-21 | 170000 | 1 | 652.5 | 0.7 | -2.3 | 19.28 | 153.4 | 232.5 | -0.048 | 0 | -888 | -888 | 92.4 | 2.43 | 9.53 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.75
499 | 2008-08-21 | 180000 | 1 | 645.2 | 0.7 | -2.2 | 18.39 | 144.1 | 221.1 | -0.049 | 0 | -888 | -888 | 83.7 | 2.48 | 9.21 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.75
500 | 2008-08-21 | 190000 | 1 | 647.9 | 0.7 | -2.3 | 18.92 | 150.2 | 228.3 | -0.05 | 0 | -888 | -888 | 92.2 | 2.42 | 9.62 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.75
501 | 2008-08-21 | 200000 | 1 | 652.3 | 0.6 | -2.7 | 19.34 | 154.3 | 233.1 | -0.051 | 0 | -888 | -888 | 95.4 | 2.42 | 9.75 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.75
502 | 2008-08-21 | 210000 | 1 | 652 | 0.6 | -2.1 | 19.11 | 151.7 | 230.4 | -0.051 | 0 | -888 | -888 | 91.6 | 2.43 | 9.7 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.75
503 | 2008-08-21 | 220000 | 0 | 550 | 33.9 | -56.7 | 1.85 | 8.5 | 16.8 | -0.05 | 0 | -888 | -888 | 17.5 | 1.96 | 6.29 | 2.9 | 7.31 | 8.8 | 0.034 | 0.011 | 19.5
504 | 2008-08-21 | 230000 | 0 | 394.7 | 34.2 | -151.5 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -888 | -888 | 0.9 | 0 | 0.23 | 0 | 0.01 | 0.6 | 0.007 | 0 | 20.8
505 | 2008-08-22 | 0 | 0 | 345.1 | 35.6 | -186.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.5 | 0 | 0.01 | -0.2 | 0.02 | 0.6 | 0.007 | 0 | 20.81
506 | 2008-08-22 | 10000 | 0 | 318.2 | 35.3 | -154.6 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.6 | 0 | -0.02 | -0.2 | 0.02 | 0.8 | 0.008 | 0 | 20.81
507 | 2008-08-22 | 20000 | 0 | 300.3 | 30.1 | -179.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -888 | -888 | 0.6 | 0 | -0.02 | -0.2 | 0.01 | 0.6 | 0.007 | 0 | 20.73
508 | 2008-08-22 | 30000 | 0 | 288.2 | 27 | -155.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.5 | 0 | -0.03 | 0 | 0.01 | 0.4 | 0.007 | 0 | 20.8
509 | 2008-08-22 | 40000 | 0 | 279.3 | 23.6 | -148.1 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | 0.1 | 0.02 | 0.7 | 0.007 | 0.001 | 20.79
510 | 2008-08-22 | 50000 | 0 | 272.3 | 23 | -142.2 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.5 | 0 | -0.03 | 0 | 0.01 | 0.6 | 0.007 | 0 | 20.79
511 | 2008-08-22 | 60000 | 0 | 268.7 | 20.5 | -156.6 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.3 | 0 | -0.03 | -0.1 | 0.01 | 0.6 | 0.006 | 0 | 20.79
512 | 2008-08-22 | 70000 | 0 | 264.3 | 21.8 | -149.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -888 | -888 | 0.3 | 0 | -0.03 | -0.1 | 0.02 | 0.6 | 0.007 | 0 | 20.8
513 | 2008-08-22 | 80000 | 0 | 259.1 | 22 | -161.5 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -888 | -888 | 0.3 | 0 | -0.03 | 0 | 0.01 | 0.2 | 0.007 | 0 | 20.8
514 | 2008-08-22 | 90000 | 0 | 254.3 | 20.6 | -196.3 | 0.05 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.3 | 0 | 2.05 | 0.1 | 0.01 | 0.6 | 0.007 | 0.001 | 20.8
515 | 2008-08-22 | 100000 | 0 | 242 | 20 | -192.5 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -888 | -888 | 0.3 | 0 | -0.03 | -0.1 | 0.01 | 0.5 | 0.008 | 0 | 20.81
516 | 2008-08-22 | 110000 | 0 | 225.9 | 18.3 | -163.9 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -888 | -888 | 0.3 | 0 | -0.02 | 0.1 | 0.01 | 0.5 | 0.007 | 0.001 | 20.8
517 | 2008-08-22 | 120000 | 0 | 209.5 | 15.8 | -134.4 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -888 | -888 | 0.3 | 0.01 | -0.01 | 0.3 | 0.02 | 0.8 | 0.007 | 0.001 | 20.79
518 | 2008-08-22 | 130000 | 0 | 198.4 | 14.3 | -147.6 | 0.14 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.4 | 0.01 | -0.02 | 0.3 | 0.01 | 0.1 | 0.005 | 0.001 | 20.78
519 | 2008-08-22 | 140000 | 0 | 196 | 13.5 | -125.2 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.4 | 0 | -0.04 | -0.1 | 0.02 | 0.5 | 0.005 | 0 | 20.76
520 | 2008-08-22 | 150000 | 0 | 195.4 | 12.5 | -105.6 | 0.05 | 0.5 | 1.2 | -0.051 | 0 | -888 | -888 | 0.4 | 0 | -0.04 | -0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.75
521 | 2008-08-22 | 160000 | 0 | 194.1 | 12.8 | -100.4 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.74
522 | 2008-08-22 | 170000 | 0 | 192.4 | 12.9 | -97.2 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -888 | -888 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.4 | 0.005 | 0 | 20.74
523 | 2008-08-22 | 180000 | 0 | 189.7 | 12.9 | -111.4 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.66
524 | 2008-08-22 | 190000 | 0 | 186.7 | 13.1 | -106.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -888 | -888 | 0.3 | 0 | -0.03 | -0.1 | 0.01 | 0.5 | 0.004 | 0 | 20.73
525 | 2008-08-22 | 200000 | 0 | 182.5 | 12.3 | -96.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -888 | -888 | 0.5 | 0 | -0.04 | -0.1 | 0.01 | 0.6 | 0.005 | 0 | 20.74
526 | 2008-08-22 | 210000 | 0 | 173.2 | 11.3 | -105.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.02 | 0.8 | 0.005 | 0 | 20.74
527 | 2008-08-22 | 220000 | 0 | 165.9 | 10.7 | -118.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.1 | 0.004 | 0 | 20.75
528 | 2008-08-22 | 230000 | 0 | 161.4 | 9.9 | -113.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -888 | -888 | 0.4 | 0 | -0.02 | -0.1 | 0.01 | 0.2 | 0.004 | 0 | 20.75
529 | 2008-08-23 | 0 | 0 | 158.7 | 9 | -111.7 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.75
530 | 2008-08-23 | 10000 | 0 | 156.8 | 8.3 | -123.7 | 0.04 | 0.5 | 1.3 | -0.045 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | -0.2 | 0.01 | 0.2 | 0.004 | 0 | 20.68
531 | 2008-08-23 | 20000 | 0 | 154.7 | 7.8 | -123.1 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -888 | -888 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.75
532 | 2008-08-23 | 30000 | 0 | 152.9 | 7.6 | -116.3 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -888 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.005 | 0 | 20.75
533 | 2008-08-23 | 40000 | 0 | 151.2 | 7.3 | -103 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.004 | 0 | 20.75
534 | 2008-08-23 | 50000 | 0 | 149.9 | 7.4 | -105.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | 0 | 0.02 | 0.7 | 0.005 | 0 | 20.75
535 | 2008-08-23 | 60000 | 0 | 148.9 | 7 | -100.4 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.02 | 0.5 | 0.005 | 0 | 20.75
536 | 2008-08-23 | 70000 | 0 | 147.4 | 8.3 | -104.7 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -888 | -888 | 0.5 | 0 | -0.03 | 0 | 0.01 | 0.2 | 0.004 | 0 | 20.75
537 | 2008-08-23 | 80000 | 0 | 146.5 | 7.6 | -104.1 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -888 | -888 | 0.4 | 0 | -0.04 | -0.1 | 0 | -0.1 | 0.004 | 0 | 20.75
538 | 2008-08-23 | 90000 | 0 | 145.8 | 7.2 | -101.5 | 0.05 | 0.5 | 1.2 | -0.048 | 0 | -888 | -888 | 0.4 | 0.01 | 2.09 | 0.4 | 0.02 | 0.7 | 0.005 | 0.001 | 20.67
539 | 2008-08-23 | 100000 | 0 | 145.5 | 6.7 | -99.6 | 0.04 | 0.5 | 1.2 | -0.047 | 0 | -888 | -888 | 0.4 | 0.01 | -0.03 | 0.4 | 0.02 | 0.4 | 0.004 | 0.001 | 20.73
540 | 2008-08-23 | 110000 | 0 | 143.9 | 6.2 | -92 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -888 | -888 | 0.5 | 0 | -0.03 | 0 | 0.01 | 0.4 | 0.004 | 0 | 20.73
541 | 2008-08-23 | 120000 | 0 | 143.8 | 5.6 | -88.7 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -888 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0 | 0 | 0.003 | 0 | 20.72
542 | 2008-08-23 | 130000 | 0 | 142.4 | 5 | -83.8 | 0.04 | 0.5 | 1.2 | -0.046 | 0 | -888 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.7
543 | 2008-08-23 | 140000 | 0 | 142.3 | 4.7 | -75.8 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | -888 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.68
544 | 2008-08-23 | 150000 | 0 | 142.3 | 4.7 | -75.6 | 0.04 | 0.5 | 1.2 | -0.046 | 0 | -888 | -888 | 0.4 | 0 | -0.04 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.6
545 | 2008-08-23 | 160000 | 0 | 140.5 | 4.3 | -62.4 | 0.04 | 0.5 | 1.2 | -0.047 | 0 | -888 | -888 | 0.6 | -0.01 | -0.03 | -0.1 | 0.02 | 0.3 | 0.003 | 0 | 20.66
546 | 2008-08-23 | 170000 | 0 | 140.4 | 5.2 | -68.9 | 0.04 | 0.5 | 1.2 | -0.047 | 0 | -888 | -888 | 0.6 | -0.01 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.65
547 | 2008-08-23 | 180000 | 0 | 139.8 | 7.2 | -60.9 | 0.04 | 0.5 | 1.2 | -0.046 | 0 | -888 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.66
548 | 2008-08-23 | 190000 | 0 | 138.7 | 7 | -74.4 | 0.04 | 0.5 | 1.2 | -0.047 | 0 | -888 | -888 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.68
549 | 2008-08-23 | 200000 | 0 | 137.3 | 6.2 | -66.7 | 0.04 | 0.5 | 1.2 | -0.047 | 0 | -888 | -888 | 0.5 | -0.01 | -0.03 | -0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.68
550 | 2008-08-23 | 210000 | 0 | 137 | 5.9 | -69.2 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | -888 | -888 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.69
551 | 2008-08-23 | 220000 | 0 | 135.4 | 5.9 | -72.1 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -888 | -888 | 0.5 | -0.01 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.69
552 | 2008-08-23 | 230000 | 1 | 393 | 26.1 | 76 | 6.13 | 15.3 | 15.8 | -0.049 | 0 | -888 | -888 | 0.5 | 9.31 | 26.91 | 13.3 | 38.69 | 54.3 | 0.2 | 0.049 | 17.06
553 | 2008-08-24 | 0 | 1 | 620.1 | 21 | 26.2 | 7.28 | 22.2 | 22.5 | -0.049 | 0 | -888 | -888 | 14.8 | 10.26 | 30.02 | 13.4 | 42.44 | 55.3 | 0.204 | 0.049 | 16.32
554 | 2008-08-24 | 10000 | 1 | 617.6 | 12.3 | 16.4 | 11.53 | 67.1 | 78.2 | -0.05 | 0 | -888 | -888 | 58.9 | 7.44 | 22.9 | 7.3 | 32.51 | 32.3 | 0.119 | 0.027 | 14.52
555 | 2008-08-24 | 20000 | 1 | 639.3 | 0.2 | -2.1 | 19.59 | 156 | 231.6 | -0.05 | 0 | -888 | -888 | 105.5 | 2.17 | 10.23 | 1.7 | 2.04 | 1.6 | 0.006 | 0.006 | 13.62
556 | 2008-08-24 | 30000 | 1 | 640.1 | 2.3 | 19.7 | 18.9 | 149 | 224.1 | -0.048 | 0 | -888 | -888 | 118 | 3.26 | 14.31 | 1.9 | 10.29 | 4.4 | 0.016 | 0.007 | 12.05
557 | 2008-08-24 | 40000 | 1 | 632.2 | 13.5 | 19.7 | 14.27 | 105.9 | 163.7 | -0.049 | 0 | -888 | -888 | 131.5 | 4.34 | 13.62 | 3.6 | 16.87 | 10.7 | 0.04 | 0.013 | 13.26
558 | 2008-08-24 | 50000 | 0 | 488.1 | 29.8 | -50.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -888 | -888 | 6.6 | 0.04 | 0.33 | 0.9 | 0.05 | 0.9 | 0.004 | 0.003 | 20.62
559 | 2008-08-24 | 60000 | 0 | 415.4 | 31.9 | -58.7 | 0.03 | 0.4 | 1.2 | -0.051 | 0 | -888 | -888 | 0.2 | 0.02 | 0.05 | 0.6 | 0.04 | 0.9 | 0.004 | 0.002 | 20.66
560 | 2008-08-24 | 70000 | 0 | 399 | 31.8 | -73.4 | 0.03 | 0.4 | 1.2 | -0.052 | 0 | -888 | -888 | 0.2 | 0.02 | -0.01 | 0.4 | 0.02 | 0.4 | 0.003 | 0.002 | 20.66
561 | 2008-08-24 | 80000 | 0 | 389.8 | 30.7 | -72 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | -0.4 | 0.01 | 0 | 0.3 | 0.01 | 0.3 | 0.003 | 0.001 | 20.59
562 | 2008-08-24 | 90000 | 0 | 382.1 | 28 | -67.8 | 0.25 | 1.5 | 2.7 | -0.051 | 0 | -888 | -888 | -0.3 | 0.01 | 2.08 | 0.2 | 0.02 | 0.2 | 0.003 | 0.001 | 20.66
563 | 2008-08-24 | 100000 | 0 | 375.6 | 27.2 | -63.3 | 0.04 | 0.5 | 1.2 | -0.049 | 0 | -888 | -888 | -0.4 | 0.01 | -0.01 | 0.1 | 0 | 0.1 | 0.002 | 0.001 | 20.66
564 | 2008-08-24 | 110000 | 0 | 372.2 | 26.4 | -67.6 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.3 | 0.01 | 0 | 0.3 | 0.01 | 0.3 | 0.003 | 0.001 | 20.66
565 | 2008-08-24 | 120000 | 0 | 372.7 | 25.8 | -66.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -888 | -888 | -0.2 | 0.01 | -0.02 | 0.3 | 0.01 | 0.2 | 0.003 | 0.001 | 20.66
566 | 2008-08-24 | 130000 | 0 | 369.5 | 24.5 | -67.4 | 0.11 | 0.5 | 1.3 | -0.048 | 0 | -888 | -888 | -0.2 | 0.01 | -0.03 | 0.3 | 0.01 | 0.3 | 0.003 | 0.001 | 20.66
567 | 2008-08-24 | 140000 | 0 | 365.5 | 23.7 | -64.9 | 0.12 | 0.5 | 1.2 | -0.05 | 0 | -888 | -888 | -0.2 | 0 | -0.04 | 0 | 0.02 | 0.6 | 0.004 | 0 | 20.66
568 | 2008-08-24 | 150000 | 0 | 360.5 | 22.6 | -84 | 0.04 | 0.5 | 1.2 | -0.05 | 0 | -888 | -888 | -0.4 | 0 | -0.03 | 0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.67
569 | 2008-08-24 | 160000 | 0 | 347.3 | 21.2 | -74.2 | 0.03 | 0.5 | 1.2 | -0.05 | 0 | -888 | -888 | -0.3 | 0 | -0.03 | 0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.67
570 | 2008-08-24 | 170000 | 0 | 329.8 | 19.8 | -72.7 | 0.79 | 3.7 | 4.6 | -0.05 | 0 | -888 | -888 | -0.2 | 0 | -0.03 | 0 | 0 | 0.1 | 0.003 | 0 | 20.68
571 | 2008-08-24 | 180000 | 0 | 320.1 | 19.3 | -69.6 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -888 | -888 | -0.3 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.68
572 | 2008-08-24 | 190000 | 0 | 314.6 | 18 | -82.1 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -888 | -888 | -0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.68
573 | 2008-08-24 | 200000 | 0 | 310.3 | 18.1 | -74.5 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.2 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.69
574 | 2008-08-24 | 210000 | 0 | 306.3 | 17.5 | -89.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.1 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.7
575 | 2008-08-24 | 220000 | 0 | 302.9 | 16.9 | -70.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -888 | -888 | 0.3 | -0.01 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.7
576 | 2008-08-24 | 230000 | 0 | 300.1 | 16.1 | -64.5 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -888 | -888 | 0.3 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.7
577 | 2008-08-25 | 0 | 0 | 297.7 | 15.1 | -80.2 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -888 | -888 | 0.2 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.7
578 | 2008-08-25 | 10000 | 0 | 295.4 | 14.2 | -75.5 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.1 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.7
579 | 2008-08-25 | 20000 | 0 | 293.8 | 13.4 | -83.1 | 0.04 | 0.5 | 1.3 | -0.046 | 0 | -888 | -888 | 0.3 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.7
580 | 2008-08-25 | 30000 | 1 | 484.6 | 22.1 | 38.5 | 6.17 | 15.5 | 16 | -0.046 | 0 | -888 | -888 | 0.1 | 9.27 | 26.96 | 13.2 | 36.07 | 51.1 | 0.188 | 0.049 | 17.07
581 | 2008-08-25 | 40000 | 1 | 620 | 23.5 | 43.9 | 8.11 | 29.3 | 30.8 | -0.047 | 0 | -888 | -888 | 24.6 | 10.29 | 30.01 | 12.5 | 36.96 | 45.2 | 0.166 | 0.046 | 16.04
582 | 2008-08-25 | 50000 | 1 | 616.9 | 16.5 | 23.2 | 10.88 | 58.9 | 99.3 | -0.048 | 0 | -888 | -888 | 47.4 | 9.1 | 26.35 | 9.5 | 38.88 | 40.3 | 0.148 | 0.035 | 14.98
583 | 2008-08-25 | 60000 | 1 | 637.2 | 3.9 | 15.9 | 19.71 | 158 | 235.3 | -0.047 | 0 | -888 | -888 | 103.9 | 3.16 | 10.69 | 2.2 | 9.01 | 3.7 | 0.014 | 0.008 | 12.13
584 | 2008-08-25 | 70000 | 1 | 639.1 | 0.4 | -2.4 | 19.27 | 153.4 | 230.4 | -0.047 | 0 | -888 | -888 | 95.2 | 2.28 | 9.82 | 1.9 | 2.14 | 1.8 | 0.006 | 0.007 | 13.71
585 | 2008-08-25 | 80000 | 1 | 641 | 0.9 | -2.5 | 19.24 | 153.1 | 230.5 | -0.048 | 0 | -888 | -888 | 93.5 | 2.34 | 9.76 | 1.9 | 2.2 | 1.8 | 0.007 | 0.007 | 13.68
586 | 2008-08-25 | 90000 | 1 | 644 | 0.9 | -2.2 | 19.28 | 153.6 | 231.6 | -0.048 | 0 | -888 | -888 | 93.3 | 2.34 | 10.17 | 1.9 | 2.2 | 1.8 | 0.007 | 0.007 | 13.68
587 | 2008-08-25 | 100000 | 1 | 645.1 | 0.9 | -2.3 | 19.29 | 153.5 | 231.9 | -0.046 | 0 | -888 | -888 | 94.9 | 2.33 | 9.68 | 1.9 | 2.18 | 1.8 | 0.007 | 0.007 | 13.7
588 | 2008-08-25 | 110000 | 1 | 645.7 | 0.8 | -2.4 | 19.65 | 156.8 | 236 | -0.048 | 0 | -888 | -888 | 104.1 | 2.37 | 10.1 | 1.9 | 2.22 | 1.8 | 0.007 | 0.007 | 13.69
589 | 2008-08-25 | 120000 | 1 | 662.2 | 0.8 | -2.3 | 21.67 | 176.3 | 263.5 | -0.045 | 0 | -888 | -888 | 135 | 2.38 | 11.85 | 1.9 | 2.23 | 1.8 | 0.007 | 0.007 | 13.52
590 | 2008-08-25 | 130000 | 1 | 662.5 | 0.7 | -2.3 | 21.55 | 175.2 | 262.4 | -0.049 | 0 | -888 | -888 | 134.4 | 2.37 | 11.82 | 1.9 | 2.22 | 1.8 | 0.007 | 0.007 | 13.54
591 | 2008-08-25 | 140000 | 1 | 662.5 | 0.7 | -2.1 | 21.69 | 176.4 | 263.4 | -0.048 | 0 | -888 | -888 | 133.7 | 2.38 | 11.73 | 1.9 | 2.23 | 1.8 | 0.007 | 0.007 | 13.53
592 | 2008-08-25 | 150000 | 1 | 660.5 | 0.7 | -2.8 | 21.56 | 175.5 | 261.6 | -0.048 | 0 | -888 | -888 | 123.3 | 2.36 | 10.98 | 1.9 | 2.21 | 1.8 | 0.007 | 0.007 | 13.6
593 | 2008-08-25 | 160000 | 1 | 659.2 | 0.7 | -2.2 | 21.56 | 175.7 | 261.5 | -0.049 | 0 | -888 | -888 | 118 | 2.33 | 10.65 | 1.9 | 2.18 | 1.8 | 0.007 | 0.007 | 13.61
594 | 2008-08-25 | 170000 | 1 | 658.1 | 0.6 | -2.2 | 17.28 | 131.3 | 134.2 | -0.047 | 0 | -888 | -888 | 74.1 | 2.42 | 9.15 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.77
595 | 2008-08-25 | 180000 | 1 | 647.4 | 0.7 | -2.3 | 16.91 | 127.7 | 131.2 | -0.047 | 0 | -888 | -888 | 74.8 | 2.31 | 9.13 | 1.9 | 2.16 | 1.8 | 0.007 | 0.007 | 13.79
596 | 2008-08-25 | 190000 | 1 | 643.4 | 0.6 | -2.6 | 16.18 | 118.9 | 132.3 | -0.049 | 0 | -888 | -888 | 76.8 | 2.31 | 9.73 | 1.9 | 2.17 | 1.8 | 0.007 | 0.007 | 13.79
597 | 2008-08-25 | 200000 | 1 | 656.9 | 0.6 | -2.3 | 19.5 | 153.8 | 221.4 | 0.037 | 0 | -888 | -888 | 114.3 | 2.37 | 11.01 | 1.9 | 2.22 | 1.8 | 0.007 | 0.007 | 13.49
598 | 2008-08-25 | 210000 | 1 | 651.2 | 0.5 | -2.2 | 18.78 | 147.9 | 227.1 | -0.046 | 0 | -888 | -888 | 90.8 | 2.27 | 9.49 | 1.9 | 2.13 | 1.8 | 0.006 | 0.007 | 13.75
599 | 2008-08-25 | 220000 | 1 | 644.1 | 0.5 | -2.4 | 19.37 | 154.2 | 233.1 | -0.049 | 0 | -888 | -888 | 93.8 | 2.37 | 9.62 | 2 | 2.22 | 1.8 | 0.007 | 0.007 | 13.75
600 | 2008-08-25 | 230000 | 1 | 644.7 | 0.4 | -2.2 | 19.29 | 153.9 | 232.5 | -0.049 | 0 | -888 | -888 | 92.5 | 2.44 | 9.6 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.75
601 | 2008-08-26 | 0 | 1 | 644.7 | 0.4 | -2.5 | 19.36 | 154.6 | 233.4 | -0.048 | 0 | -888 | -888 | 93.4 | 2.44 | 9.66 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.76
602 | 2008-08-26 | 10000 | 1 | 644.8 | 0.4 | -2.2 | 19.21 | 153.2 | 231.6 | -0.049 | 0 | -888 | -888 | 92.7 | 2.43 | 9.65 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.76
603 | 2008-08-26 | 20000 | 1 | 644.5 | 0.4 | -2.3 | 19.16 | 153 | 231.4 | -0.05 | 0 | -888 | -888 | 92.6 | 2.43 | 9.69 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.77
604 | 2008-08-26 | 30000 | 1 | 644.2 | 0.4 | -2.1 | 19.26 | 154 | 232.4 | -0.05 | 0 | -888 | -888 | 94.5 | 2.43 | 9.77 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.77
605 | 2008-08-26 | 40000 | 1 | 643.6 | 0.4 | -2 | 19.18 | 153.1 | 231.2 | -0.049 | 0 | -888 | -888 | 94.8 | 2.44 | 9.87 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.78
606 | 2008-08-26 | 50000 | 1 | 644.1 | 0.4 | -2.8 | 19.29 | 153.8 | 231.8 | -0.049 | 0 | -888 | -888 | 96.8 | 2.42 | 9.94 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.78
607 | 2008-08-26 | 60000 | 1 | 644.1 | 2.5 | 25.9 | 19.29 | 153.9 | 231.7 | -0.05 | 0 | -888 | -888 | 99.6 | 3.34 | 10.31 | 2.1 | 9.27 | 3.7 | 0.014 | 0.007 | 12.2
608 | 2008-08-26 | 70000 | 1 | 647.8 | 0.5 | -2.4 | 19.28 | 153.7 | 231.3 | -0.049 | 0 | -888 | -888 | 94.8 | 2.42 | 9.84 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.8
609 | 2008-08-26 | 80000 | 1 | 651.6 | 1 | -2.4 | 19.34 | 154.2 | 232.2 | -0.049 | 0 | -888 | -888 | 95.3 | 2.43 | 9.79 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.77
610 | 2008-08-26 | 90000 | 1 | 653.2 | 1 | -1.9 | 19.33 | 154.2 | 232.4 | -0.049 | 0 | -888 | -888 | 95 | 2.43 | 10.27 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.77
611 | 2008-08-26 | 100000 | 1 | 653.2 | 0.9 | -2.5 | 19.32 | 154.1 | 232.6 | -0.05 | 0 | -888 | -888 | 95.1 | 2.43 | 9.82 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.79
612 | 2008-08-26 | 110000 | 1 | 652.6 | 0.8 | -1.8 | 19.24 | 152.7 | 231.2 | -0.049 | 0 | -888 | -888 | 97.1 | 2.43 | 9.98 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.82
613 | 2008-08-26 | 120000 | 1 | 651.7 | 0.8 | -2 | 19.26 | 153.1 | 231.8 | -0.049 | 0 | -888 | -888 | 96.8 | 2.4 | 9.86 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.83
614 | 2008-08-26 | 130000 | 1 | 652.2 | 0.8 | -2.2 | 19.3 | 153.3 | 232.2 | -0.047 | 0 | -888 | -888 | 96.6 | 2.41 | 9.88 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.83
615 | 2008-08-26 | 140000 | 1 | 652.8 | 0.7 | -2.1 | 19.34 | 153.7 | 232.8 | -0.05 | 0 | -888 | -888 | 96.7 | 2.41 | 9.82 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.83
616 | 2008-08-26 | 150000 | 1 | 649.9 | 0.7 | -2.7 | 19.25 | 153.4 | 232.5 | -0.049 | 0 | -888 | -888 | 97.1 | 2.41 | 9.88 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.82
617 | 2008-08-26 | 160000 | 1 | 652.8 | 0.7 | -2.7 | 19.23 | 152.6 | 231.6 | -0.049 | 0 | -888 | -888 | 95.9 | 2.42 | 9.81 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.81
618 | 2008-08-26 | 170000 | 1 | 652 | 0.7 | -2.4 | 19.16 | 152.6 | 231.3 | -0.048 | 0 | -888 | -888 | 94.3 | 2.42 | 9.73 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.8
619 | 2008-08-26 | 180000 | 1 | 651.9 | 0.7 | -2.1 | 19.16 | 152.6 | 231 | -0.05 | 0 | -888 | -888 | 92.8 | 2.43 | 9.64 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.78
620 | 2008-08-26 | 190000 | 1 | 651.8 | 0.6 | -2.4 | 19.31 | 153.5 | 232 | -0.05 | 0 | -888 | -888 | 95.2 | 2.43 | 9.76 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.78
621 | 2008-08-26 | 200000 | 1 | 652.1 | 0.6 | -2.3 | 19.26 | 153.9 | 232.3 | -0.05 | 0 | -888 | -888 | 94.8 | 2.43 | 9.75 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.76
622 | 2008-08-26 | 210000 | 1 | 653.2 | 0.5 | -2.1 | 19.27 | 154 | 232.6 | -0.049 | 0 | -888 | -888 | 95 | 2.43 | 9.76 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.76
623 | 2008-08-26 | 220000 | 1 | 651.7 | 0.5 | -2.3 | 19.23 | 153.3 | 231.7 | -0.049 | 0 | -888 | -888 | 94.4 | 2.43 | 9.74 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.75
624 | 2008-08-26 | 230000 | 1 | 652.4 | 0.5 | -2.3 | 19 | 150.4 | 228.4 | -0.051 | 0 | -888 | -888 | 89 | 2.45 | 9.6 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.74
625 | 2008-08-27 | 0 | 0 | 556.5 | 27 | -47.1 | 1.55 | 6.4 | 13.1 | -0.05 | 0 | -888 | -888 | 10.7 | 2 | 6.2 | 2.8 | 7.89 | 9.1 | 0.035 | 0.011 | 19.6
626 | 2008-08-27 | 10000 | 0 | 438.8 | 19.6 | -115.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.7 | 0 | 0.03 | -0.1 | 0.01 | 0.4 | 0.005 | 0 | 20.75
627 | 2008-08-27 | 20000 | 0 | 416.2 | 19.1 | -135.2 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -888 | -888 | 0.8 | 0 | -0.01 | -0.1 | 0.01 | 0.5 | 0.005 | 0 | 20.75
628 | 2008-08-27 | 30000 | 0 | 407.3 | 16.6 | -92.9 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -888 | -888 | 0.7 | 0 | -0.03 | -0.1 | 0.02 | 0.5 | 0.004 | 0 | 20.66
629 | 2008-08-27 | 40000 | 1 | 549.9 | 22.8 | 7.6 | 6.19 | 18.3 | 18.8 | -0.049 | 0 | -888 | -888 | 1.1 | 8.54 | 25.42 | 11.6 | 33.8 | 45.8 | 0.169 | 0.043 | 17.11
630 | 2008-08-27 | 50000 | 1 | 611.3 | 13 | 17.8 | 12.25 | 73.7 | 113.5 | -0.048 | 0 | -888 | -888 | 37.6 | 7.64 | 23.59 | 7.5 | 34.65 | 34.3 | 0.126 | 0.028 | 14.57
631 | 2008-08-27 | 60000 | 1 | 639.5 | 4.2 | -3.4 | 19.57 | 156.5 | 234.7 | -0.047 | 0 | -888 | -888 | 100.8 | 3.27 | 10.5 | 2.3 | 9.29 | 3.8 | 0.015 | 0.008 | 12.16
632 | 2008-08-27 | 70000 | 1 | 646 | 0.5 | -2.3 | 19.3 | 153.6 | 231.3 | -0.047 | 0 | -888 | -888 | 95.6 | 2.48 | 9.95 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.75
633 | 2008-08-27 | 80000 | 1 | 653.6 | 3 | -21.3 | 19.34 | 153.7 | 232.1 | -0.048 | 0 | -888 | -888 | 96.1 | 3.46 | 9.88 | 2.1 | 9.61 | 3.9 | 0.015 | 0.008 | 12.06
634 | 2008-08-27 | 90000 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999 | -9999
635 | 2008-08-27 | 100000 | 1 | 645.5 | 0.1 | -4.5 | 19.09 | 151.8 | 228.5 | -0.047 | 0 | 0.79 | -888 | 95.7 | 1.16 | 9.66 | 0.5 | 2.27 | 0.9 | 0.004 | 0.002 | 11.89
636 | 2008-08-27 | 110000 | 1 | 652.6 | 5.6 | 155.9 | 19.27 | 153.1 | 231.3 | -0.047 | 0 | 20.2 | -888 | 96.8 | 9.1 | 9.69 | 3 | 52.27 | 15.4 | 0.057 | 0.011 | 2.3
637 | 2008-08-27 | 120000 | 1 | 653 | 5.8 | 76.3 | 19.32 | 154 | 232.5 | -0.049 | 0 | 9.52 | -888 | 95.7 | 5.26 | 9.81 | 2.7 | 25.95 | 8.4 | 0.031 | 0.01 | 8.99
638 | 2008-08-27 | 130000 | 1 | 649.2 | 1.2 | -2.1 | 18.78 | 148.2 | 225.5 | -0.047 | 0 | 3.14 | -888 | 93.2 | 5.58 | 9.54 | 2.2 | 8.37 | 3 | 0.011 | 0.008 | 7.56
639 | 2008-08-27 | 140000 | 1 | 652.4 | 1.7 | -6.4 | 19.34 | 154.5 | 233 | -0.048 | 0 | 0.95 | -888 | 95.9 | 3.35 | 9.79 | 2.5 | 3.17 | 2.4 | 0.009 | 0.009 | 12.43
640 | 2008-08-27 | 150000 | 1 | 652.6 | 0 | -2.4 | 19.35 | 153.7 | 232.4 | -0.047 | 0 | 0 | -888 | 97.4 | 2.37 | 10.97 | 2 | 2.22 | 1.9 | 0.007 | 0.008 | 13.98
641 | 2008-08-27 | 160000 | 1 | 652.7 | 0 | -2.2 | 19.31 | 153.5 | 232.2 | -0.048 | 0 | 0 | -888 | 98.3 | 2.34 | 9.89 | 2 | 2.2 | 1.9 | 0.007 | 0.007 | 13.96
642 | 2008-08-27 | 170000 | 1 | 651.9 | 0 | -2.2 | 19.23 | 153.1 | 231.7 | -0.047 | 0 | 0 | -888 | 98.9 | 2.24 | 9.88 | 1.9 | 2.12 | 1.8 | 0.007 | 0.007 | 13.98
643 | 2008-08-27 | 180000 | 1 | 651.2 | 0 | -2.6 | 19.24 | 153.4 | 231.8 | -0.046 | 0 | 0 | -888 | 98 | 2.34 | 9.89 | 2 | 2.2 | 1.9 | 0.007 | 0.007 | 13.98
644 | 2008-08-27 | 190000 | 1 | 652.3 | 0 | -2.4 | 19.28 | 153.4 | 231.8 | -0.049 | 0 | 0 | -888 | 97.2 | 2.35 | 9.89 | 2 | 2.21 | 1.9 | 0.007 | 0.007 | 13.98
645 | 2008-08-27 | 200000 | 1 | 652.5 | 0 | -2.5 | 19.31 | 154 | 232.3 | -0.048 | 0 | 0 | -888 | 97.3 | 2.36 | 9.93 | 2 | 2.21 | 1.9 | 0.007 | 0.007 | 13.98
646 | 2008-08-27 | 210000 | 1 | 653.7 | 0 | -2.1 | 19.09 | 151.2 | 229.3 | -0.046 | 0 | 0 | -888 | 94 | 2.38 | 9.94 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.97
647 | 2008-08-27 | 220000 | 0 | 557.4 | 27.7 | 3.1 | 1.53 | 6.4 | 12.8 | -0.05 | 0 | 6.17 | -888 | 8.8 | 1.87 | 5.71 | 3.1 | 7.18 | 9.3 | 3.201 | 6.343 | 19.95
648 | 2008-08-27 | 230000 | 0 | 446.1 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 6.4 | -888 | 1.2 | -0.01 | 0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.1
649 | 2008-08-28 | 0 | 0 | 423 | 0 | 0 | 0.04 | 0.5 | 1.2 | -0.047 | 0 | 6.4 | -888 | 0.7 | 0 | 0 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.1
650 | 2008-08-28 | 10000 | 0 | 412.1 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 6.4 | -888 | 0.8 | 0 | -0.02 | 0 | 0.02 | 0 | 0.002 | 0 | 21.1
651 | 2008-08-28 | 20000 | 0 | 401.4 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 6.4 | -888 | 0.9 | 0 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0 | 21.09
652 | 2008-08-28 | 30000 | 0 | 392.7 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 6.4 | -888 | 0.9 | 0 | -0.04 | 0 | 0.01 | 0 | 0.002 | 0 | 21.09
653 | 2008-08-28 | 40000 | 0 | 386.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 6.4 | -888 | 1.2 | 0 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0 | 21.01
654 | 2008-08-28 | 50000 | 1 | 549.8 | 22.1 | 14.9 | 6.39 | 18.9 | 19.4 | -0.049 | 0 | 4.96 | -888 | 3.9 | 8.96 | 26.23 | 13.3 | 37.39 | 54.6 | 0.201 | 0.049 | 17.31
655 | 2008-08-28 | 60000 | 1 | 613 | 14.8 | 24.8 | 11.91 | 69.8 | 106.2 | -0.049 | 0 | 6.28 | -888 | 45 | 8.24 | 24.33 | 8.8 | 37.63 | 40.5 | 0.149 | 0.032 | 15.04
656 | 2008-08-28 | 70000 | 1 | 636.7 | 2.5 | 26.5 | 18.61 | 145.5 | 221.6 | -0.048 | 0 | 3.12 | -888 | 92.9 | 3.11 | 10.36 | 1.9 | 9.16 | 3.6 | 0.013 | 0.007 | 12.38
657 | 2008-08-28 | 80000 | 1 | 638.8 | 0.1 | -2.5 | 18.52 | 144.7 | 220.9 | -0.05 | 0 | 0 | -888 | 89.4 | 2.24 | 9.44 | 1.9 | 2.09 | 1.8 | 0.007 | 0.007 | 13.98
658 | 2008-08-28 | 90000 | 1 | 643 | 0.1 | -2.3 | 18.49 | 144.3 | 220.5 | -0.05 | 0 | 0 | -888 | 88.2 | 2.24 | 9.99 | 1.9 | 2.11 | 1.8 | 0.007 | 0.007 | 13.98
659 | 2008-08-28 | 100000 | 1 | 645.5 | 0.1 | -2.4 | 18.47 | 144.3 | 220.9 | -0.05 | 0 | 0 | -888 | 88.4 | 2.24 | 9.37 | 1.9 | 2.11 | 1.8 | 0.007 | 0.007 | 13.99
660 | 2008-08-28 | 110000 | 1 | 645.5 | 0.1 | -2.4 | 18.49 | 144.4 | 221.2 | -0.049 | 0 | 0 | -888 | 89.3 | 2.23 | 9.43 | 1.9 | 2.09 | 1.8 | 0.007 | 0.007 | 13.99
661 | 2008-08-28 | 120000 | 1 | 645.6 | 0.1 | -2.5 | 18.49 | 144.6 | 221.4 | -0.05 | 0 | 0 | -888 | 88.4 | 2.23 | 9.34 | 1.9 | 2.09 | 1.8 | 0.007 | 0.007 | 13.99
662 | 2008-08-28 | 130000 | 1 | 645.8 | 0.1 | -2.5 | 18.5 | 144.1 | 220.8 | -0.049 | 0 | 1.85 | -888 | 86.5 | 2.21 | 9.18 | 1.9 | 2.08 | 1.8 | 0.007 | 0.007 | 13.98
663 | 2008-08-28 | 140000 | 1 | 646.5 | 0.1 | -2.1 | 18.56 | 145 | 221.8 | -0.051 | 0 | 2.62 | -888 | 85.4 | 2.24 | 9.15 | 1.9 | 2.1 | 1.8 | 0.007 | 0.007 | 13.96
664 | 2008-08-28 | 150000 | 1 | 646.3 | 0.1 | -2 | 18.56 | 144.6 | 221.1 | -0.05 | 0 | 2.71 | -888 | 85.7 | 2.25 | 9.12 | 1.9 | 2.11 | 1.8 | 0.007 | 0.007 | 13.95
665 | 2008-08-28 | 160000 | 1 | 646 | 0.1 | -2.1 | 18.54 | 144.9 | 221.4 | -0.05 | 0 | 2.72 | -888 | 85.2 | 2.24 | 9.07 | 1.9 | 2.11 | 1.8 | 0.007 | 0.007 | 13.94
666 | 2008-08-28 | 170000 | 1 | 645.5 | 0.1 | -2.2 | 18.57 | 144.9 | 220.9 | -0.049 | 0 | 2.54 | -888 | 82.7 | 2.26 | 8.98 | 1.9 | 2.13 | 1.8 | 0.007 | 0.007 | 13.93
667 | 2008-08-28 | 180000 | 1 | 645.3 | 0.1 | -2.7 | 18.51 | 144.3 | 220.2 | -0.049 | 0 | 2.68 | -888 | 84.2 | 2.27 | 9.05 | 1.9 | 2.13 | 1.8 | 0.007 | 0.007 | 13.92
668 | 2008-08-28 | 190000 | 1 | 645.3 | 0.1 | -2.6 | 18.51 | 144.7 | 220.7 | -0.05 | 0 | 2.72 | -888 | 84.7 | 2.3 | 9.12 | 1.9 | 2.16 | 1.8 | 0.007 | 0.007 | 13.9
669 | 2008-08-28 | 200000 | 1 | 645.3 | 0.1 | -2.2 | 18.58 | 145.3 | 221.3 | -0.049 | 0 | 2.6 | -888 | 82.5 | 2.39 | 9.06 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.89
670 | 2008-08-28 | 210000 | 1 | 645.8 | 0.1 | -2.4 | 18.27 | 142.4 | 218.1 | -0.049 | 0 | 2.52 | -888 | 79.4 | 2.41 | 8.98 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.9
671 | 2008-08-28 | 220000 | 0 | 552.9 | 24.8 | 3.1 | 1.36 | 5.6 | 11.1 | -0.049 | 0 | 53.78 | -888 | 10.1 | 1.74 | 5.39 | 2.9 | 6.42 | 7.8 | 22.19 | 11.09 | 19.95
672 | 2008-08-28 | 230000 | 0 | 444.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 65.9 | -888 | 1.1 | 0 | 0.02 | 0 | 0.01 | 0 | 0.004 | 0.001 | 21.01
673 | 2008-08-29 | 0 | 0 | 420.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 65.9 | -888 | 0.8 | -0.01 | 0 | 0 | 0.01 | 0 | 0.005 | 0.001 | 21
674 | 2008-08-29 | 10000 | 0 | 408.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 65.9 | -888 | 1 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.004 | 0.002 | 21
675 | 2008-08-29 | 20000 | 0 | 397.7 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 65.9 | -888 | 1.1 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.005 | 0.002 | 20.99
676 | 2008-08-29 | 30000 | 0 | 391.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 65.9 | -888 | 1 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.005 | 0.002 | 20.98
677 | 2008-08-29 | 40000 | 1 | 548.7 | 23.2 | 13.6 | 6.45 | 19.6 | 20 | -0.048 | 0 | 2.21 | -888 | 1.3 | 9.02 | 26.58 | 12.8 | 38.11 | 53 | 0.195 | 0.047 | 17.07
678 | 2008-08-29 | 50000 | 1 | 611 | 13.5 | 21.4 | 12.07 | 72.3 | 110.6 | -0.047 | 0 | 0.83 | -888 | 44.2 | 7.47 | 23.48 | 7.8 | 35.4 | 37.1 | 0.137 | 0.029 | 14.81
679 | 2008-08-29 | 60000 | 1 | 641.1 | 2.2 | 24 | 19.61 | 156.4 | 234.4 | -0.047 | 0 | 4.02 | -888 | 93 | 3.36 | 10.22 | 2.1 | 9.42 | 3.8 | 0.014 | 0.008 | 12.28
680 | 2008-08-29 | 70000 | 1 | 645.1 | 0.1 | -2.6 | 19.36 | 154.6 | 232.6 | -0.05 | 0 | 2.78 | -888 | 91.7 | 2.37 | 9.51 | 2 | 2.22 | 1.9 | 0.007 | 0.007 | 13.88
681 | 2008-08-29 | 80000 | 1 | 654 | 0.1 | -2.4 | 19.48 | 155.7 | 233.9 | -0.048 | 0 | 2.94 | -888 | 92.9 | 2.4 | 9.47 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.86
682 | 2008-08-29 | 90000 | 1 | 655.4 | 0.1 | -2.2 | 19.52 | 155.7 | 234.3 | -0.046 | 0 | 3.02 | -888 | 94 | 2.45 | 10.1 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.84
683 | 2008-08-29 | 100000 | 1 | 707 | 0 | -2.1 | 21.39 | 173.5 | 274.1 | 0.295 | 1 | 5.35 | -888 | 139.2 | 2.78 | 12.92 | 2.1 | 2.61 | 1.9 | 0.007 | 0.008 | 12.91
684 | 2008-08-29 | 110000 | 1 | 714.7 | 0 | -1.9 | 21.32 | 172.6 | 273 | 0.225 | 1 | 5.08 | -888 | 136.9 | 2.63 | 12.51 | 2 | 2.48 | 1.9 | 0.007 | 0.007 | 13.07
685 | 2008-08-29 | 120000 | 1 | 715.2 | 0 | -2.2 | 21.32 | 172.3 | 273.4 | 0.278 | 1 | 5.14 | -888 | 135.2 | 2.69 | 12.46 | 2 | 2.54 | 1.9 | 0.007 | 0.007 | 12.99
686 | 2008-08-29 | 130000 | 1 | 715 | 0 | -2.2 | 21.32 | 172.3 | 273.6 | 0.277 | 1 | 5.13 | -888 | 135.1 | 2.69 | 12.43 | 2 | 2.53 | 1.9 | 0.007 | 0.007 | 13
687 | 2008-08-29 | 140000 | 1 | 713.9 | 0 | -1.9 | 21.33 | 172.9 | 274 | 0.261 | 1 | 5.06 | -888 | 135 | 2.68 | 12.46 | 2 | 2.51 | 1.9 | 0.007 | 0.007 | 13.02
688 | 2008-08-29 | 150000 | 1 | 711.2 | 0 | -1.9 | 21.32 | 173.4 | 273.6 | 0.236 | 1 | 4.97 | -888 | 134 | 2.68 | 12.35 | 2 | 2.51 | 1.9 | 0.007 | 0.007 | 13.06
689 | 2008-08-29 | 160000 | 1 | 710.9 | 0 | -2.1 | 21.36 | 173.5 | 273.8 | 0.237 | 1 | 5.17 | -888 | 135.1 | 2.67 | 12.24 | 2 | 2.51 | 1.9 | 0.007 | 0.007 | 13.07
690 | 2008-08-29 | 170000 | 1 | 709.9 | 0 | -2 | 21.3 | 173 | 272.6 | 0.209 | 1 | 4.74 | -888 | 134.2 | 2.61 | 12.11 | 2 | 2.45 | 1.9 | 0.007 | 0.007 | 13.12
691 | 2008-08-29 | 180000 | 1 | 657.9 | 0 | -2.4 | 19.16 | 152.4 | 230.7 | -0.047 | 0 | 0 | -888 | 85.8 | 2.42 | 9.09 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.81
692 | 2008-08-29 | 190000 | 1 | 653.8 | 0 | -2.1 | 19.42 | 154.5 | 232.7 | -0.047 | 0 | 0 | -888 | 90.5 | 2.41 | 9.25 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.83
693 | 2008-08-29 | 200000 | 1 | 654 | 0 | -2.4 | 19.37 | 155.1 | 233.4 | -0.048 | 0 | 0 | -888 | 91.4 | 2.41 | 9.34 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.84
694 | 2008-08-29 | 210000 | 1 | 652.8 | 0.1 | -2.4 | 19.15 | 152.1 | 230.1 | -0.048 | 0 | 0 | -888 | 89.2 | 2.42 | 9.41 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.85
695 | 2008-08-29 | 220000 | 0 | 555.3 | 32.9 | -131.3 | 1.42 | 6.4 | 12.3 | -0.048 | 0 | 0 | -888 | 7.3 | 1.62 | 4.96 | 2.7 | 6.34 | 8.4 | 265.936 | 11.09 | 19.85
696 | 2008-08-29 | 230000 | 0 | 447.2 | 0.5 | 2.5 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | 0.03 | 0 | 0.01 | 0.5 | 117.134 | 0.003 | 20.87
697 | 2008-08-30 | 0 | 0 | 426.3 | 0 | -9.7 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.7 | -0.01 | -0.01 | 0 | 0.01 | 0.1 | 79.148 | 0.003 | 20.95
698 | 2008-08-30 | 10000 | 0 | 417.9 | 0.2 | -8.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0.2 | 0.011 | 0.003 | 20.95
699 | 2008-08-30 | 20000 | 0 | 409.4 | 0.3 | -39.2 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.1 | 0.01 | 0.8 | 104.472 | 3.169 | 20.95
700 | 2008-08-30 | 30000 | 0 | 404.3 | 0 | -3.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0 | 0.3 | 94.978 | 0.004 | 20.94
701 | 2008-08-30 | 40000 | 0 | 399.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 75.981 | 0.005 | 20.95
702 | 2008-08-30 | 50000 | 0 | 394.7 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.01 | 0 | 53.822 | 0.005 | 20.95
703 | 2008-08-30 | 60000 | 0 | 389 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.007 | 0.004 | 20.96
704 | 2008-08-30 | 70000 | 0 | 383.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.007 | 0.003 | 20.97
705 | 2008-08-30 | 80000 | 0 | 378.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.006 | 0.002 | 20.98
706 | 2008-08-30 | 90000 | 0 | 373.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.5 | -0.01 | 2.06 | 0 | 0.02 | 0 | 0.005 | 0.003 | 20.98
707 | 2008-08-30 | 100000 | 0 | 368.8 | 0 | 0 | 0.07 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.006 | 0.003 | 20.98
708 | 2008-08-30 | 110000 | 0 | 350.7 | 0 | 0 | 0.1 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.007 | 0.002 | 20.98
709 | 2008-08-30 | 120000 | 0 | 327 | 0 | 0 | 0.11 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.008 | 0.003 | 20.97
710 | 2008-08-30 | 130000 | 0 | 315.8 | 0 | 0 | 0.15 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.008 | 0.003 | 20.97
711 | 2008-08-30 | 140000 | 0 | 310.4 | 0 | 0 | 0.26 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.007 | 0.003 | 20.97
712 | 2008-08-30 | 150000 | 0 | 306.3 | 0 | 0 | 0.12 | 0.5 | 1.3 | -0.052 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.008 | 0.003 | 20.97
713 | 2008-08-30 | 160000 | 0 | 302.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.02 | 0 | 0.01 | 0 | 0.008 | 0.003 | 20.96
714 | 2008-08-30 | 170000 | 0 | 300.2 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.009 | 0.004 | 20.96
715 | 2008-08-30 | 180000 | 0 | 297.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 26.918 | 0.004 | 20.95
716 | 2008-08-30 | 190000 | 0 | 295.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.7 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.01 | 0.004 | 20.96
717 | 2008-08-30 | 200000 | 0 | 292.4 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.006 | 0.004 | 20.97
718 | 2008-08-30 | 210000 | 0 | 290 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.005 | 0.003 | 20.9
719 | 2008-08-30 | 220000 | 0 | 287.2 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.006 | 0.003 | 20.9
720 | 2008-08-30 | 230000 | 0 | 285 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | 0 | -888 | 0.5 | -0.01 | -0.02 | 0 | 0.01 | 0 | 0.006 | 0.003 | 20.98
721 | 2008-08-31 | 0 | 0 | 282.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.006 | 0.003 | 20.9
722 | 2008-08-31 | 10000 | 0 | 279.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.004 | 0.003 | 20.98
723 | 2008-08-31 | 20000 | 0 | 276.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.005 | 0.003 | 20.98
724 | 2008-08-31 | 30000 | 0 | 273.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.006 | 0.003 | 20.98
725 | 2008-08-31 | 40000 | 0 | 270.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.5 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.006 | 0.002 | 20.91
726 | 2008-08-31 | 50000 | 0 | 267.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.007 | 0.002 | 20.98
727 | 2008-08-31 | 60000 | 0 | 264.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.006 | 0.002 | 20.98
728 | 2008-08-31 | 70000 | 0 | 261.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | 0 | -0.03 | 0 | 0.02 | 0 | 0.005 | 0.001 | 21
729 | 2008-08-31 | 80000 | 0 | 258.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.7 | 0 | -0.03 | 0 | 0.01 | 0 | 0.005 | 0 | 21
730 | 2008-08-31 | 90000 | 0 | 255.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | 0 | 2.08 | 0 | 0.01 | 0 | 0.005 | 0 | 20.92
731 | 2008-08-31 | 100000 | 0 | 252.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | 0 | -0.03 | 0 | 0.01 | 0 | 0.005 | 0.001 | 20.92
732 | 2008-08-31 | 110000 | 0 | 250 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.005 | 0.002 | 20.92
733 | 2008-08-31 | 120000 | 0 | 247.5 | 0 | 0 | 0.1 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.006 | 0.003 | 20.98
734 | 2008-08-31 | 130000 | 0 | 244.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0 | 0 | 0.008 | 0.003 | 20.97
735 | 2008-08-31 | 140000 | 0 | 242.3 | 0 | 0 | 0.08 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.006 | 0.003 | 20.97
736 | 2008-08-31 | 150000 | 0 | 239.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.5 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.007 | 0.004 | 20.96
737 | 2008-08-31 | 160000 | 0 | 237.1 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.007 | 0.003 | 20.97
738 | 2008-08-31 | 170000 | 0 | 233.7 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.006 | 0.002 | 20.99
739 | 2008-08-31 | 180000 | 0 | 231 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.005 | 0.002 | 20.92
740 | 2008-08-31 | 190000 | 0 | 228.3 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.005 | 0.002 | 21
741 | 2008-08-31 | 200000 | 0 | 226.2 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.004 | 0.001 | 21.02
742 | 2008-08-31 | 210000 | 0 | 223.7 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.003 | 0.001 | 21.04
743 | 2008-08-31 | 220000 | 0 | 221.3 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.004 | 0.001 | 21.04
744 | 2008-08-31 | 230000 | 0 | 219 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.05
745 | / | /
[7 empty] | July Total MW-hr |  | 137025.7
Excluding non-op hours
Used gas use column to confirm operation

## September CEMS data
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-01
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-02
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-03
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-04
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | 60.6 | 2 | 114.4 | 0 | 103.7 | 5.35 | 0 | 0.4 | 0 | 368.6 | 14.6CS | 1:09
2 | 64.9 | 2 | 136.3 | 0 | 14.7 | 5.35 | 0 | 0.4 | 0 | 597.1 | 18.3CS
3 | 50.6 | 2 | 136.2 | 0 | 61.1 | 5.35 | 0 | 0.5 | 0 | 618.4 | 36.3CS
4 | 57.4 | 2 | 171.1 | 0 | 52.9 | 5.34 | 0 | 0.5 | 0 | 612.9 | 45.4CS
5 | 5.7 | 2.2 | 35.7 | 0.4 | 1.7 | 5.34 | 0.8 | 0.5 | 1.9 | 644.9 | 165.1 |  | 5:08 |  |  | ET 3:59
6 | 1.9 | 2.2 | 11.1 | 0 | 0 | 5.34 | 0.3 | 0.5 | 0.7 | 643.3 | 150.9
7 | 2 | 2.2 | 11.1 | 0.2 | 0.5 | 5.34 | 0.4 | 0.5 | 0.9 | 644.9 | 152.8
8 | 2 | 2.2 | 11.1 | 0.1 | 0.5 | 5.33 | 0.3 | 0.5 | 0.7 | 644.1 | 151.5
9 | 2.1 | 2.2 | 12.8 | 0.1 | 0.5 | 5.33 | 0.4 | 0.5 | 0.9 | 644.1 | 153
10 | 2 | 2.2 | 12.5 | 0.1 | 0.5 | 5.33 | 0.5 | 0.5 | 1.2 | 661.8 | 175
11 | 2 | 2.2 | 12.4 | 0.1 | 0.4 | 5.33 | 0.4 | 0.5 | 1 | 661.8 | 173.2
12 | 2 | 2.2 | 11.8 | 0.1 | 0.3 | 5.32 | 0.3 | 0.5 | 0.8 | 658.3 | 163.9
13 | 2 | 2.2 | 12.1 | 0.1 | 0.4 | 5.32 | 0.5 | 0.5 | 1.2 | 659.5 | 168.7
14 | 2 | 2.2 | 12.5 | 0.1 | 0.4 | 5.32 | 0.5 | 0.5 | 1.2 | 661.8 | 174.9
15 | 1.9 | 2.2 | 12.4 | 0.1 | 0.4 | 5.31 | 0.4 | 0.4 | 1 | 661.5 | 172.7
16 | 2 | 2.2 | 11.1 | 0.1 | 0.3 | 5.31 | 0.3 | 0.4 | 0.7 | 647.2 | 152.1
17 | 2 | 2.2 | 11.1 | 0.1 | 0.3 | 5.31 | 0.3 | 0.4 | 0.7 | 645.7 | 152.1
18 | 2 | 2.2 | 11.2 | 0.1 | 0.4 | 5.31 | 0.3 | 0.4 | 0.7 | 646.1 | 153
19 | 2 | 2.2 | 11.1 | 0.1 | 0.4 | 5.3 | 0.4 | 0.4 | 0.9 | 646.1 | 152.5
20 | 2 | 2.2 | 11 | 0.1 | 0.4 | 5.3 | 0.3 | 0.4 | 0.7 | 644.5 | 149.8
21 | 35.9 | 2.2 | 79.8 | 0 | 38.2 | 5.3 | 0 | 0.4 | 0 | 632.2 | 32.1SD |  |  | 21:05 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-05
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 55.2 | 2.2 | 123.2 | 0 | 27.4 | 5.3 | 0 | 0.4 | 0 | 567.9 | 25.4HS | 3:07
4 | 48.8 | 2.2 | 160.3 | 0 | 49.6 | 5.29 | 0 | 0.4 | 0 | 613.7 | 57.2HS |  | 4:56 |  |  | ET 1:49
5 | 1.6 | 2.2 | 9.6 | 0 | 0 | 5.29 | 0.3 | 0.4 | 0.6 | 642.5 | 154.4
6 | 2 | 2.2 | 11 | 0.2 | 0.7 | 5.29 | 0.4 | 0.4 | 0.9 | 642.1 | 149.2
7 | 2 | 2.2 | 11 | 0.2 | 0.6 | 5.28 | 0.4 | 0.4 | 0.9 | 642.9 | 149.5
8 | 2 | 2.2 | 11 | 0.2 | 0.5 | 5.28 | 0.3 | 0.4 | 0.7 | 643.7 | 150.1
9 | 2 | 2.2 | 11 | 0.2 | 0.5 | 5.28 | 0.4 | 0.4 | 0.9 | 642.5 | 148.7
10 | 2 | 2 | 10.9 | 0.1 | 0.5 | 5.28 | 0.3 | 0.4 | 0.7 | 642.5 | 148.5
11 | 2.1 | 2 | 11.7 | 0.2 | 0.5 | 5.27 | 0.3 | 0.4 | 0.7 | 637.8 | 134.6
12 | 2 | 2 | 10.2 | 0.2 | 0.5 | 5.27 | 0.3 | 0.4 | 0.7 | 637.8 | 134.4
13 | 2 | 2 | 11 | 0.1 | 0.4 | 5.27 | 0.3 | 0.4 | 0.7 | 644.1 | 149.2
14 | 2 | 2 | 11 | 0.1 | 0.4 | 5.27 | 0.3 | 0.4 | 0.7 | 644.1 | 149.8
15 | 2 | 2 | 11 | 0.1 | 0.4 | 5.26 | 0.3 | 0.3 | 0.7 | 642.5 | 149.7
16 | 2 | 2 | 11 | 0.1 | 0.4 | 5.26 | 0.4 | 0.3 | 0.9 | 642.5 | 150
17 | 2 | 2 | 11 | 0.1 | 0.4 | 5.26 | 0.3 | 0.3 | 0.7 | 643.3 | 150.2
18 | 2 | 2 | 11 | 0.1 | 0.4 | 5.26 | 0.4 | 0.3 | 0.9 | 644.1 | 150.8
19 | 2 | 2 | 11 | 0.1 | 0.5 | 5.25 | 0.4 | 0.3 | 0.9 | 644.5 | 151
20 | 2 | 2 | 11 | 0.2 | 0.5 | 5.25 | 0.4 | 0.3 | 0.9 | 643.7 | 148.9
21 | 34 | 2 | 78.3 | 0 | 36.2 | 5.25 | 0 | 0.3 | 0 | 631.9 | 35.6SD |  |  | 21:06 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-06
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 58.7 | 2 | 113.7 | 0 | 20.9 | 5.25 | 0 | 0.3 | 0 | 563.6 | 16.5HS | 3:06
4 | 35.6 | 2 | 128.3 | 0 | 47.3 | 5.24 | 0 | 0.3 | 0 | 617.6 | 68.8HS |  | 4:49 |  |  | ET 1:43
5 | 1.9 | 2 | 11 | 0 | 0 | 5.24 | 0.3 | 0.3 | 0.5 | 637.4 | 149
6 | 2 | 2 | 11 | 0.2 | 0.6 | 5.24 | 0.3 | 0.3 | 0.7 | 642.9 | 150.4
7 | 2 | 2 | 11 | 0.2 | 0.6 | 5.23 | 0.3 | 0.3 | 0.7 | 647.6 | 149.9
8 | 2 | 2 | 11 | 0.2 | 0.6 | 5.23 | 0.3 | 0.3 | 0.7 | 648 | 149.9
9 | 2 | 2 | 12.7 | 0.2 | 0.6 | 5.23 | 0.4 | 0.3 | 0.9 | 648.4 | 151.6
10 | 2 | 2 | 12.4 | 0.1 | 0.5 | 5.23 | 0.4 | 0.3 | 1 | 665.4 | 172.9
11 | 2 | 2 | 12.4 | 0.1 | 0.5 | 5.22 | 0.4 | 0.3 | 1 | 666.6 | 173
12 | 2 | 2 | 12.4 | 0.1 | 0.5 | 5.22 | 0.5 | 0.3 | 1.2 | 664.6 | 173.2
13 | 2 | 2 | 12.4 | 0.1 | 0.5 | 5.22 | 0.5 | 0.4 | 1.1 | 663.4 | 172.7
14 | 2 | 2 | 12.2 | 0.1 | 0.5 | 5.22 | 0.5 | 0.4 | 1.1 | 662.2 | 170.6 |  |  | 14:45 | 14:45
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-07
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 56.9 | 2 | 108.6 | 0 | 17.1 | 5.21 | 0 | 0.4 | 0 | 532.4 | 15.6WS | 3:07
4 | 36.4 | 2 | 121.5 | 0 | 35.9 | 5.21 | 0 | 0.4 | 0 | 634.6 | 60.3WS |  | 4:46 |  |  | ET 1:39
5 | 1.2 | 2 | 6.5 | 0.2 | 0.8 | 5.21 | 0.6 | 0.4 | 1.2 | 645.3 | 153.7
6 | 1.9 | 1.9 | 11.2 | 0 | 0 | 5.21 | 0.3 | 0.4 | 0.7 | 648.8 | 154.9
7 | 2 | 1.9 | 12.8 | 0.2 | 0.6 | 5.2 | 0.4 | 0.4 | 0.9 | 649.2 | 154.3
8 | 2 | 1.9 | 11.3 | 0.1 | 0.5 | 5.2 | 0.3 | 0.4 | 0.7 | 651.2 | 154.4
9 | 2 | 1.9 | 11.2 | 0.1 | 0.4 | 5.2 | 0.3 | 0.4 | 0.7 | 652 | 153.7
10 | 2 | 1.9 | 11.2 | 0.1 | 0.4 | 5.2 | 0.3 | 0.4 | 0.7 | 654.3 | 153.6
11 | 2 | 1.9 | 11.2 | 0.1 | 0.4 | 5.19 | 0.3 | 0.4 | 0.7 | 655.1 | 153.8
12 | 2 | 1.9 | 11.2 | 0.1 | 0.4 | 5.19 | 0.3 | 0.4 | 0.7 | 656.3 | 153.9
13 | 2 | 1.9 | 11.2 | 0.1 | 0.4 | 5.19 | 0.3 | 0.4 | 0.7 | 655.9 | 153.7
14 | 2 | 2 | 11.3 | 0.1 | 0.4 | 5.19 | 0.3 | 0.4 | 0.7 | 657.1 | 153.8
15 | 2 | 2 | 11.2 | 0.1 | 0.4 | 5.18 | 0.3 | 0.4 | 0.7 | 655.5 | 152.8
16 | 2 | 2 | 11.2 | 0.1 | 0.3 | 5.18 | 0.3 | 0.4 | 0.7 | 655.5 | 153.5
17 | 2 | 2 | 11.2 | 0.1 | 0.4 | 5.18 | 0.4 | 0.4 | 0.9 | 655.5 | 153.9
18 | 2 | 2 | 11.2 | 0.1 | 0.4 | 5.18 | 0.3 | 0.4 | 0.7 | 655.1 | 154.2
19 | 2 | 2 | 11.2 | 0.1 | 0.4 | 5.17 | 0.4 | 0.4 | 0.9 | 655.1 | 153.8
20 | 2 | 2 | 11 | 0.1 | 0.4 | 5.17 | 0.3 | 0.4 | 0.7 | 654 | 150.4
21 | 41 | 2 | 80.7 | 0 | 32.9 | 5.17 | 0 | 0.4 | 0 | 636.6 | 25.9SD |  |  | 21:04 | 21:19
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-08
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 58.4 | 2 | 109.6 | 0 | 11.8 | 5.17 | 0 | 0.4 | 0 | 579.4 | 15.2HS | 3:06
4 | 31.6 | 2 | 116.8 | 0 | 26 | 5.16 | 0 | 0.4 | 0 | 630.7 | 74.0HS |  | 4:40 |  |  | ET 1:34
5 | 1.9 | 1.9 | 11.4 | 0 | 0 | 5.16 | 0.3 | 0.4 | 0.7 | 641.3 | 157.7
6 | 2 | 1.9 | 11.1 | 0.3 | 0.9 | 5.16 | 0.4 | 0.3 | 0.9 | 645.3 | 151.2
7 | 2 | 1.9 | 12.7 | 0.2 | 0.7 | 5.15 | 0.4 | 0.3 | 0.9 | 647.2 | 152.1
8 | 2 | 2 | 12.3 | 0.2 | 0.7 | 5.15 | 0.5 | 0.4 | 1.2 | 661.5 | 173.2
9 | 2 | 2 | 12.2 | 0.2 | 0.6 | 5.15 | 0.5 | 0.4 | 1.1 | 663.4 | 172
10 | 1.9 | 2 | 12.2 | 0.2 | 0.6 | 5.15 | 0.5 | 0.4 | 1.1 | 663.4 | 171
11 | 2 | 2 | 13.6 | 0.1 | 0.5 | 5.15 | 0.4 | 0.4 | 0.9 | 664.6 | 165.6
12 | 2 | 2 | 13.7 | 0.1 | 0.5 | 5.14 | 0.3 | 0.4 | 0.8 | 667.4 | 166.4
13 | 2 | 2 | 12.1 | 0.1 | 0.5 | 5.14 | 0.4 | 0.4 | 1 | 667 | 168.3
14 | 2 | 2 | 12.2 | 0.2 | 0.6 | 5.14 | 0.5 | 0.4 | 1.1 | 664.6 | 170.4
15 | 2 | 2 | 12.6 | 0.1 | 0.5 | 5.13 | 0.3 | 0.4 | 0.7 | 653.6 | 149.9
16 | 2 | 2 | 12.6 | 0.2 | 0.5 | 5.13 | 0.4 | 0.4 | 0.9 | 652 | 150.3
17 | 2 | 2 | 12.3 | 0.2 | 0.6 | 5.13 | 0.5 | 0.4 | 1.1 | 662.6 | 172.7
18 | 2 | 2 | 14.1 | 0.2 | 0.6 | 5.13 | 0.5 | 0.4 | 1.1 | 663.4 | 173.1
19 | 2 | 2 | 12.3 | 0.2 | 0.6 | 5.13 | 0.5 | 0.4 | 1.1 | 663.4 | 172.9
20 | 2 | 2 | 12.2 | 0.2 | 0.6 | 5.12 | 0.4 | 0.4 | 0.9 | 664.2 | 170.8
21 | 28.5 | 2 | 66.3 | 0 | 27.9 | 5.12 | 0 | 0.4 | 0 | 641.7 | 38.4SD |  |  | 21:09 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-09
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 58.9 | 2 | 116.7 | 0 | 19.4 | 5.12 | 0 | 0.4 | 0 | 551.7 | 17.9HS | 3:08
4 | 34.6 | 2 | 121.2 | 0 | 43.3 | 5.12 | 0 | 0.4 | 0 | 615.7 | 65.5HS |  | 4:47 |  |  | ET 1:39
5 | 1.7 | 2 | 9.6 | 0 | 0 | 5.11 | 0.3 | 0.4 | 0.7 | 636.2 | 153.8
6 | 2 | 2 | 12.5 | 0.2 | 0.8 | 5.11 | 0.5 | 0.4 | 1.2 | 651.2 | 175.3
7 | 2 | 2 | 12.3 | 0.2 | 0.7 | 5.11 | 0.4 | 0.4 | 1 | 653.6 | 173
8 | 2 | 2 | 12.3 | 0.2 | 0.7 | 5.11 | 0.4 | 0.4 | 1 | 654 | 173.6
9 | 2 | 2 | 14.3 | 0.2 | 0.7 | 5.1 | 0.5 | 0.4 | 1.1 | 654.7 | 176
10 | 2 | 2 | 12.5 | 0.2 | 0.7 | 5.1 | 0.5 | 0.4 | 1.1 | 654.3 | 176
11 | 2 | 2 | 12.5 | 0.2 | 0.7 | 5.1 | 0.5 | 0.4 | 1.1 | 653.6 | 176.1
12 | 2 | 2 | 14.3 | 0.2 | 0.6 | 5.1 | 0.5 | 0.4 | 1.1 | 661.1 | 175.7
13 | 2 | 2 | 12.4 | 0.2 | 0.6 | 5.09 | 0.4 | 0.4 | 1 | 663.8 | 174.2
14 | 2 | 2 | 12.4 | 0.2 | 0.6 | 5.09 | 0.4 | 0.4 | 1 | 664.2 | 173.1
15 | 2 | 2 | 12.4 | 0.2 | 0.6 | 5.09 | 0.4 | 0.4 | 1 | 664.2 | 173.2
16 | 2 | 2 | 12.4 | 0.2 | 0.6 | 5.09 | 0.4 | 0.4 | 1 | 664.6 | 173
17 | 2 | 2 | 12.4 | 0.2 | 0.6 | 5.08 | 0.4 | 0.4 | 1 | 665.4 | 173.4
18 | 2 | 2 | 12.4 | 0.2 | 0.6 | 5.08 | 0.4 | 0.4 | 1 | 666.2 | 173.7
19 | 2 | 2 | 12.4 | 0.2 | 0.6 | 5.08 | 0.5 | 0.4 | 1.2 | 666.6 | 173.8
20 | 2 | 2 | 12.2 | 0.2 | 0.6 | 5.08 | 0.4 | 0.4 | 1 | 666.6 | 171.2
21 | 34.8 | 2 | 81.7 | 0 | 28 | 5.07 | 0 | 0.4 | 0 | 644.5 | 38.3SD |  |  | 21:08 | 21:21
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-10
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | 0 | 2 | 0 | 0 | 0 | 5.07 | 0 | 0.4 | 0 | 457.8 | 0.5HS
3 | 59.3 | 2 | 118 | 0 | 18.3 | 5.07 | 0 | 0.4 | 0 | 566.3 | 17.4HS | 3:05
4 | 39.5 | 4.1 | 136.7 | 26.9 | 56.3 | 5.08 | 4.3 | 0.6 | 5.5 | 607.8 | 63.5 |  | 4:55 |  |  | ET 1:50
5 | 2 | 4.1 | 11.7 | 0.3 | 0.9 | 5.08 | 0.4 | 0.6 | 0.9 | 640.9 | 162.6
6 | 1.9 | 4 | 12.9 | 0.2 | 0.8 | 5.07 | 0.5 | 0.6 | 1.2 | 664.6 | 182.8
7 | 1.9X | 3.9 | 12.8 | 0.0X | 0 | 5.07 | 0.4 | 0.6 | 1 | 672.5 | 180.5
8 | 2 | 3.8 | 12.6 | 0.2 | 0.8 | 5.07 | 0.4 | 0.6 | 1 | 670.5 | 177.1
9 | 2 | 3.8 | 14.3 | 0.2 | 0.7 | 5.07 | 0.4 | 0.6 | 1 | 670.1 | 176.3
10 | 2 | 3.8 | 14.1 | 0.2 | 0.7 | 5.07 | 0.4 | 0.6 | 1 | 668.2 | 172.9
11 | 2 | 3.8 | 14.1 | 0.2 | 0.7 | 5.06 | 0.4 | 0.6 | 1 | 668.6 | 173.2
12 | 2 | 3.8 | 12.4 | 0.2 | 0.7 | 5.06 | 0.4 | 0.6 | 1 | 667.8 | 172.7
13 | 2 | 3.8 | 12.4 | 0.2 | 0.7 | 5.06 | 0.4 | 0.6 | 1 | 667 | 173.1
14 | 2 | 3.8 | 12.5 | 0.2 | 0.7 | 5.06 | 0.5 | 0.6 | 1.2 | 667 | 175.4
15 | 2 | 3.8 | 12.4 | 0.2 | 0.6 | 5.05 | 0.5 | 0.6 | 1.2 | 666.2 | 173.6
16 | 2 | 3.8 | 12.3 | 0.2 | 0.6 | 5.05 | 0.5 | 0.6 | 1.2 | 667 | 173
17 | 2 | 3.8 | 12.3 | 0.2 | 0.6 | 5.05 | 0.5 | 0.6 | 1.2 | 667.4 | 173
18 | 2 | 3.8 | 12.3 | 0.2 | 0.6 | 5.05 | 0.4 | 0.6 | 1 | 667.8 | 172.9
19 | 2 | 3.8 | 12.3 | 0.2 | 0.7 | 5.04 | 0.6 | 0.6 | 1.3 | 666.6 | 171.6
20 | 1.9 | 3.8 | 12.1 | 0.2 | 0.7 | 5.04 | 0.5 | 0.6 | 1.1 | 664.2 | 169.4
21 | 34.1 | 3.9 | 79.6 | 0 | 26 | 5.04 | 0 | 0.6 | 0 | 643.3 | 37.9SD |  |  | 21:08 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-11
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | 0.9 | 4 | 0.2 | 0 | 0.2 | 5.04 | 0 | 0.7 | 0 | 459.8 | 0.5HS | 2:58
3 | 48 | 4.1 | 119.8 | 0 | 70.7 | 5.03 | 0 | 0.7 | 0 | 580.9 | 30.5HS
4 | 19 | 5 | 96.2 | 10.8 | 33 | 5.04 | 2.2 | 0.8 | 4.1 | 633.4 | 120.4 |  | 4:30 |  |  | ET 1:32
5 | 2 | 4.9 | 12.3 | 0 | 0 | 5.03 | 0.3 | 0.7 | 0.8 | 656.7 | 173
6 | 2 | 4.7 | 12.3 | 0.2 | 0.9 | 5.03 | 0.4 | 0.7 | 1 | 666.6 | 172.1
7 | 2 | 4.6 | 12.3 | 0.2 | 0.8 | 5.03 | 0.4 | 0.7 | 1 | 667.8 | 172.1
8 | 2 | 2.8 | 12.2 | 0.2 | 0.8 | 5.03 | 0.4 | 0.5 | 1 | 667.8 | 171.1
9 | 2 | 2.8 | 12.2 | 0.2 | 0.8 | 5.02 | 0.4 | 0.5 | 1 | 665.8 | 170.6
10 | 2.1 | 2.8 | 14 | 0.2 | 0.8 | 5.02 | 0.4 | 0.5 | 1 | 667.4 | 171.8
11 | 2 | 2.8 | 12.1 | 0.2 | 0.8 | 5.02 | 0.5 | 0.5 | 1.1 | 663 | 168.5
12 | 1.9 | 2.8 | 12.3 | 0.2 | 0.7 | 5.02 | 0.4 | 0.5 | 1 | 663.8 | 171.3
13 | 2 | 2.8 | 12.2 | 0.2 | 0.7 | 5.02 | 0.4 | 0.5 | 0.9 | 665.4 | 171.2
14 | 2 | 2.8 | 12.2 | 0.2 | 0.7 | 5.01 | 0.4 | 0.5 | 0.9 | 664.6 | 170.4
15 | 2.1 | 2.8 | 13.9 | 0.2 | 0.7 | 5.01 | 0.5 | 0.5 | 1.1 | 665 | 170.2
16 | 2 | 2.8 | 12.2 | 0.2 | 0.7 | 5.01 | 0.5 | 0.5 | 1.1 | 663.8 | 171
17 | 2 | 2.8 | 12.3 | 0.2 | 0.7 | 5.01 | 0.5 | 0.5 | 1.1 | 663.8 | 171.6
18 | 2 | 2.8 | 12.3 | 0.2 | 0.7 | 5 | 0.4 | 0.5 | 1 | 664.6 | 171.2
19 | 2 | 2.8 | 12.2 | 0.2 | 0.7 | 5 | 0.4 | 0.5 | 1 | 666.6 | 170.9
20 | 2 | 2.8 | 12.1 | 0.2 | 0.7 | 5 | 0.4 | 0.5 | 1 | 665.8 | 169.3
21 | 31.1 | 2.9 | 72.9 | 0 | 28 | 5 | 0 | 0.5 | 0 | 644.5 | 38.1SD |  |  | 21:09 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-12
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | 0.3 | 2.9 | 0.1 | 0 | 0.1 | 4.99 | 0 | 0.5 | 0 | 469.2 | 0.5HS | 2:59
3 | 47 | 2.9 | 119.8 | 0 | 57.8 | 4.99 | 0 | 0.5 | 0 | 585.3 | 32.8HS
4 | 3.9 | 3.1 | 20.7 | 0.5 | 1.6 | 4.99 | 0.6 | 0.5 | 1.3 | 630.3 | 137.9 |  | 4:07 |  |  | ET 2:08
5 | 1.7 | 3 | 10.6 | 0 | 0 | 4.99 | 0.4 | 0.5 | 1 | 656.7 | 174.1
6 | 2 | 2.9 | 14 | 0.2 | 0.8 | 4.99 | 0.4 | 0.5 | 1 | 665.4 | 171.5
7 | 2 | 2.9 | 12.2 | 0.2 | 0.8 | 4.98 | 0.4 | 0.5 | 1 | 666.6 | 171.5
8 | 2 | 2.1 | 14 | 0.2 | 0.8 | 4.98 | 0.4 | 0.4 | 1 | 667 | 171.9
9 | 2 | 2.1 | 12.2 | 0.2 | 0.7 | 4.98 | 0.4 | 0.4 | 1 | 665.4 | 171.3
10 | 2 | 2.1 | 14 | 0.2 | 0.7 | 4.98 | 0.4 | 0.4 | 1 | 665.4 | 170.9
11 | 2 | 2.1 | 12.2 | 0.2 | 0.7 | 4.97 | 0.4 | 0.4 | 1 | 664.6 | 171
12 | 2 | 2.1 | 12.2 | 0.2 | 0.7 | 4.97 | 0.4 | 0.4 | 1 | 662.6 | 171
13 | 2 | 2.1 | 12.1 | 0.2 | 0.6 | 4.97 | 0.4 | 0.4 | 1 | 662.2 | 168.9
14 | 2 | 2.1 | 12.1 | 0.2 | 0.6 | 4.97 | 0.4 | 0.4 | 1 | 661.8 | 168.6
15 | 2 | 2.1 | 12.1 | 0.2 | 0.6 | 4.96 | 0.5 | 0.4 | 1.1 | 661.5 | 169.4
16 | 1.9 | 2.1 | 12.1 | 0.2 | 0.6 | 4.96 | 0.4 | 0.4 | 1 | 661.5 | 169.1
17 | 2 | 2.1 | 12.2 | 0.2 | 0.7 | 4.96 | 0.4 | 0.4 | 1 | 663 | 170.6
18 | 2 | 2.1 | 12.2 | 0.2 | 0.7 | 4.96 | 0.4 | 0.4 | 1 | 664.2 | 170
19 | 2 | 2.1 | 12.2 | 0.2 | 0.7 | 4.96 | 0.4 | 0.4 | 1 | 665.4 | 171.4
20 | 2 | 2.1 | 12.1 | 0.2 | 0.6 | 4.95 | 0.4 | 0.4 | 1 | 666.6 | 169.9
21 | 34.3 | 2.1 | 80.5 | 0 | 31 | 4.95 | 0 | 0.4 | 0 | 644.1 | 37.8SD |  |  | 21:08 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-13
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 0 | 2.1 | 0 | 0 | 0 | 4.95 | 0 | 0.4 | 0 | 447.9 | 0.5HS
4 | 48 | 2.1 | 102.5 | 0 | 70.3 | 4.95 | 0 | 0.4 | 0 | 573 | 20.2HS | 4:05
5 | 32.1 | 3.8 | 115.7 | 18.4 | 40.4 | 4.95 | 3.3 | 0.6 | 4.4 | 616.9 | 69.3 |  | 5:46 |  |  | ET 1:41
6 | 1.8 | 3.7 | 11.9 | 0 | 0 | 4.95 | 0.3 | 0.6 | 0.8 | 645.3 | 167.2
7 | 2 | 3.6 | 12.2 | 0.2 | 0.9 | 4.95 | 0.4 | 0.6 | 1 | 654.3 | 171.4
8 | 2 | 3.5 | 12.3 | 0.2 | 0.8 | 4.95 | 0.4 | 0.5 | 1 | 656.3 | 172.4
9 | 2 | 3.4 | 12.2 | 0.2 | 0.8 | 4.94 | 0.4 | 0.5 | 1 | 656.3 | 172.1
10 | 2 | 3.4 | 12.2 | 0.2 | 0.8 | 4.94 | 0.4 | 0.5 | 1 | 655.5 | 172.1
11 | 2 | 3.4 | 12.3 | 0.2 | 0.8 | 4.94 | 0.4 | 0.5 | 1 | 654.7 | 171.6
12 | 2 | 3.4 | 14 | 0.2 | 0.8 | 4.94 | 0.4 | 0.5 | 1 | 654.7 | 171
13 | 2 | 3.4 | 12.2 | 0.2 | 0.8 | 4.93 | 0.4 | 0.5 | 1 | 654.3 | 170.9
14 | 2 | 3.4 | 12.2 | 0.2 | 0.8 | 4.93 | 0.4 | 0.5 | 1 | 655.5 | 171
15 | 2 | 3.4 | 12.2 | 0.2 | 0.8 | 4.93 | 0.4 | 0.5 | 1 | 654.3 | 170.9
16 | 2 | 3.4 | 12.2 | 0.2 | 0.7 | 4.93 | 0.4 | 0.5 | 1 | 663 | 170.6
17 | 2 | 3.4 | 12.2 | 0.2 | 0.7 | 4.93 | 0.4 | 0.5 | 1 | 665.8 | 171
18 | 2 | 3.4 | 12.2 | 0.2 | 0.7 | 4.92 | 0.4 | 0.5 | 1 | 666.6 | 171.4
19 | 2 | 3.4 | 12.3 | 0.2 | 0.7 | 4.92 | 0.4 | 0.5 | 1 | 667 | 171.7
20 | 2 | 3.4 | 13.8 | 0.2 | 0.7 | 4.92 | 0.3 | 0.5 | 0.8 | 668.6 | 168.9
21 | 38 | 3.5 | 83.3 | 0 | 36.7 | 4.92 | 0 | 0.5 | 0 | 642.1 | 31.9SD |  |  | 21:06 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-14
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 58 | 3.6 | 116.3 | 0 | 21 | 4.91 | 0 | 0.5 | 0 | 556.9 | 18.4HS | 3:05
4 | 42.3 | 3.7 | 148.7 | 0 | 44.6 | 4.91 | 0 | 0.6 | 0 | 609.4 | 65.4HS |  | 4:50 |  |  | ET 1:45
5 | 1.9 | 3.7 | 11.6 | 0.3 | 1.1 | 4.91 | 0.3 | 0.5 | 0.7 | 639.7 | 161.9
6 | 1.9 | 3.7 | 11.3 | 0 | 0 | 4.91 | 0.3 | 0.5 | 0.7 | 642.9 | 156.8
7 | 2 | 3.6 | 13 | 0.3 | 0.9 | 4.9 | 0.4 | 0.5 | 0.9 | 654 | 157.3
8 | 2 | 3.5 | 11.4 | 0.2 | 0.8 | 4.9 | 0.4 | 0.5 | 0.9 | 655.9 | 156.5
9 | 2 | 3.4 | 11.3 | 0.2 | 0.8 | 4.9 | 0.4 | 0.5 | 0.9 | 655.1 | 155.6
10 | 2 | 2 | 11.3 | 0.2 | 0.8 | 4.9 | 0.4 | 0.4 | 0.9 | 655.1 | 155.4
11 | 2 | 2 | 11.4 | 0.2 | 0.7 | 4.9 | 0.4 | 0.4 | 0.9 | 656.3 | 155.7
12 | 2.7 | 2 | 14.8 | 0 | 0 | 4.89 | 0.4 | 0.4 | 0.9 | 658.3 | 140.5 |  |  | 13:38 | 13:38
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-15
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | 3.4X | 2 | 0.8 | 0.0X | 8.6 | 4.89 | 0 | 0.4 | 0 | 257.3 | 0.5WS | 16:57
17 | 49.2X | 2 | 112.2 | 0.0X | 110.8 | 4.89 | 0 | 0.4 | 0 | 509.1 | 24.1WS
18 | 36.6X | 2 | 132.4 | 0.0X | 25.7 | 4.89 | 0 | 0.4 | 0 | 619.2 | 69.3WS |  | 18:47 |  |  | ET 1:50
19 | 1.8X | 2 | 12.4 | 0.0X | 0 | 4.88 | 0.5 | 0.4 | 1.3 | 670.1 | 171.6
20 | 1.9 | 2 | 12.1 | 0.2 | 0.7 | 4.88 | 0.4 | 0.4 | 1 | 659.5 | 168.9
21 | 2 | 2 | 12.9 | 0.2 | 0.6 | 4.88 | 0.4 | 0.4 | 0.9 | 647.2 | 154.9
22 | 2 | 2 | 11.2 | 0.2 | 0.6 | 4.88 | 0.4 | 0.4 | 0.9 | 654.3 | 154.8
23 | 2 | 2 | 11.3 | 0.2 | 0.6 | 4.88 | 0.4 | 0.4 | 0.9 | 655.5 | 155.4
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-16
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 2 | 2 | 11.2 | 0.2 | 0.6 | 4.87 | 0.4 | 0.4 | 0.9 | 655.5 | 155.2
1 | 2 | 2 | 11.2 | 0.2 | 0.6 | 4.87 | 0.4 | 0.4 | 0.9 | 654.7 | 154
2 | 2 | 2 | 11.2 | 0.2 | 0.6 | 4.87 | 0.4 | 0.4 | 0.9 | 655.1 | 155.2
3 | 2 | 2 | 11.2 | 0.2 | 0.6 | 4.87 | 0.4 | 0.4 | 0.9 | 655.5 | 155
4 | 2 | 2 | 11.2 | 0.2 | 0.7 | 4.86 | 0.4 | 0.4 | 0.9 | 655.1 | 155.3
5 | 1.9 | 2 | 12.4 | 0.2 | 0.6 | 4.86 | 0.4 | 0.4 | 1 | 667.8 | 173.8
6 | 2 | 2 | 14 | 0.2 | 0.6 | 4.86 | 0.4 | 0.4 | 1 | 668.2 | 172
7 | 2 | 2 | 14 | 0.2 | 0.6 | 4.86 | 0.4 | 0.4 | 1 | 669.7 | 170.9
8 | 2 | 2 | 12.2 | 0.2 | 0.6 | 4.86 | 0.4 | 0.4 | 1 | 668.2 | 170.7
9 | 1.9 | 2 | 12.2 | 0 | 0 | 4.85 | 0.4 | 0.4 | 1 | 664.6 | 169.9
10 | 2.1 | 2 | 13.9 | 0.2 | 0.8 | 4.85 | 0.5 | 0.4 | 1.1 | 662.2 | 169.2
11 | 2 | 2 | 12.1 | 0.2 | 0.8 | 4.85 | 0.5 | 0.4 | 1.1 | 660.7 | 167.6
12 | 2 | 2 | 12.3 | 0.2 | 0.7 | 4.85 | 0.4 | 0.4 | 1 | 663.4 | 170.9
13 | 2 | 2 | 12.3 | 0.2 | 0.7 | 4.84 | 0.5 | 0.4 | 1.1 | 662.6 | 170.8
14 | 2 | 2 | 13.9 | 0.2 | 0.7 | 4.84 | 0.5 | 0.4 | 1.1 | 662.2 | 169.5
15 | 2 | 2 | 14 | 0.2 | 0.7 | 4.84 | 0.5 | 0.4 | 1.1 | 661.5 | 169.8
16 | 2 | 2 | 12.2 | 0.2 | 0.7 | 4.84 | 0.5 | 0.4 | 1.1 | 661.8 | 170.6
17 | 2 | 2 | 12.2 | 0.2 | 0.7 | 4.84 | 0.4 | 0.4 | 0.9 | 663 | 171.2
18 | 2 | 2 | 12.3 | 0.2 | 0.7 | 4.83 | 0.4 | 0.4 | 1 | 664.2 | 171.7
19 | 2 | 2 | 12.3 | 0.2 | 0.7 | 4.83 | 0.4 | 0.4 | 1 | 665.8 | 172.5
20 | 2 | 2 | 12.2 | 0.2 | 0.7 | 4.83 | 0.4 | 0.4 | 1 | 666.2 | 170.7
21 | 2 | 2 | 11.2 | 0.2 | 0.8 | 4.83 | 0.4 | 0.4 | 0.9 | 654.3 | 154.6
22 | 2 | 2 | 11.2 | 0.2 | 0.8 | 4.83 | 0.4 | 0.4 | 0.9 | 653.6 | 153.4
23 | 37.9 | 2 | 78.5 | 0 | 35.4 | 4.82 | 0 | 0.4 | 0 | 635.4 | 28.2SD |  |  | 23:05 | 23:19
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-17
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | 0 | 2 | 0 | 0 | 0 | 4.82 | 0 | 0.4 | 0 | 467.3 | 0.5HS
3 | 50 | 2 | 129.9 | 0 | 21.8 | 4.82 | 0 | 0.4 | 0 | 576.2 | 37.0HS | 3:04
4 | 1.9 | 2 | 9.4 | 0.4 | 1.3 | 4.82 | 0.2 | 0.4 | 0.4 | 622.8 | 118.4 |  | 4:00 |  |  | ET 0:56
5 | 1.9 | 2 | 12.5 | 0.2 | 0.9 | 4.81 | 0.5 | 0.4 | 1.2 | 650 | 176
6 | 1.9 | 2 | 12.3 | 0 | 0 | 4.81 | 0.3 | 0.4 | 0.8 | 660.7 | 172.9
7 | 2 | 2 | 12.3 | 0.2 | 0.9 | 4.81 | 0.4 | 0.4 | 1 | 667.4 | 172.4
8 | 2 | 2 | 12.2 | 0.2 | 0.8 | 4.81 | 0.4 | 0.4 | 1 | 666.6 | 171.1
9 | 2 | 2 | 12.2 | 0.2 | 0.8 | 4.81 | 0.4 | 0.4 | 1 | 667.8 | 171.9
10 | 2 | 2 | 14 | 0.2 | 0.8 | 4.8 | 0.4 | 0.4 | 1 | 667.8 | 172.4
11 | 2 | 2 | 14 | 0.2 | 0.8 | 4.8 | 0.4 | 0.4 | 1 | 667.8 | 171.7
12 | 2 | 2 | 12.3 | 0.2 | 0.8 | 4.8 | 0.4 | 0.4 | 1 | 667 | 171.4
13 | 2 | 2 | 12.3 | 0.2 | 0.8 | 4.8 | 0.4 | 0.4 | 1 | 665 | 171.7
14 | 2 | 2 | 12.2 | 0.2 | 0.8 | 4.8 | 0.4 | 0.4 | 1 | 664.6 | 171.4
15 | 2 | 2 | 14 | 0.2 | 0.8 | 4.79 | 0.4 | 0.4 | 1 | 664.6 | 170.9
16 | 2 | 2 | 12.2 | 0.2 | 0.8 | 4.79 | 0.4 | 0.4 | 1 | 665.8 | 171.1
17 | 2 | 2 | 12.3 | 0.2 | 0.9 | 4.79 | 0.4 | 0.4 | 1 | 667 | 172.1
18 | 2 | 2 | 12.3 | 0.2 | 0.8 | 4.79 | 0.4 | 0.4 | 1 | 666.6 | 171.7
19 | 2 | 2 | 14 | 0.2 | 0.8 | 4.78 | 0.4 | 0.4 | 1 | 667.4 | 172.4
20 | 2 | 2 | 12.2 | 0.2 | 0.8 | 4.78 | 0.3 | 0.4 | 0.8 | 667.8 | 170.9
21 | 33.6 | 2 | 81.3 | 0 | 37.2 | 4.78 | 0 | 0.4 | 0 | 640.9 | 38.3SD |  |  | 21:07 | 21:22
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-18
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-19
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-20
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-21
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 62.3X | 2 | 122 | 0.0X | 93 | 4.78 | 0 | 0.4 | 0 | 392.7 | 16.3CS | 0:08
1 | 65.0X | 2 | 138.2 | 0.0X | 13.2 | 4.78 | 0 | 0.4 | 0 | 598.3 | 19.3CS
2 | 56.4X | 2 | 166.8 | 0.0X | 48.2 | 4.77 | 0 | 0.4 | 0 | 609 | 44.9CS
3 | 55.7X | 2 | 168.9 | 0.0X | 59.4 | 4.77 | 0 | 0.4 | 0 | 606.2 | 47.9CS
4 | 3.7X | 2.1 | 20.2 | 0.0X | 0 | 4.77 | 0.7 | 0.4 | 1.5 | 625.1 | 133.7 |  | 4:08 |  |  | ET 4:00
5 | 1.8 | 2.1 | 11.4 | 0.3 | 1.2 | 4.77 | 0.4 | 0.4 | 0.9 | 639 | 158.8
6 | 2 | 2.1 | 13.1 | 0.3 | 1 | 4.77 | 0.4 | 0.4 | 0.9 | 643.3 | 158.7
7 | 2 | 2.1 | 13.1 | 0.3 | 1 | 4.76 | 0.4 | 0.4 | 0.9 | 652 | 158.2
8 | 2 | 2.1 | 11.5 | 0.3 | 1 | 4.76 | 0.4 | 0.4 | 0.9 | 656.7 | 158.6
9 | 2 | 2.1 | 13.1 | 0.3 | 1 | 4.76 | 0.4 | 0.4 | 0.9 | 656.3 | 158
10 | 2 | 2.1 | 11.4 | 0.3 | 1 | 4.76 | 0.4 | 0.4 | 0.9 | 656.7 | 158.2
11 | 2 | 2.1 | 11.5 | 0.3 | 1 | 4.75 | 0.4 | 0.4 | 0.9 | 656.3 | 158.3
12 | 2 | 2.1 | 11.5 | 0.3 | 1 | 4.75 | 0.4 | 0.4 | 0.9 | 656.3 | 158.3
13 | 2 | 2.1 | 13.1 | 0.3 | 1 | 4.75 | 0.3 | 0.4 | 0.7 | 655.9 | 158
14 | 2 | 2.1 | 11.4 | 0.3 | 0.9 | 4.75 | 0.4 | 0.4 | 0.9 | 655.1 | 156.8
15 | 2 | 2.1 | 11.4 | 0.3 | 0.9 | 4.75 | 0.4 | 0.4 | 0.9 | 654 | 156.7
16 | 2 | 2.1 | 11.4 | 0.3 | 0.9 | 4.74 | 0.4 | 0.4 | 0.9 | 654 | 157
17 | 2 | 2.1 | 11.3 | 0.3 | 0.9 | 4.74 | 0.4 | 0.4 | 0.9 | 653.6 | 156.3
18 | 2 | 2.1 | 11.4 | 0.3 | 1 | 4.74 | 0.4 | 0.4 | 0.9 | 653.6 | 156.3
19 | 2 | 2.1 | 11.4 | 0.3 | 1 | 4.74 | 0.4 | 0.4 | 0.9 | 653.6 | 156.3
20 | 2 | 2.1 | 12.8 | 0.3 | 1 | 4.74 | 0.3 | 0.4 | 0.7 | 653.2 | 152.9
21 | 44.7 | 2.1 | 84.4 | 0 | 36.9 | 4.73 | 0 | 0.4 | 0 | 636.2 | 24.7SD |  |  | 21:07 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-22
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-23
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-24
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-25
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | Offline
4 | Offline
5 | Offline
6 | Offline
7 | Offline
8 | Offline
9 | Offline
10 | Offline
11 | Offline
12 | Offline
13 | Offline
14 | Offline
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-26
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | 62.9X | 2.1 | 120.9 | 0.0X | 99.1 | 4.73 | 0 | 0.4 | 0 | 366.6 | 15.5CS | 0:08
1 | 62.9X | 2.1 | 134.4 | 0.0X | 13.6 | 4.73 | 0 | 0.4 | 0 | 599.1 | 18.9CS
2 | 46.2X | 2.1 | 122.6 | 0.0X | 61.1 | 4.73 | 0 | 0.4 | 0 | 603 | 34.4CS
3 | 49.9X | 2.1 | 152.5 | 0.0X | 50.6 | 4.73 | 0 | 0.4 | 0 | 605 | 47.6CS
4 | 1.8X | 2.1 | 10.1 | 0.5X | 1.6 | 4.72 | 0.2 | 0.4 | 0.5 | 629.9 | 131.7 |  | 4:06 |  |  | ET 3:58
5 | 1.7X | 2.1 | 10.9 | 0.0X | 0 | 4.72 | 0.4 | 0.4 | 1 | 654.7 | 177.9
6 | 2 | 2 | 14.3 | 0.3 | 1.3 | 4.72 | 0.4 | 0.4 | 1 | 665 | 175.4
7 | 2 | 2 | 12.5 | 0.3 | 1.2 | 4.72 | 0.3 | 0.4 | 0.8 | 670.1 | 174.8
8 | 2 | 2 | 12.5 | 0.3 | 1.1 | 4.72 | 0.4 | 0.4 | 1 | 670.9 | 174.8
9 | 2 | 2 | 12.4 | 0.3 | 1.1 | 4.71 | 0.3 | 0.4 | 0.8 | 670.9 | 174.1
10 | 2 | 2 | 14.2 | 0.3 | 1.1 | 4.71 | 0.3 | 0.4 | 0.8 | 670.1 | 173.7
11 | 2 | 2 | 12.5 | 0.3 | 1.1 | 4.71 | 0.4 | 0.4 | 1 | 669 | 174
12 | 2 | 2 | 12.5 | 0.3 | 1.1 | 4.71 | 0.3 | 0.4 | 0.8 | 667.8 | 174
13 | 2 | 2 | 12.4 | 0.3 | 1.1 | 4.71 | 0.4 | 0.4 | 1 | 667.8 | 173.4
14 | 2 | 2 | 12.4 | 0.3 | 1.1 | 4.7 | 0.3 | 0.4 | 0.8 | 666.6 | 173.6
15 | 2 | 2 | 12.4 | 0.3 | 1.1 | 4.7 | 0.3 | 0.4 | 0.8 | 665.8 | 172.9
16 | 2 | 2 | 12.4 | 0.3 | 1.1 | 4.7 | 0.3 | 0.3 | 0.8 | 665.8 | 172.7
17 | 2 | 2 | 14.1 | 0.3 | 1.2 | 4.7 | 0.3 | 0.3 | 0.8 | 667 | 173.3
18 | 2 | 2 | 12.3 | 0.3 | 1.2 | 4.7 | 0.3 | 0.3 | 0.8 | 668.2 | 173.6
19 | 2 | 2 | 12.4 | 0.3 | 1.2 | 4.69 | 0.3 | 0.3 | 0.8 | 669.7 | 174
20 | 2 | 2 | 12.2 | 0.3 | 1.2 | 4.69 | 0.3 | 0.3 | 0.8 | 669.7 | 172.2
21 | 30.3 | 2 | 71.2 | 0 | 25.9 | 4.69 | 0 | 0.3 | 0 | 646.5 | 38.6SD |  |  | 21:08 | 21:22
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-27
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | 0 | 2 | 0 | 0 | 0.1 | 4.69 | 0 | 0.3 | 0 | 466.5 | 0.5HS
3 | 45.9 | 2 | 115.7 | 0 | 52.2 | 4.69 | 0 | 0.3 | 0 | 582.5 | 32.6HS | 3:05
4 | 4 | 2.1 | 21.7 | 0.6 | 2 | 4.68 | 0.5 | 0.3 | 1 | 631.1 | 133.7 |  | 4:08 |  |  | ET 1:03
5 | 1.8 | 2.1 | 12.6 | 0 | 0 | 4.68 | 0.3 | 0.3 | 0.8 | 657.9 | 177.9
6 | 2 | 2.1 | 12.4 | 0.4 | 1.4 | 4.68 | 0.3 | 0.3 | 0.8 | 667.8 | 174.4
7 | 2 | 2.1 | 12.4 | 0.3 | 1.3 | 4.68 | 0.3 | 0.3 | 0.8 | 667.8 | 174.7
8 | 2 | 2.1 | 12.4 | 0.3 | 1.2 | 4.68 | 0.4 | 0.3 | 1 | 670.5 | 175.2
9 | 2 | 2.1 | 12.4 | 0.3 | 1.2 | 4.67 | 0.4 | 0.3 | 1 | 671.3 | 174.8
10 | 2 | 2.1 | 12.4 | 0.3 | 1.2 | 4.67 | 0.4 | 0.3 | 1 | 670.5 | 174.2
11 | 2 | 2.1 | 14.2 | 0.3 | 1.2 | 4.67 | 0.4 | 0.3 | 1 | 669 | 174.2
12 | 2 | 2.1 | 12.4 | 0.3 | 1.2 | 4.67 | 0.5 | 0.3 | 1.2 | 666.6 | 173.7
13 | 2 | 2.1 | 12.4 | 0.3 | 1.2 | 4.67 | 0.5 | 0.4 | 1.2 | 665 | 173.2
14 | 1.9 | 2.1 | 12.3 | 0.3 | 1.2 | 4.66 | 0.5 | 0.4 | 1.2 | 664.6 | 172.6
15 | 2 | 2.1 | 12.3 | 0.3 | 1.1 | 4.66 | 0.5 | 0.4 | 1.2 | 665.8 | 172.4
16 | 2 | 2.1 | 12.3 | 0.3 | 1.1 | 4.66 | 0.5 | 0.4 | 1.2 | 665.4 | 172.9
17 | 2 | 2.1 | 12.4 | 0.3 | 1.1 | 4.66 | 0.5 | 0.4 | 1.2 | 664.2 | 174.3
18 | 2 | 2.1 | 12.3 | 0.3 | 1.1 | 4.66 | 0.5 | 0.4 | 1.2 | 665 | 173.1
19 | 2 | 2.1 | 12.4 | 0.3 | 1.2 | 4.65 | 0.4 | 0.4 | 1 | 666.2 | 173.1
20 | 2 | 2.1 | 12.3 | 0.3 | 1.1 | 4.65 | 0.4 | 0.4 | 1 | 666.6 | 171.1
21 | 34.1 | 2.1 | 79.6 | 0 | 27.4 | 4.65 | 0 | 0.4 | 0 | 644.5 | 37.0SD |  |  | 21:06 | 21:19
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-28
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 48.6 | 2.1 | 118.4 | 0 | 45.3 | 4.65 | 0 | 0.4 | 0 | 572.3 | 31.6HS | 3:05
4 | 7.7 | 2.4 | 40.9 | 0 | 0 | 4.65 | 1 | 0.5 | 2 | 629.5 | 134.4 |  | 4:09 |  |  | ET 1:04
5 | 1.3 | 2.4 | 8.2 | 0 | 0 | 4.64 | 0.5 | 0.5 | 1.1 | 652.4 | 156.8
6 | 2 | 2.3 | 11.6 | 0.4 | 1.4 | 4.64 | 0.3 | 0.5 | 0.7 | 655.5 | 160.7
7 | 2 | 2.3 | 12.6 | 0.4 | 1.4 | 4.64 | 0.4 | 0.5 | 1 | 669.3 | 176.9
8 | 2 | 2.3 | 12.5 | 0.3 | 1.3 | 4.64 | 0.4 | 0.5 | 1 | 670.1 | 176
9 | 2 | 2.2 | 14.3 | 0.3 | 1.3 | 4.64 | 0.4 | 0.4 | 1 | 669.3 | 175.4
10 | 2 | 2.2 | 12.5 | 0.4 | 1.4 | 4.63 | 0.4 | 0.5 | 1 | 668.2 | 175
11 | 2 | 2.2 | 12.5 | 0.4 | 1.4 | 4.63 | 0.5 | 0.5 | 1.2 | 666.2 | 175.3
12 | 2.1 | 2.2 | 14.3 | 0.3 | 1.3 | 4.63 | 0.4 | 0.5 | 1 | 674.5 | 173.8
13 | 2 | 2.2 | 12.6 | 0.1 | 0.4 | 4.63 | 0.8 | 0.5 | 2.1 | 768.4 | 174.7
14 | 2 | 2.2 | 12.5 | 0.1 | 0.3 | 4.63 | 0.9 | 0.5 | 2.1 | 771.2 | 173.7
15 | 2 | 2.2 | 12.5 | 0.1 | 0.3 | 4.62 | 0.9 | 0.5 | 2.2 | 771.6 | 173.3
16 | 2 | 2.2 | 12.5 | 0.1 | 0.3 | 4.62 | 0.9 | 0.6 | 2.2 | 771.2 | 173.3
17 | 1.9 | 2.2 | 12.3 | 0.3 | 1.1 | 4.62 | 0.4 | 0.5 | 1 | 683.6 | 171
18 | 2 | 2.2 | 12.5 | 0.3 | 1.2 | 4.62 | 0.5 | 0.5 | 1.2 | 667.4 | 175
19 | 2 | 2.2 | 12.5 | 0.3 | 1.2 | 4.62 | 0.4 | 0.5 | 1 | 668.2 | 175.5
20 | 1.9 | 2.2 | 12.4 | 0.3 | 1.3 | 4.61 | 0.4 | 0.5 | 1 | 668.2 | 174
21 | 27.9 | 2.2 | 69.9 | 0 | 27.4 | 4.61 | 0 | 0.5 | 0 | 646.1 | 42.6SD |  |  | 21:08 | 21:20
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-29
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 49.5 | 2.2 | 128.2 | 0 | 25.5 | 4.61 | 0 | 0.5 | 0 | 556.9 | 38.5HS | 3:06 | 3:59 |  |  | ET 0:53
4 | 1.9 | 2.2 | 9.7 | 0.6 | 1.8 | 4.61 | 0.3 | 0.5 | 0.6 | 626.7 | 126
5 | 2 | 2.2 | 12.4 | 0.4 | 1.5 | 4.61 | 0.4 | 0.5 | 1 | 664.2 | 175.4
6 | 2 | 2.2 | 12.4 | 0.4 | 1.5 | 4.61 | 0.4 | 0.5 | 1 | 669 | 175.3
7 | 2.0X | 2.2 | 12.3 | 0.4X | 1.4 | 4.6 | 0.4 | 0.5 | 1 | 670.9 | 174.4
8 | 1.3X | 2.2 | 8.8 | 0.0X | 0 | 4.6 | 0.7 | 0.5 | 1.6 | 670.1 | 174.2
9 | 1.5 | 1.9 | 10.5 | 0.4 | 1.4 | 4.6 | 0.5 | 0.5 | 1.2 | 670.1 | 173
10 | 2 | 1.9 | 12.4 | 0.4 | 1.4 | 4.6 | 0.5 | 0.5 | 1.1 | 678 | 173.8
11 | 2 | 1.9 | 12.6 | 0.1 | 0.4 | 4.6 | 0.9 | 0.5 | 2.1 | 755.8 | 175.3
12 | 1.9 | 1.9 | 12.5 | 0.1 | 0.3 | 4.59 | 0.9 | 0.6 | 2.2 | 765.3 | 173.3
13 | 1.9 | 1.9 | 12.4 | 0.1 | 0.3 | 4.59 | 0.9 | 0.6 | 2.2 | 767.6 | 172.3
14 | 1.9 | 1.9 | 12.3 | 0.1 | 0.3 | 4.59 | 1 | 0.6 | 2.3 | 768 | 171.5
15 | 1.9 | 1.9 | 12.3 | 0.1 | 0.3 | 4.59 | 1 | 0.6 | 2.3 | 768.4 | 171.1
16 | 1.9 | 1.9 | 12.4 | 0.1 | 0.3 | 4.59 | 1 | 0.7 | 2.3 | 769.2 | 171.2
17 | 1.9 | 1.9 | 12.6 | 0.1 | 0.3 | 4.58 | 0.9 | 0.7 | 2.2 | 766.4 | 174
18 | 1.9 | 1.9 | 12.6 | 0.1 | 0.3 | 4.58 | 0.9 | 0.7 | 2.1 | 760.9 | 175.7
19 | 1.9 | 1.9 | 12.6 | 0.1 | 0.4 | 4.58 | 0.9 | 0.7 | 2.1 | 758.9 | 176.1
20 | 1.9 | 1.9 | 12.7 | 0.1 | 0.4 | 4.58 | 0.9 | 0.7 | 2.2 | 758.2 | 177
21 | 4.9 | 2 | 24.2 | 0 | 0 | 4.58 | 0.6 | 0.7 | 1 | 650.4 | 118.4 |  |  | 21:58
22 | 41.2 | 2 | 82.4 | 0 | 52.4 | 4.57 | 0 | 0.7 | 0 | 627.1 | 24.1SD |  |  |  | 22:21
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-09-30
TM | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | NH3 | Catal | Load
| ppmvd | 24hr | lb/hr | ppmvd | lb/hr | Annual | slip | 24hr | lb/hr | Temp | MW
|  | ppmvd |  |  |  | avg | ppmvd | avg |  | Deg F |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
0 | Offline
1 | Offline
2 | Offline
3 | 50.7 | 2 | 132.2 | 0 | 34.6 | 4.57 | 0 | 0.7 | 0 | 569.9 | 37.9HS | 3:04
4 | 1.9 | 2 | 10.5 | 0.5 | 1.6 | 4.57 | 0.3 | 0.7 | 0.7 | 631.9 | 139.5 |  | 4:00 |  |  | ET 0:56
5 | 1.8 | 2 | 12.5 | 0 | 0 | 4.57 | 0.4 | 0.7 | 1 | 666.6 | 175.4
6 | 2 | 2 | 12.4 | 0.4 | 1.6 | 4.57 | 0.4 | 0.7 | 1 | 670.5 | 174.9
7 | 2 | 2 | 12.8 | 0.3 | 1.3 | 4.56 | 0.5 | 0.7 | 1.3 | 686.7 | 179.2
8 | 2.1 | 2 | 14.6 | 0.1 | 0.5 | 4.56 | 0.8 | 0.7 | 2 | 749.5 | 178.2
9 | 2 | 2 | 12.7 | 0.2 | 0.6 | 4.56 | 0.8 | 0.7 | 1.9 | 747.5 | 177
10 | 2 | 2 | 12.6 | 0.1 | 0.5 | 4.56 | 0.8 | 0.7 | 2 | 756.6 | 175.3
11 | 2 | 2 | 12.7 | 0.1 | 0.5 | 4.56 | 0.8 | 0.7 | 2 | 754.2 | 176.4
12 | 2 | 2.1 | 12.6 | 0.2 | 0.6 | 4.55 | 0.8 | 0.8 | 1.8 | 748.7 | 174.6
13 | 2 | 2.1 | 14.3 | 0.2 | 0.7 | 4.55 | 0.6 | 0.8 | 1.5 | 731.7 | 173.8
14 | 2.1 | 2.1 | 14.4 | 0.2 | 0.6 | 4.55 | 0.6 | 0.8 | 1.5 | 735.7 | 174.3 |  |  | 14:16 | 14:16
15 | Offline
16 | Offline
17 | Offline
18 | Offline
19 | Offline
20 | Offline
21 | Offline
22 | Offline
23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
[7 empty] | Sum NH3 (lbs): |  | 328.6

## September CEMS Raw data
This data is raw hourly CEMs database data which may include invalid data such as values obtained during calibration checks.
Sep | 2008
Record# | DATE | TIME | BOILER11 | CATTMP12 | CO_COR13 | CO_HCOR14 | GAS15 | GEN16 | GEN27 | HGAS18 | HGASON19 | NH3110 | NH3COR111 | NH3FLO112 | NOX113 | NOX1I14 | NOXCOR115 | NOXH116 | NOXHCOR117 | NOXHRT118 | NOXRT119 | OXY120
1 | 2008-09-01 | 0 | 0 | 216.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.06
2 | 2008-09-01 | 10000 | 0 | 213.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.07
3 | 2008-09-01 | 20000 | 0 | 210.3 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.7 | -0.01 | -0.04 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.08
4 | 2008-09-01 | 30000 | 0 | 207.3 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.08
5 | 2008-09-01 | 40000 | 0 | 204.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.09
6 | 2008-09-01 | 50000 | 0 | 201.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.11
7 | 2008-09-01 | 60000 | 0 | 199.2 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0 | 0 | 0.002 | 0.001 | 21.11
8 | 2008-09-01 | 70000 | 0 | 196.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.13
9 | 2008-09-01 | 80000 | 0 | 194.3 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.7 | 0 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0 | 21.13
10 | 2008-09-01 | 90000 | 0 | 192.1 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | 0 | 2.1 | 0 | 0.01 | 0 | 0.002 | 0 | 21.13
11 | 2008-09-01 | 100000 | 0 | 190 | 0 | 0 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | 0 | -888 | 0.7 | 0 | -0.03 | 0 | 0 | 0 | 0.002 | 0 | 21.14
12 | 2008-09-01 | 110000 | 0 | 188.1 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | 0 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0 | 21.15
13 | 2008-09-01 | 120000 | 0 | 186 | 0 | 0 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | 0 | -888 | 0.7 | 0 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0 | 21.15
14 | 2008-09-01 | 130000 | 0 | 183.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.7 | 0 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0 | 21.08
15 | 2008-09-01 | 140000 | 0 | 182 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.7 | 0 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0 | 21.09
16 | 2008-09-01 | 150000 | 0 | 180.2 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.16
17 | 2008-09-01 | 160000 | 0 | 178.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.15
18 | 2008-09-01 | 170000 | 0 | 176.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.15
19 | 2008-09-01 | 180000 | 0 | 175.4 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.14
20 | 2008-09-01 | 190000 | 0 | 173.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.14
21 | 2008-09-01 | 200000 | 0 | 171.4 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.15
22 | 2008-09-01 | 210000 | 0 | 169.4 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.16
23 | 2008-09-01 | 220000 | 0 | 167.4 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.08
24 | 2008-09-01 | 230000 | 0 | 165.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.16
25 | 2008-09-02 | 0 | 0 | 163.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.15
26 | 2008-09-02 | 10000 | 0 | 161.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.14
27 | 2008-09-02 | 20000 | 0 | 160.3 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.14
28 | 2008-09-02 | 30000 | 0 | 158.3 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.14
29 | 2008-09-02 | 40000 | 0 | 156.7 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0 | 0 | 0.002 | 0.001 | 21.13
30 | 2008-09-02 | 50000 | 0 | 155 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.13
31 | 2008-09-02 | 60000 | 0 | 153.1 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.7 | -0.01 | -0.04 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.05
32 | 2008-09-02 | 70000 | 0 | 151.4 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.13
33 | 2008-09-02 | 80000 | 0 | 149.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | 0 | -0.04 | 0 | 0.02 | 0 | 0.002 | 0 | 21.13
34 | 2008-09-02 | 90000 | 0 | 148.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | 0 | 2.11 | 0 | 0.01 | 0 | 0.002 | 0 | 21.06
35 | 2008-09-02 | 100000 | 0 | 147.3 | 0 | 0 | 0.06 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.06
36 | 2008-09-02 | 110000 | 0 | 146 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.12
37 | 2008-09-02 | 120000 | 0 | 145 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.11
38 | 2008-09-02 | 130000 | 0 | 143.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.1
39 | 2008-09-02 | 140000 | 0 | 142.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.1
40 | 2008-09-02 | 150000 | 0 | 142 | 0 | 0 | 0.21 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.04 | 0 | 0 | 0 | 0.003 | 0.001 | 21.08
41 | 2008-09-02 | 160000 | 0 | 140.5 | 0 | 0 | 0.53 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.06
42 | 2008-09-02 | 170000 | 0 | 140.5 | 0 | 0 | 0.43 | 0.5 | 1.2 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.06
43 | 2008-09-02 | 180000 | 0 | 138.6 | 0 | 0 | 0.1 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.06
44 | 2008-09-02 | 190000 | 0 | 138 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.003 | 0.001 | 20.99
45 | 2008-09-02 | 200000 | 0 | 136.8 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.08
46 | 2008-09-02 | 210000 | 0 | 135.1 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.01
47 | 2008-09-02 | 220000 | 0 | 134 | 0 | 0 | 0.04 | 0.5 | 1.2 | -0.047 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.09
48 | 2008-09-02 | 230000 | 0 | 132.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.09
49 | 2008-09-03 | 0 | 0 | 131.4 | 0 | 0 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.02
50 | 2008-09-03 | 10000 | 0 | 130.3 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.1
51 | 2008-09-03 | 20000 | 0 | 129.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.11
52 | 2008-09-03 | 30000 | 0 | 127.9 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.02 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.11
53 | 2008-09-03 | 40000 | 0 | 127 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.03
54 | 2008-09-03 | 50000 | 0 | 126.4 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.1
55 | 2008-09-03 | 60000 | 0 | 124.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | 0 | 0.02 | 0 | 0.002 | 0.001 | 21.03
56 | 2008-09-03 | 70000 | 0 | 124.5 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | 0 | -0.03 | 0 | 0.02 | 0 | 0.002 | 0 | 21.12
57 | 2008-09-03 | 80000 | 0 | 122.6 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | 0 | -0.03 | 0 | 0.01 | 0 | 0.002 | 0 | 21.12
58 | 2008-09-03 | 90000 | 0 | 122.8 | 0 | 0 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | 0 | -888 | 0.5 | -0.01 | 2.12 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.12
59 | 2008-09-03 | 100000 | 0 | 122.3 | 16 | -59.8 | 0.06 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | 1.69 | -0.03 | 1.6 | 7.72 | 4.6 | 58.581 | 0.007 | 17.33
60 | 2008-09-03 | 110000 | 0 | 120.9 | 9.7 | -174.8 | 0.04 | 0.5 | 1.2 | -0.049 | 0 | 0 | -888 | 0.6 | 0 | -0.03 | -0.3 | 0.01 | 0.6 | 0.008 | 0 | 20.81
61 | 2008-09-03 | 120000 | 0 | 121 | 7.8 | -205.5 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.4 | 0.01 | 0.6 | 0.007 | 0 | 20.8
62 | 2008-09-03 | 130000 | 0 | 119.9 | 6.7 | -161.9 | 0.16 | 0.5 | 1.2 | -0.047 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | -0.3 | 0.02 | 0.7 | 0.006 | 0 | 20.78
63 | 2008-09-03 | 140000 | 0 | 119.1 | 5.9 | -138.5 | 0.04 | 0.5 | 1.2 | -0.047 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | -0.3 | 0.01 | 0.5 | 0.006 | 0 | 20.78
64 | 2008-09-03 | 150000 | 0 | 119 | 5.4 | -118.8 | 0.04 | 0.6 | 1.2 | -0.048 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | -0.3 | 0.02 | 0.8 | 0.006 | 0 | 20.77
65 | 2008-09-03 | 160000 | 0 | 119.2 | 5.6 | -116.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.8 | -0.01 | -0.03 | -0.3 | 0.01 | 0.4 | 0.005 | 0 | 20.76
66 | 2008-09-03 | 170000 | 0 | 117.7 | 6.1 | -119 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.7 | -0.01 | -0.03 | -0.3 | 0.02 | 0.9 | 0.006 | 0 | 20.69
67 | 2008-09-03 | 180000 | 0 | 117.3 | 6.5 | -111.6 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.7 | -0.01 | -0.04 | -0.4 | 0.01 | 0.6 | 0.006 | 0 | 20.77
68 | 2008-09-03 | 190000 | 0 | 117.3 | 6.4 | -123.6 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.6 | -0.01 | -0.02 | -0.4 | 0.01 | 0.4 | 0.006 | 0 | 20.77
69 | 2008-09-03 | 200000 | 0 | 116.1 | 7.2 | -143.8 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.5 | 0.01 | 0.5 | 0.006 | 0 | 20.78
70 | 2008-09-03 | 210000 | 0 | 115.3 | 7.7 | -149.2 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.5 | 0.01 | 0.2 | 0.006 | 0 | 20.79
71 | 2008-09-03 | 220000 | 0 | 114.5 | 8 | -172.6 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.5 | 0.01 | 0.5 | 0.006 | 0 | 20.79
72 | 2008-09-03 | 230000 | 0 | 113.7 | 8.5 | -187.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.5 | 0.01 | 0.5 | 0.007 | 0 | 20.8
73 | 2008-09-04 | 0 | 0 | 113.3 | 8.6 | -165.5 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.5 | -0.01 | -0.04 | -0.6 | 0.02 | 1.1 | 0.009 | 0 | 20.81
74 | 2008-09-04 | 10000 | 0 | 111.8 | 8.9 | -207.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.5 | 0.01 | 0.4 | 0.007 | 0 | 20.81
75 | 2008-09-04 | 20000 | 1 | 356.9 | 30.1 | 78.9 | 5.92 | 14 | 14.5 | -0.051 | 0 | 0 | -888 | 0.6 | 9.01 | 25.88 | 13.7 | 36.36 | 54.3 | 0.201 | 0.05 | 17.4
76 | 2008-09-04 | 30000 | 1 | 597.1 | 21.1 | 12.1 | 6.88 | 18.3 | 18.7 | -0.051 | 0 | 0 | -888 | 6.3 | 10.29 | 30.02 | 15.3 | 44.03 | 65.2 | 0.24 | 0.056 | 16.92
77 | 2008-09-04 | 40000 | 1 | 618.8 | 23.2 | 38 | 8.84 | 36.3 | 46.1 | -0.052 | 0 | 0 | -888 | 24.2 | 10.29 | 30.02 | 11.9 | 43.64 | 50.3 | 0.185 | 0.044 | 15.78
78 | 2008-09-04 | 50000 | 1 | 613 | 20.9 | 30 | 9.74 | 45.3 | 75.8 | -0.052 | 0 | 0 | -888 | 30 | 10.29 | 30.02 | 10.8 | 55.39 | 57.7 | 0.212 | 0.04 | 15.25
79 | 2008-09-04 | 60000 | 1 | 644.9 | 0.5 | -2.1 | 20.53 | 164.9 | 242.4 | -0.05 | 0 | 0 | -888 | 109.7 | 2.93 | 11.96 | 2.5 | 7.06 | 6 | 0.022 | 0.009 | 13.81
80 | 2008-09-04 | 70000 | 1 | 643.5 | 7.1 | -7.2 | 19.12 | 151 | 228.5 | -0.051 | 0 | 0 | -888 | 92.1 | 3.41 | 10.08 | 2.3 | 9.45 | 3.8 | 0.015 | 1.591 | 12.2
81 | 2008-09-04 | 80000 | 1 | 644.9 | 0.2 | -2.1 | 19.22 | 152.8 | 230.6 | -0.049 | 0 | 0 | -888 | 91.7 | 2.42 | 9.51 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.78
82 | 2008-09-04 | 90000 | 1 | 644.4 | 0.1 | -2.2 | 19.12 | 151.6 | 229.5 | -0.048 | 0 | 0 | -888 | 90.6 | 2.44 | 10.06 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.78
83 | 2008-09-04 | 100000 | 1 | 644.1 | 0.1 | -2.5 | 19.31 | 153 | 231.1 | -0.049 | 0 | 0 | -888 | 92.9 | 2.46 | 9.62 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.77
84 | 2008-09-04 | 110000 | 1 | 662.1 | 0.1 | -2.2 | 21.52 | 175 | 261.7 | -0.042 | 0 | 0.3 | -888 | 124.7 | 2.4 | 11.08 | 2 | 2.25 | 1.8 | 0.007 | 0.007 | 13.68
85 | 2008-09-04 | 120000 | 1 | 662 | 0.1 | -2.3 | 21.34 | 173.3 | 259.9 | -0.048 | 0 | 0 | -888 | 124.1 | 2.41 | 11.17 | 2 | 2.26 | 1.8 | 0.007 | 0.007 | 13.67
86 | 2008-09-04 | 130000 | 1 | 658.7 | 0.1 | -2.4 | 20.39 | 163.9 | 245.7 | -0.051 | 0 | 0 | -888 | 97.4 | 2.42 | 9.45 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.88
87 | 2008-09-04 | 140000 | 1 | 659.6 | 0.1 | -2.3 | 20.94 | 168.7 | 253.6 | -0.05 | 0 | 0 | -888 | 117.4 | 2.43 | 10.7 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.72
88 | 2008-09-04 | 150000 | 1 | 662.1 | 0.1 | -2.3 | 21.54 | 174.9 | 261.8 | -0.049 | 0 | 0 | -888 | 128.6 | 2.46 | 11.53 | 2 | 2.3 | 1.8 | 0.007 | 0.007 | 13.58
89 | 2008-09-04 | 160000 | 1 | 661.8 | 0.1 | -2.3 | 21.35 | 172.8 | 258.6 | -0.049 | 0 | 0 | -888 | 113.7 | 2.43 | 10.64 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.62
90 | 2008-09-04 | 170000 | 1 | 647.4 | 0.1 | -2 | 19.17 | 152.1 | 230.4 | -0.049 | 0 | 0 | -888 | 88 | 2.42 | 9.17 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.78
91 | 2008-09-04 | 180000 | 1 | 646 | 0.1 | -2.3 | 19.2 | 152.1 | 230.2 | -0.048 | 0 | 0 | -888 | 86.3 | 2.42 | 9.1 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.77
92 | 2008-09-04 | 190000 | 1 | 646.4 | 0.1 | -2.5 | 19.28 | 153 | 231 | -0.046 | 0 | 0 | -888 | 86.7 | 2.44 | 9.11 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.75
93 | 2008-09-04 | 200000 | 1 | 646.1 | 0.1 | -2.3 | 19.19 | 152.5 | 230.2 | -0.046 | 0 | 0 | -888 | 87 | 2.45 | 9.15 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.75
94 | 2008-09-04 | 210000 | 1 | 644.8 | 0.1 | -2.4 | 18.98 | 150 | 227.2 | -0.048 | 0 | 0 | -888 | 86.6 | 2.44 | 9.25 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.74
95 | 2008-09-04 | 220000 | 0 | 557.6 | 22 | -30.8 | 2.02 | 9.2 | 17 | -0.049 | 0 | 0 | -888 | 15.6 | 2.13 | 6.6 | 2.9 | 7.85 | 9.2 | 0.035 | 0.011 | 19.35
96 | 2008-09-04 | 230000 | 0 | 439.2 | 6.8 | -107.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | 0 | 0.05 | -0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.68
97 | 2008-09-05 | 0 | 0 | 417.7 | 5.4 | -110.2 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.7 | 0 | 0 | -0.1 | 0.01 | 0.4 | 0.005 | 0 | 20.76
98 | 2008-09-05 | 10000 | 0 | 407.2 | 5.3 | -106 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.5 | 0 | 0 | -0.2 | 0.01 | 0.5 | 0.005 | 0 | 20.76
99 | 2008-09-05 | 20000 | 0 | 399.5 | 5.2 | -102.8 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.7 | -0.01 | -0.01 | -0.2 | 0.01 | 0.4 | 0.005 | 0 | 20.76
100 | 2008-09-05 | 30000 | 0 | 397.4 | 4.3 | -125.6 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 1.2 | -0.01 | -0.02 | -0.3 | 0.01 | 0.3 | 0.005 | 0 | 20.76
101 | 2008-09-05 | 40000 | 1 | 562.5 | 20.9 | 8.8 | 6.96 | 24.3 | 25.4 | -0.048 | 0 | 0 | -888 | 3.1 | 8.86 | 26.46 | 11.5 | 39.36 | 49.2 | 0.181 | 0.042 | 16.71
102 | 2008-09-05 | 50000 | 1 | 614 | 17.7 | 26.6 | 10.73 | 56.9 | 94.6 | -0.048 | 0 | 0 | -888 | 41 | 9.4 | 27.89 | 9.7 | 48.95 | 50.1 | 0.184 | 0.036 | 15.01
103 | 2008-09-05 | 60000 | 1 | 642.7 | 4.3 | 3.9 | 19.36 | 154.4 | 231.2 | -0.049 | 0 | 0 | -888 | 103.5 | 3.22 | 10.95 | 2.3 | 9.32 | 4.1 | 0.015 | 0.009 | 12.18
104 | 2008-09-05 | 70000 | 1 | 642.4 | 0.2 | -2.2 | 18.93 | 149.2 | 226.3 | -0.048 | 0 | 0 | -888 | 94.7 | 2.36 | 10.16 | 1.9 | 2.21 | 1.8 | 0.007 | 0.007 | 13.76
105 | 2008-09-05 | 80000 | 1 | 642.9 | 0.2 | -2.1 | 18.94 | 149.5 | 226.8 | -0.048 | 0 | 0 | -888 | 94.3 | 2.43 | 9.86 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.76
106 | 2008-09-05 | 90000 | 1 | 644.2 | 0.2 | -2.1 | 19.02 | 150.1 | 227.7 | -0.05 | 0 | 0 | -888 | 94.5 | 2.43 | 10.31 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.75
107 | 2008-09-05 | 100000 | 1 | 642.5 | 0.2 | -2.4 | 18.93 | 148.8 | 226.3 | -0.048 | 0 | 0 | -888 | 93 | 2.44 | 9.78 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.76
108 | 2008-09-05 | 110000 | 1 | 642.6 | 0.1 | -2.2 | 18.81 | 148.6 | 226.1 | -0.049 | 0 | 0 | -888 | 91.2 | 2.42 | 9.74 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.76
109 | 2008-09-05 | 120000 | 1 | 637.9 | 0.2 | -2.4 | 17.59 | 134.7 | 208.5 | -0.049 | 0 | 0 | -888 | 76.7 | 2.46 | 8.83 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.79
110 | 2008-09-05 | 130000 | 1 | 638.1 | 0.2 | -2.3 | 17.58 | 134.4 | 208 | -0.049 | 0 | 0 | -888 | 73.7 | 2.44 | 8.68 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.78
111 | 2008-09-05 | 140000 | 1 | 644.3 | 0.1 | -2.5 | 18.97 | 149.3 | 226.7 | -0.047 | 0 | 0 | -888 | 86.2 | 2.38 | 9.27 | 2 | 2.22 | 1.8 | 0.007 | 0.007 | 13.75
112 | 2008-09-05 | 150000 | 1 | 644.3 | 0.1 | -2.1 | 18.93 | 149.8 | 227.2 | -0.048 | 0 | 0 | -888 | 85.8 | 2.45 | 9.33 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.75
113 | 2008-09-05 | 160000 | 1 | 642.7 | 0.1 | -2.1 | 18.92 | 149.7 | 227 | -0.049 | 0 | 0 | -888 | 88.1 | 2.44 | 9.38 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.75
114 | 2008-09-05 | 170000 | 1 | 642.7 | 0.1 | -2.2 | 19.01 | 150 | 227.2 | -0.048 | 0 | 0 | -888 | 88.3 | 2.44 | 9.35 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
115 | 2008-09-05 | 180000 | 1 | 643.3 | 0.1 | -1.8 | 19.02 | 150.2 | 227.5 | -0.049 | 0 | 0 | -888 | 88.2 | 2.44 | 9.37 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.74
116 | 2008-09-05 | 190000 | 1 | 644.3 | 0.1 | -2 | 19.04 | 150.8 | 228 | -0.048 | 0 | 0 | -888 | 89.3 | 2.45 | 9.42 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.73
117 | 2008-09-05 | 200000 | 1 | 644.8 | 0.2 | -2 | 19.06 | 151 | 228.3 | -0.05 | 0 | 0 | -888 | 90.6 | 2.44 | 9.51 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.73
118 | 2008-09-05 | 210000 | 1 | 643.7 | 0.2 | -2.1 | 18.9 | 149 | 225.8 | -0.049 | 0 | 0 | -888 | 89.8 | 2.44 | 9.54 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.73
119 | 2008-09-05 | 220000 | 0 | 557.8 | 22.7 | -53.9 | 1.99 | 9.7 | 18 | -0.049 | 0 | 0 | -888 | 4 | 2.17 | 5.83 | 4.2 | 7.23 | 9.5 | 0.036 | 0.016 | 19.41
120 | 2008-09-05 | 230000 | 0 | 437.5 | 7.5 | -114.2 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.7 | -0.01 | 0.03 | -0.3 | 0.01 | 0.2 | 0.004 | 0 | 20.76
121 | 2008-09-06 | 0 | 0 | 413.8 | 6.2 | -117.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | 0 | -0.3 | 0.01 | 0 | 0.004 | 0 | 20.76
122 | 2008-09-06 | 10000 | 0 | 406.2 | 6 | -113.3 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | 0 | -0.3 | 0.01 | 0.3 | 0.005 | 0 | 20.75
123 | 2008-09-06 | 20000 | 0 | 402.3 | 6.4 | -108.5 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.8 | -0.01 | 0 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.68
124 | 2008-09-06 | 30000 | 0 | 403.1 | 5.6 | -102.1 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.02 | -0.3 | 0.01 | 0.3 | 0.005 | 0 | 20.76
125 | 2008-09-06 | 40000 | 1 | 559.3 | 23 | 4.2 | 6.12 | 15.8 | 16.3 | -0.051 | 0 | 0 | -888 | 2.5 | 9.35 | 26.69 | 13.6 | 37.4 | 53.9 | 0.199 | 0.05 | 17.18
126 | 2008-09-06 | 50000 | 1 | 617.6 | 16 | 24.8 | 11.79 | 68.5 | 102.6 | -0.05 | 0 | 0 | -888 | 80.3 | 8.51 | 26.05 | 8.9 | 36.35 | 37.7 | 0.139 | 0.033 | 14.93
127 | 2008-09-06 | 60000 | 1 | 637.6 | 3 | 2.4 | 18.9 | 149 | 225.4 | -0.049 | 0 | 0 | -888 | 92.4 | 3.33 | 9.78 | 2.1 | 9.41 | 3.7 | 0.014 | 0.008 | 12.15
128 | 2008-09-06 | 70000 | 1 | 643 | 0.2 | -2.2 | 19.04 | 150.4 | 227 | -0.049 | 0 | 0 | -888 | 91.3 | 2.43 | 10.59 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.74
129 | 2008-09-06 | 80000 | 1 | 647.8 | 0.2 | -2.4 | 18.98 | 149.9 | 227.3 | -0.051 | 0 | 0 | -888 | 90 | 2.44 | 9.72 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.74
130 | 2008-09-06 | 90000 | 1 | 648.3 | 0.2 | -2.4 | 18.98 | 150 | 227.5 | -0.049 | 0 | 0 | -888 | 89.1 | 2.43 | 10.19 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
131 | 2008-09-06 | 100000 | 1 | 648.6 | 0.2 | -2 | 19.15 | 151.6 | 229.3 | -0.048 | 0 | 0 | -888 | 91.3 | 2.49 | 9.69 | 2.1 | 2.33 | 1.9 | 0.007 | 0.007 | 13.72
132 | 2008-09-06 | 110000 | 1 | 665.7 | 0.1 | -1.9 | 21.36 | 173 | 258 | -0.048 | 0 | 0 | -888 | 111.7 | 2.38 | 10.43 | 1.9 | 2.23 | 1.8 | 0.007 | 0.007 | 13.7
133 | 2008-09-06 | 120000 | 1 | 666.8 | 0.1 | -2.1 | 21.34 | 173 | 258.8 | -0.05 | 0 | 0 | -888 | 116.8 | 2.51 | 10.88 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.65
134 | 2008-09-06 | 130000 | 1 | 664.8 | 0.1 | -2.3 | 21.33 | 173.2 | 259.6 | -0.05 | 0 | 0 | -888 | 125 | 2.51 | 11.54 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.58
135 | 2008-09-06 | 140000 | 1 | 663.5 | 0.1 | -2.4 | 21.31 | 172.8 | 259.2 | -0.049 | 0 | 0 | -888 | 130.5 | 2.51 | 12.02 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.54
136 | 2008-09-06 | 150000 | 1 | 644.6 | 2.9 | -19.7 | 13.79 | 111.4 | 167.6 | -0.05 | 0 | 0 | -888 | 83 | 1.66 | 7.68 | 1.3 | 1.57 | 1.4 | 0.006 | 0.005 | 15.88
137 | 2008-09-06 | 160000 | 0 | 476.8 | 5 | -86.1 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | 0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.69
138 | 2008-09-06 | 170000 | 0 | 416 | 4.7 | -75.1 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | 0 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.68
139 | 2008-09-06 | 180000 | 0 | 402.4 | 4.6 | -80.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.5 | -0.01 | 0 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.68
140 | 2008-09-06 | 190000 | 0 | 396.6 | 4.5 | -78.5 | 0.19 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.5 | -0.01 | -0.02 | -0.2 | 0 | 0.1 | 0.003 | 0 | 20.68
141 | 2008-09-06 | 200000 | 0 | 391.9 | 4.7 | -70 | 0.17 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.3 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.68
142 | 2008-09-06 | 210000 | 0 | 387 | 4.9 | -75.9 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.69
143 | 2008-09-06 | 220000 | 0 | 382.6 | 4.3 | -84.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.68
144 | 2008-09-06 | 230000 | 0 | 378.6 | 4.2 | -66.6 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.68
145 | 2008-09-07 | 0 | 0 | 374.3 | 4.6 | -64.9 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.68
146 | 2008-09-07 | 10000 | 0 | 369.4 | 4.3 | -62.7 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.02 | 0.4 | 0.003 | 0 | 20.68
147 | 2008-09-07 | 20000 | 0 | 364.7 | 4.3 | -80.3 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.68
148 | 2008-09-07 | 30000 | 0 | 361.5 | 3.7 | -76.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.68
149 | 2008-09-07 | 40000 | 1 | 529.1 | 21.8 | 10.4 | 6.11 | 15.3 | 15.7 | -0.048 | 0 | 0 | -888 | 0.6 | 9.18 | 26.9 | 13.1 | 36.8 | 52.4 | 0.193 | 0.048 | 17.11
150 | 2008-09-07 | 50000 | 1 | 635 | 14.9 | 19.9 | 10.92 | 60.1 | 60.3 | -0.049 | 0 | 0 | -888 | 33.2 | 8.26 | 24.8 | 9.4 | 35.32 | 39.8 | 0.147 | 0.034 | 15.18
151 | 2008-09-07 | 60000 | 1 | 645.2 | 0.2 | -2 | 19.53 | 153.6 | 206.6 | -0.049 | 0 | 0 | -888 | 125.2 | 1.52 | 10.99 | 1.2 | 1.42 | 1.1 | 0.004 | 0.005 | 13.62
152 | 2008-09-07 | 70000 | 1 | 649.2 | 2.2 | 15 | 19.38 | 154.9 | 232.8 | -0.048 | 0 | 0 | -888 | 91.8 | 3.43 | 10.22 | 2 | 9.51 | 3.8 | 0.014 | 0.008 | 12.12
153 | 2008-09-07 | 80000 | 1 | 649.3 | 0.2 | -2.6 | 19.35 | 154.3 | 232.7 | -0.047 | 0 | 0 | -888 | 92.9 | 2.46 | 9.72 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.7
154 | 2008-09-07 | 90000 | 1 | 651.5 | 0.1 | -2.2 | 19.4 | 154.4 | 233.4 | -0.048 | 0 | 0 | -888 | 92.8 | 2.45 | 10.17 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.72
155 | 2008-09-07 | 100000 | 1 | 652.1 | 0.1 | -2.3 | 19.37 | 153.7 | 232.7 | -0.049 | 0 | 0 | -888 | 91.7 | 2.43 | 9.58 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.73
156 | 2008-09-07 | 110000 | 1 | 654.5 | 0.1 | -2 | 19.35 | 153.6 | 232.8 | -0.047 | 0 | 0 | -888 | 89.2 | 2.43 | 9.39 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.74
157 | 2008-09-07 | 120000 | 1 | 655.3 | 0.1 | -2.3 | 19.39 | 153.8 | 233 | -0.047 | 0 | 0 | -888 | 87.6 | 2.42 | 9.21 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.76
158 | 2008-09-07 | 130000 | 1 | 656.3 | 0.1 | -2.1 | 19.39 | 153.9 | 233.6 | -0.048 | 0 | 0 | -888 | 86.5 | 2.45 | 9.13 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.77
159 | 2008-09-07 | 140000 | 1 | 656.2 | 0.1 | -2.1 | 19.4 | 153.8 | 233.5 | -0.045 | 0 | 0 | -888 | 85.5 | 2.41 | 9.03 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.77
160 | 2008-09-07 | 150000 | 1 | 657.2 | 0.1 | -2.5 | 19.43 | 153.8 | 233.8 | -0.046 | 0 | 0 | -888 | 87.5 | 2.44 | 9.15 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.78
161 | 2008-09-07 | 160000 | 1 | 655.6 | 0.1 | -2.3 | 19.29 | 152.8 | 232.4 | -0.048 | 0 | 0 | -888 | 88 | 2.43 | 9.2 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.77
162 | 2008-09-07 | 170000 | 1 | 655.7 | 0.1 | -2.3 | 19.35 | 153.5 | 233 | -0.047 | 0 | 0 | -888 | 88.4 | 2.43 | 9.23 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.76
163 | 2008-09-07 | 180000 | 1 | 655.6 | 0.1 | -2.2 | 19.35 | 153.9 | 233.5 | -0.048 | 0 | 0 | -888 | 89.5 | 2.44 | 9.29 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.75
164 | 2008-09-07 | 190000 | 1 | 655.4 | 0.1 | -2.7 | 19.34 | 154.2 | 233.5 | -0.047 | 0 | 0 | -888 | 89.8 | 2.44 | 9.37 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
165 | 2008-09-07 | 200000 | 1 | 655.2 | 0.1 | -2.1 | 19.31 | 153.8 | 233 | -0.047 | 0 | 0 | -888 | 90.7 | 2.45 | 9.45 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
166 | 2008-09-07 | 210000 | 1 | 654.2 | 0.1 | -2.5 | 19.01 | 150.6 | 229.4 | -0.047 | 0 | 0 | -888 | 88.3 | 2.45 | 9.5 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
167 | 2008-09-07 | 220000 | 0 | 552.5 | 17.2 | -23.3 | 1.76 | 6.2 | 12.5 | -0.048 | 0 | 0 | -888 | 3.1 | 2.14 | 5.39 | 4.3 | 7.24 | 9.7 | 0.036 | 0.016 | 19.52
168 | 2008-09-07 | 230000 | 0 | 434.3 | 5 | -57.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.8 | 0 | 0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.64
169 | 2008-09-08 | 0 | 0 | 411.6 | 4.9 | -58.7 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 1.1 | 0 | 0 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.64
170 | 2008-09-08 | 10000 | 0 | 402.1 | 5.1 | -62 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | 0 | 0 | -0.1 | 0.02 | 0.4 | 0.003 | 0 | 20.65
171 | 2008-09-08 | 20000 | 0 | 393.3 | 5.2 | -62.6 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.7 | 0 | -0.01 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.64
172 | 2008-09-08 | 30000 | 0 | 393.6 | 4.3 | -69.7 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.7 | 0 | -0.02 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.64
173 | 2008-09-08 | 40000 | 1 | 578.7 | 19.7 | 7.2 | 6.12 | 15.1 | 15.6 | -0.051 | 0 | 0 | -888 | 7.5 | 9.65 | 27.51 | 14.1 | 38.41 | 55 | 0.203 | 0.052 | 17.03
174 | 2008-09-08 | 50000 | 1 | 630.7 | 12.1 | 13.6 | 12.12 | 73.6 | 82 | -0.051 | 0 | 0 | -888 | 53.5 | 7.41 | 22.8 | 8.1 | 32.22 | 35.5 | 0.131 | 0.03 | 14.87
175 | 2008-09-08 | 60000 | 1 | 641.4 | 2.3 | 21.2 | 19.63 | 157.7 | 231.1 | -0.05 | 0 | 0 | -888 | 98.8 | 3.41 | 9.6 | 2.1 | 9.24 | 3.8 | 0.014 | 0.008 | 12.1
176 | 2008-09-08 | 70000 | 1 | 645.3 | 0.2 | -2.2 | 19.06 | 151.2 | 227.6 | -0.051 | 0 | 0 | -888 | 95.4 | 2.44 | 10.97 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.68
177 | 2008-09-08 | 80000 | 1 | 647.5 | 0.2 | -2.1 | 19.14 | 152 | 228.9 | -0.051 | 0 | 0 | -888 | 95.9 | 2.49 | 9.93 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.67
178 | 2008-09-08 | 90000 | 1 | 661.6 | 0.2 | -2.2 | 21.28 | 173.3 | 258.2 | -0.05 | 0 | 0 | -888 | 120.9 | 2.48 | 11.37 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.58
179 | 2008-09-08 | 100000 | 1 | 663.7 | 0.2 | -2.1 | 21.09 | 172 | 258.4 | -0.049 | 0 | 0 | -888 | 127.1 | 2.54 | 11.73 | 2 | 2.37 | 1.9 | 0.007 | 0.008 | 13.53
180 | 2008-09-08 | 110000 | 1 | 663.5 | 0.2 | -2.2 | 21.06 | 171 | 257 | -0.05 | 0 | 0 | -888 | 123.2 | 2.41 | 11.47 | 1.9 | 2.26 | 1.8 | 0.007 | 0.007 | 13.53
181 | 2008-09-08 | 120000 | 1 | 664.6 | 0.1 | -2.4 | 20.53 | 165.6 | 247.8 | -0.05 | 0 | 0 | -888 | 97.9 | 2.46 | 9.75 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.68
182 | 2008-09-08 | 130000 | 1 | 667.5 | 0.1 | -2.5 | 20.61 | 166.4 | 248.4 | -0.05 | 0 | 0 | -888 | 94.2 | 2.49 | 9.41 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.68
183 | 2008-09-08 | 140000 | 1 | 667 | 0.1 | -2.2 | 20.86 | 168.4 | 251.9 | -0.049 | 0 | 0 | -888 | 100.3 | 2.54 | 9.87 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.58
184 | 2008-09-08 | 150000 | 1 | 664.6 | 0.2 | -2.3 | 21.1 | 170.5 | 256.4 | -0.05 | 0 | 10.5 | -888 | 117.8 | 2.48 | 11.2 | 2 | 2.33 | 1.8 | 0.007 | 0.007 | 13.42
185 | 2008-09-08 | 160000 | 1 | 653.6 | 0.2 | -2.3 | 18.98 | 150 | 228.6 | -0.049 | 0 | 30.5 | -888 | 87 | 2.52 | 9.38 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.71
186 | 2008-09-08 | 170000 | 1 | 652 | 0.2 | -2 | 18.98 | 150.3 | 228.9 | -0.049 | 0 | 31.6 | -888 | 89.8 | 2.49 | 9.48 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.71
187 | 2008-09-08 | 180000 | 1 | 662.9 | 0.2 | -2.1 | 21.25 | 172.7 | 258.4 | -0.049 | 0 | 40.3 | -888 | 123 | 2.5 | 11.44 | 2 | 2.35 | 1.8 | 0.007 | 0.007 | 13.4
188 | 2008-09-08 | 190000 | 1 | 663.6 | 0.2 | -2.4 | 21.32 | 173.1 | 258.9 | -0.049 | 0 | 39.6 | -888 | 121.2 | 2.55 | 11.43 | 2 | 2.4 | 1.9 | 0.007 | 0.007 | 13.39
189 | 2008-09-08 | 200000 | 1 | 663.5 | 0.2 | -2 | 21.24 | 172.9 | 258 | -0.051 | 0 | 38.5 | -888 | 117.8 | 2.53 | 11.09 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.42
190 | 2008-09-08 | 210000 | 1 | 664.3 | 0.2 | -2.2 | 21.02 | 171 | 255.4 | -0.049 | 0 | 36.1 | -888 | 110.5 | 2.51 | 10.57 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.48
191 | 2008-09-08 | 220000 | 0 | 558.4 | 14.7 | -19.6 | 1.83 | 9.6 | 17.5 | -0.049 | 0 | 3.5 | -888 | 4.5 | 1.61 | 4.89 | 2.2 | 5.72 | 6.3 | 0.024 | 0.008 | 19.28
192 | 2008-09-08 | 230000 | 0 | 436.8 | 3.6 | -43.1 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.7 | -0.01 | 0.02 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.54
193 | 2008-09-09 | 0 | 0 | 412.5 | 3.1 | -50.7 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.8 | -0.01 | -0.02 | -0.1 | 0.01 | 0.3 | 0.002 | 0 | 20.54
194 | 2008-09-09 | 10000 | 0 | 400.2 | 3.2 | -42.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.8 | -0.01 | -0.03 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.54
195 | 2008-09-09 | 20000 | 0 | 389.5 | 2.9 | -49.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.8 | -0.01 | -0.03 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.54
196 | 2008-09-09 | 30000 | 0 | 389.2 | 2.5 | -45.6 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.1 | 0.02 | 0.2 | 0.002 | 0 | 20.55
197 | 2008-09-09 | 40000 | 1 | 548.5 | 21.8 | 11 | 6.29 | 17.4 | 17.8 | -0.046 | 0 | 5.6 | -888 | 0.6 | 9.25 | 26.81 | 12.5 | 39.69 | 53.3 | 0.196 | 0.046 | 16.89
198 | 2008-09-09 | 50000 | 1 | 615.7 | 14.7 | 23.4 | 11.41 | 65.2 | 97.5 | -0.049 | 0 | 31.9 | -888 | 52.5 | 8.16 | 25.04 | 8.3 | 36.46 | 36.7 | 0.135 | 0.031 | 14.73
199 | 2008-09-09 | 60000 | 1 | 636.2 | 2.2 | 20.7 | 19.25 | 153.7 | 230.1 | -0.048 | 0 | 44.1 | -888 | 94.8 | 3.37 | 10.53 | 2 | 9.41 | 3.7 | 0.014 | 0.007 | 12.06
200 | 2008-09-09 | 70000 | 1 | 651.5 | 0.2 | -1.9 | 21.5 | 175.3 | 259.6 | -0.05 | 0 | 37.9 | -888 | 119.5 | 2.5 | 10.89 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.54
201 | 2008-09-09 | 80000 | 1 | 653.7 | 0.2 | -1.9 | 21.22 | 173.1 | 256.1 | -0.048 | 0 | 36.1 | -888 | 113.4 | 2.48 | 10.5 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.61
202 | 2008-09-09 | 90000 | 1 | 654.3 | 0.2 | -2.3 | 21.24 | 173.6 | 258 | -0.049 | 0 | 36.8 | -888 | 115 | 2.5 | 10.99 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.58
203 | 2008-09-09 | 100000 | 1 | 655 | 0.2 | -2 | 21.55 | 176 | 262 | -0.05 | 0 | 42.4 | -888 | 132.1 | 2.58 | 11.95 | 2 | 2.41 | 1.9 | 0.007 | 0.007 | 13.45
204 | 2008-09-09 | 110000 | 1 | 654.5 | 0.2 | -2.2 | 21.57 | 176 | 261.9 | -0.041 | 0 | -484.4 | -888 | 130 | 2.53 | 11.84 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.43
205 | 2008-09-09 | 120000 | 1 | 653.8 | 0.2 | -2.2 | 21.56 | 176.1 | 261.4 | -0.049 | 0 | -666 | -888 | 127.1 | 2.55 | 11.69 | 2 | 2.4 | 1.9 | 0.007 | 0.007 | 13.41
206 | 2008-09-09 | 130000 | 1 | 661.3 | 0.2 | -2.1 | 21.55 | 175.7 | 261.1 | -0.048 | 0 | -666 | -888 | 125.1 | 2.55 | 11.58 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.42
207 | 2008-09-09 | 140000 | 1 | 664.2 | 0.2 | -2 | 21.46 | 174.2 | 259.5 | -0.048 | 0 | -666 | -888 | 117.1 | 2.5 | 10.98 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.46
208 | 2008-09-09 | 150000 | 1 | 664.5 | 0.2 | -2.1 | 21.32 | 173.2 | 257.6 | -0.048 | 0 | -666 | -888 | 109.3 | 2.54 | 10.42 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.51
209 | 2008-09-09 | 160000 | 1 | 664.4 | 0.2 | -2.3 | 21.31 | 173.2 | 257.8 | -0.049 | 0 | -666 | -888 | 110.9 | 2.51 | 10.46 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.52
210 | 2008-09-09 | 170000 | 1 | 665 | 0.2 | -2.4 | 21.31 | 173.1 | 257.3 | -0.049 | 0 | -666 | -888 | 110.8 | 2.48 | 10.35 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.57
211 | 2008-09-09 | 180000 | 1 | 665.7 | 0.2 | -1.7 | 21.31 | 173.4 | 256.5 | -0.047 | 0 | -666 | -888 | 109.7 | 2.5 | 10.27 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.61
212 | 2008-09-09 | 190000 | 1 | 666.5 | 0.2 | -2 | 21.33 | 173.7 | 258.3 | -0.049 | 0 | -666 | -888 | 114.8 | 2.5 | 10.56 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.61
213 | 2008-09-09 | 200000 | 1 | 666.6 | 0.2 | -2.4 | 21.32 | 173.9 | 258.3 | -0.049 | 0 | -666 | -888 | 117.4 | 2.47 | 10.69 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.65
214 | 2008-09-09 | 210000 | 1 | 666.8 | 0.2 | -2 | 21.11 | 171.4 | 255.1 | -0.046 | 0 | -666 | -888 | 112.3 | 2.43 | 10.45 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.71
215 | 2008-09-09 | 220000 | 0 | 568.8 | 15.6 | -27 | 1.94 | 10 | 18.1 | -0.049 | 0 | -666 | -888 | 4 | 1.83 | 5.46 | 2.5 | 7.19 | 8.1 | 0.031 | 0.009 | 19.31
216 | 2008-09-09 | 230000 | 0 | 451.3 | 4.3 | -67.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.8 | -0.01 | 0.03 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.63
217 | 2008-09-10 | 0 | 0 | 428.3 | 3.9 | -62.8 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | -0.01 | 0 | -0.1 | 0.02 | 0.3 | 0.003 | 0 | 20.63
218 | 2008-09-10 | 10000 | 0 | 419.6 | 3.9 | -69.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | -0.01 | -0.02 | -0.1 | 0.01 | 0 | 0.002 | 0 | 20.64
219 | 2008-09-10 | 20000 | 0 | 411 | 4.5 | -66.9 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | -0.01 | -0.03 | -0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.65
220 | 2008-09-10 | 30000 | 0 | 411.5 | 3.7 | -72 | 0.05 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.02 | 0.5 | 0.003 | 0 | 20.65
221 | 2008-09-10 | 40000 | 1 | 566.3 | 25 | 10.8 | 6.51 | 17.3 | 17.7 | -0.048 | 0 | -666 | -888 | 9.9 | 9.72 | 28.38 | 13.9 | 40.04 | 57.2 | 0.211 | 0.051 | 16.93
222 | 2008-09-10 | 50000 | 1 | 607.9 | 16.9 | 29.2 | 11.27 | 63.2 | 95 | -0.049 | 0 | -666 | -888 | 92.1 | 9.08 | 27.14 | 9.3 | 40.36 | 41.2 | 0.152 | 0.034 | 14.93
223 | 2008-09-10 | 60000 | 1 | 641.3 | 0.3 | -2.2 | 20.13 | 162.5 | 240 | -0.05 | 0 | -666 | -888 | 109.1 | 2.43 | 11.02 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.7
224 | 2008-09-10 | 70000 | 1 | 664.6 | 0.2 | -2.2 | 22.26 | 182.8 | 269.9 | -0.051 | 0 | -666 | -888 | 133.1 | 2.45 | 11.89 | 2 | 2.3 | 1.8 | 0.007 | 0.007 | 13.56
225 | 2008-09-10 | 80000 | 1 | 672.7 | 3.3 | 10.4 | 22.04 | 180.5 | 268.2 | -0.046 | 0 | -602.3 | -888 | 132.2 | 3.45 | 11.61 | 2 | 9.51 | 3.6 | 0.014 | 0.007 | 12.04
226 | 2008-09-10 | 90000 | 1 | 670.7 | 0.2 | -2.4 | 21.66 | 177.1 | 262.8 | -0.05 | 0 | -666 | -888 | 121.7 | 2.42 | 11.24 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.71
227 | 2008-09-10 | 100000 | 1 | 670.4 | 0.2 | -2.5 | 21.54 | 176.3 | 262.8 | -0.051 | 0 | -666 | -888 | 121.7 | 2.46 | 11.08 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.66
228 | 2008-09-10 | 110000 | 1 | 668.5 | 0.2 | -2.5 | 21.31 | 172.9 | 257.9 | -0.049 | 0 | -666 | -888 | 114.8 | 2.45 | 10.66 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.71
229 | 2008-09-10 | 120000 | 1 | 668.7 | 0.2 | -1.9 | 21.28 | 173.2 | 257.8 | -0.052 | 0 | -666 | -888 | 111.1 | 2.46 | 10.43 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.67
230 | 2008-09-10 | 130000 | 1 | 667.8 | 0.2 | -2 | 21.32 | 172.7 | 257.5 | -0.05 | 0 | -666 | -888 | 108.1 | 2.47 | 10.33 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.62
231 | 2008-09-10 | 140000 | 1 | 667 | 0.2 | -2.2 | 21.33 | 173.1 | 258 | -0.052 | 0 | -666 | -888 | 110.7 | 2.49 | 10.5 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.6
232 | 2008-09-10 | 150000 | 1 | 667.2 | 0.2 | -2.5 | 21.52 | 175.4 | 259.5 | -0.051 | 0 | -666 | -888 | 125.5 | 2.55 | 11.56 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.51
233 | 2008-09-10 | 160000 | 1 | 666.5 | 0.2 | -2.2 | 21.36 | 173.7 | 257.2 | -0.05 | 0 | -666 | -888 | 118.9 | 2.51 | 10.92 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.54
234 | 2008-09-10 | 170000 | 1 | 667.1 | 0.2 | -2.6 | 21.25 | 173 | 258.6 | -0.052 | 0 | -666 | -888 | 112.6 | 2.47 | 10.3 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.57
235 | 2008-09-10 | 180000 | 1 | 667.7 | 0.2 | -2.1 | 21.28 | 173 | 258.2 | -0.051 | 0 | -666 | -888 | 111.1 | 2.49 | 10.21 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.61
236 | 2008-09-10 | 190000 | 1 | 667.8 | 0.2 | -2.3 | 21.26 | 172.9 | 257.8 | -0.051 | 0 | -666 | -888 | 110.9 | 2.47 | 10.17 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.63
237 | 2008-09-10 | 200000 | 1 | 667 | 0.2 | -2.2 | 21.15 | 171.6 | 257.7 | -0.05 | 0 | -666 | -888 | 128.5 | 2.53 | 11.42 | 2 | 2.37 | 1.9 | 0.007 | 0.008 | 13.61
238 | 2008-09-10 | 210000 | 1 | 664.4 | 0.2 | -2.3 | 20.96 | 169.6 | 255.8 | -0.051 | 0 | -666 | -888 | 125.8 | 2.43 | 11.34 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.63
239 | 2008-09-10 | 220000 | 0 | 565.9 | 16.3 | -37.2 | 1.86 | 9.6 | 17.4 | -0.051 | 0 | -666 | -888 | 4.3 | 1.68 | 5.11 | 2.4 | 6.82 | 7.9 | 0.03 | 0.009 | 19.39
240 | 2008-09-10 | 230000 | 0 | 450.9 | 6.7 | -79.7 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -666 | -888 | 0.8 | 0 | 0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.67
241 | 2008-09-11 | 0 | 0 | 427.6 | 6.5 | -78.2 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | -666 | -888 | 0.7 | 0 | 0 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.67
242 | 2008-09-11 | 10000 | 0 | 419.2 | 6.3 | -72 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.8 | 0 | 0 | -0.1 | 0.02 | 0.3 | 0.003 | 0 | 20.67
243 | 2008-09-11 | 20000 | 0 | 411.2 | 6.7 | -72.7 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.7 | 0.01 | -0.01 | 0.1 | 0.02 | 0.5 | 0.003 | 0.001 | 20.66
244 | 2008-09-11 | 30000 | 0 | 416 | 5.5 | -80.7 | 0.1 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.5 | 0.01 | 0.36 | 0 | 0.02 | 0.4 | 0.003 | 0 | 20.64
245 | 2008-09-11 | 40000 | 1 | 580.8 | 23.2 | 45.8 | 8.16 | 30.4 | 31 | -0.05 | 0 | -666 | -888 | 7.2 | 10.22 | 29.42 | 12.2 | 40.66 | 48.1 | 0.177 | 0.045 | 15.95
246 | 2008-09-11 | 50000 | 1 | 633.4 | 8.6 | 14.1 | 16.53 | 120 | 177.3 | -0.015 | 0 | -476.5 | -888 | 118.8 | 5.64 | 20.18 | 5.6 | 21.66 | 21.6 | 0.079 | 0.021 | 14.2
247 | 2008-09-11 | 60000 | 1 | 656.7 | 2.3 | 19.9 | 21.29 | 173 | 256.7 | -0.049 | 0 | -666 | -888 | 112.2 | 3.39 | 10.98 | 2.1 | 9.51 | 3.8 | 0.014 | 0.008 | 12.17
248 | 2008-09-11 | 70000 | 1 | 666.7 | 0.2 | -1.9 | 21.18 | 172.2 | 255.9 | -0.049 | 0 | -666 | -888 | 111.4 | 2.43 | 10.38 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.79
249 | 2008-09-11 | 80000 | 1 | 668 | 0.2 | -2.1 | 21.16 | 172.2 | 255.5 | -0.05 | 0 | -666 | -888 | 111.8 | 2.45 | 10.38 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.73
250 | 2008-09-11 | 90000 | 1 | 667.9 | 0.2 | -2.3 | 21.07 | 171.1 | 255.7 | -0.048 | 0 | -666 | -888 | 113.3 | 2.45 | 10.88 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.71
251 | 2008-09-11 | 100000 | 1 | 666 | 0.2 | -2.1 | 21.1 | 170.6 | 255.4 | -0.051 | 0 | -666 | -888 | 111.2 | 2.43 | 10.43 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.68
252 | 2008-09-11 | 110000 | 1 | 667.5 | 0.2 | -2.1 | 21.19 | 171.8 | 256.7 | -0.051 | 0 | -666 | -888 | 112.9 | 2.6 | 10.67 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.62
253 | 2008-09-11 | 120000 | 1 | 663 | 0.2 | -2 | 20.92 | 168.5 | 254.4 | -0.048 | 0 | -666 | -888 | 128.7 | 2.5 | 11.76 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.56
254 | 2008-09-11 | 130000 | 1 | 664 | 0.2 | -2.1 | 21.18 | 171.3 | 256.9 | -0.05 | 0 | -666 | -888 | 116.9 | 2.41 | 10.97 | 1.9 | 2.27 | 1.8 | 0.007 | 0.007 | 13.52
255 | 2008-09-11 | 140000 | 1 | 665.7 | 0.2 | -2 | 21.08 | 171.2 | 256 | -0.051 | 0 | -666 | -888 | 109 | 2.54 | 10.47 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.53
256 | 2008-09-11 | 150000 | 1 | 664.7 | 0.2 | -2.4 | 21 | 170.4 | 255.4 | -0.05 | 0 | -666 | -888 | 110.6 | 2.51 | 10.61 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.51
257 | 2008-09-11 | 160000 | 1 | 665.1 | 0.2 | -2 | 21.03 | 170.2 | 254.8 | -0.049 | 0 | -666 | -888 | 112 | 2.57 | 10.63 | 2 | 2.41 | 1.9 | 0.007 | 0.008 | 13.5
258 | 2008-09-11 | 170000 | 1 | 664.2 | 0.2 | -2.3 | 21.07 | 171.1 | 256.7 | -0.049 | 0 | -666 | -888 | 117.6 | 2.54 | 11.21 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.43
259 | 2008-09-11 | 180000 | 1 | 664.1 | 0.2 | -2 | 21.18 | 171.6 | 257.1 | -0.05 | 0 | -666 | -888 | 118 | 2.55 | 11.22 | 2 | 2.4 | 1.9 | 0.007 | 0.007 | 13.42
260 | 2008-09-11 | 190000 | 1 | 664.8 | 0.2 | -1.9 | 21.16 | 171.3 | 256.2 | -0.05 | 0 | -666 | -888 | 111.4 | 2.5 | 10.69 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.48
261 | 2008-09-11 | 200000 | 1 | 666.6 | 0.2 | -2.3 | 21.04 | 170.9 | 254.9 | -0.051 | 0 | -666 | -888 | 105.9 | 2.5 | 10.19 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.57
262 | 2008-09-11 | 210000 | 1 | 666.2 | 0.2 | -2.2 | 20.92 | 169.6 | 253.7 | -0.048 | 0 | -666 | -888 | 104.1 | 2.48 | 10.15 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.58
263 | 2008-09-11 | 220000 | 0 | 568 | 16.3 | -15.4 | 2.09 | 9.7 | 17.7 | -0.049 | 0 | -666 | -888 | 3.2 | 1.69 | 5.09 | 2.2 | 6.39 | 7 | 0.027 | 0.008 | 19.29
264 | 2008-09-11 | 230000 | 0 | 454 | 5.6 | -50.2 | 0.08 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.8 | 0 | 0.04 | -0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.59
265 | 2008-09-12 | 0 | 0 | 431.7 | 4.7 | -56 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.7 | -0.01 | 0 | -0.1 | 0.02 | 0.4 | 0.003 | 0 | 20.59
266 | 2008-09-12 | 10000 | 0 | 424.1 | 5 | -57.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | -0.01 | -0.01 | -0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.59
267 | 2008-09-12 | 20000 | 0 | 416.3 | 4.6 | -52.1 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.7 | -0.01 | -0.01 | -0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.59
268 | 2008-09-12 | 30000 | 0 | 422 | 3.5 | -56.3 | 0.09 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | 0 | 0.24 | -0.1 | 0.02 | 0.3 | 0.002 | 0 | 20.59
269 | 2008-09-12 | 40000 | 1 | 585.4 | 22.2 | 36.7 | 8.33 | 32.6 | 34.6 | -0.048 | 0 | -666 | -888 | 21.4 | 10.17 | 29.23 | 11.9 | 40.45 | 46.3 | 0.171 | 0.044 | 15.8
270 | 2008-09-12 | 50000 | 1 | 630.6 | 0.5 | -1.8 | 17.88 | 137.9 | 204.8 | -0.047 | 0 | -666 | -888 | 89.8 | 2.5 | 10.67 | 2 | 5.07 | 4.3 | 0.016 | 0.008 | 13.65
271 | 2008-09-12 | 60000 | 1 | 656.7 | 2.4 | 22.9 | 21.38 | 174 | 258.5 | -0.049 | 0 | -666 | -888 | 125.2 | 3.3 | 11.45 | 1.9 | 9.37 | 3.6 | 0.013 | 0.007 | 12.03
272 | 2008-09-12 | 70000 | 1 | 665.7 | 0.2 | -2.3 | 21.1 | 171.5 | 254.8 | -0.048 | 0 | -666 | -888 | 107.3 | 2.45 | 10.13 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.73
273 | 2008-09-12 | 80000 | 1 | 666.8 | 0.2 | -2.2 | 21.06 | 171.6 | 255 | -0.049 | 0 | -666 | -888 | 108 | 2.43 | 10.11 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.73
274 | 2008-09-12 | 90000 | 1 | 667.2 | 0.2 | -2.4 | 21.13 | 172 | 255.9 | -0.048 | 0 | -666 | -888 | 108.7 | 2.46 | 10.63 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.7
275 | 2008-09-12 | 100000 | 1 | 665.6 | 0.2 | -2.1 | 21.08 | 171.3 | 255.3 | -0.047 | 0 | -666 | -888 | 110.6 | 2.45 | 10.27 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.7
276 | 2008-09-12 | 110000 | 1 | 665.6 | 0.2 | -2.5 | 21.09 | 170.9 | 254.8 | -0.048 | 0 | -666 | -888 | 107.3 | 2.46 | 10.16 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.7
277 | 2008-09-12 | 120000 | 1 | 664.7 | 0.2 | -2.6 | 21.06 | 171.1 | 255.9 | -0.047 | 0 | -666 | -888 | 110.5 | 2.49 | 10.46 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.62
278 | 2008-09-12 | 130000 | 1 | 663 | 0.2 | -2.3 | 21.11 | 171 | 256.2 | -0.047 | 0 | -666 | -888 | 115.9 | 2.52 | 10.91 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.57
279 | 2008-09-12 | 140000 | 1 | 662.5 | 0.2 | -2.1 | 20.93 | 168.9 | 253.1 | -0.048 | 0 | -666 | -888 | 111.9 | 2.47 | 10.68 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.61
280 | 2008-09-12 | 150000 | 1 | 662 | 0.2 | -2.1 | 20.89 | 168.7 | 253.3 | -0.048 | 0 | -666 | -888 | 112.2 | 2.5 | 10.67 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.58
281 | 2008-09-12 | 160000 | 1 | 661.5 | 0.2 | -2.1 | 20.94 | 169.4 | 254.3 | -0.047 | 0 | -666 | -888 | 116.5 | 2.54 | 11.03 | 2 | 2.38 | 1.9 | 0.007 | 0.008 | 13.55
282 | 2008-09-12 | 170000 | 1 | 661.7 | 0.2 | -2.1 | 20.9 | 169.1 | 253.3 | -0.047 | 0 | -666 | -888 | 111.2 | 2.44 | 10.52 | 2 | 2.28 | 1.8 | 0.007 | 0.007 | 13.61
283 | 2008-09-12 | 180000 | 1 | 663 | 0.2 | -2.2 | 21.06 | 170.6 | 254.8 | -0.047 | 0 | -666 | -888 | 109.4 | 2.46 | 10.37 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.63
284 | 2008-09-12 | 190000 | 1 | 664.4 | 0.2 | -2.1 | 20.98 | 170 | 253.1 | -0.046 | 0 | -666 | -888 | 103.2 | 2.45 | 9.9 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.72
285 | 2008-09-12 | 200000 | 1 | 665.6 | 0.2 | -2.3 | 21.07 | 171.4 | 254.8 | -0.048 | 0 | -666 | -888 | 106.6 | 2.45 | 10.05 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.73
286 | 2008-09-12 | 210000 | 1 | 666.7 | 0.2 | -2.2 | 20.89 | 170.1 | 253.6 | -0.047 | 0 | -666 | -888 | 105.6 | 2.43 | 10.16 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.74
287 | 2008-09-12 | 220000 | 0 | 568 | 18.2 | -29.7 | 1.86 | 9.5 | 17.4 | -0.048 | 0 | -666 | -888 | 3.9 | 1.77 | 5.18 | 2.5 | 6.85 | 7.8 | 0.03 | 0.009 | 19.4
288 | 2008-09-12 | 230000 | 0 | 452.7 | 5.9 | -83.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.7 | -0.01 | 0.04 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.68
289 | 2008-09-13 | 0 | 0 | 429.2 | 5.6 | -68.3 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.6 | -0.01 | -0.01 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.61
290 | 2008-09-13 | 10000 | 0 | 419.2 | 5.7 | -88.4 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.8 | -0.01 | -0.02 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.69
291 | 2008-09-13 | 20000 | 0 | 410 | 5.6 | -93.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | -0.01 | -0.03 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.69
292 | 2008-09-13 | 30000 | 0 | 404.1 | 5.6 | -73.1 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | -0.01 | -0.03 | -0.2 | 0.02 | 0.5 | 0.003 | 0 | 20.69
293 | 2008-09-13 | 40000 | 0 | 405.6 | 5 | -79.2 | 0.05 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | -0.01 | -0.03 | -0.3 | 0.01 | 0.4 | 0.004 | 0 | 20.69
294 | 2008-09-13 | 50000 | 1 | 572.6 | 24.8 | 46.7 | 6.98 | 20.1 | 20.5 | -0.05 | 0 | -666 | -888 | 11.5 | 9.7 | 28.15 | 13.2 | 34.07 | 46 | 0.17 | 0.049 | 16.73
295 | 2008-09-13 | 60000 | 1 | 616.9 | 14.4 | 21 | 11.8 | 69 | 108.9 | -0.05 | 0 | -666 | -888 | 84.1 | 7.77 | 24.6 | 8 | 33.35 | 34.4 | 0.127 | 0.03 | 14.79
296 | 2008-09-13 | 70000 | 1 | 645.5 | 3.6 | 8.7 | 20.56 | 167.2 | 247 | -0.049 | 0 | -666 | -888 | 109.9 | 3.28 | 11.01 | 2 | 9.48 | 3.6 | 0.014 | 0.007 | 12.18
297 | 2008-09-13 | 80000 | 1 | 654.5 | 0.2 | -2.2 | 21.01 | 171.5 | 253.9 | -0.049 | 0 | -666 | -888 | 111.9 | 2.36 | 10.32 | 2 | 2.21 | 1.8 | 0.007 | 0.007 | 13.83
298 | 2008-09-13 | 90000 | 1 | 656.5 | 0.2 | -2.5 | 21.12 | 172.4 | 255.3 | -0.05 | 0 | -666 | -888 | 110.5 | 2.41 | 10.65 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.85
299 | 2008-09-13 | 100000 | 1 | 656.6 | 0.2 | -2.5 | 21.08 | 172.1 | 255.1 | -0.049 | 0 | -666 | -888 | 109.4 | 2.39 | 10.14 | 2 | 2.24 | 1.9 | 0.007 | 0.007 | 13.85
300 | 2008-09-13 | 110000 | 1 | 655.8 | 0.2 | -1.9 | 21.08 | 172.1 | 255.5 | -0.05 | 0 | -666 | -888 | 108.8 | 2.42 | 10.17 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.81
301 | 2008-09-13 | 120000 | 1 | 654.8 | 0.2 | -2.4 | 21.14 | 171.6 | 255.5 | -0.049 | 0 | -666 | -888 | 109 | 2.44 | 10.28 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.75
302 | 2008-09-13 | 130000 | 1 | 654.9 | 0.2 | -2.2 | 21.06 | 171 | 255.2 | -0.051 | 0 | -666 | -888 | 115.7 | 2.46 | 10.77 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.66
303 | 2008-09-13 | 140000 | 1 | 654.7 | 0.2 | -2.4 | 21.07 | 170.9 | 254.7 | -0.05 | 0 | -666 | -888 | 104.8 | 2.46 | 10.18 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.64
304 | 2008-09-13 | 150000 | 1 | 655.5 | 0.2 | -2.1 | 21.06 | 171 | 255.1 | -0.049 | 0 | -666 | -888 | 105.5 | 2.5 | 10.24 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.59
305 | 2008-09-13 | 160000 | 1 | 654.5 | 0.2 | -2 | 21.1 | 170.9 | 254.8 | -0.048 | 0 | -666 | -888 | 106.8 | 2.49 | 10.34 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.6
306 | 2008-09-13 | 170000 | 1 | 663.3 | 0.2 | -2.1 | 21.08 | 170.7 | 254.3 | -0.052 | 0 | -666 | -888 | 105.6 | 2.49 | 10.21 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.61
307 | 2008-09-13 | 180000 | 1 | 666.1 | 0.2 | -2.3 | 21.1 | 171 | 255.6 | -0.049 | 0 | -666 | -888 | 105.6 | 2.47 | 10.18 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.62
308 | 2008-09-13 | 190000 | 1 | 666.9 | 0.2 | -2.6 | 21.08 | 171.5 | 255.8 | -0.049 | 0 | -666 | -888 | 106.2 | 2.48 | 10.18 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.63
309 | 2008-09-13 | 200000 | 1 | 667.2 | 0.2 | -2.3 | 21.14 | 171.7 | 256 | -0.049 | 0 | -666 | -888 | 106.2 | 2.47 | 10.15 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.65
310 | 2008-09-13 | 210000 | 1 | 668.7 | 0.2 | -2 | 20.91 | 169.1 | 252.1 | -0.049 | 0 | -666 | -888 | 103 | 2.45 | 10.09 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.67
311 | 2008-09-13 | 220000 | 0 | 562 | 20.1 | -31.5 | 1.83 | 8.5 | 16 | -0.048 | 0 | -666 | -888 | 14.8 | 1.97 | 5.93 | 2.6 | 7.6 | 8.5 | 0.032 | 0.01 | 19.4
312 | 2008-09-13 | 230000 | 0 | 446.1 | 7.8 | -80.8 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | 0 | 0.05 | -0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.68
313 | 2008-09-14 | 0 | 0 | 425.2 | 7.1 | -73.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.7 | 0 | 0 | -0.1 | 0.02 | 0.4 | 0.003 | 0 | 20.68
314 | 2008-09-14 | 10000 | 0 | 414.3 | 7.6 | -78.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.7 | 0 | 0 | 0 | 0.02 | 0.3 | 0.003 | 0 | 20.69
315 | 2008-09-14 | 20000 | 0 | 406.1 | 7.5 | -73.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.5 | 0 | -0.01 | 0 | 0.01 | 0.3 | 0.003 | 0 | 20.68
316 | 2008-09-14 | 30000 | 0 | 406.9 | 6.8 | -72.9 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.68
317 | 2008-09-14 | 40000 | 1 | 556.1 | 24.4 | 11.7 | 6.5 | 18.2 | 18.6 | -0.049 | 0 | -666 | -888 | 0.5 | 9.21 | 27.45 | 12.8 | 38.92 | 53.6 | 0.198 | 0.047 | 16.93
318 | 2008-09-14 | 50000 | 1 | 609.6 | 15.1 | 22.8 | 11.47 | 65.1 | 98.4 | -0.049 | 0 | -666 | -888 | 52.5 | 8.46 | 25.92 | 8.4 | 44.52 | 44.3 | 0.163 | 0.031 | 14.7
319 | 2008-09-14 | 60000 | 1 | 639.9 | 0.3 | -1.9 | 20.08 | 161.9 | 240.7 | -0.048 | 0 | -666 | -888 | 103.7 | 2.29 | 10.49 | 1.9 | 2.14 | 1.8 | 0.007 | 0.007 | 13.74
320 | 2008-09-14 | 70000 | 1 | 643.1 | 3 | 17.6 | 19.56 | 156.8 | 235 | -0.047 | 0 | -666 | -888 | 99.9 | 3.38 | 10.33 | 2.1 | 9.34 | 3.7 | 0.014 | 0.008 | 12.19
321 | 2008-09-14 | 80000 | 1 | 654 | 0.3 | -2.4 | 19.64 | 157.3 | 236 | -0.048 | 0 | -666 | -888 | 96.7 | 2.47 | 9.78 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.74
322 | 2008-09-14 | 90000 | 1 | 656.1 | 0.2 | -2.3 | 19.59 | 156.6 | 235.8 | -0.047 | 0 | -666 | -888 | 96.7 | 2.44 | 10.26 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.74
323 | 2008-09-14 | 100000 | 1 | 655.3 | 0.2 | -2.3 | 19.54 | 155.7 | 235.1 | -0.046 | 0 | -666 | -888 | 95.2 | 2.45 | 9.75 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.75
324 | 2008-09-14 | 110000 | 1 | 655.3 | 0.2 | -2.2 | 19.49 | 155.4 | 234.8 | -0.047 | 0 | -666 | -888 | 95.1 | 2.42 | 9.7 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.76
325 | 2008-09-14 | 120000 | 1 | 656.4 | 0.2 | -2.3 | 19.61 | 155.8 | 235.6 | -0.048 | 0 | -666 | -888 | 93.6 | 2.42 | 9.49 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.79
326 | 2008-09-14 | 130000 | 1 | 621.4 | 10.6 | -17.7 | 10.31 | 80.8 | 125.2 | -0.048 | 0 | -666 | -888 | 53.1 | 1.75 | 6.06 | 2.1 | 1.88 | 2.2 | 0.009 | 0.008 | 16.76
327 | 2008-09-14 | 140000 | 0 | 439.4 | 7 | -69.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.9 | -0.01 | 0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.66
328 | 2008-09-14 | 150000 | 0 | 399 | 5.8 | -60.3 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | -0.01 | 0.01 | -0.1 | 0.02 | 0.3 | 0.003 | 0 | 20.65
329 | 2008-09-14 | 160000 | 0 | 387.6 | 5.8 | -65.8 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.6 | 0 | 0 | -0.1 | 0 | 0 | 0.002 | 0 | 20.64
330 | 2008-09-14 | 170000 | 0 | 373 | 5.6 | -62 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | 0 | -0.01 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.64
331 | 2008-09-14 | 180000 | 0 | 363.7 | 5.3 | -61.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.7 | 0 | -0.03 | -0.1 | 0.02 | 0.4 | 0.003 | 0 | 20.64
332 | 2008-09-14 | 190000 | 0 | 358.4 | 5.4 | -54.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.64
333 | 2008-09-14 | 200000 | 0 | 353.2 | 5.8 | -67.6 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.7 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.65
334 | 2008-09-14 | 210000 | 0 | 348.6 | 6.3 | -67.8 | 0.16 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | 0 | -0.03 | 0 | 0.01 | 0.1 | 0.003 | 0 | 20.65
335 | 2008-09-14 | 220000 | 0 | 345 | 6.7 | -63.6 | 0.09 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | 0 | -0.03 | 0 | 0.02 | 0.2 | 0.003 | 0 | 20.66
336 | 2008-09-14 | 230000 | 0 | 341.4 | 6.9 | -69.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.66
337 | 2008-09-15 | 0 | 0 | 337.6 | 6.9 | -67.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.67
338 | 2008-09-15 | 10000 | 0 | 334 | 7.3 | -67.1 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.67
339 | 2008-09-15 | 20000 | 0 | 330.3 | 7.3 | -65.4 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | 0 | -0.04 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.67
340 | 2008-09-15 | 30000 | 0 | 326.6 | 7.4 | -61 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.7 | 0 | -0.03 | 0 | 0.02 | 0.3 | 0.003 | 0 | 20.67
341 | 2008-09-15 | 40000 | 0 | 323 | 7.4 | -67.4 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.67
342 | 2008-09-15 | 50000 | 0 | 319.1 | 6.4 | -73.3 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.67
343 | 2008-09-15 | 60000 | 0 | 304.9 | 6.9 | -74.2 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0 | 0 | 0.003 | 0 | 20.68
344 | 2008-09-15 | 70000 | 0 | 291.7 | 7.3 | -78.8 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.6 | 0 | -0.02 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.68
345 | 2008-09-15 | 80000 | 0 | 283.2 | 8.9 | -77.5 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.7 | 0 | -0.02 | 0.1 | 0.02 | 0.3 | 0.003 | 0 | 20.68
346 | 2008-09-15 | 90000 | 0 | 276.7 | 9.4 | -72.7 | 0.05 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.7 | 0 | 2.1 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.61
347 | 2008-09-15 | 100000 | 0 | 271.6 | 9.2 | -65 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.7 | 0 | -0.02 | 0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.69
348 | 2008-09-15 | 110000 | 0 | 267.1 | 8.7 | -73.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.8 | 0 | -0.03 | 0.1 | 0.02 | 0.5 | 0.004 | 0.001 | 20.68
349 | 2008-09-15 | 120000 | 0 | 264.4 | 8.5 | -61.5 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.8 | 0.02 | 0 | 0.5 | 0.03 | 0.8 | 0.004 | 0.002 | 20.67
350 | 2008-09-15 | 130000 | 0 | 261.3 | 7.9 | -82.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.7 | 0.01 | -0.01 | 0.2 | 0.02 | 0.4 | 0.003 | 0.001 | 20.65
351 | 2008-09-15 | 140000 | 0 | 258.5 | 7 | -66.2 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.9 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.64
352 | 2008-09-15 | 150000 | 0 | 255.9 | 6.3 | -58.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -666 | -888 | 0.8 | -0.01 | -0.02 | -0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.62
353 | 2008-09-15 | 160000 | 0 | 253.2 | 5.8 | -52.4 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | -666 | -888 | 0.9 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.002 | 0 | 20.61
354 | 2008-09-15 | 170000 | 0 | 254.3 | 7.6 | -56.2 | 0.08 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 1 | 0.05 | 0.24 | 0.1 | 0.06 | 0.4 | 0.003 | 0.001 | 20.59
355 | 2008-09-15 | 180000 | 1 | 508.3 | 25.1 | 91.1 | 7.46 | 24 | 24.3 | -0.051 | 0 | -666 | -888 | 0.8 | 10.25 | 29.29 | 12.8 | 39.88 | 49 | 0.181 | 0.047 | 16.14
356 | 2008-09-15 | 190000 | 1 | 619.5 | 13.4 | 13.4 | 11.81 | 68.9 | 88.8 | -0.051 | 0 | -666 | -888 | 38.6 | 7.99 | 24.77 | 7.6 | 39.87 | 38.2 | 0.141 | 0.028 | 14.47
357 | 2008-09-15 | 200000 | 1 | 670.4 | 2.5 | 21.7 | 21.28 | 171.6 | 261.6 | 0.13 | 1 | -159.8 | -888 | 133.6 | 3.54 | 12.35 | 2.2 | 9.55 | 4 | 0.015 | 0.008 | 11.64
358 | 2008-09-15 | 210000 | 1 | 659.8 | 0.2 | -2.4 | 20.95 | 169 | 253 | -0.048 | 0 | -654.9 | -888 | 107.4 | 2.42 | 10.5 | 1.9 | 2.25 | 1.8 | 0.007 | 0.007 | 13.56
359 | 2008-09-15 | 220000 | 1 | 647.5 | 0.2 | -2.1 | 19.48 | 154.9 | 233.2 | -0.051 | 0 | -666 | -888 | 88.9 | 2.5 | 9.35 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.68
360 | 2008-09-15 | 230000 | 1 | 654.5 | 0.2 | -2.4 | 19.4 | 154.8 | 233.2 | -0.051 | 0 | -666 | -888 | 89.2 | 2.47 | 9.36 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.65
361 | 2008-09-16 | 0 | 1 | 655.5 | 0.2 | -2 | 19.46 | 155.5 | 234 | -0.046 | 0 | -666 | -888 | 91.8 | 2.49 | 9.5 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.65
362 | 2008-09-16 | 10000 | 1 | 655.6 | 0.2 | -2.5 | 19.39 | 155.2 | 233 | -0.045 | 0 | -666 | -888 | 93.5 | 2.47 | 9.63 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.65
363 | 2008-09-16 | 20000 | 1 | 655.1 | 0.2 | -1.9 | 19.35 | 154 | 232.3 | -0.046 | 0 | -666 | -888 | 92 | 2.48 | 9.61 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.64
364 | 2008-09-16 | 30000 | 1 | 655.1 | 0.2 | -2.6 | 19.38 | 155.3 | 233.4 | -0.047 | 0 | -666 | -888 | 91.7 | 2.47 | 9.62 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.64
365 | 2008-09-16 | 40000 | 1 | 655.6 | 0.2 | -2.2 | 19.35 | 155 | 233.2 | -0.047 | 0 | -666 | -888 | 92.1 | 2.49 | 9.63 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.63
366 | 2008-09-16 | 50000 | 1 | 655.5 | 0.2 | -2.5 | 19.39 | 155.3 | 233.4 | -0.048 | 0 | -666 | -888 | 92.4 | 2.48 | 9.66 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.63
367 | 2008-09-16 | 60000 | 1 | 668 | 0.2 | -2.7 | 21.33 | 173.8 | 256.9 | -0.047 | 0 | -142.2 | -888 | 111.9 | 2.43 | 10.39 | 2 | 2.26 | 1.8 | 0.007 | 0.007 | 13.64
368 | 2008-09-16 | 70000 | 1 | 668.5 | 0.2 | -2.4 | 21.14 | 172 | 255.3 | -0.046 | 0 | 14.2 | -888 | 107.2 | 2.46 | 10.12 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.71
369 | 2008-09-16 | 80000 | 1 | 669.8 | 0.2 | -2.3 | 21.06 | 170.9 | 254.1 | -0.046 | 0 | 14 | -888 | 105 | 2.47 | 10.05 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.67
370 | 2008-09-16 | 90000 | 1 | 668.2 | 1.6 | 13.2 | 21.08 | 170.8 | 254.9 | -0.046 | 0 | 11.9 | -888 | 109.2 | 3.35 | 10.7 | 2 | 8.15 | 3.2 | 0.012 | 0.007 | 12.21
371 | 2008-09-16 | 100000 | 1 | 664.8 | 1 | 3.9 | 21.01 | 170 | 254.6 | -0.055 | 0 | 2.3 | -888 | 114.6 | 2.61 | 10.81 | 2.1 | 3.82 | 2.3 | 0.009 | 0.008 | 13.43
372 | 2008-09-16 | 110000 | 1 | 662.5 | 0.2 | -2.3 | 20.99 | 169.3 | 254.1 | -0.055 | 0 | 2.2 | -888 | 126.2 | 2.56 | 11.75 | 2 | 2.4 | 1.9 | 0.007 | 0.008 | 13.52
373 | 2008-09-16 | 120000 | 1 | 660.9 | 0.2 | -2.3 | 20.85 | 167.6 | 252.7 | -0.055 | 0 | 2.2 | -888 | 123.5 | 2.49 | 11.51 | 2 | 2.32 | 1.8 | 0.007 | 0.007 | 13.51
374 | 2008-09-16 | 130000 | 1 | 663.5 | 0.2 | -2 | 21.18 | 170.9 | 255.7 | -0.048 | 0 | 1.9 | -888 | 112 | 2.54 | 10.85 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.46
375 | 2008-09-16 | 140000 | 1 | 662.9 | 0.2 | -2.1 | 21.17 | 170.8 | 256 | -0.049 | 0 | 2.1 | -888 | 117.5 | 2.55 | 11.23 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.4
376 | 2008-09-16 | 150000 | 1 | 662.2 | 0.2 | -2.1 | 21.06 | 169.5 | 254.1 | -0.047 | 0 | 2 | -888 | 114.1 | 2.56 | 11.04 | 2 | 2.4 | 1.9 | 0.007 | 0.007 | 13.38
377 | 2008-09-16 | 160000 | 1 | 661.5 | 0.2 | -2.3 | 21.06 | 169.8 | 254.2 | -0.046 | 0 | 2 | -888 | 114.2 | 2.56 | 11.01 | 2 | 2.41 | 1.9 | 0.007 | 0.007 | 13.39
378 | 2008-09-16 | 170000 | 1 | 662.2 | 0.2 | -1.9 | 21.11 | 170.7 | 255 | -0.046 | 0 | 2 | -888 | 114.5 | 2.52 | 10.93 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.42
379 | 2008-09-16 | 180000 | 1 | 663.3 | 0.2 | -2.5 | 21.11 | 171.3 | 255.7 | -0.047 | 0 | 1.9 | -888 | 108.4 | 2.53 | 10.49 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.47
380 | 2008-09-16 | 190000 | 1 | 664.3 | 0.2 | -2 | 21.15 | 171.8 | 255.8 | -0.048 | 0 | 1.8 | -888 | 106.7 | 2.51 | 10.27 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.54
381 | 2008-09-16 | 200000 | 1 | 665.9 | 0.2 | -2.4 | 21.25 | 172.5 | 256.6 | -0.047 | 0 | 1.8 | -888 | 109.2 | 2.51 | 10.39 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.58
382 | 2008-09-16 | 210000 | 1 | 666.5 | 0.2 | -2.1 | 21.03 | 170.8 | 254.2 | -0.049 | 0 | 1.8 | -888 | 106.5 | 2.46 | 10.25 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.64
383 | 2008-09-16 | 220000 | 1 | 654.6 | 0.2 | -2 | 19.36 | 154.7 | 232.2 | -0.048 | 0 | 1.7 | -888 | 93.7 | 2.51 | 9.75 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.65
384 | 2008-09-16 | 230000 | 1 | 653.8 | 0.2 | -2.2 | 19.32 | 153.6 | 231 | -0.048 | 0 | 1.7 | -888 | 92.9 | 2.47 | 9.82 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.65
385 | 2008-09-17 | 0 | 0 | 558.3 | 18.1 | -23.5 | 1.67 | 7.3 | 14.3 | -0.048 | 0 | 7.5 | -888 | 22.2 | 1.93 | 5.87 | 2.6 | 7.19 | 8.1 | 0.031 | 0.01 | 19.41
386 | 2008-09-17 | 10000 | 0 | 438.9 | 6.4 | -51 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 8.5 | -888 | 0.7 | -0.01 | 0.04 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.62
387 | 2008-09-17 | 20000 | 0 | 416.1 | 5.9 | -66.7 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 8.5 | -888 | 0.6 | -0.01 | 0 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.62
388 | 2008-09-17 | 30000 | 0 | 416.5 | 5.1 | -59.7 | 0.05 | 0.5 | 1.3 | -0.048 | 0 | 8.3 | -888 | 0.6 | -0.01 | -0.02 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.61
389 | 2008-09-17 | 40000 | 1 | 576 | 19.7 | 13.8 | 8.49 | 36.7 | 37.9 | -0.049 | 0 | 3.2 | -888 | 13.4 | 9.06 | 27.37 | 11 | 42.44 | 48.8 | 0.18 | 0.041 | 15.95
390 | 2008-09-17 | 50000 | 1 | 622.9 | 0.4 | -2.2 | 16.12 | 118.2 | 172.1 | -0.049 | 0 | 1.6 | -888 | 78.2 | 2.34 | 10.37 | 1.9 | 2.18 | 1.8 | 0.007 | 0.007 | 13.66
391 | 2008-09-17 | 60000 | 1 | 650.1 | 0.2 | -2.3 | 21.53 | 176 | 260.3 | -0.049 | 0 | 2.1 | -888 | 126.4 | 2.3 | 11.29 | 1.9 | 2.15 | 1.7 | 0.006 | 0.007 | 13.56
392 | 2008-09-17 | 70000 | 1 | 660.9 | 2.6 | 21.2 | 21.23 | 172.9 | 256 | -0.049 | 0 | 3.8 | -888 | 110.6 | 3.48 | 10.72 | 2.1 | 9.54 | 3.8 | 0.014 | 0.008 | 12.11
393 | 2008-09-17 | 80000 | 1 | 667.7 | 0.2 | -2.4 | 21.2 | 172.5 | 256.3 | -0.049 | 0 | 1.9 | -888 | 111.9 | 2.45 | 10.44 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.72
394 | 2008-09-17 | 90000 | 1 | 666.8 | 0.2 | -2.3 | 21.08 | 171.1 | 254.2 | -0.048 | 0 | 1.8 | -888 | 109.1 | 2.43 | 10.63 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.76
395 | 2008-09-17 | 100000 | 1 | 668 | 0.2 | -2.2 | 21.12 | 171.9 | 255.5 | -0.048 | 0 | 1.8 | -888 | 108.7 | 2.44 | 10.26 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.72
396 | 2008-09-17 | 110000 | 1 | 668.2 | 0.2 | -2.2 | 21.16 | 172.4 | 256.5 | -0.048 | 0 | 1.8 | -888 | 108.8 | 2.46 | 10.34 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.68
397 | 2008-09-17 | 120000 | 1 | 667.9 | 0.2 | -2.4 | 21.12 | 171.8 | 255.8 | -0.052 | 0 | 1.8 | -888 | 109.3 | 2.46 | 10.39 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.66
398 | 2008-09-17 | 130000 | 1 | 667 | 0.2 | -2.2 | 21.13 | 171.5 | 255.7 | -0.05 | 0 | 1.9 | -888 | 111.5 | 2.5 | 10.56 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.64
399 | 2008-09-17 | 140000 | 1 | 665.4 | 0.2 | -2.3 | 21.15 | 171.8 | 256.4 | -0.052 | 0 | 1.9 | -888 | 112.4 | 2.48 | 10.71 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.6
400 | 2008-09-17 | 150000 | 1 | 664.9 | 0.2 | -2 | 21.07 | 171.4 | 255.9 | -0.051 | 0 | 1.9 | -888 | 111.9 | 2.48 | 10.68 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.61
401 | 2008-09-17 | 160000 | 1 | 665 | 0.2 | -2 | 21.06 | 171 | 254.5 | -0.052 | 0 | 1.8 | -888 | 108.1 | 2.46 | 10.38 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.66
402 | 2008-09-17 | 170000 | 1 | 666.1 | 0.2 | -2.3 | 21.06 | 171.1 | 254.4 | -0.052 | 0 | 1.8 | -888 | 107.4 | 2.45 | 10.25 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.72
403 | 2008-09-17 | 180000 | 1 | 667.1 | 0.2 | -2.1 | 21.19 | 172.1 | 255.7 | -0.052 | 0 | 1.8 | -888 | 109.5 | 2.45 | 10.39 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.71
404 | 2008-09-17 | 190000 | 1 | 666.7 | 0.2 | -2.1 | 21.12 | 171.8 | 255 | -0.054 | 0 | 1.8 | -888 | 108.2 | 2.45 | 10.29 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.72
405 | 2008-09-17 | 200000 | 1 | 667.5 | 0.2 | -2.2 | 21.17 | 172.4 | 254 | -0.053 | 0 | 1.8 | -888 | 109.2 | 2.46 | 10.38 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.72
406 | 2008-09-17 | 210000 | 1 | 668 | 0.2 | -2.2 | 21.07 | 171.1 | 254.7 | -0.054 | 0 | 1.8 | -888 | 107.6 | 2.43 | 10.37 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.71
407 | 2008-09-17 | 220000 | 0 | 566.5 | 20.2 | -28.4 | 2.34 | 11.6 | 22 | -0.053 | 0 | 0.5 | -888 | 4.2 | 2.47 | 6.63 | 4.3 | 8.41 | 10.7 | 0.04 | 0.016 | 19.14
408 | 2008-09-17 | 230000 | 0 | 444 | 9.2 | -78.9 | 0.04 | 0.5 | 1.3 | -0.054 | 0 | 0 | -888 | 0.7 | -0.01 | 0.04 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.67
409 | 2008-09-18 | 0 | 0 | 422.1 | 8.6 | -85.4 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | 0 | -888 | 0.8 | -0.01 | 0 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.68
410 | 2008-09-18 | 10000 | 0 | 411.2 | 8.6 | -79.5 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.6 | -0.01 | -0.01 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.67
411 | 2008-09-18 | 20000 | 0 | 402.8 | 8.2 | -70.2 | 0.04 | 0.5 | 1.2 | -0.053 | 0 | 0 | -888 | 0.6 | -0.01 | -0.02 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.67
412 | 2008-09-18 | 30000 | 0 | 398.1 | 8.5 | -66.9 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.7 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.67
413 | 2008-09-18 | 40000 | 0 | 393.4 | 8.3 | -72.7 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.7 | 0 | -0.03 | -0.1 | 0.02 | 0.4 | 0.003 | 0 | 20.67
414 | 2008-09-18 | 50000 | 0 | 388 | 8.4 | -73.6 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | 0 | -888 | 0.7 | -0.01 | -0.04 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.67
415 | 2008-09-18 | 60000 | 0 | 383.1 | 8.4 | -62.4 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.8 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.67
416 | 2008-09-18 | 70000 | 0 | 377.5 | 9.5 | -75.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.68
417 | 2008-09-18 | 80000 | 0 | 363.1 | 9.8 | -80.3 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.02 | 0.4 | 0.004 | 0 | 20.68
418 | 2008-09-18 | 90000 | 0 | 350.2 | 10.3 | -85.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 0 | -888 | 0.5 | 0 | 2.02 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.69
419 | 2008-09-18 | 100000 | 0 | 341.8 | 10.4 | -77.4 | 0.04 | 0.5 | 1.2 | -0.053 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.7
420 | 2008-09-18 | 110000 | 0 | 336.1 | 10.2 | -74.2 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.62
421 | 2008-09-18 | 120000 | 0 | 331.3 | 10 | -80.6 | 0.03 | 0.5 | 1.2 | -0.053 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.69
422 | 2008-09-18 | 130000 | 0 | 327.5 | 9.7 | -91 | 0.03 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.69
423 | 2008-09-18 | 140000 | 0 | 324.1 | 9.1 | -74.8 | 0.03 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.5 | -0.01 | -0.04 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.61
424 | 2008-09-18 | 150000 | 0 | 320.7 | 8.8 | -76.2 | 0.03 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.68
425 | 2008-09-18 | 160000 | 0 | 317.5 | 8.3 | -75 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.02 | 0.4 | 0.003 | 0 | 20.67
426 | 2008-09-18 | 170000 | 0 | 314.1 | 8 | -69.6 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.67
427 | 2008-09-18 | 180000 | 0 | 310.9 | 8.3 | -62.1 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.67
428 | 2008-09-18 | 190000 | 0 | 307.6 | 8.3 | -67.9 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.02 | 0.3 | 0.003 | 0 | 20.66
429 | 2008-09-18 | 200000 | 0 | 304.5 | 8.4 | -68.5 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.67
430 | 2008-09-18 | 210000 | 0 | 301.7 | 8.2 | -70.7 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.66
431 | 2008-09-18 | 220000 | 0 | 298.8 | 8 | -64 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.66
432 | 2008-09-18 | 230000 | 0 | 295.8 | 7.9 | -66.3 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.02 | 0.5 | 0.003 | 0 | 20.66
433 | 2008-09-19 | 0 | 0 | 292.6 | 8 | -66.3 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.1 | 0.002 | 0 | 20.66
434 | 2008-09-19 | 10000 | 0 | 289.3 | 7.8 | -73.1 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.02 | 0.3 | 0.003 | 0 | 20.66
435 | 2008-09-19 | 20000 | 0 | 285.9 | 7.5 | -72.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.1 | 0.002 | 0 | 20.65
436 | 2008-09-19 | 30000 | 0 | 282.4 | 7.6 | -63.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.65
437 | 2008-09-19 | 40000 | 0 | 279.1 | 7.3 | -68.8 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.65
438 | 2008-09-19 | 50000 | 0 | 275.8 | 7.7 | -63.4 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.65
439 | 2008-09-19 | 60000 | 0 | 273 | 8 | -62.7 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.65
440 | 2008-09-19 | 70000 | 0 | 269.1 | 8.1 | -65.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | -0.02 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.66
441 | 2008-09-19 | 80000 | 0 | 265.9 | 8.6 | -67.8 | 0.04 | 0.6 | 1.3 | -0.047 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.02 | 0.3 | 0.003 | 0 | 20.66
442 | 2008-09-19 | 90000 | 0 | 262.9 | 8.7 | -70.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | -0.01 | 2.09 | -0.2 | 0.02 | 0.5 | 0.003 | 0 | 20.66
443 | 2008-09-19 | 100000 | 0 | 260.1 | 8.2 | -68.2 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.66
444 | 2008-09-19 | 110000 | 0 | 256.9 | 8.3 | -65.5 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.66
445 | 2008-09-19 | 120000 | 0 | 253.8 | 7.9 | -68.2 | 0.08 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.66
446 | 2008-09-19 | 130000 | 0 | 251.2 | 8 | -60.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.65
447 | 2008-09-19 | 140000 | 0 | 248.1 | 7.7 | -63.9 | 0.18 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.64
448 | 2008-09-19 | 150000 | 0 | 245.7 | 7.3 | -57.7 | 0.26 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.63
449 | 2008-09-19 | 160000 | 0 | 243.2 | 7.7 | -56.3 | 0.25 | 0.5 | 1.3 | -0.052 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.02 | 0.5 | 0.003 | 0 | 20.64
450 | 2008-09-19 | 170000 | 0 | 240.5 | 8.3 | -69.1 | 0.21 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.02 | 0.4 | 0.003 | 0 | 20.66
451 | 2008-09-19 | 180000 | 0 | 237.3 | 8.6 | -65.8 | 0.04 | 0.5 | 1.2 | -0.051 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.66
452 | 2008-09-19 | 190000 | 0 | 234.5 | 8.5 | -66.8 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.66
453 | 2008-09-19 | 200000 | 0 | 231.7 | 9.1 | -68.4 | 0.04 | 0.5 | 1.2 | -0.054 | 0 | 0 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.02 | 0.5 | 0.003 | 0 | 20.68
454 | 2008-09-19 | 210000 | 0 | 228.9 | 9.3 | -81 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.68
455 | 2008-09-19 | 220000 | 0 | 226.3 | 9.1 | -85 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.01 | 0.4 | 0.004 | 0 | 20.68
456 | 2008-09-19 | 230000 | 0 | 223.5 | 9 | -67.8 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.2 | 0.003 | 0 | 20.68
457 | 2008-09-20 | 0 | 0 | 221 | 9.1 | -77.9 | 0.04 | 0.5 | 1.3 | -0.053 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.003 | 0 | 20.69
458 | 2008-09-20 | 10000 | 0 | 218.5 | 9.3 | -77.4 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.003 | 0 | 20.69
459 | 2008-09-20 | 20000 | 0 | 216 | 9.5 | -69.3 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.003 | 0 | 20.69
460 | 2008-09-20 | 30000 | 0 | 213.7 | 9.4 | -75.7 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | 0 | -888 | 0.4 | -0.01 | -0.04 | -0.3 | 0.01 | 0.2 | 0.003 | 0 | 20.69
461 | 2008-09-20 | 40000 | 0 | 208.4 | 9 | -71.6 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.68
462 | 2008-09-20 | 50000 | 0 | 200.6 | 9.1 | -72.6 | 0.04 | 0.5 | 1.2 | -0.05 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.003 | 0 | 20.68
463 | 2008-09-20 | 60000 | 0 | 194.5 | 9.2 | -83.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.69
464 | 2008-09-20 | 70000 | 0 | 190.5 | 9.5 | -79.6 | 0.04 | 0.5 | 1.2 | -0.051 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.69
465 | 2008-09-20 | 80000 | 0 | 187.2 | 9.7 | -80.6 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.7
466 | 2008-09-20 | 90000 | 0 | 184.5 | 10.2 | -77.5 | 0.04 | 0.5 | 1.2 | -0.05 | 0 | 0 | -888 | 0.4 | -0.01 | 2.11 | -0.2 | 0.02 | 0.4 | 0.004 | 0 | 20.7
467 | 2008-09-20 | 100000 | 0 | 181.9 | 10.4 | -94.3 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.71
468 | 2008-09-20 | 110000 | 0 | 179.8 | 10.8 | -79.2 | 0.04 | 0.5 | 1.2 | -0.051 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.01 | 0.4 | 0.004 | 0 | 20.64
469 | 2008-09-20 | 120000 | 0 | 177.7 | 10.8 | -89.3 | 0.04 | 0.5 | 1.2 | -0.053 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.02 | 0.6 | 0.004 | 0 | 20.64
470 | 2008-09-20 | 130000 | 0 | 175.8 | 11 | -96.9 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.02 | 0.5 | 0.004 | 0 | 20.71
471 | 2008-09-20 | 140000 | 0 | 174 | 11.2 | -90.5 | 0.04 | 0.5 | 1.2 | -0.051 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.02 | 0.6 | 0.004 | 0 | 20.72
472 | 2008-09-20 | 150000 | 0 | 172.1 | 11.1 | -91.7 | 0.04 | 0.5 | 1.2 | -0.052 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.1 | 0.003 | 0 | 20.72
473 | 2008-09-20 | 160000 | 0 | 170.1 | 11.7 | -103 | 0.04 | 0.5 | 1.2 | -0.051 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.01 | 0.5 | 0.004 | 0 | 20.72
474 | 2008-09-20 | 170000 | 0 | 168.5 | 10.9 | -93.8 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.003 | 0 | 20.72
475 | 2008-09-20 | 180000 | 0 | 166.7 | 10.2 | -82.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.3 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.003 | 0 | 20.71
476 | 2008-09-20 | 190000 | 0 | 165.4 | 10 | -90.9 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.71
477 | 2008-09-20 | 200000 | 0 | 163.5 | 10 | -85.9 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.71
478 | 2008-09-20 | 210000 | 0 | 161.7 | 9.9 | -82.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.003 | 0 | 20.71
479 | 2008-09-20 | 220000 | 0 | 160.3 | 9.9 | -87.3 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.5 | -0.01 | -0.03 | -0.3 | 0.01 | 0.3 | 0.003 | 0 | 20.71
480 | 2008-09-20 | 230000 | 0 | 158.7 | 9.7 | -90.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.3 | 0 | 0.1 | 0.003 | 0 | 20.71
481 | 2008-09-21 | 0 | 0 | 156.7 | 9.1 | -88.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 0 | -888 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.1 | 0.003 | 0 | 20.63
482 | 2008-09-21 | 10000 | 1 | 386.3 | 26.5 | 81.8 | 6.24 | 16 | 16.4 | -0.048 | 0 | 2.3 | -888 | 0.4 | 9.25 | 26.54 | 13.3 | 40.13 | 56.9 | 0.21 | 0.049 | 17.12
483 | 2008-09-21 | 20000 | 1 | 598.4 | 20.8 | 10.6 | 6.95 | 19.3 | 19.7 | -0.048 | 0 | 2.8 | -888 | 4.5 | 10.26 | 30.02 | 14.6 | 46.32 | 65.7 | 0.242 | 0.054 | 16.74
484 | 2008-09-21 | 30000 | 1 | 609.1 | 20.6 | 27.7 | 9.68 | 44.9 | 45.8 | -0.047 | 0 | 5.2 | -888 | 23.5 | 10.29 | 30.01 | 10.6 | 55.43 | 56.6 | 0.209 | 0.039 | 15.14
485 | 2008-09-21 | 40000 | 1 | 606.3 | 19.9 | 33 | 9.93 | 47.7 | 78.9 | -0.048 | 0 | 5.4 | -888 | 27.8 | 10.29 | 30.02 | 10.4 | 55.62 | 55.9 | 0.206 | 0.038 | 15.04
486 | 2008-09-21 | 50000 | 1 | 625.4 | 3 | 19.3 | 17.43 | 133.6 | 202.6 | -0.048 | 0 | 4.4 | -888 | 98.4 | 3.41 | 10.94 | 2.1 | 10.89 | 5.1 | 0.019 | 0.008 | 12.09
487 | 2008-09-21 | 60000 | 1 | 639 | 0.5 | -2.9 | 19.72 | 158.8 | 236.4 | -0.047 | 0 | 1.7 | -888 | 95.7 | 2.19 | 9.6 | 1.8 | 2.04 | 1.7 | 0.006 | 0.007 | 13.76
488 | 2008-09-21 | 70000 | 1 | 643.5 | 0.3 | -2.4 | 19.76 | 158.7 | 236.8 | -0.049 | 0 | 1.7 | -888 | 94.3 | 2.47 | 9.63 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.7
489 | 2008-09-21 | 80000 | 1 | 652.1 | 0.3 | -2.1 | 19.71 | 158.2 | 236.2 | -0.048 | 0 | 1.7 | -888 | 97.1 | 2.45 | 9.93 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.71
490 | 2008-09-21 | 90000 | 1 | 656.7 | 0.3 | -1.8 | 19.77 | 158.6 | 236.9 | -0.05 | 0 | 1.7 | -888 | 97.2 | 2.44 | 10.36 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.71
491 | 2008-09-21 | 100000 | 1 | 656.7 | 0.3 | -2.4 | 19.7 | 158.1 | 236.2 | -0.047 | 0 | 1.7 | -888 | 96.7 | 2.46 | 9.87 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.71
492 | 2008-09-21 | 110000 | 1 | 656.7 | 0.3 | -1.9 | 19.75 | 158.2 | 236.6 | -0.047 | 0 | 1.7 | -888 | 97.1 | 2.44 | 9.89 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.71
493 | 2008-09-21 | 120000 | 1 | 656.6 | 0.3 | -2.4 | 19.79 | 158.3 | 236.8 | -0.048 | 0 | 1.7 | -888 | 97.2 | 2.45 | 9.85 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.72
494 | 2008-09-21 | 130000 | 1 | 656.5 | 0.3 | -2.3 | 19.8 | 158.3 | 236.9 | -0.047 | 0 | 1.7 | -888 | 96.1 | 2.42 | 9.77 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.74
495 | 2008-09-21 | 140000 | 1 | 656.2 | 0.3 | -2.2 | 19.79 | 158.1 | 236.6 | -0.049 | 0 | 1.6 | -888 | 93.2 | 2.46 | 9.68 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.75
496 | 2008-09-21 | 150000 | 1 | 655.4 | 0.3 | -2.4 | 19.61 | 156.8 | 235.1 | -0.048 | 0 | 1.7 | -888 | 95.5 | 2.44 | 9.79 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
497 | 2008-09-21 | 160000 | 1 | 654.2 | 0.3 | -2.4 | 19.62 | 156.8 | 235 | -0.048 | 0 | 1.7 | -888 | 95.5 | 2.45 | 9.8 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.75
498 | 2008-09-21 | 170000 | 1 | 654 | 0.3 | -2.3 | 19.61 | 157 | 235.2 | -0.049 | 0 | 1.7 | -888 | 95.7 | 2.43 | 9.79 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.75
499 | 2008-09-21 | 180000 | 1 | 653.7 | 0.3 | -2.4 | 19.55 | 156.3 | 234.4 | -0.049 | 0 | 1.7 | -888 | 94.9 | 2.44 | 9.78 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.75
500 | 2008-09-21 | 190000 | 1 | 653.6 | 0.3 | -2.1 | 19.58 | 156.3 | 234.2 | -0.049 | 0 | 1.7 | -888 | 95 | 2.44 | 9.78 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.74
501 | 2008-09-21 | 200000 | 1 | 653.6 | 0.3 | -2.1 | 19.58 | 156.3 | 234.2 | -0.05 | 0 | 1.7 | -888 | 95.5 | 2.44 | 9.84 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
502 | 2008-09-21 | 210000 | 1 | 653.5 | 0.3 | -2.3 | 19.28 | 153.1 | 230.6 | -0.05 | 0 | 1.6 | -888 | 92.3 | 2.46 | 9.85 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.75
503 | 2008-09-21 | 220000 | 0 | 552 | 24.5 | -54.2 | 1.33 | 5.6 | 11 | -0.051 | 0 | 18.6 | -888 | 2.4 | 1.71 | 5.12 | 2.6 | 6.8 | 8.1 | 0.031 | 0.01 | 19.72
504 | 2008-09-21 | 230000 | 0 | 439.5 | 13.7 | -104.3 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.7 | -0.01 | 0.02 | -0.2 | 0 | 0 | 0.004 | 0 | 20.75
505 | 2008-09-22 | 0 | 0 | 421.1 | 14 | -108.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.7 | -0.01 | 0 | -0.3 | 0.01 | 0.2 | 0.004 | 0 | 20.75
506 | 2008-09-22 | 10000 | 0 | 411.5 | 15.4 | -121.5 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.7 | -0.01 | 0 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.76
507 | 2008-09-22 | 20000 | 0 | 403.1 | 16.1 | -142 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.6 | -0.01 | 0 | -0.3 | 0.01 | 0.4 | 0.005 | 0 | 20.77
508 | 2008-09-22 | 30000 | 0 | 398.4 | 16.3 | -142.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.7 | -0.01 | -0.02 | -0.3 | 0.01 | 0.3 | 0.006 | 0 | 20.78
509 | 2008-09-22 | 40000 | 0 | 393.8 | 16.4 | -131.2 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.7 | -0.01 | -0.02 | -0.4 | 0.01 | 0.5 | 0.006 | 0 | 20.78
510 | 2008-09-22 | 50000 | 0 | 388.7 | 16.8 | -152.5 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.7 | -0.01 | -0.03 | -0.4 | 0.02 | 0.8 | 0.006 | 0 | 20.78
511 | 2008-09-22 | 60000 | 0 | 383.6 | 18.6 | -162.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.6 | -0.01 | -0.03 | -0.4 | 0.01 | 0.6 | 0.007 | 0 | 20.79
512 | 2008-09-22 | 70000 | 0 | 378.4 | 22.2 | -157.1 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.04 | -0.3 | 0.01 | 0.2 | 0.006 | 0 | 20.73
513 | 2008-09-22 | 80000 | 0 | 369 | 27.4 | -189.9 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.3 | 0 | -0.02 | 0 | 0.01 | 0.7 | 0.008 | 0 | 20.81
514 | 2008-09-22 | 90000 | 0 | 354.9 | 30.8 | -248 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.4 | 0 | 2.09 | -0.2 | 0.02 | 1.4 | 0.011 | 0 | 20.82
515 | 2008-09-22 | 100000 | 0 | 345 | 32.3 | -249 | 0.09 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -0.7 | 0.01 | 0.9 | 0.01 | 0 | 20.83
516 | 2008-09-22 | 110000 | 0 | 337.8 | 37.4 | -344.3 | 0.08 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -0.9 | 0.01 | 0.9 | 0.012 | 0 | 20.84
517 | 2008-09-22 | 120000 | 0 | 332.4 | 46.6 | -393 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.3 | -0.01 | -0.03 | -1.4 | 0.02 | 3.4 | 0.021 | 0 | 20.78
518 | 2008-09-22 | 130000 | 0 | 328 | 44.2 | -373.7 | 0.23 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -1.3 | 0.01 | 2.3 | 0.018 | 0 | 20.77
519 | 2008-09-22 | 140000 | 0 | 322.8 | 38.2 | -260.5 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.3 | -0.01 | -0.04 | -1 | 0.01 | 1 | 0.013 | 0 | 20.84
520 | 2008-09-22 | 150000 | 0 | 310.4 | 38.1 | -345.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -1 | 0.01 | 0.8 | 0.012 | 0 | 20.84
521 | 2008-09-22 | 160000 | 0 | 296.7 | 38.6 | -330 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -1 | 0.01 | 1 | 0.012 | 0 | 20.84
522 | 2008-09-22 | 170000 | 0 | 279.1 | 39.3 | -337.1 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -1.1 | 0.01 | 1.2 | 0.014 | 0 | 20.84
523 | 2008-09-22 | 180000 | 0 | 239.4 | 41.1 | -400.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.02 | -1.3 | 0.01 | 1.5 | 0.015 | 0 | 20.85
524 | 2008-09-22 | 190000 | 0 | 208.1 | 45.9 | -341.1 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -1.3 | 0.02 | 1.7 | 7.929 | 0 | 20.85
525 | 2008-09-22 | 200000 | 0 | 186.1 | 56.3 | -475.5 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -1.5 | 0.02 | 2.9 | 36.426 | 0 | 20.86
526 | 2008-09-22 | 210000 | 0 | 172.7 | 63.5 | -540.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -1.8 | 0.01 | 1.5 | 74.411 | 0 | 20.87
527 | 2008-09-22 | 220000 | 0 | 159.9 | 66.6 | -614 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -1.7 | 0 | 0.6 | 39.589 | 0 | 20.87
528 | 2008-09-22 | 230000 | 0 | 149.6 | 62.9 | -526.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.3 | -0.01 | -0.03 | -1.1 | 0.01 | 0.5 | 72.823 | 1.583 | 20.79
529 | 2008-09-23 | 0 | 0 | 141.6 | 67.9 | -528.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.3 | -0.01 | -0.04 | -1.3 | 0.01 | 1.7 | 55.417 | 0 | 20.86
530 | 2008-09-23 | 10000 | 0 | 135.3 | 59 | -509.6 | 0.12 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -1.4 | 0.02 | 2 | 44.337 | 1.583 | 20.79
531 | 2008-09-23 | 20000 | 0 | 128.7 | 56.4 | -516.8 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.3 | -0.01 | -0.03 | -1.1 | 0.01 | 1.2 | 7.931 | 0 | 20.86
532 | 2008-09-23 | 30000 | 0 | 123.2 | 41.7 | -313.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.9 | 0.01 | 1.4 | 0.014 | 0 | 20.85
533 | 2008-09-23 | 40000 | 0 | 118.2 | 36.2 | -270.9 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.7 | 0.01 | 1.1 | 0.012 | 0 | 20.84
534 | 2008-09-23 | 50000 | 0 | 111.8 | 34.8 | -249.7 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -0.6 | 0.01 | 0.5 | 0.011 | 0 | 20.84
535 | 2008-09-23 | 60000 | 0 | 105.5 | 37.7 | -298.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.7 | 0.01 | 0.4 | 0.01 | 0 | 20.84
536 | 2008-09-23 | 70000 | 0 | 99.7 | 34.3 | -234 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | 0 | -0.04 | 0 | 0.01 | 0.6 | 0.009 | 0 | 20.76
537 | 2008-09-23 | 80000 | 0 | 94.4 | 36.6 | -187.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.5 | 0 | -0.03 | 0.2 | 0.01 | 0.7 | 0.009 | 0.001 | 20.83
538 | 2008-09-23 | 90000 | 0 | 90.6 | 29.2 | -203.5 | 0.06 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.3 | 0.01 | 2.12 | 0.5 | 0.02 | 0.7 | 0.009 | 0.002 | 20.81
539 | 2008-09-23 | 100000 | 0 | 88.1 | 25.7 | -150.6 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0.02 | 0.01 | 1.5 | 0.04 | 2 | 0.01 | 0.006 | 20.8
540 | 2008-09-23 | 110000 | 0 | 86.3 | 18.5 | -141.8 | 0.07 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0 | -0.02 | 0 | 0.01 | 0.6 | 0.005 | 0 | 20.78
541 | 2008-09-23 | 120000 | 0 | 85.3 | 17.4 | -99.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0 | -0.02 | 0.1 | 0.01 | 0.3 | 0.005 | 0.001 | 20.76
542 | 2008-09-23 | 130000 | 0 | 83.8 | 13.9 | -110.4 | 0.09 | 0.6 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.02 | -0.3 | 0.02 | 0.6 | 0.005 | 0 | 20.75
543 | 2008-09-23 | 140000 | 0 | 83.6 | 11.8 | -100.4 | 0.04 | 0.6 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.04 | -0.2 | 0.02 | 0.7 | 0.005 | 0 | 20.73
544 | 2008-09-23 | 150000 | 0 | 82.4 | 10.5 | -86.6 | 0.04 | 0.6 | 1.3 | -0.047 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.71
545 | 2008-09-23 | 160000 | 0 | 82.2 | 9.7 | -77.3 | 0.04 | 0.6 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.02 | 0.5 | 0.004 | 0 | 20.69
546 | 2008-09-23 | 170000 | 0 | 82.1 | 9 | -68.2 | 0.04 | 0.6 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.68
547 | 2008-09-23 | 180000 | 0 | 82.2 | 9 | -73.8 | 0.04 | 0.6 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.67
548 | 2008-09-23 | 190000 | 0 | 82.2 | 9.2 | -72.6 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.5 | 0 | -0.04 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.66
549 | 2008-09-23 | 200000 | 0 | 82.1 | 9.8 | -68.6 | 0.04 | 0.6 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.66
550 | 2008-09-23 | 210000 | 0 | 80.6 | 10.1 | -71.2 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | 0 | 0.01 | 0.3 | 0.003 | 0 | 20.66
551 | 2008-09-23 | 220000 | 0 | 80.1 | 10.1 | -55 | 0.04 | 0.6 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.3 | 0 | -0.03 | 0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.65
552 | 2008-09-23 | 230000 | 0 | 79.8 | 11 | -62.6 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0.01 | -0.03 | 0.1 | 0.01 | 0.3 | 0.003 | 0.001 | 20.65
553 | 2008-09-24 | 0 | 0 | 78.6 | 11.4 | -63.6 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.5 | 0 | -0.04 | 0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.65
554 | 2008-09-24 | 10000 | 0 | 78.4 | 11.3 | -64.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.64
555 | 2008-09-24 | 20000 | 0 | 77.3 | 11.1 | -62.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | 0 | 0.01 | 0.2 | 0.002 | 0 | 20.64
556 | 2008-09-24 | 30000 | 0 | 76.3 | 10.6 | -64.6 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.3 | 0 | -0.03 | 0 | 0.01 | 0.2 | 0.002 | 0 | 20.64
557 | 2008-09-24 | 40000 | 0 | 76 | 10.3 | -62.1 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.63
558 | 2008-09-24 | 50000 | 0 | 74.7 | 10.2 | -66 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | 0 | 0.01 | 0.2 | 0.002 | 0 | 20.63
559 | 2008-09-24 | 60000 | 0 | 74.7 | 10.5 | -55.8 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | 0 | -0.04 | 0.1 | 0.02 | 0.3 | 0.003 | 0 | 20.62
560 | 2008-09-24 | 70000 | 0 | 74.5 | 11.9 | -59.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | 0.01 | -0.02 | 0.1 | 0.02 | 0.3 | 0.003 | 0.001 | 20.62
561 | 2008-09-24 | 80000 | 0 | 72.8 | 14.2 | -59.5 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.4 | 0.02 | -0.01 | 0.4 | 0.03 | 0.5 | 0.003 | 0.002 | 20.61
562 | 2008-09-24 | 90000 | 0 | 73.8 | 12.8 | -51.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | 0.02 | 2.13 | 0.5 | 0.02 | 0.5 | 0.003 | 0.002 | 20.61
563 | 2008-09-24 | 100000 | 0 | 74.8 | 10.9 | -61 | 0.08 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | 0.01 | -0.01 | 0.2 | 0.01 | 0.2 | 0.002 | 0.001 | 20.62
564 | 2008-09-24 | 110000 | 0 | 74.7 | 10.5 | -57.8 | 0.04 | 0.5 | 1.2 | -0.05 | 0 | 22.8 | -888 | 0.4 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.61
565 | 2008-09-24 | 120000 | 0 | 74.8 | 10.2 | -53 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.5 | 0 | -0.01 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.61
566 | 2008-09-24 | 130000 | 0 | 74.8 | 10 | -57.8 | 0.04 | 0.5 | 1.2 | -0.05 | 0 | 22.8 | -888 | 0.5 | 0 | -0.01 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.61
567 | 2008-09-24 | 140000 | 0 | 74.8 | 9.3 | -50.1 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | 0 | -0.02 | 0.1 | 0.01 | 0.3 | 0.002 | 0 | 20.61
568 | 2008-09-24 | 150000 | 0 | 74.8 | 10.7 | -40.7 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | 0.09 | 0 | 1.7 | 0.09 | 1.7 | 0.007 | 0.006 | 20.6
569 | 2008-09-24 | 160000 | 0 | 74.8 | 9.6 | -53.8 | 0.04 | 0.5 | 1.2 | -0.051 | 0 | 22.8 | -888 | 0.5 | 0.02 | -0.02 | 0.4 | 0.03 | 0.5 | 0.003 | 0.002 | 20.6
570 | 2008-09-24 | 170000 | 0 | 75.4 | 8.6 | -55.5 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | 0.01 | -0.02 | 0.1 | 0.01 | 0.1 | 0.002 | 0.001 | 20.6
571 | 2008-09-24 | 180000 | 0 | 76.4 | 8.7 | -54.9 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0.01 | 0 | 0.1 | 0.01 | 0.2 | 0.002 | 0.001 | 20.59
572 | 2008-09-24 | 190000 | 0 | 76.2 | 8.9 | -56.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.5 | 0 | -0.03 | 0 | 0.01 | 0.2 | 0.002 | 0 | 20.6
573 | 2008-09-24 | 200000 | 0 | 76.4 | 9.3 | -62.3 | 0.04 | 0.5 | 1.3 | -0.052 | 0 | 22.8 | -888 | 0.5 | 0 | -0.03 | 0 | 0 | 0.1 | 0.002 | 0 | 20.61
574 | 2008-09-24 | 210000 | 0 | 76.4 | 9.7 | -54.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.4 | 0.01 | -0.03 | 0.1 | 0.01 | 0.2 | 0.002 | 0.001 | 20.61
575 | 2008-09-24 | 220000 | 0 | 76.3 | 9.9 | -60.4 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.4 | 0.01 | -0.01 | 0.2 | 0.01 | 0.3 | 0.003 | 0.001 | 20.62
576 | 2008-09-24 | 230000 | 0 | 76.2 | 10.1 | -56.8 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | 22.8 | -888 | 0.5 | 0.01 | -0.03 | 0.1 | 0.02 | 0.3 | 0.003 | 0.001 | 20.62
577 | 2008-09-25 | 0 | 0 | 76.3 | 10 | -69.5 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | 0 | 0.01 | 0.4 | 0.003 | 0 | 20.63
578 | 2008-09-25 | 10000 | 0 | 76.3 | 9.4 | -66.5 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.3 | 0 | -0.03 | -0.1 | 0 | 0.1 | 0.002 | 0 | 20.64
579 | 2008-09-25 | 20000 | 0 | 76.3 | 8.8 | -62.7 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.63
580 | 2008-09-25 | 30000 | 0 | 76.3 | 8.8 | -65.5 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.02 | 0.3 | 0.003 | 0 | 20.64
581 | 2008-09-25 | 40000 | 0 | 76.3 | 9.3 | -59.5 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.65
582 | 2008-09-25 | 50000 | 0 | 76.3 | 9.4 | -73.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.66
583 | 2008-09-25 | 60000 | 0 | 76.3 | 9.5 | -75.1 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.66
584 | 2008-09-25 | 70000 | 0 | 76.3 | 11.4 | -66.8 | 0.04 | 0.6 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0 | -0.04 | 0.1 | 0.02 | 0.3 | 0.003 | 0 | 20.67
585 | 2008-09-25 | 80000 | 0 | 76.2 | 12.2 | -66.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | 0 | 0.01 | 0.4 | 0.003 | 0 | 20.69
586 | 2008-09-25 | 90000 | 0 | 76.3 | 12.2 | -87.4 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0 | 2.14 | 0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.7
587 | 2008-09-25 | 100000 | 0 | 76.3 | 14.3 | -85.7 | 0.04 | 0.6 | 1.3 | -0.046 | 0 | 22.8 | -888 | 0.3 | 0.01 | -0.03 | 0.4 | 0.02 | 0.5 | 0.004 | 0.002 | 20.71
588 | 2008-09-25 | 110000 | 0 | 76.2 | 13.1 | -87.4 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | -0.1 | 0.02 | 0.6 | 0.004 | 0 | 20.72
589 | 2008-09-25 | 120000 | 0 | 76.3 | 13 | -89.7 | 0.04 | 0.6 | 1.2 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0 | -0.02 | 0.1 | 0.02 | 0.5 | 0.005 | 0.001 | 20.72
590 | 2008-09-25 | 130000 | 0 | 76.3 | 13.6 | -96 | 0.04 | 0.5 | 1.2 | -0.047 | 0 | 22.8 | -888 | 0.5 | 0 | -0.04 | 0 | 0.02 | 0.5 | 0.004 | 0 | 20.72
591 | 2008-09-25 | 140000 | 0 | 76.3 | 14.9 | -90.3 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.4 | 0.01 | -0.03 | 0.2 | 0.02 | 0.7 | 0.004 | 0.001 | 20.72
592 | 2008-09-25 | 150000 | 0 | 76.2 | 13.8 | -95.1 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | 22.8 | -888 | 0.5 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.73
593 | 2008-09-25 | 160000 | 0 | 76.3 | 14.7 | -98.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.04 | -0.2 | 0.02 | 0.7 | 0.005 | 0 | 20.74
594 | 2008-09-25 | 170000 | 0 | 76.3 | 15.4 | -107.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 22.8 | -888 | 0.5 | 0 | -0.03 | -0.2 | 0.02 | 0.6 | 0.005 | 0 | 20.75
595 | 2008-09-25 | 180000 | 0 | 76.2 | 16.6 | -121.2 | 0.04 | 0.5 | 1.2 | -0.048 | 0 | 22.8 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.02 | 0.5 | 0.005 | 0 | 20.75
596 | 2008-09-25 | 190000 | 0 | 76.2 | 17.5 | -125.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | -0.01 | -0.03 | -0.3 | 0.01 | 0.4 | 0.005 | 0 | 20.76
597 | 2008-09-25 | 200000 | 0 | 76.2 | 19.6 | -112.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.4 | 0.005 | 0 | 20.77
598 | 2008-09-25 | 210000 | 0 | 76.3 | 20.5 | -116 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 22.8 | -888 | 0.5 | 0 | -0.03 | -0.1 | 0.01 | 0.5 | 0.005 | 0 | 20.7
599 | 2008-09-25 | 220000 | 0 | 76.3 | 24.6 | -111.4 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0 | -0.03 | 0.1 | 0.01 | 0.4 | 0.005 | 0.001 | 20.77
600 | 2008-09-25 | 230000 | 0 | 76.2 | 22.5 | -115.7 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.5 | 0 | -0.03 | 0.1 | 0.01 | 0.4 | 0.005 | 0.001 | 20.77
601 | 2008-09-26 | 0 | 0 | 77 | 21.7 | -123.4 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | 22.8 | -888 | 0.4 | 0 | -0.04 | 0 | 0.01 | 0.3 | 0.005 | 0 | 20.77
602 | 2008-09-26 | 10000 | 1 | 360.5 | 27.9 | 95.1 | 6.17 | 15.3 | 15.8 | -0.049 | 0 | 2.7 | -888 | 0.4 | 9.19 | 26.52 | 13.5 | 39.7 | 57.6 | 0.212 | 0.05 | 17.2
603 | 2008-09-26 | 20000 | 1 | 599.3 | 20.3 | 10.7 | 6.99 | 18.8 | 19.2 | -0.049 | 0 | 2.5 | -888 | 6.1 | 10.29 | 30.01 | 14.9 | 43.73 | 63.5 | 0.234 | 0.055 | 16.82
604 | 2008-09-26 | 30000 | 1 | 603.2 | 23.4 | 39.3 | 8.71 | 34.4 | 45.7 | -0.052 | 0 | 3.3 | -888 | 35.5 | 10.29 | 30.03 | 12 | 39.88 | 46.3 | 0.171 | 0.044 | 15.84
605 | 2008-09-26 | 40000 | 1 | 605.4 | 20.2 | 28.3 | 9.99 | 47.5 | 77.2 | -0.05 | 0 | 5.5 | -888 | 54.5 | 10.29 | 29.97 | 10.7 | 48.38 | 50 | 0.184 | 0.039 | 15.19
606 | 2008-09-26 | 50000 | 1 | 629.9 | 0.5 | -2.3 | 17.34 | 131.5 | 200.7 | -0.051 | 0 | 1.5 | -888 | 79.4 | 2.17 | 9.86 | 1.8 | 2.03 | 1.7 | 0.006 | 0.007 | 13.75
607 | 2008-09-26 | 60000 | 1 | 655 | 4.4 | 6.4 | 21.84 | 178 | 263.2 | -0.051 | 0 | 3.9 | -888 | 120.8 | 3.25 | 10.84 | 1.9 | 9.08 | 3.7 | 0.014 | 0.007 | 12.11
608 | 2008-09-26 | 70000 | 1 | 665.2 | 0.3 | -2 | 21.54 | 175.5 | 259.4 | -0.053 | 0 | 1.8 | -888 | 108.1 | 2.46 | 9.99 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.75
609 | 2008-09-26 | 80000 | 1 | 670.4 | 0.3 | -2.1 | 21.48 | 174.9 | 259.2 | -0.049 | 0 | -189.4 | -888 | 109.6 | 2.43 | 10.26 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.77
610 | 2008-09-26 | 90000 | 1 | 670.9 | 0.3 | -2.2 | 21.49 | 174.8 | 259.1 | -0.052 | 0 | -666 | -888 | 109.4 | 2.44 | 10.72 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.74
611 | 2008-09-26 | 100000 | 1 | 671.2 | 0.3 | -2.5 | 21.43 | 174.1 | 258.6 | -0.051 | 0 | -666 | -888 | 109.3 | 2.45 | 10.37 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.72
612 | 2008-09-26 | 110000 | 1 | 670.4 | 0.3 | -2.3 | 21.4 | 173.8 | 258.8 | -0.05 | 0 | -666 | -888 | 110 | 2.47 | 10.69 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.68
613 | 2008-09-26 | 120000 | 1 | 669.3 | 0.3 | -2.3 | 21.47 | 174.1 | 258.5 | -0.051 | 0 | -666 | -888 | 113.1 | 2.48 | 10.9 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.64
614 | 2008-09-26 | 130000 | 1 | 668 | 0.3 | -1.9 | 21.5 | 174 | 259.5 | -0.051 | 0 | -666 | -888 | 113.8 | 2.48 | 10.96 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.63
615 | 2008-09-26 | 140000 | 1 | 667.9 | 0.3 | -2.4 | 21.46 | 173.4 | 259.3 | -0.05 | 0 | -666 | -888 | 114.8 | 2.48 | 11.15 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.61
616 | 2008-09-26 | 150000 | 1 | 666.6 | 0.3 | -2.3 | 21.41 | 173.6 | 259.5 | -0.049 | 0 | -666 | -888 | 117.2 | 2.52 | 11.38 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.59
617 | 2008-09-26 | 160000 | 1 | 666 | 0.3 | -2.2 | 21.32 | 172.9 | 258.5 | -0.051 | 0 | -666 | -888 | 113.8 | 2.47 | 11.11 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.61
618 | 2008-09-26 | 170000 | 1 | 666 | 0.3 | -2.2 | 21.33 | 172.7 | 257.9 | -0.048 | 0 | -666 | -888 | 109.7 | 2.47 | 10.79 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.64
619 | 2008-09-26 | 180000 | 1 | 667.3 | 0.3 | -2.2 | 21.34 | 173.3 | 258.3 | -0.05 | 0 | -666 | -888 | 109.3 | 2.46 | 10.68 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.68
620 | 2008-09-26 | 190000 | 1 | 668.2 | 0.3 | -2.3 | 21.28 | 173.6 | 258.2 | -0.051 | 0 | -666 | -888 | 108.1 | 2.44 | 10.56 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.72
621 | 2008-09-26 | 200000 | 1 | 670.1 | 0.3 | -2.5 | 21.31 | 174 | 258.6 | -0.05 | 0 | -666 | -888 | 109.7 | 2.44 | 10.58 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.74
622 | 2008-09-26 | 210000 | 1 | 670 | 0.3 | -2 | 21.12 | 172.4 | 256.8 | -0.05 | 0 | -666 | -888 | 108.4 | 2.43 | 10.53 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.76
623 | 2008-09-26 | 220000 | 0 | 571.1 | 27.5 | -48.7 | 1.91 | 9.9 | 17.9 | -0.05 | 0 | -666 | -888 | 9.3 | 1.81 | 5.33 | 2.6 | 6.1 | 7.3 | 0.028 | 0.01 | 19.48
624 | 2008-09-26 | 230000 | 0 | 455.7 | 22.3 | -154 | 0.04 | 0.5 | 1.3 | -0.051 | 0 | -666 | -888 | 0.7 | 0 | 0.05 | -0.1 | 0.01 | 0.3 | 0.006 | 0 | 20.78
625 | 2008-09-27 | 0 | 0 | 434.4 | 20.8 | -124.2 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.6 | 0 | 0 | -0.2 | 0.02 | 0.9 | 0.006 | 0 | 20.78
626 | 2008-09-27 | 10000 | 0 | 428.2 | 22 | -140.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.6 | -0.01 | 0 | -0.3 | 0.01 | 0.5 | 0.006 | 0 | 20.78
627 | 2008-09-27 | 20000 | 0 | 421.6 | 25.2 | -171.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.7 | -0.01 | -0.03 | -0.4 | 0.01 | 0.7 | 0.007 | 0 | 20.8
628 | 2008-09-27 | 30000 | 0 | 423.2 | 22.6 | -155.4 | 0.06 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.6 | -0.01 | -0.01 | -0.3 | 0.01 | 0.6 | 0.007 | 0 | 20.79
629 | 2008-09-27 | 40000 | 1 | 582.5 | 22.3 | 31 | 8.23 | 32.3 | 35.6 | -0.049 | 0 | -666 | -888 | 25.5 | 9.86 | 28.75 | 11.9 | 37.94 | 44.4 | 0.164 | 0.044 | 16.05
630 | 2008-09-27 | 50000 | 1 | 631.3 | 0.6 | -2.2 | 17.49 | 133.5 | 199.6 | -0.048 | 0 | -666 | -888 | 77.4 | 2.55 | 10.37 | 2.1 | 5.05 | 4.2 | 0.015 | 0.008 | 13.78
631 | 2008-09-27 | 60000 | 1 | 657.9 | 8.2 | -5.2 | 21.72 | 178 | 262.6 | -0.05 | 0 | -666 | -888 | 118.7 | 3.42 | 10.97 | 2.1 | 9.44 | 3.8 | 11.095 | 1.591 | 12.17
632 | 2008-09-27 | 70000 | 1 | 667.9 | 0.4 | -2.4 | 21.34 | 174.4 | 258.3 | -0.048 | 0 | -666 | -888 | 109.5 | 2.38 | 10.16 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.88
633 | 2008-09-27 | 80000 | 1 | 667.8 | 0.3 | -2.2 | 21.39 | 174.7 | 258.3 | -0.047 | 0 | -666 | -888 | 110.4 | 2.4 | 10.15 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.86
634 | 2008-09-27 | 90000 | 1 | 670.6 | 0.3 | -2.3 | 21.46 | 175.2 | 259.8 | -0.048 | 0 | -666 | -888 | 111.1 | 2.41 | 10.68 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.81
635 | 2008-09-27 | 100000 | 1 | 671.7 | 0.3 | -2.2 | 21.43 | 174.8 | 259.7 | -0.047 | 0 | -666 | -888 | 111.2 | 2.43 | 10.3 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.79
636 | 2008-09-27 | 110000 | 1 | 670.7 | 0.3 | -2.3 | 21.36 | 174.2 | 258.9 | -0.049 | 0 | -666 | -888 | 111.7 | 2.43 | 10.34 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.77
637 | 2008-09-27 | 120000 | 1 | 669.2 | 0.3 | -2.4 | 21.38 | 174.2 | 259.6 | -0.049 | 0 | -666 | -888 | 115.4 | 2.47 | 10.64 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.7
638 | 2008-09-27 | 130000 | 1 | 666.7 | 0.3 | -2.4 | 21.41 | 173.7 | 259.5 | -0.048 | 0 | -666 | -888 | 121.8 | 2.5 | 11.23 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.65
639 | 2008-09-27 | 140000 | 1 | 665.3 | 0.3 | -2.6 | 21.33 | 173.3 | 259.8 | -0.049 | 0 | -666 | -888 | 134.3 | 2.52 | 12.08 | 2 | 2.37 | 1.9 | 0.007 | 0.008 | 13.6
640 | 2008-09-27 | 150000 | 1 | 664.6 | 0.3 | -2.1 | 21.26 | 172.6 | 258.6 | -0.049 | 0 | -666 | -888 | 124.9 | 2.41 | 11.39 | 1.9 | 2.24 | 1.8 | 0.007 | 0.007 | 13.61
641 | 2008-09-27 | 160000 | 1 | 665.9 | 0.3 | -2.5 | 21.25 | 172.5 | 258.3 | -0.048 | 0 | -666 | -888 | 121.6 | 2.52 | 11.24 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.61
642 | 2008-09-27 | 170000 | 1 | 665.5 | 0.3 | -2.4 | 21.25 | 172.9 | 259.3 | -0.048 | 0 | -666 | -888 | 125.4 | 2.53 | 11.54 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.59
643 | 2008-09-27 | 180000 | 1 | 664.4 | 0.3 | -2.2 | 21.39 | 174.3 | 260.7 | -0.049 | 0 | -666 | -888 | 127.4 | 2.47 | 11.58 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.57
644 | 2008-09-27 | 190000 | 1 | 665.3 | 0.3 | -2.1 | 21.3 | 173.1 | 258.2 | -0.048 | 0 | -666 | -888 | 123.5 | 2.47 | 11.31 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.62
645 | 2008-09-27 | 200000 | 1 | 666.3 | 0.3 | -2.3 | 21.31 | 173.1 | 258.6 | -0.048 | 0 | -666 | -888 | 118 | 2.45 | 10.87 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.66
646 | 2008-09-27 | 210000 | 1 | 666.7 | 0.3 | -2.3 | 21.15 | 171.3 | 256.6 | -0.047 | 0 | -666 | -888 | 111.9 | 2.43 | 10.54 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.69
647 | 2008-09-27 | 220000 | 0 | 568.7 | 25.2 | -46.9 | 1.93 | 9.7 | 17.3 | -0.047 | 0 | -666 | -888 | 4.1 | 1.83 | 5.48 | 2.5 | 6.91 | 8.1 | 0.031 | 0.009 | 19.43
648 | 2008-09-27 | 230000 | 0 | 454 | 19.3 | -116.5 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | -0.01 | 0.04 | -0.2 | 0.01 | 0.5 | 0.005 | 0 | 20.69
649 | 2008-09-28 | 0 | 0 | 434.1 | 18.6 | -97.6 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.7 | 0 | 0 | -0.2 | 0.01 | 0.4 | 0.005 | 0 | 20.76
650 | 2008-09-28 | 10000 | 0 | 426.7 | 18 | -113.2 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.7 | -0.01 | -0.03 | -0.2 | 0.01 | 0.4 | 0.005 | 0 | 20.76
651 | 2008-09-28 | 20000 | 0 | 418.7 | 18 | -124.3 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.8 | -0.01 | -0.02 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.76
652 | 2008-09-28 | 30000 | 0 | 418.6 | 16.5 | -102.2 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.7 | -0.01 | -0.03 | -0.3 | 0.01 | 0.4 | 0.005 | 0 | 20.75
653 | 2008-09-28 | 40000 | 1 | 569.5 | 21.4 | 19.2 | 7.78 | 30.8 | 32.3 | -0.049 | 0 | -666 | -888 | 14.5 | 9.32 | 27.13 | 11 | 38.55 | 44.6 | 0.164 | 0.04 | 16.22
654 | 2008-09-28 | 50000 | 1 | 629.8 | 1.9 | -0.6 | 17.61 | 134.2 | 202.2 | -0.048 | 0 | -666 | -888 | 89.1 | 3.26 | 12.55 | 2.8 | 9.45 | 8.4 | 0.031 | 0.01 | 13.82
655 | 2008-09-28 | 60000 | 1 | 652.7 | 6.4 | 0.7 | 19.72 | 156.8 | 236.4 | -0.049 | 0 | -666 | -888 | 121.1 | 2.87 | 10.65 | 1.6 | 8.95 | 3.4 | 0.013 | 0.006 | 12.15
656 | 2008-09-28 | 70000 | 1 | 655.5 | 0.4 | -2 | 19.96 | 160.7 | 239.5 | -0.049 | 0 | -666 | -888 | 98.4 | 2.41 | 10.21 | 2 | 2.26 | 1.9 | 0.007 | 0.007 | 13.76
657 | 2008-09-28 | 80000 | 1 | 669.4 | 0.4 | -2.3 | 21.66 | 176.9 | 262.3 | -0.051 | 0 | -666 | -888 | 118.5 | 2.4 | 10.94 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.72
658 | 2008-09-28 | 90000 | 1 | 670.3 | 0.3 | -2.4 | 21.56 | 176 | 261.4 | -0.053 | 0 | -666 | -888 | 118 | 2.45 | 11.26 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.72
659 | 2008-09-28 | 100000 | 1 | 669.5 | 0.3 | -2.3 | 21.53 | 175.4 | 261.2 | -0.051 | 0 | -666 | -888 | 117.5 | 2.48 | 11.02 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.69
660 | 2008-09-28 | 110000 | 1 | 668.2 | 0.4 | -2.4 | 21.54 | 175 | 261.2 | -0.051 | 0 | -666 | -888 | 124.2 | 2.49 | 11.42 | 2 | 2.34 | 1.9 | 0.007 | 0.007 | 13.64
661 | 2008-09-28 | 120000 | 1 | 666.2 | 0.4 | -2.3 | 21.52 | 175.2 | 261.8 | -0.051 | 0 | -666 | -888 | 129.4 | 2.48 | 11.89 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.58
662 | 2008-09-28 | 130000 | 1 | 674.6 | 0.3 | -2.5 | 21.42 | 173.8 | 262.3 | 0.077 | 0 | -387.7 | -888 | 117.2 | 2.7 | 11.49 | 2.1 | 2.54 | 2 | 0.007 | 0.008 | 13.37
663 | 2008-09-28 | 140000 | 1 | 768.4 | 0.1 | -1.9 | 21.53 | 174.7 | 303.5 | 0.724 | 1 | 3.9 | -888 | 171 | 3.14 | 15.68 | 2 | 2.95 | 1.9 | 0.007 | 0.007 | 11.84
664 | 2008-09-28 | 150000 | 1 | 771.5 | 0.1 | -1.6 | 21.38 | 173.7 | 302.4 | 0.71 | 1 | 3.9 | -888 | 169.3 | 3.08 | 15.47 | 2 | 2.89 | 1.9 | 0.007 | 0.007 | 11.86
665 | 2008-09-28 | 160000 | 1 | 771.7 | 0.1 | -1.8 | 21.33 | 173.3 | 302.5 | 0.708 | 1 | 3.9 | -888 | 169.9 | 3.09 | 15.48 | 2 | 2.91 | 1.9 | 0.007 | 0.007 | 11.84
666 | 2008-09-28 | 170000 | 1 | 771.4 | 0.1 | -1.7 | 21.32 | 173.4 | 302.6 | 0.697 | 1 | 3.9 | -888 | 169.5 | 3.07 | 15.39 | 2 | 2.9 | 1.9 | 0.007 | 0.007 | 11.85
667 | 2008-09-28 | 180000 | 1 | 683.9 | 0.3 | -2.2 | 21.09 | 171.1 | 259.4 | -0.039 | 0 | -591.9 | -888 | 114.8 | 2.36 | 10.77 | 1.9 | 2.21 | 1.8 | 0.007 | 0.007 | 13.56
668 | 2008-09-28 | 190000 | 1 | 667.7 | 0.3 | -2.6 | 21.48 | 175 | 261.9 | -0.051 | 0 | -666 | -888 | 126.6 | 2.48 | 11.73 | 2 | 2.33 | 1.8 | 0.007 | 0.007 | 13.5
669 | 2008-09-28 | 200000 | 1 | 668.5 | 0.3 | -2.1 | 21.48 | 175.5 | 262 | -0.052 | 0 | -666 | -888 | 122.4 | 2.53 | 11.53 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.53
670 | 2008-09-28 | 210000 | 1 | 668.3 | 0.3 | -2.2 | 21.43 | 174.2 | 260.4 | -0.052 | 0 | -666 | -888 | 123.1 | 2.42 | 11.49 | 1.9 | 2.28 | 1.8 | 0.007 | 0.007 | 13.56
671 | 2008-09-28 | 220000 | 0 | 566.2 | 23 | -35.2 | 2.13 | 11.4 | 20.8 | -0.049 | 0 | -666 | -888 | 9.1 | 1.75 | 5.39 | 2.3 | 6.08 | 6.7 | 0.026 | 0.009 | 19.32
672 | 2008-09-28 | 230000 | 0 | 446 | 16.4 | -72 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | 0 | 0.04 | 0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.71
673 | 2008-09-29 | 0 | 0 | 428.9 | 16.2 | -80.7 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.7 | 0 | -0.01 | 0.1 | 0.02 | 0.7 | 0.004 | 0 | 20.71
674 | 2008-09-29 | 10000 | 0 | 421.8 | 15.9 | -83.5 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.6 | 0 | -0.03 | 0 | 0.01 | 0.1 | 0.003 | 0 | 20.71
675 | 2008-09-29 | 20000 | 0 | 414.8 | 16 | -78 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.6 | 0 | -0.04 | 0 | 0.02 | 0.5 | 0.004 | 0 | 20.71
676 | 2008-09-29 | 30000 | 0 | 413.2 | 14.5 | -85.8 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | -666 | -888 | 0.6 | 0 | -0.03 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.7
677 | 2008-09-29 | 40000 | 1 | 551.9 | 19.4 | 9.2 | 8.05 | 36.4 | 37.9 | -0.049 | 0 | -666 | -888 | 8.3 | 8.65 | 24.91 | 10.5 | 38.38 | 44.7 | 0.165 | 0.039 | 16.33
678 | 2008-09-29 | 50000 | 1 | 626.7 | 0.6 | -2.3 | 16.77 | 125.9 | 169.3 | -0.05 | 0 | -666 | -888 | 82.9 | 2.25 | 10.16 | 1.9 | 2.1 | 1.7 | 0.006 | 0.007 | 13.72
679 | 2008-09-29 | 60000 | 1 | 664.4 | 0.4 | -2.3 | 21.41 | 175.5 | 259.3 | -0.049 | 0 | -666 | -888 | 120.6 | 2.36 | 11.19 | 1.9 | 2.22 | 1.8 | 0.007 | 0.007 | 13.68
680 | 2008-09-29 | 70000 | 1 | 669.3 | 0.4 | -2.1 | 21.37 | 175.3 | 259.1 | -0.051 | 0 | -666 | -888 | 117.7 | 2.43 | 10.85 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.74
681 | 2008-09-29 | 80000 | 1 | 671.1 | 0.4 | -2.1 | 21.3 | 174.5 | 258.8 | -0.051 | 0 | -666 | -888 | 115.5 | 2.44 | 10.77 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.72
682 | 2008-09-29 | 90000 | 1 | 670.2 | 3.5 | 19.1 | 21.32 | 174.2 | 256.9 | -0.047 | 0 | -666 | -888 | 148 | 3.05 | 11.31 | 1.8 | 9.07 | 3.5 | 0.013 | 0.006 | 12.07
683 | 2008-09-29 | 100000 | 1 | 670.4 | 0.4 | -2.2 | 21.2 | 173 | 257.9 | -0.047 | 0 | -666 | -888 | 128.4 | 1.9 | 10.92 | 1.5 | 1.78 | 1.5 | 0.005 | 0.006 | 13.65
684 | 2008-09-29 | 110000 | 1 | 678 | 0.4 | -2 | 21.27 | 173.9 | 262.8 | 0.058 | 0 | -469.1 | -888 | 126.4 | 2.47 | 11.63 | 1.9 | 2.31 | 1.8 | 0.007 | 0.007 | 13.38
685 | 2008-09-29 | 120000 | 1 | 755.9 | 0.1 | -1.9 | 21.48 | 175.3 | 299.2 | 0.641 | 1 | 3.7 | -888 | 167.3 | 3 | 15.12 | 2 | 2.82 | 1.9 | 0.007 | 0.007 | 11.99
686 | 2008-09-29 | 130000 | 1 | 765.4 | 0.1 | -1.9 | 21.32 | 173.4 | 299.3 | 0.667 | 1 | 3.9 | -888 | 168.9 | 2.9 | 15.03 | 1.9 | 2.72 | 1.8 | 0.007 | 0.007 | 11.9
687 | 2008-09-29 | 140000 | 1 | 767.8 | 0.1 | -1.6 | 21.18 | 172.3 | 299.9 | 0.709 | 1 | 4 | -888 | 170.1 | 2.96 | 15.22 | 1.9 | 2.78 | 1.8 | 0.007 | 0.007 | 11.79
688 | 2008-09-29 | 150000 | 1 | 768 | 0.1 | -1.8 | 21.06 | 171.5 | 299 | 0.712 | 1 | 4.1 | -888 | 170.5 | 2.97 | 15.21 | 1.9 | 2.79 | 1.8 | 0.007 | 0.007 | 11.77
689 | 2008-09-29 | 160000 | 1 | 768.6 | 0.1 | -1.8 | 21.06 | 171.1 | 299.2 | 0.726 | 1 | 4.1 | -888 | 170.8 | 2.96 | 15.21 | 1.9 | 2.78 | 1.8 | 0.007 | 0.007 | 11.73
690 | 2008-09-29 | 170000 | 1 | 769.5 | 0.1 | -1.9 | 21.13 | 171.3 | 300.2 | 0.737 | 1 | 4.1 | -888 | 170 | 2.98 | 15.21 | 1.9 | 2.8 | 1.8 | 0.007 | 0.007 | 11.7
691 | 2008-09-29 | 180000 | 1 | 766.5 | 0.1 | -1.8 | 21.45 | 174 | 300.8 | 0.702 | 1 | 4 | -888 | 171.7 | 2.93 | 15.16 | 1.9 | 2.75 | 1.8 | 0.007 | 0.007 | 11.84
692 | 2008-09-29 | 190000 | 1 | 761 | 0.1 | -1.7 | 21.55 | 175.7 | 300.8 | 0.648 | 1 | 3.9 | -888 | 171.7 | 2.89 | 15.06 | 1.9 | 2.72 | 1.8 | 0.007 | 0.007 | 11.96
693 | 2008-09-29 | 200000 | 1 | 759 | 0.1 | -1.8 | 21.59 | 176.2 | 300.1 | 0.619 | 1 | 3.8 | -888 | 170.8 | 2.87 | 14.95 | 1.9 | 2.69 | 1.8 | 0.007 | 0.007 | 12.02
694 | 2008-09-29 | 210000 | 1 | 758.5 | 0.1 | -1.7 | 21.79 | 177 | 300.2 | 0.581 | 1 | 3.7 | -888 | 171.6 | 2.83 | 14.89 | 1.9 | 2.64 | 1.8 | 0.007 | 0.007 | 12.09
695 | 2008-09-29 | 220000 | 1 | 650.9 | 1.4 | -1 | 16.24 | 118.8 | 190.3 | -0.049 | 0 | -632.7 | -888 | 76.4 | 2.81 | 11.22 | 2.4 | 5.88 | 5.2 | 0.019 | 0.009 | 13.73
696 | 2008-09-29 | 230000 | 0 | 563.2 | 23.3 | -20.9 | 1.99 | 7.6 | 12.1 | -0.047 | 0 | -666 | -888 | 10.5 | 2.65 | 8.11 | 3.5 | 9.2 | 11.3 | 0.042 | 0.013 | 19.27
697 | 2008-09-30 | 0 | 0 | 446.3 | 11.9 | -66.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.8 | 0 | 0.09 | -0.1 | 0.02 | 0.4 | 0.003 | 0 | 20.66
698 | 2008-09-30 | 10000 | 0 | 426 | 11.6 | -64.8 | 0.04 | 0.5 | 1.3 | -0.048 | 0 | -666 | -888 | 0.6 | -0.01 | 0 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.67
699 | 2008-09-30 | 20000 | 0 | 418.5 | 12 | -76.5 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | -666 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.02 | 0.3 | 0.003 | 0 | 20.68
700 | 2008-09-30 | 30000 | 0 | 418.5 | 11.6 | -76.7 | 0.04 | 0.5 | 1.3 | -0.047 | 0 | -666 | -888 | 0.7 | -0.01 | -0.03 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.69
701 | 2008-09-30 | 40000 | 1 | 568.8 | 19.5 | 13.6 | 8.4 | 37.2 | 38.7 | -0.047 | 0 | -666 | -888 | 10.8 | 8.96 | 26.79 | 10.3 | 42.49 | 47.3 | 0.175 | 0.038 | 16.01
702 | 2008-09-30 | 50000 | 1 | 631.9 | 0.5 | -2 | 18.08 | 139.3 | 199.4 | -0.049 | 0 | -666 | -888 | 92.7 | 2.28 | 10.54 | 1.9 | 2.14 | 1.8 | 0.007 | 0.007 | 13.71
703 | 2008-09-30 | 60000 | 1 | 666.9 | 4.6 | 17.9 | 21.52 | 175.4 | 260.5 | -0.05 | 0 | -666 | -888 | 121.5 | 3.4 | 11.29 | 2 | 9.4 | 3.7 | 0.014 | 0.007 | 12.11
704 | 2008-09-30 | 70000 | 1 | 670.6 | 0.4 | -2.4 | 21.45 | 174.9 | 259.9 | -0.048 | 0 | -589.9 | -888 | 116.2 | 2.41 | 10.77 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.69
705 | 2008-09-30 | 80000 | 1 | 686.7 | 0.3 | -2.1 | 22.01 | 179.2 | 273.4 | 0.117 | 1 | 2.4 | -888 | 139 | 2.63 | 12.7 | 2 | 2.47 | 1.9 | 0.007 | 0.007 | 13.25
706 | 2008-09-30 | 90000 | 1 | 749.6 | 0.1 | -1.7 | 21.84 | 178.3 | 299.8 | 0.592 | 1 | 3.6 | -888 | 167.6 | 3.08 | 14.68 | 2.1 | 2.89 | 1.9 | 0.007 | 0.007 | 12.17
707 | 2008-09-30 | 100000 | 1 | 747.6 | 0.1 | -1.9 | 21.78 | 177 | 294.9 | 0.51 | 1 | 3.4 | -888 | 162.9 | 2.93 | 14.64 | 2 | 2.76 | 1.9 | 0.007 | 0.007 | 12.36
708 | 2008-09-30 | 110000 | 1 | 756.9 | 0.1 | -1.8 | 21.57 | 175.4 | 297.5 | 0.589 | 1 | 3.6 | -888 | 167.6 | 2.96 | 14.96 | 2 | 2.78 | 1.9 | 0.007 | 0.007 | 12.17
709 | 2008-09-30 | 120000 | 1 | 754.3 | 0.1 | -1.8 | 21.75 | 176.4 | 297.1 | 0.57 | 1 | 3.5 | -888 | 163 | 2.95 | 14.69 | 2 | 2.78 | 1.9 | 0.007 | 0.007 | 12.18
710 | 2008-09-30 | 130000 | 1 | 749.2 | 0.2 | -1.8 | 21.54 | 174.6 | 291.5 | 0.491 | 1 | 3.3 | -888 | 156.6 | 2.86 | 14.11 | 2 | 2.69 | 1.8 | 0.007 | 0.007 | 12.32
711 | 2008-09-30 | 140000 | 1 | 731.8 | 0.2 | -1.9 | 21.52 | 173.8 | 283.3 | 0.387 | 1 | 2.9 | -888 | 145 | 2.85 | 13.51 | 2 | 2.68 | 1.9 | 0.007 | 0.007 | 12.55
712 | 2008-09-30 | 150000 | 0 | 589.2 | 11.3 | -49.9 | 3.72 | 30.3 | 55.2 | 0.039 | 0 | 3 | -888 | 36.9 | 0.57 | 2.64 | 0.6 | 0.55 | 0.8 | 0.004 | 0.002 | 19.08
713 | 2008-09-30 | 160000 | 0 | 420.1 | 12.7 | -86.6 | 0.25 | 0.5 | 1.3 | -0.05 | 0 | 3 | -888 | 2.4 | -0.01 | 0.06 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.68
714 | 2008-09-30 | 170000 | 0 | 393.3 | 12.3 | -76.9 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 3 | -888 | 0.6 | -0.01 | -0.02 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.68
715 | 2008-09-30 | 180000 | 0 | 384.5 | 13.1 | -86.3 | 0.04 | 0.5 | 1.3 | -0.049 | 0 | 3 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.61
716 | 2008-09-30 | 190000 | 0 | 384 | 13.9 | -72.1 | 0.04 | 0.5 | 1.2 | -0.051 | 0 | 3 | -888 | 0.7 | -0.01 | -0.04 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.69
717 | 2008-09-30 | 200000 | 0 | 381 | 14.5 | -71.2 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 3 | -888 | 0.7 | -0.01 | -0.03 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.7
718 | 2008-09-30 | 210000 | 0 | 378 | 14.7 | -90.4 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 3 | -888 | 0.6 | -0.01 | -0.02 | -0.2 | 0.01 | 0.3 | 0.004 | 0 | 20.71
719 | 2008-09-30 | 220000 | 0 | 374.4 | 14.9 | -93.3 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 3 | -888 | 0.7 | -0.01 | -0.03 | -0.2 | 0.02 | 0.5 | 0.004 | 0 | 20.71
720 | 2008-09-30 | 230000 | 0 | 370.3 | 14.4 | -91.9 | 0.04 | 0.5 | 1.3 | -0.05 | 0 | 3 | -888 | 0.6 | -0.01 | -0.03 | -0.2 | 0.01 | 0.6 | 0.004 | 0 | 20.7
721 | / | /
722 | / | / | AVE | 0.474 | 448.714 | 7.056 | -44.924 | 9.165 | 72.13 | 108.849 | -0.029 | 0.031 | -219.717 | -888 | 48.493 | 1.605 | 6.114 | 1.425 | 3.527 | 3.812 | 0.583 | 0.014 | 17.398
[7 empty] | July Total MW-hr |  | 77904.5
Excluding non-op hours
Used gas use column to confirm operation

## Monthly Emissions Report
==============================================================================
| Monthly | Emissions | Report
| Plant: | MINT | FARM | ENERGY | CTR
| Unit: | Unit | 1
==============================================================================
Report | Dates: | 2008-07-01 | - | 2008-09-30
| Month | NOx | Heat Input | SO2 | CO2 | Megawatts | CO
|  | tons | mmBtu | tons | tons | MW-hours | tons
| July | 3.9 | 316369 | 0.2 | 18801.6 | 42454 | 1.2
| August | 4.6 | 945441 | 0.7 | 56186.7 | 137298 | 1
| September | 4.5 | 549003 | 0.4 | 32626.5 | 78027 | 1.2
Report | Totals | 13 | 1810813 | 1.3 | 107614.8 | 257779 | 3.4
Ozone | Season | 13 | 1810813 |  |  | 257779

## CEM INCIDENTS
Turbine CEMS Downtime
NOx ppm @15% O2 NOx lb/hr CO ppm @15% O2 and CO lb/hr CEMS Downtime for 7/1/2008 thru 9/30/2008
Parameter | Date/Time | Duration | Duration (minutes) | Reason |  | Action
CO/NOx | 8/27/08 0900 | 2.0 hrs | 120 | Quarterly QA audit |  | Complete
Turbine Excess Emissions
NOx ppm @15% O2 24-Hr Rolling NOx lb/hr CO ppm @15% O2 and CO lb/hr Excess Emissions for 7/1/2008 thru 9/30/2008
Parameter | Date/Time | Duration | Duration (minutes) | Average | Min | Max | Limit | Reason | Action
NOx lb/hr | 8/13/2008 1800 | 1 hr | 60 | 22.5 lbs/hr | 22.5 lbs/hr | 22.5 lbs/hr | 21.3 lbs/hr | Initial commissioning of the turbine steam augmentation system | Completed control system tuning
Start-up and shutdown periods are indicated in the monthly "CEMS data" tabs. These periods are excluded from short term emission limits

## CEM Qrtly QA
Quarterly Linearity Check Form
Mint Farm Energy Center
| Date: | 2008-08-27 |  |  | Initials: | RL
| Time: | 09:09 |  |  | Analyzer: | O2
|  | Reference |  | Monitor |  | Monitor | Linearity
|  | Value |  | Response |  | Average | Error *
1 | Low-Level | 5.496 |  | 5.56
2 | Low-Level | 5.496 |  | 5.58 |  | 5.57 | 1.3464
3 | Low-Level | 5.496 |  | 5.57
1 | Mid-Level | 11.51 |  | 11.6
2 | Mid-Level | 11.51 |  | 11.57 |  | 11.5733 | 0.55025
3 | Mid-Level | 11.51 |  | 11.55
1 | High-Level | 21 |  | 21.11
2 | High-Level | 21 |  | 21.1 |  | 21.1 | 0.47619
3 | High-Level | 21 |  | 21.09
* The percent error is based on the reference value of the cylinder gas concentration.
Linearity error for pollutant and diluent analyzers is determined as follows:
¦ R - A ¦
| LE = | ---------------- | * 100
R
Where:
LE = Percent linearity error, based on the reference value
R = Reference value of cylinder gas
A = Average of three monitoring system responses
Quarterly Linearity Check Form
Mint Farm Energy Center
| Date: | 2008-08-27 |  |  | Initials: | RL
| Time: | 12:01 |  |  | Analyzer: | CO (Low Range)
|  | Reference |  | Monitor |  | Monitor | Linearity
|  | Value |  | Response |  | Average | Error *
1 | Low-Level | 5.338 |  | 5.53
2 | Low-Level | 5.338 |  | 5.57 |  | 5.5233 | 3.472
3 | Low-Level | 5.338 |  | 5.47
1 | Mid-Level | 11.2 |  | 11.21
2 | Mid-Level | 11.2 |  | 11.22 |  | 11.2167 | 0.14881
3 | Mid-Level | 11.2 |  | 11.22
1 | High-Level | N/A |  | N/A
2 | High-Level | N/A |  | N/A |  | N\A | N\A
3 | High-Level | N/A |  | N/A
* The percent error is based on the reference value of the cylinder gas concentration.
Linearity error for pollutant and diluent analyzers is determined as follows:
¦ R - A ¦
| LE = | ---------------- | * 100
R
Where:
LE = Percent linearity error, based on the reference value
R = Reference value of cylinder gas
A = Average of three monitoring system responses
Quarterly Linearity Check Form
Mint Farm Energy Center
| Date: | 2008-08-27 |  |  | Initials: | RL
| Time: | 10:53 |  |  | Analyzer: | CO (High Range)
|  | Reference |  | Monitor |  | Monitor | Linearity
|  | Value |  | Response |  | Average | Error *
1 | Low-Level | 513.65 |  | 520
2 | Low-Level | 513.65 |  | 519.5 |  | 519.5 | 1.1389
3 | Low-Level | 513.65 |  | 519
1 | Mid-Level | 1107 |  | 1111.3
2 | Mid-Level | 1107 |  | 1095.7 |  | 1105.8 | 0.1084
3 | Mid-Level | 1107 |  | 1110.4
1 | High-Level | N/A |  | N/A
2 | High-Level | N/A |  | N/A |  | N\A | N\A
3 | High-Level | N/A |  | N/A
* The percent error is based on the reference value of the cylinder gas concentration.
Linearity error for pollutant and diluent analyzers is determined as follows:
¦ R - A ¦
| LE = | ---------------- | * 100
R
Where:
LE = Percent linearity error, based on the reference value
R = Reference value of cylinder gas
A = Average of three monitoring system responses
Quarterly Linearity Check Form
Mint Farm Energy Center
| Date: | 2008-08-27 |  |  | Initials: | RL
| Time: | 09:59 |  |  | Analyzer: | NOx
|  | Reference |  | Monitor |  | Monitor | Linearity
|  | Value |  | Response |  | Average | Error *
1 | Low-Level | 25.13 |  | 24.27
2 | Low-Level | 25.13 |  | 24.24 |  | 24.3333 | 3.1702
3 | Low-Level | 25.13 |  | 24.49
1 | Mid-Level | 54.874 |  | 53.96
2 | Mid-Level | 54.874 |  | 54.22 |  | 54.0933 | 1.4227
3 | Mid-Level | 54.874 |  | 54.1
1 | High-Level | 89.12 |  | 89.11
2 | High-Level | 89.12 |  | 89.06 |  | 89.0933 | 0.029922
3 | High-Level | 89.12 |  | 89.11
* The percent error is based on the reference value of the cylinder gas concentration.
Linearity error for pollutant and diluent analyzers is determined as follows:
¦ R - A ¦
| LE = | ---------------- | * 100
R
Where:
LE = Percent linearity error, based on the reference value
R = Reference value of cylinder gas
A = Average of three monitoring system responses

## Cooling Tower Emissions
TDS Sampling
Cooling Tower Discharge Samples
Date Taken |  | Value (ppm)
2008-07-03 |  | 493
2008-07-18 |  | 643
2008-07-24 |  | 498
| Avg: | 544.6667 | ppmw
PM Emission Rate
100% PM is PM10
|  | 5e-06 | Max drift rate (0.0005%)
|  | 8.34 | weight of water (lb/gal)
|  | 77000 | Water circulation rate (gpm)
| PM/PM10 = | 0.10493 | lb/hr
PM/PM10 Emissions
| Month | Hours | Emissions
| Jul | 218.5833 | 22.9364 | lbs
| Aug | 559.2667 | 58.6851 | lbs
| Sep | 344.35 | 36.1334 | lbs
|  | Total PM/PM10: | 0.058877 | tons

## PM & VOC factors
Mint Farm Energy Center
Emission Factor Calculations for Total PM and VOC
Calculations are derived from results of emission testing conducted on February 19-20, 2008.
Total Particulate Matter |  |  |  | VOC
| Emission Rate | Heat Input |  |  | Emission Rate | Heat Input
Run # | lb/hr | MMBtuH | lb/MMBtu | Run # | lb/hr | MMBtuH | lb/MMBtu
1 | 11.1 | 2338.5 | 0.0047466 | 1 | 1.9 | 2338.5 | 0.00081249
2 | 8.6 | 2288.9 | 0.0037573 | 2 | 0 | 2288.9 | 0
3 | 10.1 | 2322 | 0.0043497 | 3 | 0 | 2322 | 0
Average | 9.9333 | 2316.4667 | 0.0042845 | Average | 0.63333 | 2316.4667 | 0.00027083
Filterable Particulate Matter
| Emission Rate | Heat Input
Run # | lb/hr | MMBtuH | lb/MMBtu
1 | 1.8 | 2338.5 | 0.00076972
2 | 1.9 | 2288.9 | 0.00083009
3 | 0.72 | 2322 | 0.00031008
Average | 1.4733 | 2316.4667 | 0.00063663
Condensable Particulate Matter
| Emission Rate | Heat Input
Run # | lb/hr | MMBtuH | lb/MMBtu
1 | 9.3 | 2338.5 | 0.0039769
2 | 6.8 | 2288.9 | 0.0029709
3 | 9.3 | 2322 | 0.0040052
Average | 8.4667 | 2316.4667 | 0.003651

## Diesel Calcs
Mint Farm Generation |  |  |  | Facility ID # | 2111
Diesel Generator
| Operation: | 10 | Hours
Pollutant | Emission Factor |  |  | Emissions
NOx | 14.57 | lb/hr |  | 0.07285 | tons
CO | 0.55 | lb/hr |  | 0.00275 | tons
SOx | 0.29 | lb/hr |  | 0.00145 | tons
PM/PM10/PM2.5 | 0.68 | lb/hr |  | 0.0034 | tons
VOC | 0.06 | lb/hr |  | 0.0003 | tons
Emission Factors per ADP 04-2571R1 TSD, Section 6.e