WASHINGTON

SERVICE QUALITY

REVIEW

January 1 – December 31, 2013

Annual Report

TABLE OF CONTENTS

EXECUTIVE SUMMARY	3

1	Service Standards Program Summary	3

1.1	Pacific Power Customer Guarantees	4

1.2	Pacific Power Performance Standards	5

1.3	Reliability Definitions	6

1.4	Service Territory	9

2	CUSTOMER GUARANTEES SUMMARY	10

3	RELIABILITY PERFORMANCE	11

3.1	Multi-Year Historical Performance	11

3.2	System Average Interruption Duration Index (SAIDI)	13

3.3	System Average Interruption Frequency Index (SAIFI)	15

3.4	Operating Area Metrics	16

3.5	Cause Code Analysis	17

3.6	Areas of Greatest Concern	21

3.7	Reduce CPI for Worst Performing Circuits by 20%	22

3.8	Restore Service to 80% of Customers within 3 Hours	23

3.9	Telephone Service and Response to Commission Complaints	23

4	CUSTOMER RELIABILITY COMMUNICATIONS	24

4.1	Reliability Complaint Process Overview	24

4.2	Customer Complaint Tracking	25

4.3	Customer Complaints Recorded During the Period	25

5	WASHINGTON RELIABILITY RESULTS DURING 2013	26

5.1	State Reliability	27

5.2	5W2:  Memorial Feeder	29

5.3	5Y382:  Occidental Feeder	31

5.4	5Y380:  Tampico Feeder	33

5.5	5Y437:  10th Street Feeder	35

5.6	5Y99:  Gravel Feeder	38

APPENDIX A:  2013 MAJOR EVENT FILINGS	40

# EXECUTIVE SUMMARY

During January 1 through December 31, 2013, Pacific Power & Light Company (Pacific Power or Company) delivered reliable service to its Washington customers.  The level of performance met established baselines.  Also, the Customer Guarantee program continued to deliver high quality results consistent with the prior year’s performance.  The Company has noted in the past that the service it delivers ranks high when compared across the industry.

The company’s service reliability can be impacted by uncontrollable interference events, such as car-hit-pole accidents, and by significant events that exceed the normal underlying level of interruptions but that do not reach the qualifying major event threshold for exclusion from the company’s underlying performance metrics.  To provide a perspective on their impact during the reporting period, the significant events experienced during 2013 are listed in Section 3.2.  Consideration of the root causes of these significant days is important when evaluating year-on-year performance.  When the Company develops reliability improvement projects it evaluates these root causes and prepares plans that reflect the certainty of repetition of these events.  The outcomes are reflective of the plans outlined in the Areas of Great Concern, shown in Section 3.6.

# Service Standards Program Summary

Pacific Power has a number of Customer Service Standards and Service Quality Measures with performance reporting mechanisms currently in place.  These standards and measures define Pacific Power's target performance (both personnel and network reliability performance) in delivering quality customer service.  The Company developed these standards and measures using relevant industry standards for collecting and reporting performance data.  In some cases, Pacific Power has expanded upon these standards.  In other cases, largely where the industry has no established standards, Pacific Power has developed metrics, targets and reporting.  While industry standards are not focused around threshold performance levels, the Company has developed targets or performance levels against which it evaluates its performance.  These standards and measures can be used over time, both historically and prospectively, to measure the service quality delivered to our customers.  In its entirety, these measures comply with WAC 480-100-393 and 398 requirements for routine reliability reporting.

In UE-042131, the company applied for, and received approval, to extend the core program through March 31, 2008.  During the MidAmerican acquisition of Pacific Power, in UE-051090, the program was extended again through 2011.  While the term of this program has lapsed, the Company has continued to perform all programs as performed historically.  No actions have been taken by the Company to recommend any suspension or changes to the program as was extended in UE-042131.

## Pacific Power Customer Guarantees

| Customer Guarantee 1: Restoring Supply After an Outage | The company will restore supply after an outage within 24 hours of notification from the customer with certain exceptions as described in Rule 25. |
| --- | --- |
| Customer Guarantee 2: Appointments | The company will keep mutually agreed upon appointments which will be scheduled within a two-hour time window. |
| Customer Guarantee 3: Switching on Power | The company will switch on power within 24 hours of the customer or applicant’s request, provided no construction is required, all government inspections are met and communicated to the company and required payments are made. Disconnections for nonpayment, subterfuge or theft/diversion of service are excluded. |
| Customer Guarantee 4: Estimates For New Supply | The company will provide an estimate for new supply to the applicant or customer within 15 working days after the initial meeting and all necessary information is provided to the company. |
| Customer Guarantee 5: Respond To Billing Inquiries | The company will respond to most billing inquiries at the time of the initial contact. For those that require further investigation, the company will investigate and respond to the Customer within 10 working days. |
| Customer Guarantee 6: Resolving Meter Problems | The company will investigate and respond to reported problems with a meter or conduct a meter test and report results to the customer within 10 working days. |
| Customer Guarantee 7: Notification of Planned Interruptions | The company will provide the customer with at least two days’ notice prior to turning off power for planned interruptions. |

Note:  See Rules for a complete description of terms and conditions for the Customer Guarantee Program.

## Pacific Power Performance Standards

| Network Performance Standard 1: Improve System Average Interruption Duration Index (SAIDI) | The company will maintain SAIDI commitment target. |
| --- | --- |
| Network Performance Standard 2: Improve System Average Interruption Frequency Index (SAIFI) | The company will maintain SAIFI commitment target. |
| Network Performance Standard 3: Improve Under Performing Circuits | The company will reduce by 20% the circuit performance indicator (CPI) for a maximum of five under-performing circuits on an annual basis within five years after selection. |
| Network Performance Standard 4: Supply Restoration | The company will restore power outages due to loss of supply or damage to the distribution system within three hours to 80% of customers on average. |
| Customer Service Performance Standard 5: Telephone Service Level | The company will answer 80% of telephone calls within 30 seconds. The company will monitor customer satisfaction with the company’s Customer Service Associates and quality of response received by customers through the company’s eQuality monitoring system. |
| Customer Service Performance Standard 6: Commission Complaint Response/Resolution | The company will: a) respond to at least 95% of non-disconnect Commission complaints within two working days per state administrative code; b) respond to at least 95% of disconnect Commission complaints within four working hours; and c) resolve 95% of informal Commission complaints within 30 days. |

Note: Performance Standards 1, 2 & 4 are for underlying performance days, excluding days classified as Major Events.

## Reliability Definitions

This section will define the various terms used when referring to interruption types, performance metrics and the internal measures developed to meet performance plans.  A map of Pacific Power’s service territory is included.

Interruption Types

Sustained Outage

A sustained outage is defined as an outage of equal to or greater than 5 minutes in duration.

Momentary Outage

A momentary outage event is defined as an outage equal to or less than 5 minutes in duration, and comprises all operations of the device during the momentary duration; if a breaker goes to lockout (it is unable to clear the faulted condition after the equipment’s prescribed number of operations) the momentary operations are part of the ensuing sustained interruption.  This sequence of events typically occurs when the system is trying to re-establish energy flow after a faulted condition, and is associated with circuit breakers or other automatic reclosing devices.  Pacific Power uses the locations where SCADA (Supervisory Control and Data Acquisition) exists and calculates consistent with IEEE 1366-2003/2012.  Where no substation breaker SCADA exists fault counts at substation breakers are to be used.

Reliability Indices

SAIDI

SAIDI (system average interruption duration index) is an industry-defined term to define the average duration summed for all sustained outages a customer experiences in a given period.  It is calculated by summing all customer minutes lost for sustained outages (those exceeding 5 minutes) and dividing by all customers served within the study area.  When not explicitly stated otherwise, this value can be assumed to be for a one-year period.

Daily SAIDI

In order to evaluate trends during a year and to establish Major Event Thresholds, a daily SAIDI value is often used as a measure.  This concept was introduced in IEEE Standard P1366-2003/2012.  This is the day’s total customer minutes out of service divided by the static customer count for the year.  It is the total average outage duration customers experienced for that given day.  When these daily values are accumulated through the year, it yields the year’s SAIDI results.

SAIFI

SAIFI (system average interruption frequency index) is an industry-defined term that attempts to identify the frequency of all sustained outages that the average customer experiences during a given period.  It is calculated by summing all customer interruptions for sustained outages (those exceeding 5 minutes in duration) and dividing by all customers served within the study area.

CAIDI

CAIDI (customer average interruption duration index) is an industry-defined term that is the result of dividing the duration of the average customer’s sustained outages by the frequency of outages for that average customer.  While the Company did not originally specify this metric under the umbrella of the Performance Standards Program within the context of the Service Standards Commitments, it has since been determined to be valuable for reporting purposes.  It is derived by dividing PS1 (SAIDI) by PS2 (SAIFI).

CEMI

CEMI is an acronym for Customers Experiencing Multiple (Sustained and Momentary) Interruptions.  This index depicts repetition of outages across the period being reported and can be an indicator of recent portions of the system that have experienced reliability challenges.  This metric is used to evaluate customer-specific reliability in Section 4 Customer Reliability Communications.

MAIFIE

MAIFIE (momentary average interruption event frequency index) is an industry standard index that quantifies the frequency of all momentary interruption events that the average customer experiences during a given time-frame.  It is calculated by counting all momentary interruptions which occur within a 5 minute time period, as long as the interruption event did not result in a device experiencing a sustained interruption.

CPI99

CPI99 is an acronym for Circuit Performance Indicator, which uses key reliability metrics of the circuit to identify underperforming circuits.  It excludes Major Event and Loss of Supply or Transmission outages.  The variables and equation for calculating CPI are:

CPI = Index * ((SAIDI * WF * NF) + (SAIFI * WF * NF) + (MAIFI * WF * NF) + (Lockouts * WF * NF))

Index:  10.645

SAIDI: Weighting Factor 0.30, Normalizing Factor 0.029

SAIFI:  Weighting Factor 0.30, Normalizing Factor 2.439

MAIFI:  Weighting Factor 0.20, Normalizing Factor 0.70

Lockouts:  Weighting Factor 0.20, Normalizing Factor 2.00

Therefore, 10.645 * ((3-year SAIDI * 0.30 * 0.029) + (3-year SAIFI * 0.30 * 2.439) + (3-year MAIFI * 0.20 * 0.70) + (3-year breaker lockouts * 0.20 * 2.00)) = CPI Score

CPI05

CPI05 is an acronym for Circuit Performance Indicator, which uses key reliability metrics of the circuit to identify underperforming circuits.  Unlike CPI99 it includes Major Event and Loss of Supply or Transmission outages.  The calculation of CPI05 uses the same weighting and normalizing factors as CPI99.

Performance Types & Commitments

Pacific Power recognizes two categories of performance:  underlying performance and major events.  Major events represent the atypical, with extraordinary numbers and durations for outages beyond the usual.  Ordinary outages are incorporated within underlying performance.  These types of events are further defined below.

Major Events

Pursuant to WAC 480-100-393 Electric Reliability Annual Monitoring and Reporting Plan, modified February 2011, the company recognizes two types of major events in Washington:

- A SAIDI-based Major Event is defined as a 24-hour period where SAIDI exceeds a statistically derived threshold value, as detailed in IEEE Distribution Reliability Standard 1366-2003/2012.

- A SAIFI-Based Major Event is defined as an event in which more than 10% of an operating area’s customers are simultaneously without service as a result of a sustained interruption.

Underlying Events

Within the industry, there has been a great need to develop methodologies to evaluate year-on-year performance.  This has led to the development of methods for segregating outlier days.  Those days which fall below the statistically derived threshold represent “underlying” performance, and are valid (with some minor considerations for changes in reporting practices) for establishing and evaluating meaningful performance trends over time.

Performance Targets

The Company and Commission, in the MidAmerican transaction docket, UE05-01590, agreed to extend Service Standards through 12/31/2011.  Within Washington, because performance delivered by the Company falls within industry second quartile performance levels, the Company committed that it would achieve performance by 12/31/2011 that maintains performance targets set in prior Merger Commitment Periods.  Additionally in WAC 480-100-393 the Company is required to set baseline metrics and when performance deviates from those baselines, explain the reasons for that deviation and any action plans which may result from that level of performance.

## Service Territory

Service Territory Map

Contained below is a graphic of the Company’s Washington service territory, colored by operating area.

# CUSTOMER GUARANTEES SUMMARY

Overall guarantee performance remains above 99%, demonstrating Pacific Power’s continued commitment to customer satisfaction.

Customer Communications: The Customer Guarantee program was highlighted throughout the year in customer communications as follows:

- performance reports are included in June's billing statements

- the program is highlighted in Voices

- the program is highlighted in the company's newsletter

- each new customer is mailed a welcome aboard pamphlet that features the program and how to file a claim

- Pacific Power's website features the program with information for our customers

(Major Events are excluded from the Customer Guarantees program.)

# RELIABILITY PERFORMANCE

During the reporting period, the company’s reliability compared favorably to its baseline performance level as established in 2003.  The year’s “Major Events Excluded As Reported” SAIDI performance of 107 minutes was much better than the approved SAIDI baseline of 150 minutes, while the year’s “Major Events Excluded As Reported” SAIFI performance of 0.760 events was also much better than the approved SAIFI baseline of 0.975 events.  Various reliability metrics are shown below providing a historical perspective, including an additional 5-year rolling average metric.

## Multi-Year Historical Performance

## System Average Interruption Duration Index (SAIDI)

During the reporting period, the company delivered reliability results better than baseline for both outage duration (SAIDI) and outage frequency (SAIFI); the performance compared to baselines is identified in Section 3.1 above.

During the year, there were four SAIDI-based major events: loss of substation February 18 and March 11, and thunderstorms September 5-6 and September 15.  There was one SAIFI-based major event:  October 28 due to windstorm.   These events excluded 91 minutes from underlying SAIDI.  (As noted in the Definitions section of this report, the company records two major event types and reports reliability metrics reflecting results under both methods.)  Copies of the Company’s filed major events are included in the Appendix of this report.

During the period, there were twelve significant event days (daily underlying SAIDI of 2.12 minutes or more).  These twelve days account for 47 SAIDI minutes, representing 44% of the total underlying SAIDI results for the year.

| January 1 through December 31, 2013 |
| --- |
| 2013 SAIDI Goal = 130 | SAIDI Actual |
| Total Performance | 198 |
| SAIDI-based Major Events Excluded | 114 |
| Reported Major Events Excluded | 107 |

## System Average Interruption Frequency Index (SAIFI)

Like outage duration, outage frequency was better than baseline and internal goal in 2013.

| January 1 through December 31, 2013 |
| --- |
| 2013 SAIFI Goal = 1.000 | SAIFI Actual |
| Total Performance | 1.048 |
| SAIDI-based Major Events Excluded | 0.791 |
| Reported Major Events Excluded | 0.760 |

## Operating Area Metrics

Washington operating area performance for the reporting period is listed in the table below.

| January 1 – December 31, 2013 | Including Major Events | Excluding SAIDI-based Major Events | Reported Major Events Excluded |
| --- | --- | --- | --- |
|  | SAIDI | SAIFI | CAIDI | SAIDI | SAIFI | CAIDI | SAIDI | SAIFI | CAIDI |
| SUNNYSIDE | 189 | 1.241 | 152 | 109 | 1.014 | 107 | 103 | 0.846 | 121 |
| WALLA WALLA | 296 | 1.214 | 244 | 77 | 0.756 | 102 | 77 | 0.756 | 102 |
| YAKIMA | 186 | 0.985 | 189 | 124 | 0.765 | 163 | 124 | 0.765 | 163 |

2013 Sunnyside Customer Count:		24,630

2013 Walla Walla Customer Count:	27,370

2013 Yakima Customer Count:		81,709

## Cause Code Analysis

The table and charts below break out the number of incidents, customer hours lost, and sustained interruptions by cause code.  Customer Minutes Lost is directly related to SAIDI (average outage duration); Sustained Interruptions is directly related to SAIFI (average outage frequency).  Certain types of outages typically result in high duration, but are infrequent, such as Loss of Supply outages.  Others tend to be more frequent, but are generally shorter duration.  The pie charts depict the breakdown of performance results by percentage of each cause category.  Following the pie charts, a cause category table lists the direct causes with definitions and examples.  Thereafter is a historical view of cause codes, as they summarize to annual SAIDI and SAIFI performance.

| Cause Category | Description and Examples |
| --- | --- |
| Environment | Contamination or Airborne Deposit (i.e., salt, trona ash, other chemical dust, sawdust, etc.); corrosive environment; flooding due to rivers, broken water main, etc.; fire/smoke related to forest, brush or building fires (not including fires due to faults or lightning). |
| Weather | Wind (excluding windborne material); snow, sleet or blizzard; ice; freezing fog; frost; lightning. |
| Equipment Failure | Structural deterioration due to age (incl. pole rot); electrical load above limits; failure for no apparent reason; conditions resulting in a pole/cross arm fire due to reduced insulation qualities; equipment affected by fault on nearby equipment (i.e. broken conductor hits another line). |
| Interference | Willful damage, interference or theft; such as gun shots, rock throwing, etc.; customer, contractor or other utility dig-in; contact by outside utility, contractor or other third-party individual; vehicle accident, including car, truck, tractor, aircraft, manned balloon; other interfering object such as straw, shoes, string, balloon. |
| Animals and Birds | Any problem nest that requires removal, relocation, trimming, etc.; any birds, squirrels or other animals, whether or not remains found. |
| Operational | Accidental Contact by Pacific Power or Pacific Power’s Contractors (including live-line work); switching error; testing or commissioning error; relay setting error, including wrong fuse size, equipment by-passed; incorrect circuit records or identification; faulty installation or construction; operational or safety restriction. |
| Loss of Supply | Failure of supply from Generator or Transmission system; failure of distribution substation equipment. |
| Planned | Transmission requested, affects distribution sub and distribution circuits; company outage taken to make repairs after storm damage, car hit pole, etc.; construction work, regardless if notice is given; rolling blackouts. |
| Trees | Growing or falling trees. |
| Other | Cause Unknown. |

## Areas of Greatest Concern

During 2013, reliability enhancement efforts continue to focus on improved system hardening and protection.  Through history this has included replacement of hydraulic reclosers, upgrades of substation breakers and/or relays and coordination of circuit protection devices, such as fuses and reclosers.  The company regularly finds some of its most cost-effective reliability improvements can be achieved by focusing on circuits that do not appear to be well coordinated, which it finds through data mining of its outage reporting data.  A well-coordinated circuit will minimize how many customers experience an interruption as the result of a fault event.

Additionally, it has continued its circuit hardening efforts by strategic deployment of circuit inspection, pole and/or crossarm replacement and vegetation hot-spotting.  Along with circuit hardening and protection efforts, it has reviewed opportunities for localized activities such as feeder ties and cable replacement activities.

In this year’s improvement plans, replacement of mechanical relays with electronic relays is planned.  These devices have fault memories which allow for targeted inspection when faults occur.  They also provide better coordination between the substation circuit equipment and down-line protective equipment, such as reclosers and fuses.

Additional devices that help diagnose the location of circuit’s fault events are planned with the installation of fault indicators.  These allow for faster restoration after an event as well as targeting specific hardening opportunities for segments where the fault indicators exist.

Another area of concern within Yakima and Sunnyside, particularly around Toppenish and Selah substations, has been animal-caused interruptions.  With the encroachment of new species into the area these two substations have experienced significant interruption activity which precipitated the initiation of projects designed to animal-guard substation equipment.  While this activity is no guarantee that future animal outages will not occur, it should result in improved performance against such intrusion.

Finally, the implementation of a web-based notification tool, which alerts when interrupting devices (such as substation breakers, line reclosers or fuses) have exceeded proscribed performance thresholds has helped to promptly focus field investigative activities; this new capability has delivered substantial improvements to customers.

The table below lists reliability projects identified and currently underway for Washington’s Areas of Greatest Concern; these circuits will be subsequently reported as Program Year 14 circuits in Section 3.7.

| Sub | Circuit Name | Circuit | 2014 Project | Baseline CPI05 |
| --- | --- | --- | --- | --- |
| CENTRAL (WA) | Memorial | 5W2 | Install 3 sets of remote fault indicators. 2 at reclosers, 1 at 3-phase switch. | 92 |
| WILEY | Occidental | 5Y382 | Replace relays on 5Y382 at Wiley Sub (Engineering CY13, Construction CY14) | 97 |
| WILEY | Tampico | 5Y380 | Replace relays on 5Y380 at Wiley Sub (Engineering CY14; Construction CY15) | 103 |
| SELAH | 10th Street | 5Y437 | Add 2 switches. FP#336001 on west side FP#330400 | 157 |
| SELAH | Gravel | 5Y99 | Replace relays on 5Y99 at Selah Sub (Engineering CY14; Construction CY15) | 180 |

## Reduce CPI for Worst Performing Circuits by 20%

On a routine basis, the company reviews circuits for performance.  One of the measures that it uses is called circuit performance indicator (CPI), which is a blended weighting of key reliability metrics covering a three-year time frame.  The higher the number, the poorer the blended performance the circuit is delivering.  As part of the company’s Performance Standards Program, it annually selects a set of Worst Performing Circuits for target improvement.  The improvements are to be completed within two years of selection.   Within five years of selection, the average performance is to be improved by at least 20% (as measured by comparing current performance against baseline performance).  Program years 1-12 have previously met improvement targets so are no longer shown in the performance update below.

| WASHINGTON WORST PERFORMING CIRCUITS | BASELINE | Performance 12/31/2012 |
| --- | --- | --- |
| PROGRAM YEAR 13: |
| DONALD 5Y330 | 90 | n/a |
| FORNEY 5Y94 | 207 | n/a |
| PRESCOTT 5W305 | 94 | n/a |
| STEIN 5Y164 | 156 | n/a |
| TERRACE HTS 5Y10 | 114 | n/a |
| TARGET SCORE = 106 | 132 | n/a |

## Restore Service to 80% of Customers within 3 Hours

The Company targets restoring power to 80% of its customers within 3 hours, however during 2013 this target was not met, mostly due to the impact of certain significant events that resulted in longer than-desired restoration.

| WASHINGTON RESTORATIONS WITHIN 3 HOURS |
| --- |
| January 1 through December 31, 2013 | 79% |
| January | February | March | April | May | June |
| 70% | 87% | 74% | 81% | 74% | 70% |
| July | August | September | October | November | December |
| 83% | 82% | 85% | 82% | 63% | 83% |

## Telephone Service and Response to Commission Complaints

| COMMITMENT | GOAL | PERFORMANCE |
| --- | --- | --- |
| PS5-Answer calls within 30 seconds | 80% | 80% |
| PS6a) Respond to commission complaints within 3 days | 95% | 97% |
| PS6b) Respond to commission complaints regarding service disconnects within 4 hours | 95% | 100% |
| PS6c) Resolve commission complaints within 30 days | 95% | 98% |

# CUSTOMER RELIABILITY COMMUNICATIONS

## Reliability Complaint Process Overview

The company’s process for managing customers’ concerns about reliability are to provide opportunities to hear customer concerns, respond to those concerns, and where necessary, provide customers an opportunity to elevate those concerns.

## Customer Complaint Tracking

Listed below are the various avenues available to a customer to resolve concerns about reliability performance.

- Customer Reliability Inquiry

The company records customer inquiries about reliability as Outage Power Quality transactions in its customer service system, referred to as “OPQ” transactions.

- Customer Complaint

If a customer’s reliability concerns are not met through the process associated with the OPQ transaction, a customer can register a 1-800 complaint with the company.  This is recorded in a complaint repository from which regular reports are prepared and circulated for resolution.

- Commission Complaint

If a customer’s reliability concerns are not met through the process associated with a 1-800 complaint, a customer can register a complaint with the Commission.  This is recorded by the Commission staff and also by the company in a complaint repository.  Regular reports are prepared and circulated for resolution of these items.

## Customer Complaints Recorded During the Period

Listed below, by the recording source, are reliability-related customer complaints if any were received for Washington services during the reporting period.

- Informal Complaints (1-800 Customer Advocacy Team)

There was one Informal Complaint received by the company in the reporting period.

- Commission Complaints

There was one Commission Complaint in the reporting period.

# WASHINGTON RELIABILITY RESULTS DURING 2013

To geospatially display reliability results the Company has developed its GREAT tool which blends circuit topology with outage history and uses a variety of industry metrics (differentiated by color) to indicate areas where reliability analysis should be targeted. In the subsequent plots, two important reliability indicators are depicted. In each plot thumbnails are used to orient the graphic.  First, plots with customers experiencing multiple interruptions (CEMI) are shown. This measure shows how many sustained and momentary outages a given service transformer has experienced. The greater the color intensity, with red as the most severe, the more interruptions the transformer has had.  Note that this depiction exceeds the requirements of the reporting rule, but is helpful to the Company in selecting areas of reliability concern.  Second sustained interruptions are shown.  This measure shows how many sustained outages a service transformer has experienced, which is aligned with the requirements of the reporting rules. Third, service transformer-level SAIDI is shown. While technically SAIDI is a “system-level” metric, the local application of this metric can be revealing in determining service transformers that have had long cumulative durations of outages during the period. As explained previously, the greater the color intensity, the longer the outage duration during the period. (Major events, customer requested and prearranged outages are excluded from underlying results.)

## State Reliability

## 5W2:  Memorial Feeder

## 5Y382:  Occidental Feeder

## 5Y380:  Tampico Feeder

## 5Y437:  10th Street Feeder

## 5Y99:  Gravel Feeder

# APPENDIX A:  2013 MAJOR EVENT FILINGS

# Footnotes

The Company committed to Service Standards Programs that expired on 12/31/2011; during the program all elements committed to were delivered successfully.  By terms of the commitment any changes to the program required the approval of the Commission.  The Company has proposed no changes to the program, but continues at this time, to operate consistently with its historical program.  State reliability reporting rules establish requirements that the Company interprets as generally encompassing the requirements of Network Performance Standards 1-3.

Although the Performance Standard indicates that complaints will be responded to within 3 days, the Company acknowledges and adheres to the requirements set forth in 480-100-173(3)(a).

IEEE1366-2003/2012 was first adopted by the IEEE Commissioners on December 23, 2003.  The definitions and methodology detailed therein are now industry standards, which have since been affirmed in recent balloting activities.

During calendar 2013, the calculated threshold for a major event was 10.56 minutes; for 2014, it will be 8.06 minutes.

On a trial basis, the Company established a variable of 1.75 times the standard deviation of its natural log SAIDI results.

Although the Performance Standard indicates that complaints will be responded to within 3 days, the Company acknowledges and adheres to the requirements set forth in 480-100-173(3)(a).