## Sheet 1
REDACTED VERSION

## BDJ-3 (R)
PUGET SOUND ENERGY
PEAK CREDIT METHOD FOR 2019 GRC WITH UPDATED DATA
COMPANY PROPOSAL
REDACTED VERSION
Peak
|  |  |  | Peaker | CCCT | Credit
|  | Levelized Cost ($/MWh) |  |  | 72.4175
|  | Levelized Cost ($/kW-yr) |  | 95.7177 | 507.5018 | 18.86%
Assumptions
Plant Assumptions
|  |  |  | Peaker | CCCT | Notes
1 | Capital Costs ($/kW-yr) |  |  | 671.3542 | 1341.9466 | 2019 Dollars
2 | Fixed Charge Rate |  |  | 9.54% | 9.54%
3 | Fixed O&M ($/kW-yr) |  |  | 12.6376 | 56.7024 | 2019 Dollars
4 | Variable O&M ($/MWh) |  |  | 24.3593 | 2.6477 | 2019 Dollars
5 | Heat Rate (Btu/kWh) |  |  | 9822.6 | 6650.4
6 | Weighted Cost of Capital |  |  | 7.44% | 7.44%
7 | Capacity Factor |  |  | 0% | 80%
8 | Reserve Margin |  |  | 3% | 3%
9 | Planning Margin |  |  | 13.5% | 13.5%
10 | CO2 Emissions (tons/GWh) |  |  | 574.6221 | 389.0484
Weighted Cost of Capital
|  |  |  | Pro Forma |  | Cost of
|  |  |  | Capital % | Cost % | Capital
11 | Other |  |  |  |  | 0%
12 | Debt |  |  | 51.5% | 5.5% | 2.83%
13 | Common Equity |  |  | 48.5% | 9.5% | 4.61%
14 | TOTAL |  |  | 100% |  | 7.44%
Combined Cycle Plant (Nominal $)
| Capital Cost | Fixed O&M | Variable O&M | Natural Gas | Emissions | Margin | Total | Annual
Year | $/MWh | $/MWh | $/MWh | $/MWh | $/MWh | $/MWh | $/MWh | Inflation
2019 | 18.27 | 8.09 | 2.65 | 18.5704 | 0 | 4.3494 | 51.9298 | 0%
2020 | 18.27 | 8.29 | 2.72 | 18.7722 | 0 | 4.3824 | 52.4346 | 2.5%
2021 | 18.27 | 8.5 | 2.79 | 19.3306 | 0 | 4.417 | 53.3077 | 2.5%
2022 | 18.27 | 8.71 | 2.86 |  | 0 | 4.4517 |  | 2.5%
2023 | 18.27 | 8.93 | 2.93 |  | 0 | 4.488 |  | 2.5%
2024 | 18.27 | 9.15 | 3 |  | 0 | 4.5243 |  | 2.5%
2025 | 18.27 | 9.38 | 3.08 |  | 0 | 4.5622 |  | 2.5%
2026 | 18.27 | 9.61 | 3.16 |  | 0 | 4.6002 |  | 2.5%
2027 | 18.27 | 9.85 | 3.24 |  | 0 | 4.6398 |  | 2.5%
2028 | 18.27 | 10.1 | 3.32 |  | 0 | 4.681 |  | 2.5%
2029 | 18.27 | 10.35 | 3.4 |  | 0 | 4.7223 |  | 2.5%
2030 | 18.27 | 10.61 | 3.49 |  | 0 | 4.7652 |  | 2.5%
2031 | 18.27 | 10.88 | 3.58 |  | 0 | 4.8098 |  | 2.5%
2032 | 18.27 | 11.15 | 3.67 |  | 0 | 4.8543 |  | 2.5%
2033 | 18.27 | 11.43 | 3.76 |  | 0 | 4.9005 |  | 2.5%
2034 | 18.27 | 11.72 | 3.85 |  | 0 | 4.9484 |  | 2.5%
2035 | 18.27 | 12.01 | 3.95 |  | 0 | 4.9962 |  | 2.5%
2036 | 18.27 | 12.31 | 4.05 |  | 0 | 5.0457 |  | 2.5%
2037 | 18.27 | 12.62 | 4.15 |  | 0 | 5.0969 |  | 2.5%
2038 | 18.27 | 12.94 | 4.25 |  | 0 | 5.1497 |  | 2.5%
2039 | 18.27 | 13.26 | 4.36 |  | 0 | 5.2025 |  | 2.5%
2040 | 18.27 | 13.59 | 4.47 |  | 0 | 5.2569 |  | 2.5%
2041 | 18.27 | 13.93 | 4.58 |  | 0 | 5.313 |  | 2.5%
2042 | 18.27 | 14.28 | 4.69 |  | 0 | 5.3708 |  | 2.5%
2043 | 18.27 | 14.64 | 4.81 |  | 0 | 5.4301 |  | 2.5%
2044 | 18.27 | 15.01 | 4.93 |  | 0 | 5.4912 |  | 2.5%
Peaker Plant (Nominal $)
| Capital Cost | Fixed O&M | Variable O&M | Natural Gas | Emissions | Margin | Total | Annual
Year | $/kW-yr | $/kW-yr | $/kW-yr | $/kW-yr | $/kW-yr | $/kW-yr | $/kW-yr | Inflation
2019 | 64.05 | 12.64 | 0 | 0 | 0 | 12.6539 | 89.3439 | 0%
2020 | 64.05 | 12.96 | 0 | 0 | 0 | 12.7066 | 89.7166 | 2.5%
2021 | 64.05 | 13.28 | 0 | 0 | 0 | 12.7595 | 90.0894 | 2.5%
2022 | 64.05 | 13.61 | 0 |  | 0 | 12.8139 |  | 2.5%
2023 | 64.05 | 13.95 | 0 |  | 0 | 12.87 |  | 2.5%
2024 | 64.05 | 14.3 | 0 |  | 0 | 12.9277 |  | 2.5%
2025 | 64.05 | 14.66 | 0 |  | 0 | 12.9871 |  | 2.5%
2026 | 64.05 | 15.03 | 0 |  | 0 | 13.0482 |  | 2.5%
2027 | 64.05 | 15.41 | 0 |  | 0 | 13.1109 |  | 2.5%
2028 | 64.05 | 15.8 | 0 |  | 0 | 13.1753 |  | 2.5%
2029 | 64.05 | 16.2 | 0 |  | 0 | 13.2413 |  | 2.5%
2030 | 64.05 | 16.61 | 0 |  | 0 | 13.3089 |  | 2.5%
2031 | 64.05 | 17.03 | 0 |  | 0 | 13.3782 |  | 2.5%
2032 | 64.05 | 17.46 | 0 |  | 0 | 13.4491 |  | 2.5%
2033 | 64.05 | 17.9 | 0 |  | 0 | 13.5217 |  | 2.5%
2034 | 64.05 | 18.35 | 0 |  | 0 | 13.596 |  | 2.5%
2035 | 64.05 | 18.81 | 0 |  | 0 | 13.6719 |  | 2.5%
2036 | 64.05 | 19.28 | 0 |  | 0 | 13.7494 |  | 2.5%
2037 | 64.05 | 19.76 | 0 |  | 0 | 13.8287 |  | 2.5%
2038 | 64.05 | 20.25 | 0 |  | 0 | 13.9095 |  | 2.5%
2039 | 64.05 | 20.76 | 0 |  | 0 | 13.9937 |  | 2.5%
2040 | 64.05 | 21.28 | 0 |  | 0 | 14.0794 |  | 2.5%
2041 | 64.05 | 21.81 | 0 |  | 0 | 14.1669 |  | 2.5%
2042 | 64.05 | 22.36 | 0 |  | 0 | 14.2576 |  | 2.5%
2043 | 64.05 | 22.92 | 0 |  | 0 | 14.3501 |  | 2.5%
2044 | 64.05 | 23.49 | 0 |  | 0 | 14.4441 |  | 2.5%

## Natural Gas Price Project (R)
Puget Sound Energy
Projected Natural Gas Prices |  |  |  |  | Fuel Price Adders
[6 empty] | CCCT | Peaker
Sumas Prices |  |  |  |  | Fuel loss (%) | 5.5% | 1.41%
2016-2021 Prices = | 3 month average forward marks from Sep 23 thru Dec 27, 2016 (65 business days). |  |  |  | Variable Gas Transport ($/MMBtu) | 0.0096 | 0.25335
2022 - 2038 Prices = | Wood Mackenzie Fall 2016 Long Term View Price Update |  |  |  | Taxes (%) | 3.852% | 3.852%
2039 - 2048 Prices = |  | 10 Year Trend
| ($/MMBtu) |  | ($/MMBtu) | ($/MMBtu)
| 2017 IRP |  | CCCT | Peaker
2016 | 2.1588 |  | 2.3772 | 2.5262
2017 | 2.8108 |  | 3.0923 | 3.2127
2018 | 2.5949 |  | 2.8555 | 2.9853
2019 | 2.5374 |  | 2.7924 | 2.9247
2020 | 2.565 |  | 2.8227 | 2.9539
2021 | 2.6416 |  | 2.9067 | 3.0345
2022
2023
2024
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2036
2037
2038
2039 |  | TREND
2040 |  | TREND
2041 |  | TREND
2042 |  | TREND
2043 |  | TREND
2044 |  | TREND
2045 |  | TREND
2046 |  | TREND
2047 |  | TREND
2048 |  | TREND
Note on H3: Jhaveri, Birud: 2017 IRP Appendix D page 31 for CCCT
Note on I3: Jhaveri, Birud: 2017 IRP Appendix D page 32 for Peaker w/ Oil Backup
Note on B12: 2017 IRP Base Gas price forecast using the 3 month average forward marks as of Sept 23, 2016 (2016-21) with the Wood Mac forecast (2022-2038)

## 2017 IRP Resource Costs
2017 IRP Electric Supply-Side Resources - Thermal
2016 $ | Units | CCCT - A | CCCT - B | Frame Peaker | Frame Peaker w/ Oil | Aero Peaker | Aero Peaker w/ Oil | Recip Engine | Recip Engine w/Oil | Update 2016$ to 2019$ = | 1.0591
ISO Capacity Primary | MW | 359.1 | 405.1 | 239 | 239 | 227.3 | 227.3 | 222 | 202.02
Capacity DF | MW | 53.865 | 60.765
Capital Cost + Duct Fire* | $/KW | 1267.0632 | 1298.5903 | 571.1297 | 633.8912 | 1003.9595 | 1069.9516 | 1276.5766 | 1477.0815
O&M Fixed | $/KW-yr | 8.1 | 7.3 | 6.4 | 11.2333 | 6.5 | 10.9217 | 6.5 | 10.6959
Flexibility | $/KW-yr | 2.5 | 2.4 | 23 | 23 | 10.2 | 10.1 | 7.8 | 7.8
O&M Variable (1) | $/MWh | 2.5 | 2.4 | 0.95 | 0.95 | 10.2 | 10.1 | 7.8 | 7.8
Start Up Costs (Major Maintenance) | $/Start | 2.7847 | 2.6907 | 9250 | 9250 |  |  |  |  | Peaker VOM + Major Maintenance = |  | 23
Capacity Credit | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Operating Reserves | % | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3%
Forced Outage Rate |  | 3% | 3% | 3% | 3% | 3% per unit | 3% per unit | 1% per unit | 1% per unit
Heat Rate – Baseload (HHV) (4) | Btu/KWh | 6650.4 | 6514.74 | 9822.6 | 9822.6 | 8986.2 | 8986.2 | 8425.2 | 8527.2
Heat Rate – Turndown (HHV) (4) | Btu/KWh | 7338.9 | 7472.52 | 12750 | 12750 | 14463.6 | 14463.6 | 10924.2 | 11026.2
Heat Rate – DF | Btu/KWh | 8500 | 8500
Min Capacity | % | 50% | 42% | 45% | 45% | 13% (25% per unit) | 13% (25% per unit) | 2% (25% per unit) | 2% (25% per unit)
Start Time (2) | minutes | 150 | 150 | 11.5 | 11.5 | 8 | 8 | 5 | 5
Location |  | PSE | PSE | PSE | PSE | PSE | PSE | PSE | PSE
Fixed Gas Transport | $/Dth/Day | 0.77996 | 0.77996 | 0.77996 | 0.008125 | 0.77996 | 0.008125 | 0.77996 | 0.008125
Fixed Gas Transport | $/KW-yr | 45.4383 | 44.5114 | 67.112 | 0.69913 | 61.3974 | 0.6396 | 57.5644 | 0.60693
Variable Gas Transport | $/MMBtu | 0.0096 | 0.0096 | 0.0096 | 0.25335 | 0.0096 | 0.25335 | 0.0096 | 0.25335
Fixed Transmission | $/KW-yr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Transmission | $/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions:
CO2 (3) - Natural Gas | lbs/MMBtu | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
CO2 (3) - Distillate Fuel Oil | lbs/MMBtu |  |  |  | 153 |  | 153 |  | 153
CO2 (3) - Ethane | lbs/MMBtu
Nox - Natural Gas | lbs/MMBtu | 0.0072 | 0.0072 | 0.0072 | 0.0072 | 0.0072 | 0.0072 | 0.0072 | 0.0072
Nox - Distillate Fuel Oil | lbs/MMBtu |  |  |  | 0.077 |  | 0.077 |  | 0.077
Nox - Ethane | lbs/MMBtu
First Year Available |  | 2022 | 2022 | 2021 | 2021 | 2021 | 2021 | 2021 | 2021
Economic Life | Years | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Greenfield Dev. & Const. Lead-time | years | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3
(1) Variable cost reflect the operating costs and major maintenance for all technologies except for the frame peaker which includes major maintenance in the start up costs.
(2) Start time for all technologies reflects the warm start on all units. The hot start follows a shutdown period of less than 8 hours.
(3) CO2 emissions reflect natural gas as the main source of fuel under normal operating conditions. In the event that the gas pipeline is constrained, the CO2 emissions would be higher for those plant that can run on oil backup as the secondary fuel source. The dual fuel reciprocating engines would require a minimal amount of diesel fuel when operating with natural gas as the primary fuel which is not captured in the emission rates.
(4) Includes 2% for degredation
|  | CCCT |  |  | Peaker |  | Notes
Capacity Factor | % | 80% |  |  | 2%
Reserve Margin | % | 3% |  |  | 3%
Planning Margin | % | 13.5% |  |  | 13.5% |  | 2017 IRP 5% LOLP
Emissions:
CO2 (3) - Natural Gas | Tons/MWh | 389.0484 |  |  | 574.6221
Note on P2: Jhaveri, Birud: Bureau of Labor Statistics US Inflation Rate, Cumulative price change: 5.91%
Note on Q9: Jhaveri, Birud: 2017 IRP Appendix P page 5-5 & 5-6 CC-A (CCCT) Variable O&M: $2.50/MWh PP-F (Peaker) Variable O&M: $23/MWh ->$0.095/MWh Operations Cost + ->$9,250/Start Marjor Maintenance

## EPA Table A1 Emission Costs
EPA Technical Support Document; Technical Update of the Social Cost of Carbon for Regulatory Impact Analysis; Under Executive Order 12866 - Page 25 (Appendix A)
https://www.epa.gov/sites/production/files/2016-12/documents/sc_co2_tsd_august_2016.pdf
| Table A1: Annual SC-CO2 Values: 2010-2050 (2007$/metric ton CO2) |  |  |  |  | Convert Metric to Short tons |  |  |  | Convert 2007$ to 2019$ |  |  |  | Nominal
[6 empty] | 1.1023 |  |  |  | 1.226 |  |  |  | 2.5%
| Year | 5% Average | 3% Average | 2.5% Average | High Impact (95th Pct at 3%) | 5% Average | 3% Average | 2.5% Average | High Impact (95th Pct at 3%) | 5% Average | 3% Average | 2.5% Average | High Impact (95th Pct at 3%)
| 2010 | 10 | 31 | 50 | 86 | 11.0231 | 34.1716 | 55.1155 | 94.7987 | 13.5143 | 41.8944 | 67.5716 | 116.2232
| 2011 | 11 | 32 | 51 | 90 | 12.1254 | 35.2739 | 56.2178 | 99.2079 | 14.8658 | 43.2458 | 68.923 | 121.6289
| 2012 | 11 | 33 | 53 | 93 | 12.1254 | 36.3762 | 58.4224 | 102.5148 | 14.8658 | 44.5973 | 71.6259 | 125.6832
| 2013 | 11 | 34 | 54 | 97 | 12.1254 | 37.4785 | 59.5247 | 106.9241 | 14.8658 | 45.9487 | 72.9773 | 131.0889
| 2014 | 11 | 35 | 55 | 101 | 12.1254 | 38.5808 | 60.627 | 111.3333 | 14.8658 | 47.3001 | 74.3288 | 136.4946
| 2015 | 11 | 36 | 56 | 105 | 12.1254 | 39.6832 | 61.7294 | 115.7425 | 14.8658 | 48.6516 | 75.6802 | 141.9004
| 2016 | 11 | 38 | 57 | 108 | 12.1254 | 41.8878 | 62.8317 | 119.0495 | 14.8658 | 51.3544 | 77.0316 | 145.9547
| 2017 | 11 | 39 | 59 | 112 | 12.1254 | 42.9901 | 65.0363 | 123.4587 | 14.8658 | 52.7059 | 79.7345 | 151.3604
| 2018 | 12 | 40 | 60 | 116 | 13.2277 | 44.0924 | 66.1386 | 127.868 | 16.2172 | 54.0573 | 81.0859 | 156.7661
| 2019 | 12 | 41 | 61 | 120 | 13.2277 | 45.1947 | 67.2409 | 132.2772 | 16.2172 | 55.4087 | 82.4374 | 162.1718 | 0
| 2020 | 12 | 42 | 62 | 123 | 13.2277 | 46.297 | 68.3432 | 135.5841 | 16.2172 | 56.7601 | 83.7888 | 166.2261 | 0
| 2021 | 12 | 42 | 63 | 126 | 13.2277 | 46.297 | 69.4455 | 138.8911 | 16.2172 | 56.7601 | 85.1402 | 170.2804 | 0
| 2022 | 13 | 43 | 64 | 129 | 14.33 | 47.3993 | 70.5478 | 142.198 | 17.5686 | 58.1116 | 86.4917 | 174.3347 | 0
| 2023 | 13 | 44 | 65 | 132 | 14.33 | 48.5016 | 71.6501 | 145.5049 | 17.5686 | 59.463 | 87.8431 | 178.389 | 0
| 2024 | 13 | 45 | 66 | 135 | 14.33 | 49.6039 | 72.7525 | 148.8118 | 17.5686 | 60.8144 | 89.1945 | 182.4433 | 0
| 2025 | 14 | 46 | 68 | 138 | 15.4323 | 50.7063 | 74.9571 | 152.1188 | 18.92 | 62.1659 | 91.8974 | 186.4976 | 0
| 2026 | 14 | 47 | 69 | 141 | 15.4323 | 51.8086 | 76.0594 | 155.4257 | 18.92 | 63.5173 | 93.2488 | 190.5519 | 0
| 2027 | 15 | 48 | 70 | 143 | 16.5346 | 52.9109 | 77.1617 | 157.6303 | 20.2715 | 64.8687 | 94.6002 | 193.2548 | 0
| 2028 | 15 | 49 | 71 | 146 | 16.5346 | 54.0132 | 78.264 | 160.9373 | 20.2715 | 66.2202 | 95.9517 | 197.3091 | 0
| 2029 | 15 | 49 | 72 | 149 | 16.5346 | 54.0132 | 79.3663 | 164.2442 | 20.2715 | 66.2202 | 97.3031 | 201.3634 | 0
| 2030 | 16 | 50 | 73 | 152 | 17.637 | 55.1155 | 80.4686 | 167.5511 | 21.6229 | 67.5716 | 98.6545 | 205.4177 | 0
| 2031 | 16 | 51 | 74 | 155 | 17.637 | 56.2178 | 81.5709 | 170.858 | 21.6229 | 68.923 | 100.006 | 209.472 | 0
| 2032 | 17 | 52 | 75 | 158 | 18.7393 | 57.3201 | 82.6732 | 174.165 | 22.9743 | 70.2745 | 101.3574 | 213.5263 | 0
| 2033 | 17 | 53 | 76 | 161 | 18.7393 | 58.4224 | 83.7756 | 177.4719 | 22.9743 | 71.6259 | 102.7088 | 217.5806 | 0
| 2034 | 18 | 54 | 77 | 164 | 19.8416 | 59.5247 | 84.8779 | 180.7788 | 24.3258 | 72.9773 | 104.0603 | 221.6349 | 0
| 2035 | 18 | 55 | 78 | 168 | 19.8416 | 60.627 | 85.9802 | 185.1881 | 24.3258 | 74.3288 | 105.4117 | 227.0406 | 0
| 2036 | 19 | 56 | 79 | 171 | 20.9439 | 61.7294 | 87.0825 | 188.495 | 25.6772 | 75.6802 | 106.7631 | 231.0949 | 0
| 2037 | 19 | 57 | 81 | 174 | 20.9439 | 62.8317 | 89.2871 | 191.8019 | 25.6772 | 77.0316 | 109.466 | 235.1492 | 0
| 2038 | 20 | 58 | 82 | 177 | 22.0462 | 63.934 | 90.3894 | 195.1089 | 27.0286 | 78.3831 | 110.8174 | 239.2035 | 0
| 2039 | 20 | 59 | 83 | 180 | 22.0462 | 65.0363 | 91.4917 | 198.4158 | 27.0286 | 79.7345 | 112.1689 | 243.2578 | 0
| 2040 | 21 | 60 | 84 | 183 | 23.1485 | 66.1386 | 92.594 | 201.7227 | 28.3801 | 81.0859 | 113.5203 | 247.3121 | 0
| 2041 | 21 | 61 | 85 | 186 | 23.1485 | 67.2409 | 93.6963 | 205.0297 | 28.3801 | 82.4374 | 114.8717 | 251.3664 | 0
| 2042 | 22 | 61 | 86 | 189 | 24.2508 | 67.2409 | 94.7987 | 208.3366 | 29.7315 | 82.4374 | 116.2232 | 255.4207 | 0
| 2043 | 22 | 62 | 87 | 192 | 24.2508 | 68.3432 | 95.901 | 211.6435 | 29.7315 | 83.7888 | 117.5746 | 259.475 | 0
| 2044 | 23 | 63 | 88 | 194 | 25.3531 | 69.4455 | 97.0033 | 213.8481 | 31.0829 | 85.1402 | 118.926 | 262.1778 | 0
| 2045 | 23 | 64 | 89 | 197 | 25.3531 | 70.5478 | 98.1056 | 217.1551 | 31.0829 | 86.4917 | 120.2775 | 266.2321 | 0
| 2046 | 24 | 65 | 90 | 200 | 26.4554 | 71.6501 | 99.2079 | 220.462 | 32.4344 | 87.8431 | 121.6289 | 270.2864 | 0
| 2047 | 24 | 66 | 92 | 203 | 26.4554 | 72.7525 | 101.4125 | 223.7689 | 32.4344 | 89.1945 | 124.3317 | 274.3407 | 0
| 2048 | 25 | 67 | 93 | 206 | 27.5577 | 73.8548 | 102.5148 | 227.0759 | 33.7858 | 90.5459 | 125.6832 | 278.395 | 0
| 2049 | 25 | 68 | 94 | 209 | 27.5577 | 74.9571 | 103.6171 | 230.3828 | 33.7858 | 91.8974 | 127.0346 | 282.4493 | 0
| 2050 | 26 | 69 | 95 | 212 | 28.6601 | 76.0594 | 104.7194 | 233.6897 | 35.1372 | 93.2488 | 128.386 | 286.5036 | 0

## Fixed Charge Rate
Summary Results 35 Years
Net Present Value of Cash Flows (NPV) | -34.5222 | Levelized Revenue Requirement Rate | 9.535%
Present Value of Regulated Revenues | 1177.6706 | Present Value of Capital Investments | 1000
Present Value of Unregulated Revenues | 0 | Capital Recovery Factor | 8.097%
Present Value of Total Revenues | 1177.6706 | Annuitized Revenue Requirement | 95.355
Cumulative PV of Cash Flows