## QTRLY-SUM
Mint Farm Energy Center, LLC
4th QUARTER 2007
CT/HRSG |  |  |  | Total
|  |  |  | THIS | PREV | 12 Mth
Month | Jan | Feb | Mar | QTR | 3 QTRs | RLG TOT
CT Hours | 579.2 | 333.93 | 313.72 | 1226.85 | N/A | N/A
HRSG - Duct Burners Hrs | 7.57 | 16.72 | 0 | 24.29 | N/A | N/A
Fuel Use (KSCF) | 1011935 | 546305 | 450966 | 2009206 | N/A | N/A
BTU/SCF |  | 1020
Heat Input (MMBTU) | 1032173.7 | 557231.1 | 459985.32 | 2049390.12 | N/A | N/A
Annual Capacity Factor |  | N/A
Factor (lb/MMBtu) |  | permit limit
NOx (lbs) | 12336.96 | 7112.709 | 6682.236 | 26131.905 | N/A | N/A
Factor (lb/MMBtu) |  | permit limit
CO (lbs) | 18013.12 | 10385.223 | 9756.692 | 38155.035 | N/A | N/A
Factor (lb/MMBtu) |  | 0.0006
SO2 (lbs) | 619.3042 | 334.3387 | 275.9912 | 1229.6341 | N/A | N/A
Factor (lb/MMBtu) |  | 0.0051
PM (lbs) | 5264.0859 | 2841.8786 | 2345.9251 | 10451.8896 | N/A | N/A
Factor (lb/MMBtu) |  | permit limit
VOC (lbs) | 5154.88 | 2971.977 | 2792.108 | 10918.965 | N/A | N/A
Factor (lb/MMBtu) |  | 0.00033
NH3 (lbs) | 340.6173 | 183.8863 | 151.7952 | 676.2987 | N/A | N/A
|  |  |  | 0 | N/A | N/A
Cooling Tower Hrs* | 579.2 | 333.93 | 313.72 | 67.27 | N/A | N/A
Diesel Fire Pump Hrs | N/A | N/A | N/A | N/A | N/A | N/A
Emergency Generator Hrs | 0 | 0 | 1 | 0 | N/A | N/A
Fuel Preheater Hrs | N/A | N/A | N/A | N/A | N/A | N/A
*Assume Cooling Tower Operating hours equals Combustion Turbine operating hours
Note on D22: .0051 utilized per input from nearby similar plant

## Summary of CT hours
Summary of GT Fired Hours
Date | CT Fire St Hr | CT Fire St Min | Trip/End Hr | Trip/ End Min | Total Fired Hrs
2008-01-01 |  |  |  |  | 0
2008-01-02 |  |  |  |  | 0
2008-01-03 |  |  |  |  | 0
2008-01-04 | 7 | 49 | 8 | 6 | -0.28333
2008-01-05 |  |  |  |  | 0
2008-01-06 | 9 | 6 | 22 | 6 | -13
2008-01-06 |  |  |  |  | 0
2008-01-07 | 6 | 46 | 24 |  | -17.2333
2008-01-08 |  |  | 24 |  | -24
2008-01-09 |  |  | 24 |  | -24
2008-01-10 |  |  | 0 | 23 | -0.38333
2008-01-10 | 6 | 50 | 22 | 24 | -15.5667
2008-01-11 | 10 | 49 | 22 | 21 | -11.5333
2008-01-12 | 6 | 48 | 24 |  | -17.2
2008-01-13 |  |  | 24 |  | -24
2008-01-14 |  |  | 24 |  | -24
2008-01-15 |  |  | 24 |  | -24
2008-01-16 |  |  | 24 |  | -24
2008-01-17 |  |  | 24 |  | -24
2008-01-18 |  |  | 24 |  | -24
2008-01-19 |  |  | 24 |  | -24
2008-01-20 |  |  | 24 |  | -24
2008-01-21 |  |  | 24 |  | -24
2008-01-22 |  |  | 24 |  | -24
2008-01-23 |  |  | 24 |  | -24
2008-01-24 |  |  | 24 |  | -24
2008-01-25 |  |  | 24 |  | -24
2008-01-26 |  |  | 24 |  | -24
2008-01-27 |  |  | 24 |  | -24
2008-01-28 |  |  | 24 |  | -24
2008-01-29 |  |  | 24 |  | -24
2008-01-30 |  |  | 24 |  | -24
2008-01-31 |  |  | 24 |  | -24
-579.2
Date | CT Fire St Hr | CT Fire St Min | Trip/End Hr | Trip/ End Min | Total Fired Hrs
2008-02-01 |  |  | 24 |  | -24
2008-02-02 |  |  | 24 |  | -24
2008-02-03 |  |  | 24 |  | -24
2008-02-04 |  |  | 24 |  | -24
2008-02-05 |  |  | 24 |  | -24
2008-02-06 |  |  | 24 |  | -24
2008-02-07 |  |  | 22 | 22 | -22.3667
2008-02-08 |  |  |  |  | 0
2008-02-09 |  |  |  |  | 0
2008-02-10 |  |  |  |  | 0
2008-02-11 | 13 | 49 | 18 | 58 | -5.15
2008-02-11 |  |  |  |  | 0
2008-02-12 |  |  |  |  | 0
2008-02-13 |  |  |  |  | 0
2008-02-14 |  |  |  |  | 0
2008-02-15 | 0 | 50 | 19 | 20 | -18.5
2008-02-16 |  |  |  |  | 0
2008-02-17 |  |  |  |  | 0
2008-02-18 | 2 | 50 | 11 | 22 | -8.5333
2008-02-19 | 3 | 48 | 22 | 18 | -18.5
2008-02-20 | 3 | 49 | 22 | 17 | -18.4667
2008-02-21 | 3 | 48 | 22 | 18 | -18.5
2008-02-22 |  |  |  |  | 0
2008-02-23 |  |  |  |  | 0
2008-02-24 |  |  |  |  | 0
2008-02-25 | 12 | 50 | 15 | 8 | -2.3
2008-02-26 | 1 | 46 | 23 | 35 | -21.8167
2008-02-27 | 2 | 53 | 3 | 3 | -0.16667
2008-02-27 | 3 | 48 | 22 | 20 | -18.5333
2008-02-28 | 3 | 44 | 22 | 19 | -18.5833
2008-02-29 | 3 | 49 | 22 | 20 | -18.5167
0
0
0
0
-333.9333
Date | CT Fire St Hr | CT Fire St Min | Trip/End Hr | Trip/ End Min | Total Fired Hrs
2008-03-01 | 5 | 53 | 10 | 24 | -4.5167
2008-03-02 |  |  |  |  | 0
2008-03-03 | 15 | 47 | 21 | 22 | -5.5833
2008-03-04 | 4 | 49 | 23 | 18 | -18.4833
2008-03-05 | 3 | 48 | 22 | 19 | -18.5167
2008-03-06 | 3 | 45 | 10 | 22 | -6.6167
2008-03-07 |  |  |  |  | 0
2008-03-08 |  |  |  |  | 0
2008-03-09 | 2 | 49 | 22 | 23 | -19.5667
2008-03-10 | 5 | 52 | 20 | 20 | -14.4667
2008-03-11 | 3 | 46 | 22 | 20 | -18.5667
2008-03-12 |  |  |  |  | 0
2008-03-12 | 3 | 55 | 9 | 18 | -5.3833
2008-03-13 | 3 | 48 | 19 | 19 | -15.5167
2008-03-14 |  |  |  |  | 0
2008-03-15 | 8 | 50 | 24 |  | -15.1667
2008-03-16 |  |  | 0 | 19 | -0.31667
2008-03-17 | 4 | 47 | 24 |  | -19.2167
2008-03-18 |  |  | 0 | 18 | -0.3
2008-03-18 | 3 | 50 | 24 |  | -20.1667
2008-03-19 |  |  | 1 | 16 | -1.2667
2008-03-19 | 4 | 49 | 24 |  | -19.1833
2008-03-20 |  |  | 0 | 14 | -0.23333
2008-03-20 | 5 | 5 | 24 |  | -18.9167
2008-03-21 |  |  | 0 | 14 | -0.23333
2008-03-21 | 8 | 21 | 8 | 48 | -0.45
2008-03-21 | 9 | 21 | 17 | 18 | -7.95
2008-03-22 |  |  |  |  | 0
2008-03-23 |  |  |  |  | 0
2008-03-24 |  |  |  |  | 0
2008-03-25 | 0 | 0 | 0 | 0 | 0
2008-03-25 | 2 | 55 | 22 | 17 | -19.3667
2008-03-26 | 3 | 50 | 4 | 41 | -0.85
2008-03-26 | 6 | 46 | 11 | 13 | -4.45
2008-03-27 |  |  |  |  | 0
2008-03-28 | 10 | 49 | 22 | 26 | -11.6167
2008-03-29 | 23 | 40 | 24 |  | -0.33333
2008-03-30 |  |  | 24 |  | -24
2008-03-31 |  |  | 19 | 55 | -19.9167
2008-03-31 | 21 | 26 | 24 |  | -2.5667
-313.7167
Note on E3: GE Transportation: Time that flame is out.

## Summary of Duct burner hours
Duct Burner Operating Time
| DUCT BURNER |  | OPER
DATE | ON | OFF | TIME
2008-01-24 | 5:49 | 7:59 | 2:10
2008-01-25 | 5:39 | 7:59 | 2:20
2008-01-27 | 16:43 | 19:25 | 2:42
2008-01-27 | 21:38 | 22:00 | 0:22
2008-02-19 | 7:56 | 17:10 | 9:14
2008-02-20 | 6:53 | 12:09 | 5:16
2008-02-21 | 6:46 | 8:59 | 2:13
|  | Total: | 1899-12-31 00:17
|  | January | 7:34
|  | February | 16.43

## March CEMS data
March | 2008
| Record# | DATE | TIME | CO_COR12 | NOXHCOR111 | OXY114 | NH3FLO18 | CATTMP11 | CO_HCOR13 | GAS14 | GEN15 | GEN26 | HGAS17 | NOX19 | NOX1I10 | NOXHRT112 | NOXRT113 | NOXCOR115
| 1 | 2008-03-01 | 0 | 42.7 | -3 | 20.85 | 0.9 | 457.7 | -340.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | 0.01 | 0.006 | 0 | -3.7
| 2 | 2008-03-01 | 10000 | 45 | -3.4 | 20.85 | 0.8 | 435.7 | -397.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.04 | 0.007 | 0 | -4.1
| 3 | 2008-03-01 | 20000 | 67.4 | -6.5 | 20.86 | 0.9 | 427.9 | -626.5 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.04 | 0.008 | 0 | -7.3
| 4 | 2008-03-01 | 30000 | 59.1 | -1.7 | 20.89 | 0.9 | 418.7 | -565.6 | 0.21 | 0.5 | 1.3 | -0.9 | -0.04 | -0.06 | 109.229 | 0.005 | -7.4
| 5 | 2008-03-01 | 40000 | 58.6 | 0.4 | 20.9 | 0.9 | 411.4 | -563.2 | 0.05 | 0.5 | 1.3 | -1 | -0.03 | -0.04 | 221.612 | 0.006 | -5.9
| 6 | 2008-03-01 | 50000 | 26.2 | 0.4 | 20.91 | 0.9 | 402.8 | -206.9 | 0.07 | 0.5 | 1.3 | -0.9 | -0.04 | -0.06 | 322.902 | 0.017 | -2.6
| 7 | 2008-03-01 | 60000 | 6.3 | 7 | 20.45 | 0.9 | 410.4 | -28 | 0.86 | 2.6 | 3.4 | -0.9 | 1.27 | 3.27 | 275.437 | 0.028 | 2
| 8 | 2008-03-01 | 70000 | 22.5 | 67.6 | 16.07 | 14.7 | 596 | 31 | 8.51 | 33.7 | 37.6 | -0.9 | 10.26 | 30.01 | 0.249 | 0.048 | 12.9
| 9 | 2008-03-01 | 80000 | 7.1 | 11.6 | 12.38 | 97.8 | 631 | 14.9 | 17.98 | 137.9 | 201.9 | -0.9 | 4.02 | 13.11 | 11.122 | 14.256 | 3.1
| 10 | 2008-03-01 | 90000 | 2 | 4.1 | 12.37 | 72 | 634.9 | 26.4 | 17.19 | 128.7 | 193.3 | -0.9 | 3.18 | 7.54 | 0.015 | 0.007 | 1.9
| 11 | 2008-03-01 | 100000 | 0.2 | 1.9 | 13.91 | 119.3 | 667.9 | -2.3 | 22.13 | 182.2 | 260.9 | -1 | 2.24 | 10.54 | 0.007 | 0.007 | 1.9
| 12 | 2008-03-01 | 110000 | 39.7 | 8.3 | 19.08 | 51.8 | 572.2 | 7.5 | 3.39 | 18.8 | 31.7 | -1 | 2.46 | 7.63 | 30.107 | 6.345 | 3.4
| 13 | 2008-03-01 | 120000 | 0 | 0 | 21.03 | 0.9 | 423.4 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | 0.05 | 0.005 | 0.005 | 0
| 14 | 2008-03-01 | 130000 | 0 | 0 | 21.05 | 0.9 | 395.5 | 0 | 0.05 | 0.5 | 1.3 | -1 | -0.03 | -0.03 | 0.005 | 0.005 | 0
| 15 | 2008-03-01 | 140000 | 0 | 0 | 21.06 | 0.9 | 385.5 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.03 | 0.005 | 0.005 | 0
| 16 | 2008-03-01 | 150000 | 0 | 0 | 21 | 0.9 | 377.6 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.04 | 0.004 | 0.005 | 0
| 17 | 2008-03-01 | 160000 | 0 | 0 | 21.1 | 0.9 | 375.9 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.06 | 0.003 | 0.004 | 0
| 18 | 2008-03-01 | 170000 | 0 | 0 | 21.12 | 0.8 | 375 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.06 | 0.003 | 0.004 | 0
| 19 | 2008-03-01 | 180000 | 0 | 0 | 21.14 | 0.8 | 370.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.06 | 0.003 | 0.004 | 0
| 20 | 2008-03-01 | 190000 | 0 | 0 | 21.16 | 0.9 | 364.3 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.06 | 0.003 | 0.003 | 0
| 21 | 2008-03-01 | 200000 | 0 | 0 | 21.17 | 0.8 | 357.8 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.07 | 0.003 | 0.003 | 0
| 22 | 2008-03-01 | 210000 | 0 | 0 | 21.2 | 0.9 | 342.8 | 0 | 0.21 | 0.5 | 1.3 | -1 | -0.04 | -0.06 | 0.003 | 0.003 | 0
| 23 | 2008-03-01 | 220000 | 0 | 0 | 21.21 | 0.9 | 332 | 0 | 0.26 | 0.5 | 1.3 | -1 | -0.04 | -0.06 | 0.002 | 0.002 | 0
| 24 | 2008-03-01 | 230000 | 0 | 0 | 21.23 | 0.9 | 325.4 | 0 | 0.17 | 0.5 | 1.3 | -1 | -0.04 | -0.06 | 0.002 | 0.003 | 0
| 25 | 2008-03-02 | 0 | 0 | 0 | 21.24 | 0.9 | 321.6 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.04 | -0.07 | 0.002 | 0.003 | 0
| 26 | 2008-03-02 | 10000 | 0 | 0 | 21.25 | 0.9 | 318.3 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.002 | 0.002 | 0
| 27 | 2008-03-02 | 20000 | 0 | 0 | 21.19 | 0.8 | 315 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.002 | 0.002 | 0
| 28 | 2008-03-02 | 30000 | 0 | 0 | 21.27 | 0.8 | 311.3 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.002 | 0.002 | 0
| 29 | 2008-03-02 | 40000 | 0 | 0 | 21.28 | 0.9 | 307.9 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.002 | 0.002 | 0
| 30 | 2008-03-02 | 50000 | 0 | 0 | 21.29 | 0.8 | 304.8 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.002 | 0.002 | 0
| 31 | 2008-03-02 | 60000 | 0 | 0 | 21.23 | 0.8 | 301.7 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.002 | 0.002 | 0
| 32 | 2008-03-02 | 70000 | 0 | 0 | 21.31 | 0.7 | 298.7 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.002 | 0.002 | 0
| 33 | 2008-03-02 | 80000 | 0 | 0 | 21.31 | 0.7 | 295.6 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.02 | -0.07 | 0.002 | 0.001 | 0
| 34 | 2008-03-02 | 90000 | 0 | 0 | 21.32 | 1 | 292.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.002 | 0.001 | 0
| 35 | 2008-03-02 | 100000 | 0 | 0 | 21.25 | 0.8 | 289.2 | 0 | 0.06 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.002 | 0.001 | 0
| 36 | 2008-03-02 | 110000 | 0 | 0 | 21.24 | 0.9 | 286.2 | 0 | 0.06 | 0.5 | 1.3 | -1 | -0.02 | -0.07 | 0.002 | 0.001 | 0
| 37 | 2008-03-02 | 120000 | 0 | 0 | 21.31 | 0.8 | 283 | 0 | 0.11 | 0.5 | 1.3 | -1 | -0.01 | -0.06 | 0.001 | 0.001 | 0
| 38 | 2008-03-02 | 130000 | 0 | 0 | 21.3 | 0.8 | 279.9 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.06 | 0.002 | 0.002 | 0
| 39 | 2008-03-02 | 140000 | 0 | 0 | 21.28 | 0.8 | 276.4 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.06 | 0.002 | 0.002 | 0
| 40 | 2008-03-02 | 150000 | 0 | 0 | 21.27 | 0.8 | 273.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.04 | -0.07 | 0.002 | 0.002 | 0
| 41 | 2008-03-02 | 160000 | 0 | 0 | 21.26 | 0.8 | 270.1 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.002 | 0.002 | 0
| 42 | 2008-03-02 | 170000 | 0 | 0 | 21.26 | 0.8 | 266.9 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.002 | 0.002 | 0
| 43 | 2008-03-02 | 180000 | 0 | 0 | 21.26 | 0.9 | 263.5 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.002 | 0.002 | 0
| 44 | 2008-03-02 | 190000 | 0 | 0 | 21.25 | 0.9 | 260.2 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 0.002 | 0.002 | 0
| 45 | 2008-03-02 | 200000 | 0 | 0 | 21.23 | 0.9 | 257 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 0.002 | 0.002 | 0
| 46 | 2008-03-02 | 210000 | 0 | 0 | 21.22 | 0.8 | 253.7 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 0.002 | 0.002 | 0
| 47 | 2008-03-02 | 220000 | 0 | 0 | 21.21 | 0.8 | 250.6 | 0 | 0.08 | 0.5 | 1.3 | -0.9 | -0.03 | -0.07 | 0.002 | 0.002 | 0
| 48 | 2008-03-02 | 230000 | 0 | 0 | 21.19 | 0.8 | 247.6 | 0 | 0.27 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.002 | 0.002 | 0
| 49 | 2008-03-03 | 0 | 0 | 0 | 21.18 | 0.9 | 244.4 | 0 | 0.27 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.003 | 0.002 | 0
| 50 | 2008-03-03 | 10000 | 0 | 0 | 21.15 | 0.7 | 241.2 | 0 | 0.1 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.003 | 0.002 | 0
| 51 | 2008-03-03 | 20000 | 0 | 0 | 21.14 | 0.8 | 238 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.003 | 0.002 | 0
| 52 | 2008-03-03 | 30000 | 0 | 0 | 21.14 | 0.9 | 235 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.02 | -0.06 | 0.004 | 0.002 | 0
| 53 | 2008-03-03 | 40000 | 0 | 0 | 21.12 | 0.8 | 231.9 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.07 | 0.003 | 0.003 | 0
| 54 | 2008-03-03 | 50000 | 0 | 0 | 21.11 | 0.9 | 228.8 | 0 | 0.06 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 0.004 | 0.003 | 0
| 55 | 2008-03-03 | 60000 | 0 | 0 | 21.09 | 0.8 | 225.9 | 0 | 0.1 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 0.003 | 0.002 | 0
| 56 | 2008-03-03 | 70000 | 0 | 0 | 21.09 | 0.8 | 222.6 | 0 | 0.27 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 0.004 | 0.003 | 0
| 57 | 2008-03-03 | 80000 | 0 | 0 | 21.08 | 0.8 | 219 | 0 | 0.24 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 0.004 | 0.003 | 0
| 58 | 2008-03-03 | 90000 | 0 | 0 | 21.05 | 0.9 | 215 | 0 | 0.11 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 0.004 | 0.003 | 0
| 59 | 2008-03-03 | 100000 | 0 | 0 | 21.05 | 0.8 | 211 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.006 | 0.005 | 0
| 60 | 2008-03-03 | 110000 | 0 | 0 | 21.03 | 0.9 | 207.5 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.006 | 0.005 | 0
| 61 | 2008-03-03 | 120000 | 0 | 0 | 21.02 | 1 | 204.4 | 0 | 0.16 | 0.5 | 1.3 | -1 | -0.03 | -0.07 | 0.006 | 0.005 | 0
| 62 | 2008-03-03 | 130000 | 0 | 0 | 21.01 | 0.8 | 201.4 | 0 | 0.16 | 0.5 | 1.3 | -1 | -0.02 | -0.04 | 0.006 | 0.004 | 0
| 63 | 2008-03-03 | 140000 | 0 | 0 | 21.01 | 0.8 | 198.4 | 0 | 0.26 | 0.5 | 1.3 | -1 | -0.01 | -0.04 | 0.006 | 0.003 | 0
| 64 | 2008-03-03 | 150000 | 0.8 | -0.1 | 20.99 | 1 | 194.4 | 9 | 0.09 | 0.5 | 1.3 | -1 | -0.03 | -0.05 | 0.006 | 0.007 | -0.2
| 65 | 2008-03-03 | 160000 | 64.4 | 40.4 | 13.11 | 0.9 | 193.8 | 34.9 | 1.31 | 2.5 | 3.2 | -1 | 5.73 | 6.87 | 1557.584 | 1467.318 | 27.1
| 66 | 2008-03-03 | 170000 | 21.9 | 69.6 | 17.31 | 1 | 541.6 | 19.2 | 6.37 | 13 | 13.4 | -1 | 10.29 | 30 | 0.256 | 0.062 | 17
| 67 | 2008-03-03 | 180000 | 22.7 | 55.1 | 16.73 | 81.9 | 598.9 | 29.1 | 7.49 | 23.7 | 25.5 | -1 | 10.29 | 30 | 0.203 | 0.055 | 14.9
| 68 | 2008-03-03 | 190000 | 21 | 45.6 | 15.48 | 137.7 | 608.5 | 33.9 | 9.93 | 47.8 | 82.3 | -1 | 10.14 | 29.61 | 0.168 | 0.041 | 11.2
| 69 | 2008-03-03 | 200000 | 0.2 | 1.8 | 13.73 | 141.1 | 649.8 | -2.4 | 22.44 | 185.2 | 263.5 | -1 | 2.2 | 12.86 | 0.007 | 0.006 | 1.8
| 70 | 2008-03-03 | 210000 | 0.2 | 1.9 | 13.82 | 118 | 659.5 | -2.4 | 22.36 | 184.2 | 264.2 | -1 | 2.34 | 10.93 | 0.007 | 0.007 | 1.9
| 71 | 2008-03-03 | 220000 | 34.6 | 7.5 | 19.1 | 8.2 | 575.7 | -69.5 | 3.18 | 18.5 | 30.6 | -1 | 2.18 | 6.24 | 0.105 | 0.083 | -0.9
| 72 | 2008-03-03 | 230000 | 4.1 | -2.3 | 20.93 | 0.9 | 451.9 | -18.1 | 0.35 | 0.5 | 1.2 | -1 | -0.33 | 0.02 | 0.186 | 0.208 | -3.5
| 73 | 2008-03-04 | 0 | 0.6 | -0.3 | 20.94 | 1 | 429 | -3.9 | 0.23 | 0.5 | 1.3 | -1 | -0.33 | -0.03 | 0.169 | 0.186 | -0.6
| 74 | 2008-03-04 | 10000 | 0 | 0 | 20.88 | 0.9 | 417.7 | 0 | 0.25 | 0.5 | 1.3 | -1 | -0.33 | -0.04 | 0.131 | 0.138 | 0
| 75 | 2008-03-04 | 20000 | 0 | 0 | 20.96 | 0.9 | 408.9 | 0 | 0.25 | 0.5 | 1.3 | -1 | -0.33 | -0.03 | 0.116 | 0.124 | 0
| 76 | 2008-03-04 | 30000 | 0 | 0 | 20.96 | 0.9 | 402.6 | 0 | 0.24 | 0.5 | 1.3 | -1 | -0.33 | -0.04 | 0.129 | 0.142 | 0
| 77 | 2008-03-04 | 40000 | 0 | 0 | 20.95 | 1 | 398.1 | 0 | 0.07 | 0.5 | 1.3 | -1 | -0.34 | -0.03 | 0.154 | 0.16 | 0
| 78 | 2008-03-04 | 50000 | 5.3 | 9.8 | 20.34 | 0.9 | 412 | 3.7 | 1.06 | 1.6 | 2.4 | -1 | 1.61 | 4.72 | 0.13 | 0.115 | 3.8
| 79 | 2008-03-04 | 60000 | 22.2 | 66.2 | 16.34 | 46.9 | 594.1 | 25 | 8.27 | 30.7 | 33.7 | -1 | 10.26 | 30.01 | 0.244 | 0.05 | 13.6
| 80 | 2008-03-04 | 70000 | 1 | 7.3 | 13.93 | 68.6 | 627.6 | -1.5 | 17.94 | 136.5 | 200.8 | -1 | 2.79 | 9.67 | 0.027 | 0.009 | 2.4
| 81 | 2008-03-04 | 80000 | 4.6 | 7.4 | 10.64 | 146.1 | 657 | 36.9 | 22.44 | 184.6 | 264.2 | -0.9 | 4.44 | 10.76 | 177.295 | 204.186 | 3.2
| 82 | 2008-03-04 | 90000 | 0 | 1.8 | 13.97 | 56 | 638.1 | -2 | 16.93 | 125.5 | 190.6 | -0.9 | 2.09 | 8.24 | 0.007 | 0.007 | 1.8
| 83 | 2008-03-04 | 100000 | 0 | 2 | 13.95 | 54.6 | 638.4 | -2.4 | 17.13 | 127.8 | 193.3 | -1 | 2.33 | 7.28 | 0.007 | 0.007 | 2
| 84 | 2008-03-04 | 110000 | 0 | 2 | 13.95 | 55.5 | 637.5 | -2.1 | 17.07 | 127.4 | 193 | -0.9 | 2.38 | 7.34 | 0.007 | 0.007 | 2
| 85 | 2008-03-04 | 120000 | -0.1 | 2 | 13.76 | 148.5 | 670.6 | -2.2 | 22.54 | 185.4 | 266 | -1 | 2.43 | 12.21 | 0.007 | 0.007 | 2
| 86 | 2008-03-04 | 130000 | -0.1 | 1.9 | 13.87 | 124.1 | 674.9 | -2.2 | 22.25 | 183.1 | 263.5 | -1 | 2.28 | 10.72 | 0.007 | 0.007 | 1.9
| 87 | 2008-03-04 | 140000 | -0.1 | 2 | 13.83 | 133.8 | 675.4 | -2.4 | 22.24 | 183.3 | 263.7 | -1 | 2.46 | 11.4 | 0.008 | 0.008 | 2.1
| 88 | 2008-03-04 | 150000 | -0.1 | 2 | 13.83 | 132.4 | 675.1 | -2.2 | 22.25 | 183.3 | 263.3 | -1 | 2.38 | 11.37 | 0.007 | 0.007 | 2
| 89 | 2008-03-04 | 160000 | -0.1 | 2.1 | 13.82 | 131.5 | 675.1 | -2.3 | 22.34 | 183.8 | 263.8 | -1 | 2.49 | 11.38 | 0.008 | 0.008 | 2.1
| 90 | 2008-03-04 | 170000 | -0.1 | 1.9 | 13.82 | 132.3 | 674.8 | -2.2 | 22.32 | 183.8 | 263.6 | -1 | 2.32 | 11.4 | 0.007 | 0.007 | 1.9
| 91 | 2008-03-04 | 180000 | -0.1 | 2 | 13.85 | 124.5 | 674.6 | -2.5 | 22.27 | 183.5 | 263.6 | -1 | 2.39 | 10.84 | 0.007 | 0.007 | 2
| 92 | 2008-03-04 | 190000 | -0.1 | 2 | 13.87 | 117.4 | 674.6 | -2.5 | 22.27 | 183.6 | 263.2 | -1 | 2.4 | 10.41 | 0.007 | 0.007 | 2
| 93 | 2008-03-04 | 200000 | -0.1 | 2 | 13.88 | 114.6 | 674.5 | -2.6 | 22.27 | 183.8 | 263.3 | -1 | 2.37 | 10.16 | 0.007 | 0.007 | 2
| 94 | 2008-03-04 | 210000 | -0.1 | 2 | 13.87 | 118.1 | 674.8 | -2.3 | 22.42 | 185 | 264.6 | -1 | 2.43 | 10.39 | 0.008 | 0.008 | 2
| 95 | 2008-03-04 | 220000 | -0.1 | 2 | 13.9 | 112.4 | 674.2 | -2.4 | 22.39 | 184.8 | 264.1 | -0.9 | 2.38 | 9.95 | 0.007 | 0.007 | 2
| 96 | 2008-03-04 | 230000 | -0.1 | 1.9 | 13.95 | 55 | 645.1 | -2.3 | 17 | 126.6 | 192.4 | -1 | 2.31 | 7.44 | 0.007 | 0.007 | 2
| 97 | 2008-03-05 | 0 | 22 | 13.8 | 19.76 | 2.8 | 560.1 | 2.9 | 1.98 | 8.2 | 15 | -1 | 2.19 | 5.51 | 85.52 | 60.169 | 6.7
| 98 | 2008-03-05 | 10000 | 0 | 0 | 21 | 0.8 | 453.7 | 0 | 0.26 | 0.5 | 1.3 | -1 | -0.02 | 0.01 | 0.008 | 0.004 | 0
| 99 | 2008-03-05 | 20000 | 0 | 0 | 20.99 | 0.8 | 435.9 | 0 | 0.18 | 0.5 | 1.3 | -0.9 | -0.02 | -0.03 | 0.008 | 0.006 | 0
| 100 | 2008-03-05 | 30000 | 0 | 0 | 20.99 | 0.8 | 423.6 | 0 | 0.05 | 0.5 | 1.3 | -0.9 | -0.02 | -0.04 | 0.009 | 0.006 | 0
| 101 | 2008-03-05 | 40000 | 5.1 | 10.3 | 20.34 | 0.9 | 445 | 2.7 | 1.09 | 1.5 | 2.3 | -1 | 1.95 | 5.05 | 0.045 | 0.02 | 4
| 102 | 2008-03-05 | 50000 | 23.3 | 52.5 | 15.92 | 62.2 | 604.1 | 43.9 | 9.06 | 38 | 43.2 | -0.9 | 10.29 | 30.01 | 0.193 | 0.045 | 12.3
| 103 | 2008-03-05 | 60000 | 1.1 | 7.9 | 13.97 | 75.5 | 631.1 | -0.9 | 17.97 | 136.1 | 199.9 | -1 | 2.84 | 10.26 | 0.029 | 0.009 | 2.5
| 104 | 2008-03-05 | 70000 | -0.1 | 1.9 | 13.93 | 108.8 | 665.3 | -2.4 | 22.44 | 185.2 | 263.7 | -0.9 | 2.25 | 9.6 | 0.007 | 0.007 | 1.9
| 105 | 2008-03-05 | 80000 | 3.8 | 7.5 | 10.72 | 105.2 | 672 | 38.8 | 22.35 | 184.8 | 263.2 | -1 | 4.81 | 9.37 | 185.207 | 215.263 | 3.1
| 106 | 2008-03-05 | 90000 | -0.1 | 2 | 13.96 | 107.4 | 673.1 | -2.2 | 22.38 | 184.7 | 263.4 | -0.9 | 2.28 | 9.89 | 0.007 | 0.007 | 1.9
| 107 | 2008-03-05 | 100000 | -0.1 | 2.1 | 13.92 | 112 | 673.5 | -2.6 | 22.34 | 184.9 | 264 | -0.9 | 2.42 | 9.88 | 0.008 | 0.008 | 2
| 108 | 2008-03-05 | 110000 | -0.1 | 2.1 | 13.88 | 118.1 | 674.9 | -2.4 | 22.33 | 184.3 | 264.4 | -1 | 2.42 | 10.33 | 0.008 | 0.008 | 2
| 109 | 2008-03-05 | 120000 | -0.1 | 2.1 | 13.83 | 126.2 | 676.9 | -2.4 | 22.24 | 183.4 | 263.4 | -0.9 | 2.42 | 11.02 | 0.008 | 0.007 | 2
| 110 | 2008-03-05 | 130000 | -0.1 | 2.1 | 13.79 | 136.7 | 676.3 | -2.3 | 22.2 | 182.6 | 263.1 | -0.9 | 2.44 | 11.91 | 0.008 | 0.007 | 2
| 111 | 2008-03-05 | 140000 | -0.1 | 2.1 | 13.73 | 150 | 675.6 | -2.6 | 22.23 | 182.4 | 263.3 | -1 | 2.48 | 12.89 | 0.008 | 0.007 | 2
| 112 | 2008-03-05 | 150000 | 0.1 | 1.2 | 13.19 | 101.6 | 642.9 | -2.2 | 16.44 | 121 | 184.9 | -0.9 | 1.66 | 8.41 | 0.004 | 0.004 | 1.1
| 113 | 2008-03-05 | 160000 | 0.3 | 1.7 | 12.43 | 66.2 | 636.5 | -1.7 | 16.71 | 124.2 | 188 | -0.9 | 2.59 | 8.31 | 0.006 | 0.006 | 1.7
| 114 | 2008-03-05 | 170000 | 0 | 2.1 | 13.87 | 64.6 | 636.3 | -2.4 | 16.53 | 123.1 | 186.8 | -0.9 | 2.48 | 8.37 | 0.008 | 0.007 | 2.1
| 115 | 2008-03-05 | 180000 | 0 | 2 | 13.91 | 64.4 | 635.4 | -2.3 | 16.72 | 124.9 | 188.6 | -1 | 2.37 | 8.08 | 0.008 | 0.007 | 2
| 116 | 2008-03-05 | 190000 | 0 | 2.1 | 13.7 | 150.5 | 668.8 | -2.1 | 22.25 | 182.6 | 262.5 | -0.9 | 2.43 | 12.74 | 0.008 | 0.007 | 2
| 117 | 2008-03-05 | 200000 | 0 | 2.1 | 13.69 | 147.1 | 674.1 | -2.4 | 22.27 | 183.4 | 264.7 | -0.9 | 2.44 | 12.69 | 0.008 | 0.007 | 2
| 118 | 2008-03-05 | 210000 | 0 | 2 | 13.75 | 134.7 | 675.7 | -2.1 | 22.25 | 183 | 263.5 | -0.9 | 2.4 | 11.74 | 0.008 | 0.007 | 2
| 119 | 2008-03-05 | 220000 | -0.1 | 2 | 13.77 | 123.1 | 676.6 | -2.4 | 21.9 | 179.4 | 259.3 | -1 | 2.35 | 11.06 | 0.007 | 0.007 | 1.9
| 120 | 2008-03-05 | 230000 | 48 | 20.2 | 19.23 | 2 | 569.3 | -215.8 | 2.65 | 11.2 | 17.7 | -0.9 | 3.17 | 8.25 | 14.323 | 15.858 | 8.3
| 121 | 2008-03-06 | 0 | 35.3 | 4.5 | 20.89 | 0.9 | 432.6 | -561 | 0.09 | 0.5 | 1.3 | -0.9 | 0 | 0.04 | 77.587 | 25.324 | -0.5
| 122 | 2008-03-06 | 10000 | 25.8 | 3.4 | 20.89 | 0.9 | 410.3 | -524.1 | 0.05 | 0.5 | 1.3 | -0.9 | -0.01 | -0.02 | 267.513 | 0.001 | -2.1
| 123 | 2008-03-06 | 20000 | 18.4 | 2 | 20.89 | 0.9 | 403.1 | -511 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.04 | 262.757 | 0.002 | -2.6
| 124 | 2008-03-06 | 30000 | 27.3 | 3.1 | 20.89 | 0.9 | 397.6 | -522.1 | 0.04 | 0.5 | 1.3 | -1 | -0.01 | -0.03 | 333.983 | 1.584 | -1.9
| 125 | 2008-03-06 | 40000 | 13.1 | 13.5 | 20.18 | 0.9 | 416.3 | -430.9 | 1.1 | 1.3 | 2.1 | -1 | 2 | 5.14 | 288.119 | 0.016 | 2.8
| 126 | 2008-03-06 | 50000 | 22.4 | 68 | 15.89 | 0.9 | 588.6 | 35.2 | 8.9 | 37.4 | 38.3 | -1 | 10.29 | 30 | 0.251 | 0.045 | 12.3
| 127 | 2008-03-06 | 60000 | 8.2 | 31.3 | 14.34 | 80.2 | 627.6 | 12.8 | 17.1 | 126.1 | 182.5 | -1 | 5.73 | 19.49 | 0.115 | 0.021 | 5.6
| 128 | 2008-03-06 | 70000 | -0.1 | 1.9 | 14.25 | 114.8 | 657.5 | -3.2 | 22.57 | 187.1 | 266.5 | -1 | 2.08 | 10.19 | 0.007 | 0.007 | 1.7
| 129 | 2008-03-06 | 80000 | 4.7 | 7.1 | 10.3 | 132.8 | 668.6 | 38.9 | 22.71 | 187.6 | 267.5 | -1 | 4.6 | 10.36 | 19.019 | 19.004 | 2.9
| 130 | 2008-03-06 | 90000 | 0 | 1.9 | 13.85 | 114.1 | 673.4 | -2.2 | 22.57 | 186.5 | 266.8 | -1 | 2.38 | 10.47 | 0.007 | 0.007 | 2
| 131 | 2008-03-06 | 100000 | 0 | 2 | 13.82 | 122.4 | 675.1 | -2.2 | 22.44 | 185.7 | 266.4 | -0.9 | 2.41 | 10.8 | 0.007 | 0.007 | 2
| 132 | 2008-03-06 | 110000 | 40.1 | 8 | 19.15 | 41.9 | 571.8 | -55.6 | 3.19 | 18.8 | 31.6 | -0.9 | 1.96 | 6.29 | 134.568 | 75.985 | 3.7
| 133 | 2008-03-06 | 120000 | 0.2 | 0.1 | 20.93 | 0.9 | 433.3 | 5.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | 0.06 | 121.88 | 0.005 | 0
| 134 | 2008-03-06 | 130000 | 0 | 0 | 20.94 | 1 | 407.4 | 0 | 0.05 | 0.5 | 1.3 | -0.9 | -0.01 | -0.02 | 56.988 | 0.009 | 0
| 135 | 2008-03-06 | 140000 | 0 | 0 | 20.93 | 1 | 397.5 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.01 | -0.04 | 153.538 | 0.009 | 0
| 136 | 2008-03-06 | 150000 | 0.2 | 0.3 | 20.93 | 0.9 | 395.1 | -5.6 | 0.04 | 0.5 | 1.3 | -1 | -0.01 | -0.03 | 170.95 | 4.752 | 0
| 137 | 2008-03-06 | 160000 | 0.3 | -0.1 | 20.93 | 0.9 | 394 | -6.4 | 0.05 | 0.5 | 1.3 | -1 | -0.02 | -0.03 | 147.217 | 0.012 | 0
| 138 | 2008-03-06 | 170000 | 0.1 | 0.1 | 20.93 | 0.8 | 390.9 | -8 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.03 | 156.709 | 0.015 | -0.1
| 139 | 2008-03-06 | 180000 | 0 | 0 | 20.93 | 0.8 | 386.9 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.04 | 113.976 | 0.017 | 0
| 140 | 2008-03-06 | 190000 | 0 | 0 | 20.93 | 0.9 | 382.3 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.05 | 115.562 | 0.016 | 0
| 141 | 2008-03-06 | 200000 | 0 | 0 | 20.94 | 0.8 | 376.8 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 31.673 | 0.017 | 0
| 142 | 2008-03-06 | 210000 | 0 | 0 | 20.95 | 0.9 | 371.5 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 19.007 | 0.011 | 0
| 143 | 2008-03-06 | 220000 | 0 | 0 | 20.95 | 0.9 | 365.8 | 0 | 0.05 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 15.841 | 0.012 | 0
| 144 | 2008-03-06 | 230000 | 0 | 0 | 20.94 | 0.9 | 350.1 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 30.087 | 0.011 | 0
| 145 | 2008-03-07 | 0 | 0 | 0 | 20.95 | 0.9 | 336.5 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 0.014 | 0.013 | 0
| 146 | 2008-03-07 | 10000 | 0 | 0 | 20.95 | 0.9 | 328.1 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.07 | 0.014 | 0.013 | 0
| 147 | 2008-03-07 | 20000 | 0 | 0 | 20.87 | 0.7 | 322.8 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 19.009 | 0.015 | 0
| 148 | 2008-03-07 | 30000 | 0 | 0 | 20.94 | 0.8 | 319.1 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 11.098 | 0.013 | 0
| 149 | 2008-03-07 | 40000 | 0 | 0 | 20.94 | 0.8 | 315.5 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 41.167 | 0.014 | 0
| 150 | 2008-03-07 | 50000 | 0.2 | 0.1 | 20.86 | 0.8 | 312 | -5.2 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 38.006 | 0.017 | -0.1
| 151 | 2008-03-07 | 60000 | 0.3 | 0 | 20.93 | 0.8 | 308.7 | -5.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 224.768 | 0.012 | -0.1
| 152 | 2008-03-07 | 70000 | 4.8 | 1.5 | 20.91 | 0.8 | 305.5 | -98 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.06 | 542.902 | 52.238 | -0.4
| 153 | 2008-03-07 | 80000 | 4.3 | 0.9 | 20.92 | 0.7 | 302.5 | -56 | 0.04 | 0.5 | 1.3 | -0.9 | 0.02 | -0.07 | 663.175 | 243.741 | 0.4
| 154 | 2008-03-07 | 90000 | 9.1 | 1.7 | 20.91 | 0.9 | 299.3 | -122.4 | 0.04 | 0.5 | 1.3 | -0.9 | 0.01 | 2.03 | 609.372 | 118.706 | 0.3
| 155 | 2008-03-07 | 100000 | 15.7 | 3.5 | 20.9 | 0.7 | 296.2 | -291.2 | 0.09 | 0.5 | 1.3 | -0.9 | 0 | -0.06 | 652.113 | 60.146 | 0.3
| 156 | 2008-03-07 | 110000 | 28.2 | 5.1 | 20.89 | 0.8 | 288.3 | -538.9 | 0.17 | 0.5 | 1.3 | -0.9 | 0.01 | -0.06 | 515.998 | 261.157 | 1.6
| 157 | 2008-03-07 | 120000 | 32.1 | 3 | 20.88 | 0.8 | 282.5 | -614.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.06 | 106.07 | 6.332 | -1.7
| 158 | 2008-03-07 | 130000 | 26.7 | 0 | 20.87 | 0.8 | 279 | -543.7 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.06 | 42.75 | 0 | -2
| 159 | 2008-03-07 | 140000 | 13.3 | 0.2 | 20.85 | 0.8 | 275.3 | -261.8 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.07 | 0.01 | 0 | -0.9
| 160 | 2008-03-07 | 150000 | 12.3 | 0 | 20.83 | 0.9 | 271.1 | -232.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.06 | 0.008 | 0 | -0.5
| 161 | 2008-03-07 | 160000 | 7.1 | -2.1 | 20.83 | 0.9 | 260.5 | -251 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 0.004 | 0 | -1.9
| 162 | 2008-03-07 | 170000 | 22.7 | 0.9 | 20.83 | 0.9 | 253.7 | -237.6 | 0.05 | 0.5 | 1.3 | -1 | -0.01 | -0.07 | 0.008 | 0 | -0.7
| 163 | 2008-03-07 | 180000 | 13 | -1.3 | 20.82 | 0.8 | 249.5 | -214.7 | 0.04 | 0.5 | 1.3 | -1 | -0.01 | -0.06 | 0.005 | 0 | -1.1
| 164 | 2008-03-07 | 190000 | 15.7 | 0.7 | 20.83 | 0.9 | 246.1 | -222.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.06 | 0.008 | 0 | -0.6
| 165 | 2008-03-07 | 200000 | 17.8 | 1.2 | 20.83 | 0.9 | 242.8 | -228.8 | 0.04 | 0.5 | 1.3 | -0.9 | 0 | -0.06 | 0.01 | 0.001 | 0
| 166 | 2008-03-07 | 210000 | 27.7 | 0.1 | 20.83 | 0.9 | 240.5 | -237.5 | 0.04 | 0.5 | 1.3 | -0.9 | 0.01 | -0.06 | 0.008 | 0.002 | 0.6
| 167 | 2008-03-07 | 220000 | 30.6 | 0.7 | 20.84 | 0.9 | 237.8 | -254.9 | 0.04 | 0.5 | 1.3 | -0.9 | 0 | -0.06 | 0.009 | 0.001 | 0.3
| 168 | 2008-03-07 | 230000 | 30.8 | 0.2 | 20.84 | 0.9 | 235.6 | -295.7 | 0.04 | 0.5 | 1.3 | -0.9 | 0 | -0.06 | 0.009 | 0.001 | -0.1
| 169 | 2008-03-08 | 0 | 24.7 | -0.3 | 20.78 | 0.9 | 233.4 | -290.8 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.07 | 0.011 | 0 | -1.3
| 170 | 2008-03-08 | 10000 | 43.3 | 0.4 | 20.86 | 0.8 | 231.3 | -499.9 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.06 | 3.181 | 0 | -1.6
| 171 | 2008-03-08 | 20000 | 52.5 | 0.7 | 20.87 | 1 | 228.7 | -571.7 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.06 | 41.171 | 0 | -1.6
| 172 | 2008-03-08 | 30000 | 49.8 | -0.9 | 20.88 | 0.9 | 226.6 | -583.6 | 0.04 | 0.5 | 1.3 | -1 | -0.01 | -0.06 | 207.355 | 0 | -3.3
| 173 | 2008-03-08 | 40000 | 15.1 | 1.1 | 20.9 | 0.9 | 224.3 | -406.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.07 | 270.672 | 0.004 | -3.4
| 174 | 2008-03-08 | 50000 | 2.3 | 0.7 | 20.91 | 0.9 | 221.5 | -127.9 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.07 | 302.331 | 0.018 | -1.6
| 175 | 2008-03-08 | 60000 | 0 | 0 | 20.93 | 0.9 | 219.3 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 57.001 | 0.022 | 0
| 176 | 2008-03-08 | 70000 | 0 | 0.1 | 20.94 | 0.8 | 217 | -1.6 | 0.18 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 36.419 | 0.016 | 0
| 177 | 2008-03-08 | 80000 | 0 | 0 | 20.96 | 0.9 | 214.3 | 0 | 0.05 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 7.926 | 0.011 | 0
| 178 | 2008-03-08 | 90000 | 0 | 0 | 20.83 | 0.9 | 212 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | 2.06 | 0.009 | 0.009 | 0
| 179 | 2008-03-08 | 100000 | 0 | 0 | 20.98 | 0.8 | 209.6 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 0.009 | 0.008 | 0
| 180 | 2008-03-08 | 110000 | 0 | 0 | 20.98 | 0.9 | 207.2 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 0.009 | 0.009 | 0
| 181 | 2008-03-08 | 120000 | 0 | 0 | 20.9 | 0.9 | 204.8 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 0.01 | 0.009 | 0
| 182 | 2008-03-08 | 130000 | 0 | 0 | 20.97 | 0.8 | 202.2 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.07 | 0.011 | 0.01 | 0
| 183 | 2008-03-08 | 140000 | 0 | 0 | 20.97 | 0.9 | 199.6 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.01 | 0.011 | 0
| 184 | 2008-03-08 | 150000 | 0 | 0 | 20.96 | 0.8 | 197 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.012 | 0.011 | 0
| 185 | 2008-03-08 | 160000 | 0 | 0 | 20.95 | 0.9 | 194.4 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.016 | 0.013 | 0
| 186 | 2008-03-08 | 170000 | 0 | 0 | 20.94 | 0.9 | 192.4 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 0.014 | 0.018 | 0
| 187 | 2008-03-08 | 180000 | 0 | 0 | 20.93 | 0.9 | 190.1 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.03 | -0.06 | 156.71 | 0.02 | 0
| 188 | 2008-03-08 | 190000 | 0.9 | 0.8 | 20.92 | 1 | 187.3 | -55 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 303.912 | 0.02 | -0.4
| 189 | 2008-03-08 | 200000 | 3.1 | 0.6 | 20.91 | 1 | 185.4 | -154.4 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 314.991 | 0.015 | -1.5
| 190 | 2008-03-08 | 210000 | 3.3 | 0.4 | 20.91 | 0.9 | 183 | -121.4 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 294.414 | 0.014 | -1.6
| 191 | 2008-03-08 | 220000 | 7.3 | 1.4 | 20.91 | 0.9 | 180.5 | -101.4 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.07 | 364.057 | 0.014 | -1
| 192 | 2008-03-08 | 230000 | 25.6 | 0.4 | 20.9 | 0.9 | 178.6 | -307 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 277.002 | 1.59 | -1.9
| 193 | 2008-03-09 | 0 | 37.5 | 0.1 | 20.82 | 0.9 | 176.7 | -431.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 338.727 | 0.004 | -3.1
| 194 | 2008-03-09 | 10000 | 48.9 | -3.8 | 20.81 | 0.9 | 174.8 | -672.8 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 68.073 | 0.001 | -4.8
| 195 | 2008-03-09 | 20000 | 42.6 | 5.7 | 20.26 | 0.9 | 180.9 | -434.1 | 1.11 | 1.6 | 2.4 | -0.9 | 1.84 | 4.61 | 69.688 | 0.015 | -1.1
| 196 | 2008-03-09 | 30000 | 24.1 | 74.6 | 17.06 | 0.9 | 488.7 | 23.2 | 6.93 | 17.7 | 18.2 | -0.9 | 10.29 | 30 | 0.275 | 0.058 | 15.8
| 197 | 2008-03-09 | 40000 | 24.7 | 61.2 | 16.39 | 0.9 | 586.3 | 55.8 | 8.15 | 29.1 | 33.4 | -0.9 | 10.29 | 30 | 0.225 | 0.05 | 13.6
| 198 | 2008-03-09 | 50000 | 17.9 | 61 | 15.06 | 27 | 610.8 | 26 | 11.34 | 63.1 | 100.1 | -0.9 | 9.26 | 27.7 | 0.225 | 0.035 | 9.6
| 199 | 2008-03-09 | 60000 | 0 | 1.8 | 13.69 | 144.7 | 657.3 | -2 | 22.6 | 186.9 | 266.9 | -0.9 | 2.29 | 12.47 | 0.007 | 0.007 | 1.9
| 200 | 2008-03-09 | 70000 | 0 | 2 | 13.68 | 141.2 | 662.7 | -2.1 | 22.62 | 187.3 | 268.5 | -0.9 | 2.46 | 11.87 | 0.007 | 0.007 | 2
| 201 | 2008-03-09 | 80000 | 0 | 2 | 13.68 | 141.6 | 668.2 | -2.2 | 22.59 | 187.3 | 268.5 | -0.9 | 2.45 | 11.82 | 0.007 | 0.007 | 2
| 202 | 2008-03-09 | 90000 | 6.1 | 12.6 | 10.56 | 149.4 | 676.8 | 2.3 | 22.55 | 187 | 269.1 | -0.9 | 4.75 | 11.93 | 547.672 | 509.671 | 8.5
| 203 | 2008-03-09 | 100000 | 0.2 | 2.1 | 13.74 | 146.2 | 675.4 | -4.6 | 22.53 | 186.1 | 268 | -0.9 | 2.34 | 11.96 | 0.008 | 0.008 | 2.2
| 204 | 2008-03-09 | 110000 | 0 | 2 | 13.69 | 144.1 | 674.5 | -2.3 | 22.34 | 184.9 | 266.6 | -0.9 | 2.47 | 12 | 0.007 | 0.007 | 2
| 205 | 2008-03-09 | 120000 | 0 | 2 | 13.69 | 146.3 | 673 | -2.3 | 22.19 | 183 | 264 | -0.9 | 2.48 | 12.18 | 0.007 | 0.007 | 2
| 206 | 2008-03-09 | 130000 | 0 | 2 | 13.69 | 147.9 | 671.7 | -1.9 | 22.05 | 181.1 | 261.7 | -0.9 | 2.47 | 12.34 | 0.007 | 0.007 | 2
| 207 | 2008-03-09 | 140000 | 0 | 2 | 13.68 | 148.3 | 670.5 | -2.1 | 21.98 | 180.1 | 260.3 | -0.9 | 2.47 | 12.42 | 0.007 | 0.007 | 2
| 208 | 2008-03-09 | 150000 | 0 | 2 | 13.68 | 151.3 | 669.3 | -2.2 | 21.83 | 179.1 | 259.4 | -0.9 | 2.47 | 12.64 | 0.007 | 0.007 | 2
| 209 | 2008-03-09 | 160000 | 0 | 2 | 13.67 | 153.2 | 669.2 | -2.2 | 21.83 | 178.7 | 258.8 | -0.9 | 2.47 | 12.76 | 0.007 | 0.007 | 2
| 210 | 2008-03-09 | 170000 | 0 | 2 | 13.67 | 152.1 | 668.9 | -2.1 | 21.82 | 178.3 | 258.5 | -0.9 | 2.46 | 12.69 | 0.007 | 0.007 | 2
| 211 | 2008-03-09 | 180000 | 0 | 1.9 | 13.88 | 56.3 | 642.2 | -2.8 | 16.75 | 125.2 | 190.4 | -0.9 | 2.36 | 7.85 | 0.007 | 0.007 | 2
| 212 | 2008-03-09 | 190000 | 0 | 1.9 | 13.87 | 58 | 637.7 | -2.5 | 16.97 | 128.5 | 193.3 | -0.9 | 2.37 | 7.52 | 0.007 | 0.007 | 2
| 213 | 2008-03-09 | 200000 | 0 | 2 | 13.65 | 150 | 667.4 | -2.1 | 21.98 | 179.9 | 259.4 | -1 | 2.51 | 12.35 | 0.007 | 0.007 | 2
| 214 | 2008-03-09 | 210000 | 0 | 1.9 | 13.7 | 138.1 | 672.1 | -2.4 | 21.88 | 179.6 | 259.3 | -1 | 2.41 | 11.72 | 0.007 | 0.007 | 2
| 215 | 2008-03-09 | 220000 | 26 | 10.5 | 18.99 | 13.1 | 574.1 | -57.1 | 3.17 | 18.3 | 31.1 | -0.9 | 2.1 | 6.73 | 0.04 | 0.012 | 3.2
| 216 | 2008-03-09 | 230000 | 12.7 | -0.5 | 20.81 | 1 | 434.4 | -167.3 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | 0.04 | 0.005 | 0 | -0.8
| 217 | 2008-03-10 | 0 | 8.6 | -1.3 | 20.8 | 1.1 | 405.1 | -163.2 | 0.04 | 0.5 | 1.3 | -1 | -0.02 | -0.03 | 0.004 | 0 | -1.1
| 218 | 2008-03-10 | 10000 | 7.1 | -1.2 | 20.81 | 0.9 | 397.7 | -194.3 | 0.04 | 0.5 | 1.3 | -1 | -0.02 | -0.03 | 0.004 | 0 | -1.1
| 219 | 2008-03-10 | 20000 | 5.8 | -1.2 | 20.73 | 1 | 390.7 | -192.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.04 | 0.004 | 0 | -1
| 220 | 2008-03-10 | 30000 | 6.5 | 0.1 | 20.8 | 0.9 | 384.6 | -190.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.05 | 0.006 | 0 | -0.6
| 221 | 2008-03-10 | 40000 | 6.1 | -0.4 | 20.79 | 1 | 377.5 | -129.7 | 0.04 | 0.5 | 1.3 | -0.9 | -0.01 | -0.06 | 0.004 | 0 | -0.5
| 222 | 2008-03-10 | 50000 | 6.2 | 4 | 20.31 | 0.8 | 385.5 | -128.1 | 0.78 | 1.5 | 2.3 | -0.9 | 1.23 | 3.41 | 0.022 | 0.007 | 1
| 223 | 2008-03-10 | 60000 | 22.4 | 67.3 | 16.61 | 1 | 573.8 | 26.5 | 7.35 | 23 | 23.6 | -0.9 | 10.29 | 30.01 | 0.248 | 0.053 | 14.4
| 224 | 2008-03-10 | 70000 | 17.1 | 45.2 | 14.93 | 138.9 | 616.3 | 30.1 | 11.53 | 65.7 | 104.6 | -1 | 9.22 | 27.63 | 0.167 | 0.035 | 9.4
| 225 | 2008-03-10 | 80000 | 2 | 4.1 | 12.54 | 150.4 | 660.2 | -13.6 | 22.05 | 181.5 | 262.3 | -0.9 | 3.38 | 13.41 | 0.016 | 0.009 | 2.4
| 226 | 2008-03-10 | 90000 | 2.3 | 5.5 | 11.66 | 151.4 | 668.2 | 20 | 22.05 | 181.3 | 262.6 | -0.9 | 3.94 | 12.78 | 0.02 | 0.012 | 3.2
| 227 | 2008-03-10 | 100000 | 0 | 1.9 | 13.64 | 151.3 | 672.8 | -2.1 | 22.06 | 180.6 | 262.3 | -1 | 2.48 | 12.61 | 0.007 | 0.007 | 2
| 228 | 2008-03-10 | 110000 | 0 | 1.9 | 13.63 | 151.7 | 672.5 | -2 | 21.94 | 179.9 | 261.6 | -0.9 | 2.48 | 12.65 | 0.007 | 0.007 | 2
| 229 | 2008-03-10 | 120000 | 0 | 1.9 | 13.62 | 150.7 | 671.6 | -1.9 | 21.83 | 179.2 | 260.7 | -0.9 | 2.48 | 12.62 | 0.007 | 0.007 | 2
| 230 | 2008-03-10 | 130000 | 0 | 1.9 | 13.62 | 150.7 | 671.6 | -2.4 | 21.83 | 179.1 | 260.5 | -0.9 | 2.48 | 12.71 | 0.007 | 0.007 | 2
| 231 | 2008-03-10 | 140000 | 0 | 1.9 | 13.61 | 151.4 | 671.7 | -2.2 | 21.83 | 178.2 | 259.9 | -1 | 2.48 | 12.96 | 0.007 | 0.007 | 2
| 232 | 2008-03-10 | 150000 | 0 | 1.9 | 13.6 | 151 | 671.5 | -2.2 | 21.83 | 178.1 | 259.7 | -0.9 | 2.49 | 13 | 0.007 | 0.007 | 2
| 233 | 2008-03-10 | 160000 | 0 | 1.8 | 13.81 | 62 | 645.2 | -2.5 | 16.94 | 127.8 | 194.1 | -0.9 | 2.23 | 8.16 | 0.007 | 0.007 | 1.9
| 234 | 2008-03-10 | 170000 | 0 | 1.9 | 13.81 | 55.8 | 639.9 | -2.6 | 16.99 | 128.2 | 193.4 | -0.9 | 2.38 | 7.55 | 0.007 | 0.007 | 2
| 235 | 2008-03-10 | 180000 | 0 | 1.9 | 13.81 | 55 | 639.4 | -2.5 | 16.98 | 128.1 | 193.1 | -0.9 | 2.44 | 7.52 | 0.007 | 0.007 | 2
| 236 | 2008-03-10 | 190000 | 0 | 1.9 | 13.81 | 55.4 | 639.6 | -2.3 | 16.99 | 128 | 192.6 | -0.9 | 2.4 | 7.54 | 0.007 | 0.007 | 2
| 237 | 2008-03-10 | 200000 | 27.8 | 10.2 | 19.36 | 9.3 | 552 | -90 | 2.2 | 11 | 17.9 | -0.9 | 2.05 | 6.29 | 0.041 | 0.012 | 2.9
| 238 | 2008-03-10 | 210000 | 11 | -3.9 | 20.77 | 1 | 425.3 | -311 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | 0.01 | 0.006 | 0 | -2.7
| 239 | 2008-03-10 | 220000 | 13.7 | -6 | 20.87 | 1 | 399.1 | -544.4 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.04 | 0.007 | 0 | -4.5
| 240 | 2008-03-10 | 230000 | 11.2 | -5.3 | 20.88 | 1 | 387.5 | -690.4 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.04 | 20.589 | 0 | -5.3
| 241 | 2008-03-11 | 0 | 9 | -2 | 20.89 | 0.9 | 378.7 | -528.9 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 112.395 | 1.585 | -4.6
| 242 | 2008-03-11 | 10000 | 6.3 | -1.6 | 20.9 | 0.9 | 370.8 | -488.9 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 117.144 | 0.006 | -4.2
| 243 | 2008-03-11 | 20000 | 4.7 | 0 | 20.9 | 1 | 363.5 | -363.9 | 0.04 | 0.5 | 1.3 | -0.9 | -0.03 | -0.06 | 308.659 | 0.009 | -3.1
| 244 | 2008-03-11 | 30000 | 6.3 | 14.8 | 19.98 | 0.9 | 388.3 | -81.7 | 1.58 | 4.2 | 4.9 | -0.9 | 2.24 | 6.46 | 183.673 | 0.024 | 2.1
| 245 | 2008-03-11 | 40000 | 26.5 | 53.9 | 16.48 | 0.9 | 604.4 | 82.9 | 7.92 | 26.2 | 26.4 | -0.9 | 10.29 | 30.01 | 0.198 | 0.051 | 13.8
| 246 | 2008-03-11 | 50000 | 14.9 | 34.2 | 15.11 | 86 | 615.3 | 30 | 11.85 | 69.4 | 104.4 | -0.9 | 7.54 | 23.49 | 0.126 | 0.031 | 8.5
| 247 | 2008-03-11 | 60000 | 0 | 1.9 | 13.73 | 150 | 657 | -2.3 | 22.47 | 185.2 | 265.6 | -0.9 | 2.45 | 12.96 | 0.007 | 0.007 | 2
| 248 | 2008-03-11 | 70000 | 0 | 1.9 | 13.81 | 133.8 | 661.3 | -2 | 22.36 | 184.4 | 264.8 | -0.9 | 2.41 | 11.77 | 0.007 | 0.007 | 2
| 249 | 2008-03-11 | 80000 | 0.9 | 4.2 | 12.04 | 147.7 | 672.1 | 20.1 | 22.53 | 186.5 | 268.4 | -0.9 | 3.6 | 12.83 | 7.93 | 0.008 | 2.1
| 250 | 2008-03-11 | 90000 | 3.6 | 5.9 | 12.3 | 146.9 | 676.9 | 11.5 | 22.56 | 186.6 | 269.1 | -0.9 | 3.64 | 12.71 | 96.568 | 88.647 | 3.9
| 251 | 2008-03-11 | 100000 | 0 | 2.1 | 13.73 | 147.7 | 676.8 | -2.2 | 22.61 | 186.9 | 269.4 | -0.9 | 2.44 | 12.93 | 0.008 | 0.007 | 2
| 252 | 2008-03-11 | 110000 | 0 | 2.1 | 13.74 | 149.4 | 675.6 | -2.3 | 22.54 | 186.2 | 268.8 | -0.9 | 2.45 | 13.11 | 0.008 | 0.007 | 2
| 253 | 2008-03-11 | 120000 | 0 | 2.1 | 13.74 | 150.2 | 674.9 | -2.1 | 22.54 | 186 | 268.6 | -0.9 | 2.44 | 12.93 | 0.008 | 0.007 | 2
| 254 | 2008-03-11 | 130000 | 0 | 2.1 | 13.74 | 148.9 | 674.9 | -2.6 | 22.58 | 187 | 268.5 | -0.9 | 2.43 | 12.69 | 0.008 | 0.007 | 2
| 255 | 2008-03-11 | 140000 | 0 | 2.1 | 13.74 | 147.3 | 675.3 | -2 | 22.61 | 187.1 | 268.7 | -1 | 2.43 | 12.61 | 0.008 | 0.007 | 2
| 256 | 2008-03-11 | 150000 | 0 | 2.1 | 13.73 | 148.1 | 675.1 | -2.2 | 22.54 | 186.4 | 268.1 | -0.9 | 2.45 | 12.67 | 0.008 | 0.007 | 2
| 257 | 2008-03-11 | 160000 | 0 | 2 | 13.75 | 143.8 | 674.6 | -2.1 | 22.15 | 182.1 | 263.3 | -0.9 | 2.33 | 12.4 | 0.007 | 0.007 | 1.9
| 258 | 2008-03-11 | 170000 | 0 | 2 | 13.94 | 58.8 | 641.3 | -2.7 | 17.1 | 128.7 | 194.3 | -0.9 | 2.25 | 8 | 0.007 | 0.007 | 1.9
| 259 | 2008-03-11 | 180000 | 0 | 2.1 | 13.93 | 58.4 | 637.8 | -2.3 | 17.05 | 127.9 | 192.9 | -0.9 | 2.37 | 8.03 | 0.008 | 0.007 | 2
| 260 | 2008-03-11 | 190000 | 0 | 2.1 | 13.92 | 58.2 | 636.4 | -2.4 | 17.08 | 127.9 | 192.9 | -0.9 | 2.36 | 7.97 | 0.008 | 0.007 | 2
| 261 | 2008-03-11 | 200000 | 0 | 2.1 | 13.91 | 57.2 | 637.3 | -2.5 | 17.11 | 128 | 193 | -0.9 | 2.39 | 7.9 | 0.008 | 0.007 | 2
| 262 | 2008-03-11 | 210000 | 0.1 | 2.1 | 13.9 | 57 | 637.5 | -2.4 | 17.13 | 127.6 | 192.7 | -0.9 | 2.38 | 7.87 | 0.008 | 0.007 | 2
| 263 | 2008-03-11 | 220000 | 56.3 | 14.8 | 19.48 | 4 | 553.9 | -169.8 | 2.2 | 10.1 | 17.9 | -1 | 2.52 | 6.68 | 112.44 | 7.939 | 6.2
| 264 | 2008-03-11 | 230000 | 18.7 | -0.6 | 20.9 | 0.9 | 425.9 | -328.2 | 0.3 | 0.5 | 1.3 | -0.9 | -0.02 | 0.01 | 182.038 | 0.006 | -2.7
| 265 | 2008-03-12 | 0 | 22.6 | -1.9 | 20.89 | 0.9 | 399.7 | -540.8 | 0.26 | 0.5 | 1.3 | -0.9 | -0.02 | -0.03 | 140.886 | 0.004 | -4
| 266 | 2008-03-12 | 10000 | 24.2 | -2.7 | 20.88 | 0.9 | 387.8 | -583.5 | 0.15 | 0.5 | 1.3 | -0.9 | -0.02 | -0.05 | 94.981 | 0.001 | -5.1
| 267 | 2008-03-12 | 20000 | 25.5 | -5.4 | 20.87 | 0.9 | 376.9 | -534.3 | 0.05 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 19.005 | 0 | -4
| 268 | 2008-03-12 | 30000 | 12 | -1.9 | 20.59 | 0.9 | 390.7 | -525.7 | 0.41 | 0.5 | 1.3 | -1 | 0.79 | 1.77 | 3.183 | 0.006 | -1.5
| 269 | 2008-03-12 | 40000 | 24.2 | 66.5 | 16.58 | 0.9 | 585.8 | 40.5 | 7.69 | 24.9 | 25.2 | -1 | 10.29 | 29.98 | 0.245 | 0.053 | 14.3
| 270 | 2008-03-12 | 50000 | 15.7 | 44.2 | 15.15 | 30.1 | 617 | 32.1 | 11.87 | 69.4 | 107.6 | -1 | 7.81 | 24.18 | 0.163 | 0.032 | 8.8
| 271 | 2008-03-12 | 60000 | 0.1 | 2 | 13.85 | 62 | 634.1 | -2.3 | 17.27 | 129.3 | 194 | -1 | 2.25 | 8.43 | 0.007 | 0.007 | 1.9
| 272 | 2008-03-12 | 70000 | 0.1 | 2.1 | 13.84 | 60 | 635.4 | -2.4 | 17.18 | 128.9 | 193.8 | -1 | 2.4 | 8.1 | 0.008 | 0.007 | 2
| 273 | 2008-03-12 | 80000 | 0.1 | 2.1 | 13.83 | 58.9 | 636.7 | -2.2 | 17.06 | 127.4 | 192.5 | -1 | 2.47 | 8.2 | 0.008 | 0.007 | 2
| 274 | 2008-03-12 | 90000 | 31.2 | 18.6 | 15.03 | 1 | 552.1 | -30.9 | 1.69 | 6 | 11.7 | -0.9 | 4.52 | 3.07 | 0.07 | 0.028 | 7.4
| 275 | 2008-03-12 | 100000 | 30.4 | 27.2 | 18.52 | 0.9 | 443.5 | -168 | 0.22 | 0.5 | 1.3 | -0.9 | 1.47 | -0.01 | 91.899 | 38.069 | 22.7
| 276 | 2008-03-12 | 110000 | 10.5 | 1.5 | 20.71 | 1 | 427.9 | -137.4 | 0.04 | 0.5 | 1.3 | -1 | 0.02 | -0.03 | 0.008 | 0.005 | 1.4
| 277 | 2008-03-12 | 120000 | 6.3 | 0 | 20.77 | 0.9 | 422.5 | -123.4 | 0.04 | 0.5 | 1.3 | -1 | -0.01 | -0.03 | 0.004 | 0 | -0.3
| 278 | 2008-03-12 | 130000 | 7.7 | 0 | 20.77 | 1 | 417.7 | -129.2 | 0.04 | 0.5 | 1.3 | -1 | -0.01 | -0.03 | 0.004 | 0 | -0.5
| 279 | 2008-03-12 | 140000 | 6 | -0.9 | 20.75 | 0.9 | 414 | -123.6 | 0.04 | 0.5 | 1.3 | -1 | -0.02 | -0.03 | 0.003 | 0 | -0.6
| 280 | 2008-03-12 | 150000 | 5.9 | -0.1 | 20.74 | 0.8 | 408.6 | -115 | 0.04 | 0.5 | 1.3 | -1 | -0.01 | -0.04 | 0.003 | 0 | -0.2
| 281 | 2008-03-12 | 160000 | 4.1 | -0.7 | 20.72 | 1 | 403.3 | -86 | 0.04 | 0.5 | 1.3 | -1 | -0.02 | -0.03 | 0.002 | 0 | -0.6
| 282 | 2008-03-12 | 170000 | 4 | -0.6 | 20.71 | 1 | 403.8 | -83.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.03 | 0.002 | 0 | -0.6
| 283 | 2008-03-12 | 180000 | 3.5 | -0.5 | 20.69 | 1 | 400.2 | -75.2 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.04 | 0.002 | 0 | -0.6
| 284 | 2008-03-12 | 190000 | 3.2 | -0.7 | 20.68 | 1 | 393.9 | -71.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 0.001 | 0 | -0.6
| 285 | 2008-03-12 | 200000 | 3.4 | -0.7 | 20.67 | 0.8 | 387.6 | -70.8 | 0.04 | 0.5 | 1.3 | -0.9 | -0.02 | -0.07 | 0.001 | 0 | -0.6
| 286 | 2008-03-12 | 210000 | 3.2 | -0.4 | 20.66 | 0.8 | 381.2 | -74.7 | 0.04 | 0.5 | 1.3 | -1 | -0.02 | -0.06 | 0.001 | 0 | -0.6
| 287 | 2008-03-12 | 220000 | 2.9 | -0.6 | 20.65 | 0.9 | 374.4 | -59.6 | 0.04 | 0.5 | 1.3 | -1 | -0.02 | -0.06 | 0.001 | 0 | -0.5
| 288 | 2008-03-12 | 230000 | 2.8 | -0.6 | 20.64 | 0.9 | 367.2 | -61.6 | 0.18 | 0.5 | 1.3 | -1 | -0.02 | -0.06 | 0.001 | 0 | -0.5
| 289 | 2008-03-13 | 0 | 2.9 | -0.5 | 20.63 | 0.9 | 360.2 | -58.1 | 0.26 | 0.5 | 1.3 | -0.9 | -0.02 | -0.06 | 0.001 | 0 | -0.5
| 290 | 2008-03-13 | 10000 | 2.8 | -0.5 | 20.61 | 0.8 | 353.9 | -54.1 | 0.26 | 0.5 | 1.3 | -1 | -0.02 | -0.07 | 0.001 | 0 | -0.5
| 291 | 2008-03-13 | 20000 | 2.2 | -0.5 | 20.59 | 1 | 347.2 | -50.4 | 0.34 | 0.5 | 1.3 | -1 | -0.02 | -0.06 | 0.001 | 0 | -0.5
| 292 | 2008-03-13 | 30000 | 6.7 | 9.1 | 19.88 | 0.9 | 353.3 | -26.1 | 1.53 | 1.8 | 2.6 | -1 | 2.03 | 5.17 | 0.036 | 0.012 | 3
| 293 | 2008-03-13 | 40000 | 23.4 | 61.7 | 16.39 | 1 | 568.4 | 37 | 7.45 | 23.3 | 23.7 | -0.9 | 10.29 | 30 | 0.227 | 0.05 | 13.6
| 294 | 2008-03-13 | 50000 | 19.1 | 52.1 | 15.26 | 14.7 | 608 | 34.6 | 10.02 | 49.7 | 75.7 | -0.9 | 9.56 | 28.09 | 0.192 | 0.038 | 10.3
| 295 | 2008-03-13 | 60000 | 0 | 1.9 | 13.63 | 58.4 | 633.7 | -2.4 | 17.26 | 130.8 | 194.4 | -0.9 | 2.35 | 8.17 | 0.007 | 0.007 | 1.9
| 296 | 2008-03-13 | 70000 | 2.8 | 6.4 | 11.79 | 60.6 | 638.5 | -0.2 | 17.22 | 130.9 | 195.3 | -0.9 | 3.95 | 7.69 | 0.024 | 0.015 | 4
| 297 | 2008-03-13 | 80000 | 1.3 | 3.9 | 12.56 | 57.3 | 636.9 | 10 | 17.13 | 129.6 | 193.6 | -0.9 | 3.05 | 7.77 | 0.014 | 0.008 | 2
| 298 | 2008-03-13 | 90000 | 0.1 | 2 | 13.88 | 55.5 | 635.8 | -2.3 | 17.15 | 129.6 | 193.6 | -1 | 2.38 | 8.68 | 0.007 | 0.007 | 2
| 299 | 2008-03-13 | 100000 | 0.1 | 2 | 13.88 | 53.2 | 636.3 | -2.2 | 17.14 | 129.3 | 193 | -1 | 2.4 | 7.76 | 0.007 | 0.007 | 2
| 300 | 2008-03-13 | 110000 | 0.1 | 2 | 13.87 | 52.3 | 635.6 | -2.2 | 17.15 | 129.4 | 193.1 | -0.9 | 2.4 | 7.65 | 0.007 | 0.007 | 2
| 301 | 2008-03-13 | 120000 | 0.1 | 2 | 13.87 | 53.8 | 636.4 | -2.4 | 17.16 | 129.9 | 193.6 | -0.9 | 2.4 | 7.66 | 0.007 | 0.007 | 2
| 302 | 2008-03-13 | 130000 | 0.1 | 2 | 13.86 | 53 | 636.2 | -2.4 | 17.16 | 130.4 | 194.4 | -1 | 2.4 | 7.58 | 0.007 | 0.007 | 2
| 303 | 2008-03-13 | 140000 | 0.1 | 2 | 13.86 | 52.2 | 636.6 | -2.7 | 17.15 | 129.8 | 193 | -0.9 | 2.4 | 7.52 | 0.007 | 0.007 | 2
| 304 | 2008-03-13 | 150000 | 0.1 | 2 | 13.86 | 52 | 636.7 | -1.9 | 17.15 | 130.1 | 193.2 | -0.9 | 2.4 | 7.5 | 0.007 | 0.007 | 2
| 305 | 2008-03-13 | 160000 | 0.1 | 2 | 13.86 | 53 | 636.2 | -2.1 | 17.15 | 130.4 | 193.7 | -0.9 | 2.41 | 7.58 | 0.007 | 0.007 | 2
| 306 | 2008-03-13 | 170000 | 0.1 | 2 | 13.86 | 53 | 635.9 | -2.6 | 17.16 | 130.6 | 194.2 | -0.9 | 2.4 | 7.53 | 0.007 | 0.007 | 2
| 307 | 2008-03-13 | 180000 | 0.1 | 2 | 13.86 | 52.2 | 635.8 | -2.4 | 17.09 | 129.8 | 193.4 | -0.9 | 2.41 | 7.53 | 0.007 | 0.007 | 2
| 308 | 2008-03-13 | 190000 | 35.9 | -12 | 19.64 | 5.3 | 549.8 | -144.6 | 1.67 | 7.2 | 13.2 | -0.9 | 1.88 | 6.07 | 0.042 | 0.013 | -21.4
| 309 | 2008-03-13 | 200000 | 19.6 | -63.8 | 20.85 | 0.9 | 436 | -342.3 | 0.04 | 0.5 | 1.3 | -0.9 | -0.48 | 0.01 | 0 | 0 | -68.2
| 310 | 2008-03-13 | 210000 | 24.6 | -65.6 | 20.85 | 0.9 | 414.2 | -330.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.48 | -0.03 | 0 | 0 | -70.7
| 311 | 2008-03-13 | 220000 | 18.9 | -64.5 | 20.85 | 0.9 | 401.9 | -448.3 | 0.17 | 0.5 | 1.3 | -0.9 | -0.48 | -0.03 | 0 | 0 | -67.9
| 312 | 2008-03-13 | 230000 | 12.4 | -46.9 | 20.84 | 0.8 | 390.7 | -294.4 | 0.31 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0 | 0 | -50.3
| 313 | 2008-03-14 | 0 | 12.2 | -45 | 20.84 | 0.8 | 383 | -264.5 | 0.36 | 0.5 | 1.3 | -0.9 | -0.49 | -0.07 | 0 | 0 | -47.7
| 314 | 2008-03-14 | 10000 | 10.1 | -42.4 | 20.76 | 0.8 | 377.1 | -260 | 0.47 | 0.5 | 1.3 | -0.9 | -0.49 | -0.07 | 0 | 0 | -44.5
| 315 | 2008-03-14 | 20000 | 10 | -42.3 | 20.83 | 0.9 | 370.3 | -274.2 | 0.27 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0 | 0 | -45.1
| 316 | 2008-03-14 | 30000 | 9.5 | -37.1 | 20.83 | 0.8 | 358.1 | -271 | 0.27 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0 | 0 | -40.1
| 317 | 2008-03-14 | 40000 | 9 | -37.2 | 20.82 | 0.9 | 339.1 | -216.5 | 0.26 | 0.5 | 1.3 | -0.9 | -0.49 | -0.07 | 0 | 0 | -39.9
| 318 | 2008-03-14 | 50000 | 10.9 | -39.5 | 20.83 | 0.9 | 329 | -264.4 | 0.26 | 0.5 | 1.3 | -1 | -0.48 | -0.06 | 0 | 0 | -42.6
| 319 | 2008-03-14 | 60000 | 11.5 | -40.2 | 20.83 | 1 | 322.2 | -219.3 | 0.18 | 0.5 | 1.3 | -0.9 | -0.49 | -0.07 | 0 | 0 | -42.8
| 320 | 2008-03-14 | 70000 | 11.5 | -37.7 | 20.75 | 0.9 | 317.8 | -217.1 | 0.26 | 0.5 | 1.3 | -0.9 | -0.48 | -0.06 | 0 | 0 | -39.6
| 321 | 2008-03-14 | 80000 | 11.2 | -37.5 | 20.75 | 1 | 314.2 | -206.3 | 0.26 | 0.5 | 1.3 | -0.9 | -0.48 | -0.06 | 0 | 0 | -39.8
| 322 | 2008-03-14 | 90000 | 13.1 | -39.1 | 20.83 | 0.9 | 310.4 | -225 | 0.19 | 0.5 | 1.3 | -0.9 | -0.48 | 2.08 | 0 | 0 | -42
| 323 | 2008-03-14 | 100000 | 12.8 | -42.6 | 20.83 | 0.9 | 306.9 | -242 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.07 | 0 | 0 | -45.2
| 324 | 2008-03-14 | 110000 | 14.6 | -47.1 | 20.84 | 0.9 | 303.5 | -273.5 | 0.04 | 0.5 | 1.3 | -1 | -0.48 | -0.06 | 0 | 0 | -50.9
| 325 | 2008-03-14 | 120000 | 17.4 | -53 | 20.84 | 0.9 | 300.1 | -327.6 | 0.04 | 0.5 | 1.3 | -1 | -0.48 | -0.07 | 0 | 0 | -56.8
| 326 | 2008-03-14 | 130000 | 16.9 | -54.1 | 20.84 | 1 | 296.6 | -374.4 | 0.04 | 0.5 | 1.3 | -0.9 | -0.48 | -0.06 | 0 | 0 | -57.8
| 327 | 2008-03-14 | 140000 | 13.9 | -47.5 | 20.84 | 0.9 | 293 | -319.2 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0 | 0 | -51.1
| 328 | 2008-03-14 | 150000 | 13.4 | -46.7 | 20.84 | 0.9 | 289.8 | -299.7 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0 | 0 | -51
| 329 | 2008-03-14 | 160000 | 13.5 | -46.2 | 20.84 | 1 | 286.4 | -264 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.07 | 0 | 0 | -49.9
| 330 | 2008-03-14 | 170000 | 14.8 | -47.8 | 20.84 | 0.9 | 283.2 | -308.9 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0 | 0 | -50.9
| 331 | 2008-03-14 | 180000 | 15.1 | -54.2 | 20.84 | 0.9 | 279.9 | -293.5 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.07 | 0 | 0 | -58
| 332 | 2008-03-14 | 190000 | 23.7 | -62.4 | 20.85 | 1 | 276.4 | -382.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.48 | -0.06 | 0 | 0 | -66.1
| 333 | 2008-03-14 | 200000 | 25 | -74.2 | 20.86 | 0.8 | 273.3 | -500.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.48 | -0.07 | 0.001 | 0.001 | -79.1
| 334 | 2008-03-14 | 210000 | 31.5 | -88.6 | 20.87 | 0.9 | 270.1 | -561.2 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.005 | 0.006 | -96.4
| 335 | 2008-03-14 | 220000 | 44.4 | -106.9 | 20.88 | 0.8 | 266.7 | -701.4 | 0.04 | 0.5 | 1.3 | -1 | -0.48 | -0.07 | 0.006 | 0.007 | -111.2
| 336 | 2008-03-14 | 230000 | 42 | -102.6 | 20.88 | 0.9 | 263.5 | -644.3 | 0.04 | 0.5 | 1.3 | -0.9 | -0.48 | -0.06 | 0.02 | 0.023 | -106.9
| 337 | 2008-03-15 | 0 | 31 | -100.1 | 20.89 | 0.8 | 260.2 | -586.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.045 | 0.052 | -107.1
| 338 | 2008-03-15 | 10000 | 25.9 | -81.3 | 20.89 | 1 | 257.2 | -428.8 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.07 | 0.081 | -83
| 339 | 2008-03-15 | 20000 | 16.4 | -65.8 | 20.9 | 0.9 | 254.1 | -304.9 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.143 | 0.162 | -65.3
| 340 | 2008-03-15 | 30000 | 8 | -29.2 | 20.91 | 0.9 | 251.1 | -161.6 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.212 | 0.233 | -30
| 341 | 2008-03-15 | 40000 | 5.2 | -17 | 20.92 | 0.8 | 247.8 | -125.7 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.268 | 0.292 | -17.5
| 342 | 2008-03-15 | 50000 | 1.2 | -4 | 20.85 | 0.8 | 244.6 | -26.9 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.284 | 0.305 | -3.9
| 343 | 2008-03-15 | 60000 | 0.2 | -0.9 | 20.94 | 0.8 | 241.6 | -11.1 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.259 | 0.276 | -0.8
| 344 | 2008-03-15 | 70000 | 0 | 0 | 20.95 | 0.9 | 238.4 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.23 | 0.24 | 0
| 345 | 2008-03-15 | 80000 | 18.1 | 7.1 | 20.46 | 0.8 | 231.3 | 95.9 | 0.86 | 1.2 | 2.1 | -0.9 | 1.07 | 3.59 | 0.168 | 0.158 | 2.8
| 346 | 2008-03-15 | 90000 | 18.6 | 87.5 | 16.84 | 1 | 513.4 | 20.2 | 7.37 | 22.2 | 22.6 | -0.9 | 10.29 | 27.16 | 0.322 | 0.055 | 15
| 347 | 2008-03-15 | 100000 | 20.2 | 75.8 | 15.93 | 1 | 600 | 24.3 | 8.91 | 37.5 | 40.1 | -1 | 10.29 | 30 | 0.279 | 0.046 | 12.4
| 348 | 2008-03-15 | 110000 | 18.1 | 63.9 | 15.15 | 12.4 | 601.6 | 25.5 | 11.02 | 59.5 | 95.5 | -0.9 | 9.51 | 27.82 | 0.235 | 0.037 | 10
| 349 | 2008-03-15 | 120000 | 0 | 1.9 | 13.91 | 67.3 | 643.1 | -2.3 | 18.48 | 143.7 | 210.8 | -0.9 | 2.29 | 8.96 | 0.007 | 0.007 | 1.9
| 350 | 2008-03-15 | 130000 | 0 | 2 | 13.92 | 58 | 644.7 | -2.3 | 18.13 | 140.7 | 208.6 | -0.9 | 2.46 | 8.09 | 0.008 | 0.008 | 2.1
| 351 | 2008-03-15 | 140000 | 0 | 2.1 | 13.92 | 58.1 | 645.5 | -2.5 | 18.14 | 141.2 | 209.3 | -0.9 | 2.49 | 7.98 | 0.008 | 0.008 | 2.1
| 352 | 2008-03-15 | 150000 | 0 | 2.1 | 13.92 | 59.2 | 645.3 | -2 | 18.14 | 141.2 | 209.4 | -0.9 | 2.51 | 7.96 | 0.008 | 0.008 | 2.1
| 353 | 2008-03-15 | 160000 | 0 | 2.1 | 13.93 | 59.8 | 644.3 | -2.5 | 18.14 | 141 | 209.1 | -0.9 | 2.49 | 7.99 | 0.008 | 0.008 | 2.1
| 354 | 2008-03-15 | 170000 | 0 | 2.1 | 13.93 | 59.1 | 644 | -2.3 | 18.18 | 141.7 | 209.7 | -1 | 2.49 | 7.89 | 0.008 | 0.008 | 2.1
| 355 | 2008-03-15 | 180000 | 0 | 2.1 | 13.77 | 136.2 | 669.2 | -2.2 | 22.33 | 184.3 | 265.1 | -1 | 2.51 | 12.65 | 0.008 | 0.008 | 2.1
| 356 | 2008-03-15 | 190000 | 0 | 2.1 | 13.78 | 135.6 | 674.7 | -2.2 | 22.51 | 185.1 | 267 | -0.9 | 2.55 | 12.76 | 0.008 | 0.008 | 2.1
| 357 | 2008-03-15 | 200000 | 0 | 2.1 | 13.78 | 135.7 | 675.1 | -2.3 | 22.53 | 185.3 | 266.3 | -0.9 | 2.54 | 12.73 | 0.008 | 0.008 | 2.1
| 358 | 2008-03-15 | 210000 | 0 | 2.2 | 13.79 | 133.1 | 675.8 | -2.6 | 22.53 | 185.7 | 266.3 | -0.9 | 2.7 | 12.64 | 0.008 | 0.008 | 2.2
| 359 | 2008-03-15 | 220000 | 0 | 2.2 | 13.98 | 56.3 | 650.5 | -2.1 | 18.06 | 139.1 | 207.1 | -0.9 | 2.58 | 8 | 0.008 | 0.008 | 2.2
| 360 | 2008-03-15 | 230000 | 0 | 2.1 | 13.99 | 57.6 | 644.6 | -2.5 | 18.11 | 139.8 | 207.1 | -0.9 | 2.45 | 7.83 | 0.008 | 0.008 | 2.1
| 361 | 2008-03-16 | 0 | 26 | 8 | 19.76 | 16.1 | 568.2 | -3.8 | 1.9 | 8.7 | 15.9 | -0.9 | 1.7 | 6.26 | 0.082 | 0.053 | -0.2
| 362 | 2008-03-16 | 10000 | 0 | 0 | 21.1 | 0.9 | 453.5 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.48 | 0.02 | 0.051 | 0.053 | 0
| 363 | 2008-03-16 | 20000 | 0 | 0 | 21.12 | 0.9 | 435.6 | 0 | 0.1 | 0.5 | 1.3 | -0.9 | -0.49 | -0.04 | 0.047 | 0.049 | 0
| 364 | 2008-03-16 | 30000 | 0 | 0 | 21.05 | 0.9 | 427.8 | 0 | 0.35 | 0.5 | 1.3 | -0.9 | -0.49 | -0.03 | 0.045 | 0.047 | 0
| 365 | 2008-03-16 | 40000 | 0 | 0 | 21.13 | 0.9 | 420.8 | 0 | 0.26 | 0.5 | 1.3 | -0.9 | -0.49 | -0.03 | 0.044 | 0.046 | 0
| 366 | 2008-03-16 | 50000 | 0 | 0 | 21.13 | 0.8 | 414.9 | 0 | 0.25 | 0.5 | 1.3 | -0.9 | -0.49 | -0.04 | 0.044 | 0.046 | 0
| 367 | 2008-03-16 | 60000 | 0 | 0 | 21.14 | 0.8 | 410 | 0 | 0.26 | 0.5 | 1.3 | -0.9 | -0.49 | -0.05 | 0.041 | 0.044 | 0
| 368 | 2008-03-16 | 70000 | 0 | 0 | 21.16 | 0.9 | 404 | 0 | 0.13 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.039 | 0.041 | 0
| 369 | 2008-03-16 | 80000 | 0 | 0 | 21.11 | 0.8 | 398.1 | 0 | 0.23 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.036 | 0.038 | 0
| 370 | 2008-03-16 | 90000 | 0 | 0 | 21.2 | 0.9 | 392.5 | 0 | 0.27 | 0.5 | 1.3 | -0.9 | -0.49 | 2.09 | 0.033 | 0.035 | 0
| 371 | 2008-03-16 | 100000 | 0 | 0 | 21.21 | 1 | 387.4 | 0 | 0.06 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.032 | 0.034 | 0
| 372 | 2008-03-16 | 110000 | 0 | 0 | 21.22 | 1 | 381.4 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.07 | 0.032 | 0.033 | 0
| 373 | 2008-03-16 | 120000 | 0 | 0 | 21.22 | 0.9 | 375.8 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.031 | 0.033 | 0
| 374 | 2008-03-16 | 130000 | 0 | 0 | 21.21 | 1 | 370.7 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.48 | -0.07 | 0.032 | 0.034 | 0
| 375 | 2008-03-16 | 140000 | 0 | 0 | 21.21 | 0.9 | 365.1 | 0 | 0.05 | 0.5 | 1.3 | -0.9 | -0.49 | -0.07 | 0.033 | 0.034 | 0
| 376 | 2008-03-16 | 150000 | 0 | 0 | 21.21 | 0.9 | 357.4 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.07 | 0.032 | 0.034 | 0
| 377 | 2008-03-16 | 160000 | 0 | 0 | 21.21 | 1 | 336.1 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.032 | 0.034 | 0
| 378 | 2008-03-16 | 170000 | 0 | 0 | 21.2 | 0.9 | 319.6 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.033 | 0.035 | 0
| 379 | 2008-03-16 | 180000 | 0 | 0 | 21.21 | 0.9 | 310.5 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.033 | 0.035 | 0
| 380 | 2008-03-16 | 190000 | 0 | 0 | 21.21 | 0.9 | 304.9 | 0 | 0.12 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.033 | 0.034 | 0
| 381 | 2008-03-16 | 200000 | 0 | 0 | 21.22 | 0.9 | 300.9 | 0 | 0.2 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.031 | 0.034 | 0
| 382 | 2008-03-16 | 210000 | 0 | 0 | 21.21 | 0.8 | 297.8 | 0 | 0.06 | 0.5 | 1.3 | -1 | -0.49 | -0.07 | 0.033 | 0.035 | 0
| 383 | 2008-03-16 | 220000 | 0 | 0 | 21.2 | 0.8 | 294.9 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.034 | 0.036 | 0
| 384 | 2008-03-16 | 230000 | 0 | 0 | 21.12 | 0.9 | 291.7 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.07 | 0.035 | 0.037 | 0
| 385 | 2008-03-17 | 0 | 0 | 0 | 21.18 | 0.9 | 288.4 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.07 | 0.037 | 0.039 | 0
| 386 | 2008-03-17 | 10000 | 0 | 0 | 21.16 | 0.9 | 285.3 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.039 | 0.041 | 0
| 387 | 2008-03-17 | 20000 | 0 | 0 | 21.17 | 0.8 | 282.3 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.49 | -0.06 | 0.038 | 0.039 | 0
| 388 | 2008-03-17 | 30000 | 0 | 0 | 21.16 | 0.9 | 279 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.49 | -0.06 | 0.039 | 0.041 | 0
| 389 | 2008-03-17 | 40000 | 8 | 8.4 | 20.56 | 0.8 | 281.1 | 83.7 | 1 | 1.4 | 2.1 | -0.9 | 1.31 | 4.3 | 0.065 | 0.048 | 3.3
| 390 | 2008-03-17 | 50000 | 22 | 78.5 | 17.09 | 0.9 | 536.9 | 23.2 | 7.19 | 20.2 | 20.6 | -1 | 10.29 | 30.01 | 0.289 | 0.059 | 16
| 391 | 2008-03-17 | 60000 | 18.2 | 40 | 15.55 | 84 | 614.7 | 36.2 | 11.04 | 60.1 | 83.7 | -1 | 8.15 | 25.37 | 0.147 | 0.037 | 9.9
| 392 | 2008-03-17 | 70000 | 13 | 8 | 10.67 | 50.9 | 627 | -25.7 | 17.53 | 132.6 | 194.4 | -1 | 4.8 | 8.28 | 3.205 | 0.023 | 3.3
| 393 | 2008-03-17 | 80000 | 0.1 | 2.1 | 13.69 | 138.3 | 658.5 | -2.2 | 22.48 | 185.6 | 264.3 | -1 | 2.6 | 12.52 | 0.008 | 0.008 | 2.1
| 394 | 2008-03-17 | 90000 | 0 | 2.1 | 13.76 | 118.2 | 674.6 | -2 | 22.27 | 183.4 | 263.6 | -1 | 2.5 | 11.31 | 0.008 | 0.008 | 2.1
| 395 | 2008-03-17 | 100000 | 0.1 | 2.2 | 13.85 | 52.1 | 644.5 | -2.4 | 16.82 | 124.8 | 190.2 | -1 | 2.6 | 7.99 | 0.008 | 0.008 | 2.2
| 396 | 2008-03-17 | 110000 | 0.1 | 2.1 | 13.85 | 55.4 | 638.9 | -2.1 | 17.14 | 127.9 | 192.9 | -0.9 | 2.51 | 7.85 | 0.008 | 0.008 | 2.1
| 397 | 2008-03-17 | 120000 | 0.1 | 2.1 | 13.85 | 55.2 | 638.9 | -2.5 | 17.1 | 128.1 | 193.5 | -1 | 2.52 | 7.79 | 0.008 | 0.008 | 2.1
| 398 | 2008-03-17 | 130000 | 0.1 | 2.1 | 13.85 | 55.8 | 637.7 | -2.2 | 17.07 | 127.9 | 192.8 | -1 | 2.51 | 7.8 | 0.008 | 0.008 | 2.1
| 399 | 2008-03-17 | 140000 | 0.1 | 2.1 | 13.84 | 55.1 | 639.2 | -2.1 | 17.1 | 127.7 | 192.4 | -1 | 2.54 | 7.77 | 0.008 | 0.008 | 2.1
| 400 | 2008-03-17 | 150000 | 0.1 | 2.1 | 13.84 | 55.2 | 638.5 | -2.3 | 17.13 | 128.5 | 193.3 | -1 | 2.52 | 7.72 | 0.008 | 0.008 | 2.1
| 401 | 2008-03-17 | 160000 | 0.1 | 2.1 | 13.83 | 55.3 | 639.7 | -2.2 | 17.15 | 128.5 | 193.3 | -1 | 2.54 | 7.71 | 0.008 | 0.008 | 2.1
| 402 | 2008-03-17 | 170000 | 0.1 | 2.1 | 13.82 | 55.2 | 639.3 | -2.3 | 17.13 | 128.7 | 193.1 | -1 | 2.53 | 7.73 | 0.008 | 0.008 | 2.1
| 403 | 2008-03-17 | 180000 | 0.1 | 2 | 13.82 | 56.7 | 638.2 | -2.4 | 17.15 | 128.7 | 193 | -1 | 2.43 | 7.77 | 0.007 | 0.007 | 2
| 404 | 2008-03-17 | 190000 | 0.1 | 2 | 13.82 | 57.1 | 637.5 | -2.2 | 17.14 | 128.4 | 192.5 | -1 | 2.41 | 7.84 | 0.007 | 0.007 | 2
| 405 | 2008-03-17 | 200000 | 0.1 | 2 | 13.83 | 57.6 | 638.1 | -2.3 | 17.19 | 129 | 193.4 | -0.9 | 2.4 | 7.84 | 0.007 | 0.007 | 2
| 406 | 2008-03-17 | 210000 | 0.1 | 2 | 13.83 | 57.2 | 637.6 | -2.1 | 17.16 | 128.8 | 193.2 | -1 | 2.43 | 7.86 | 0.007 | 0.007 | 2
| 407 | 2008-03-17 | 220000 | 0.1 | 2 | 13.83 | 57.1 | 637.7 | -2.2 | 17.15 | 128.8 | 193.3 | -0.9 | 2.41 | 7.82 | 0.007 | 0.007 | 2
| 408 | 2008-03-17 | 230000 | 0.1 | 2 | 13.82 | 56.9 | 637.8 | -2.6 | 17.14 | 128.6 | 193.1 | -0.9 | 2.4 | 7.78 | 0.007 | 0.007 | 2
| 409 | 2008-03-18 | 0 | 25.7 | 10.4 | 19.38 | 3 | 565 | -62.3 | 2.22 | 10.6 | 18.9 | -0.9 | 2.42 | 6.46 | 0.049 | 0.018 | 1.8
| 410 | 2008-03-18 | 10000 | 13.5 | -8.3 | 20.81 | 0.9 | 448.7 | -157.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.14 | 0 | 0 | 0 | -9.4
| 411 | 2008-03-18 | 20000 | 12 | -8 | 20.8 | 0.9 | 423.9 | -159 | 0.04 | 0.5 | 1.3 | -0.9 | -0.14 | -0.03 | 0 | 0 | -9.2
| 412 | 2008-03-18 | 30000 | 8.9 | 0 | 20.34 | 0.9 | 443.2 | -117.3 | 0.73 | 1.1 | 1.8 | -0.9 | 1.21 | 3.44 | 0.021 | 0.009 | -4.1
| 413 | 2008-03-18 | 40000 | 22.4 | 56.5 | 15.63 | 16.9 | 605.9 | 37.9 | 9.07 | 38.4 | 44.5 | -0.9 | 10.26 | 30 | 0.208 | 0.043 | 11.6
| 414 | 2008-03-18 | 50000 | 1.6 | 9.7 | 13.83 | 71.8 | 630.9 | -0.3 | 17.78 | 135.8 | 199.4 | -0.9 | 3.24 | 11.45 | 0.036 | 0.01 | 2.8
| 415 | 2008-03-18 | 60000 | 3.4 | 6.4 | 11.83 | 136.7 | 664.3 | 9.9 | 22.44 | 184.5 | 264.2 | -0.9 | 4.01 | 12.67 | 0.025 | 0.016 | 3.9
| 416 | 2008-03-18 | 70000 | 1.2 | 4 | 12.33 | 130.8 | 674.9 | 10.8 | 22.25 | 183 | 263.7 | -0.9 | 3.28 | 11.77 | 0.015 | 0.008 | 2.2
| 417 | 2008-03-18 | 80000 | 0 | 2 | 13.64 | 131.7 | 676.2 | -2.3 | 22.3 | 183.2 | 264.1 | -0.9 | 2.47 | 11.88 | 0.007 | 0.007 | 2
| 418 | 2008-03-18 | 90000 | 0 | 2 | 13.64 | 132.1 | 675.1 | -2.1 | 22.23 | 182.6 | 263.6 | -0.9 | 2.52 | 12.07 | 0.007 | 0.008 | 2
| 419 | 2008-03-18 | 100000 | 0 | 2 | 13.64 | 134.9 | 673.9 | -2.2 | 22.19 | 182.4 | 263.3 | -0.9 | 2.48 | 12.2 | 0.007 | 0.007 | 2
| 420 | 2008-03-18 | 110000 | 0 | 2 | 13.66 | 134.9 | 674.4 | -2.2 | 22.26 | 182.8 | 263.6 | -0.9 | 2.45 | 12.24 | 0.007 | 0.007 | 2
| 421 | 2008-03-18 | 120000 | 0 | 2 | 13.69 | 137.7 | 673.2 | -2.4 | 22.15 | 182.7 | 263.1 | -1 | 2.44 | 12.47 | 0.007 | 0.007 | 2
| 422 | 2008-03-18 | 130000 | 0.1 | 1.2 | 13.87 | 74.6 | 641.6 | -2.2 | 16.75 | 124.5 | 189.6 | -1 | 1.44 | 8.23 | 0.004 | 0.004 | 1.2
| 423 | 2008-03-18 | 140000 | 0.1 | 2 | 13.89 | 57 | 635.7 | -2.3 | 17.06 | 128.1 | 192.7 | -1 | 2.36 | 7.88 | 0.007 | 0.007 | 2
| 424 | 2008-03-18 | 150000 | 0.1 | 2 | 13.91 | 57.2 | 635.2 | -2.1 | 17.02 | 127.8 | 192.5 | -1 | 2.39 | 7.93 | 0.007 | 0.007 | 2
| 425 | 2008-03-18 | 160000 | 0.1 | 2 | 13.91 | 57.4 | 635.3 | -2.4 | 17.04 | 128.2 | 193 | -1 | 2.38 | 7.96 | 0.007 | 0.007 | 2
| 426 | 2008-03-18 | 170000 | 0.1 | 2 | 13.91 | 57.4 | 635.1 | -2.1 | 17.12 | 128.4 | 193.1 | -1 | 2.39 | 7.98 | 0.007 | 0.007 | 2
| 427 | 2008-03-18 | 180000 | 0.1 | 2 | 13.91 | 58.9 | 635.3 | -2.1 | 17.08 | 128.1 | 192.9 | -1 | 2.39 | 8.04 | 0.007 | 0.007 | 2
| 428 | 2008-03-18 | 190000 | 0.1 | 2 | 13.91 | 59.1 | 635.5 | -2.1 | 17.09 | 127.9 | 192.6 | -1 | 2.36 | 8.07 | 0.007 | 0.007 | 2
| 429 | 2008-03-18 | 200000 | 0.1 | 2 | 13.9 | 59 | 635.6 | -2 | 17.11 | 128.1 | 193 | -0.9 | 2.39 | 8.07 | 0.007 | 0.007 | 2
| 430 | 2008-03-18 | 210000 | 0.1 | 2 | 13.9 | 59 | 636.3 | -2.4 | 17.1 | 127.9 | 192.6 | -0.9 | 2.38 | 8.03 | 0.007 | 0.007 | 2
| 431 | 2008-03-18 | 220000 | 0.1 | 2 | 13.9 | 58.3 | 636.7 | -2.2 | 17.15 | 128.2 | 192.9 | -1 | 2.42 | 8.04 | 0.007 | 0.008 | 2
| 432 | 2008-03-18 | 230000 | 0.1 | 2 | 13.89 | 57.9 | 637.2 | -2.1 | 17.11 | 127.9 | 192.5 | -0.9 | 2.46 | 8.02 | 0.008 | 0.008 | 2.1
| 433 | 2008-03-19 | 0 | 0.1 | 2 | 13.88 | 57.4 | 637.3 | -2.3 | 17.11 | 127.5 | 192.2 | -1 | 2.46 | 8 | 0.007 | 0.008 | 2.1
| 434 | 2008-03-19 | 10000 | 42.7 | 5.2 | 19.59 | 3.1 | 558.9 | -163.2 | 2.06 | 9.1 | 16.4 | -0.9 | 2.14 | 5.71 | 0.045 | 0.017 | -2.2
| 435 | 2008-03-19 | 20000 | 45 | -17.9 | 20.86 | 0.8 | 452 | -383.6 | 0.26 | 0.5 | 1.3 | -1 | -0.14 | 0.01 | 0 | 0 | -21.4
| 436 | 2008-03-19 | 30000 | 31 | -14.7 | 20.85 | 0.8 | 432.2 | -321.3 | 0.13 | 0.5 | 1.3 | -0.9 | -0.14 | -0.04 | 0 | 0 | -16.3
| 437 | 2008-03-19 | 40000 | 20.9 | -1.7 | 20.35 | 1 | 448.1 | -190.6 | 0.84 | 1.1 | 1.8 | -0.9 | 1.4 | 4.06 | 0.025 | 0.01 | -8.4
| 438 | 2008-03-19 | 50000 | 19.7 | 58.3 | 15.35 | 19.3 | 607.7 | 28.6 | 10.32 | 51.5 | 67.9 | -1 | 9.92 | 28.87 | 0.215 | 0.039 | 10.8
| 439 | 2008-03-19 | 60000 | 1.2 | 1.5 | 14.17 | 63.8 | 633.4 | -30.4 | 17.28 | 129.1 | 192.9 | -1 | 2.2 | 8.69 | 0.007 | 0.007 | 1.5
| 440 | 2008-03-19 | 70000 | 4.5 | 7.7 | 10.3 | 62.8 | 636.9 | 22.3 | 17.17 | 128.1 | 193.3 | -1 | 4.78 | 8.11 | 0.029 | 0.013 | 3.5
| 441 | 2008-03-19 | 80000 | 0.2 | 2.1 | 13.84 | 59.7 | 640.1 | -2.2 | 17.12 | 127.5 | 192.8 | -1 | 2.46 | 8.06 | 0.008 | 0.008 | 2.1
| 442 | 2008-03-19 | 90000 | 0.2 | 2.1 | 13.83 | 59.9 | 640.1 | -2.4 | 17.17 | 127.9 | 193.2 | -1 | 2.45 | 8.81 | 0.008 | 0.008 | 2
| 443 | 2008-03-19 | 100000 | 0.2 | 2.1 | 13.83 | 62.2 | 639.9 | -2.3 | 17.17 | 127.9 | 193.3 | -1 | 2.47 | 8.12 | 0.008 | 0.008 | 2.1
| 444 | 2008-03-19 | 110000 | 0.1 | 2 | 13.63 | 144.1 | 671.8 | -2.3 | 22.43 | 184.1 | 264.5 | -1 | 2.49 | 12.56 | 0.008 | 0.008 | 2
| 445 | 2008-03-19 | 120000 | 0.1 | 2 | 13.69 | 136.4 | 677.5 | -2.1 | 22.15 | 182.2 | 263.6 | -1 | 2.48 | 12.1 | 0.008 | 0.008 | 2
| 446 | 2008-03-19 | 130000 | 0.1 | 2.1 | 13.83 | 54.4 | 643.3 | -2.1 | 16.66 | 124 | 189.9 | -1 | 2.54 | 8.03 | 0.008 | 0.008 | 2.1
| 447 | 2008-03-19 | 140000 | 0.1 | 2.1 | 13.81 | 57.3 | 639.2 | -2.3 | 16.99 | 127.6 | 193.1 | -1 | 2.46 | 7.79 | 0.008 | 0.008 | 2.1
| 448 | 2008-03-19 | 150000 | 0.3 | 2.1 | 13.81 | 57.2 | 638.1 | -2.5 | 16.93 | 127.3 | 192.4 | -1 | 2.48 | 7.82 | 0.008 | 0.008 | 2.1
| 449 | 2008-03-19 | 160000 | 0.5 | 2.1 | 13.8 | 57.3 | 638.3 | -2.3 | 17.04 | 127.9 | 192.9 | -1 | 2.47 | 7.81 | 0.008 | 0.008 | 2.1
| 450 | 2008-03-19 | 170000 | 0.5 | 2.1 | 13.8 | 57.4 | 639 | -2.2 | 17.14 | 128.4 | 193 | -0.9 | 2.48 | 7.79 | 0.008 | 0.008 | 2.1
| 451 | 2008-03-19 | 180000 | 0.5 | 2.1 | 13.8 | 57.9 | 639.3 | -2.4 | 17.14 | 128.9 | 193.7 | -0.9 | 2.47 | 7.76 | 0.008 | 0.008 | 2.1
| 452 | 2008-03-19 | 190000 | 0.5 | 2.1 | 13.81 | 57.1 | 638.3 | -2.4 | 17.14 | 128 | 192.6 | -0.9 | 2.49 | 7.8 | 0.008 | 0.008 | 2.1
| 453 | 2008-03-19 | 200000 | 0.5 | 2.1 | 13.81 | 57.3 | 638.3 | -2.3 | 17.14 | 127.9 | 192.3 | -0.9 | 2.46 | 7.77 | 0.008 | 0.008 | 2.1
| 454 | 2008-03-19 | 210000 | 0.5 | 2.1 | 13.81 | 57.3 | 639.4 | -2.3 | 17.18 | 128.5 | 193.1 | -0.9 | 2.48 | 7.71 | 0.008 | 0.008 | 2.1
| 455 | 2008-03-19 | 220000 | 0.5 | 2.1 | 13.81 | 56.8 | 639.8 | -2.3 | 17.17 | 128.6 | 193.3 | -0.9 | 2.5 | 7.73 | 0.008 | 0.008 | 2.1
| 456 | 2008-03-19 | 230000 | 0.5 | 2.1 | 13.82 | 56.7 | 639.9 | -2.3 | 17.11 | 128.2 | 193 | -0.9 | 2.54 | 7.8 | 0.008 | 0.008 | 2.1
| 457 | 2008-03-20 | 0 | 36 | 11.8 | 19.6 | 2.2 | 557 | -59 | 1.88 | 7.2 | 12.8 | -0.9 | 2.05 | 5.06 | 0.046 | 0.018 | 4.8
| 458 | 2008-03-20 | 10000 | 36.4 | -1.1 | 20.79 | 1 | 445.1 | -150.4 | 0.27 | 0.5 | 1.3 | -0.9 | -0.02 | 0 | 0.003 | 0 | -1.3
| 459 | 2008-03-20 | 20000 | 39.3 | -1.5 | 20.8 | 1 | 430.6 | -141.3 | 0.27 | 0.5 | 1.3 | -0.9 | -0.03 | -0.04 | 0.003 | 0 | -1.7
| 460 | 2008-03-20 | 30000 | 38.7 | -1.7 | 20.8 | 0.8 | 424.4 | -154.8 | 0.27 | 0.5 | 1.3 | -0.9 | -0.03 | -0.07 | 0.003 | 0 | -1.5
| 461 | 2008-03-20 | 40000 | 37.8 | -1.8 | 20.8 | 0.9 | 418.1 | -157.5 | 0.26 | 0.5 | 1.3 | -0.9 | -0.02 | -0.05 | 0.003 | 0 | -1.3
| 462 | 2008-03-20 | 50000 | 18.1 | 44.8 | 15.96 | 11.6 | 572.3 | -2.2 | 9.59 | 52.5 | 58.3 | -0.9 | 7.81 | 22.14 | 0.166 | 0.033 | 8.7
| 463 | 2008-03-20 | 60000 | 3.6 | 1.7 | 13.51 | 65.7 | 630.5 | -15.7 | 17.49 | 131.8 | 194.3 | -0.9 | 2.39 | 8.24 | 0.007 | 0.006 | 1.7
| 464 | 2008-03-20 | 70000 | 8.3 | 8.6 | 10.96 | 59.5 | 635.3 | 31.8 | 17.25 | 128.8 | 193.5 | -0.9 | 4.33 | 7.91 | 0.032 | 0.016 | 4.2
| 465 | 2008-03-20 | 80000 | 0.5 | 2.1 | 13.84 | 51 | 638 | -2.2 | 17.26 | 128.3 | 193.5 | -0.9 | 2.52 | 7.84 | 0.008 | 0.008 | 2.1
| 466 | 2008-03-20 | 90000 | 0.5 | 2.1 | 13.84 | 51.3 | 639.1 | -2.1 | 17.17 | 128.5 | 193.8 | -0.9 | 2.52 | 8.67 | 0.008 | 0.008 | 2.1
| 467 | 2008-03-20 | 100000 | 0.5 | 2.1 | 13.84 | 51.1 | 638.8 | -2.2 | 17.14 | 127.8 | 193 | -0.9 | 2.54 | 7.88 | 0.008 | 0.008 | 2.1
| 468 | 2008-03-20 | 110000 | 0.5 | 2.1 | 13.85 | 51.3 | 638.9 | -2.2 | 17.14 | 127.7 | 192.9 | -0.9 | 2.51 | 7.86 | 0.008 | 0.008 | 2.1
| 469 | 2008-03-20 | 120000 | 0.5 | 2.1 | 13.85 | 51.7 | 637.9 | -2.2 | 17.09 | 127.2 | 192.2 | -0.9 | 2.52 | 7.9 | 0.008 | 0.008 | 2.1
| 470 | 2008-03-20 | 130000 | 0.5 | 2.1 | 13.84 | 50.5 | 638.2 | -2.3 | 17.14 | 127.7 | 192.8 | -0.9 | 2.53 | 7.78 | 0.008 | 0.008 | 2.1
| 471 | 2008-03-20 | 140000 | 0.5 | 2.1 | 13.84 | 51.3 | 637.4 | -1.9 | 17.1 | 127.3 | 192.3 | -0.9 | 2.54 | 7.79 | 0.008 | 0.008 | 2.1
| 472 | 2008-03-20 | 150000 | 0.5 | 2.1 | 13.83 | 50.6 | 637.6 | -2.3 | 17.12 | 127.6 | 192.6 | -0.9 | 2.52 | 7.74 | 0.008 | 0.008 | 2.1
| 473 | 2008-03-20 | 160000 | 0.5 | 2.1 | 13.82 | 49.8 | 637.9 | -2.3 | 17.18 | 128.3 | 192.7 | -0.9 | 2.52 | 7.64 | 0.008 | 0.008 | 2.1
| 474 | 2008-03-20 | 170000 | 0.5 | 2.1 | 13.81 | 49.3 | 638.5 | -2.5 | 17.19 | 128.6 | 192.9 | -1 | 2.54 | 7.64 | 0.008 | 0.008 | 2.1
| 475 | 2008-03-20 | 180000 | 0.5 | 2.1 | 13.8 | 49.3 | 638.3 | -2.4 | 17.16 | 128.8 | 193 | -0.9 | 2.54 | 7.73 | 0.008 | 0.008 | 2.1
| 476 | 2008-03-20 | 190000 | 0.5 | 2 | 13.82 | 51.2 | 637.4 | -2.6 | 17.19 | 128.5 | 192.7 | -1 | 2.46 | 7.86 | 0.007 | 0.008 | 2.1
| 477 | 2008-03-20 | 200000 | 0.5 | 2.1 | 13.84 | 51.2 | 636.8 | -2.4 | 17.33 | 129 | 193.5 | -1 | 2.51 | 7.96 | 0.008 | 0.008 | 2.1
| 478 | 2008-03-20 | 210000 | 0.5 | 2.1 | 13.87 | 51.1 | 636.8 | -2.5 | 17.25 | 128.6 | 192.9 | -1 | 2.51 | 7.99 | 0.008 | 0.008 | 2.1
| 479 | 2008-03-20 | 220000 | 0.5 | 2.1 | 13.89 | 51.9 | 637.2 | -2.3 | 17.25 | 128.8 | 193.4 | -1 | 2.51 | 8 | 0.008 | 0.008 | 2.1
| 480 | 2008-03-20 | 230000 | 0.5 | 2.1 | 13.9 | 51.7 | 637 | -2.4 | 17.14 | 127.3 | 191.7 | -1 | 2.49 | 8.08 | 0.008 | 0.008 | 2.1
| 481 | 2008-03-21 | 0 | 58.9 | -2.6 | 19.76 | 2 | 557.6 | -104.3 | 1.82 | 7.6 | 13.9 | -1 | 1.86 | 5.47 | 0.134 | 0.109 | -12
| 482 | 2008-03-21 | 10000 | 0 | 0 | 20.95 | 0.9 | 450.5 | 0 | 0.25 | 0.5 | 1.3 | -0.9 | -0.46 | 0 | 0.208 | 0.216 | 0
| 483 | 2008-03-21 | 20000 | 0 | 0 | 20.97 | 0.8 | 430.5 | 0 | 0.16 | 0.5 | 1.3 | -1 | -0.47 | -0.04 | 0.149 | 0.153 | 0
| 484 | 2008-03-21 | 30000 | 0 | 0 | 20.99 | 0.8 | 421.4 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0.119 | 0.12 | 0
| 485 | 2008-03-21 | 40000 | 0 | 0 | 21.01 | 0.8 | 409.1 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0.094 | 0.098 | 0
| 486 | 2008-03-21 | 50000 | 0 | 0 | 21.03 | 0.8 | 395.6 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.07 | 0.077 | 0.08 | 0
| 487 | 2008-03-21 | 60000 | 0 | 0 | 21.05 | 0.9 | 389.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0.068 | 0.07 | 0
| 488 | 2008-03-21 | 70000 | 0 | 0 | 21.06 | 0.8 | 382.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.07 | 0.06 | 0.063 | 0
| 489 | 2008-03-21 | 80000 | 11.5 | 26.1 | 19.42 | 1 | 475 | 9.6 | 2.75 | 8.2 | 8.9 | -1 | 3.88 | 11.38 | 0.122 | 0.055 | 7.5
| 490 | 2008-03-21 | 90000 | 13.8 | 38.8 | 17.98 | 9 | 568.8 | 17 | 5.4 | 21.8 | 22.3 | -1 | 6.18 | 20.2 | 0.159 | 0.051 | 9
| 491 | 2008-03-21 | 100000 | 1.2 | 8.7 | 13.99 | 76.5 | 636.3 | -1.7 | 18.98 | 147.3 | 201.4 | -1 | 3.02 | 11.24 | 0.032 | 0.01 | 2.6
| 492 | 2008-03-21 | 110000 | 5.7 | 8 | 10.78 | 58.2 | 637.8 | 37.2 | 17.32 | 129.1 | 194.4 | -1 | 4.52 | 7.96 | 0.036 | 0.021 | 3.8
| 493 | 2008-03-21 | 120000 | 0.6 | 2.5 | 14.07 | 54 | 638.6 | -2.2 | 17.15 | 126.8 | 192.3 | -1 | 2.87 | 7.96 | 0.009 | 0.009 | 2.5
| 494 | 2008-03-21 | 130000 | 0.5 | 2.1 | 14.05 | 53.3 | 639.7 | -2.5 | 17.37 | 129.1 | 195 | -1 | 2.44 | 7.88 | 0.008 | 0.008 | 2.1
| 495 | 2008-03-21 | 140000 | 0.5 | 2.1 | 14.05 | 53.6 | 639.4 | -2.4 | 17.32 | 129 | 194.8 | -1 | 2.45 | 7.99 | 0.008 | 0.008 | 2.1
| 496 | 2008-03-21 | 150000 | 0.5 | 2.1 | 14.06 | 53 | 639.5 | -2.4 | 17.35 | 129.3 | 195.1 | -1 | 2.45 | 7.97 | 0.008 | 0.008 | 2.1
| 497 | 2008-03-21 | 160000 | 0.5 | 2.1 | 14.06 | 52.6 | 639.5 | -2.2 | 17.21 | 128 | 193.5 | -1 | 2.47 | 7.94 | 0.008 | 0.008 | 2.1
| 498 | 2008-03-21 | 170000 | 25.2 | 13.3 | 19.63 | 4.9 | 557.2 | 5.6 | 2.26 | 10.8 | 19.6 | -0.9 | 2.11 | 6.65 | 0.082 | 0.053 | 4.6
| 499 | 2008-03-21 | 180000 | 0 | 0 | 20.96 | 0.9 | 437.9 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.46 | 0.01 | 0.044 | 0.048 | 0
| 500 | 2008-03-21 | 190000 | 0 | 0 | 21.1 | 1 | 421 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.03 | 0.046 | 0.05 | 0
| 501 | 2008-03-21 | 200000 | 0 | 0 | 21.12 | 1 | 411.7 | 0 | 0.15 | 0.5 | 1.3 | -1 | -0.47 | -0.04 | 0.045 | 0.047 | 0
| 502 | 2008-03-21 | 210000 | 0 | 0 | 21.12 | 0.9 | 403.5 | 0 | 0.21 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0.043 | 0.047 | 0
| 503 | 2008-03-21 | 220000 | 0 | 0 | 21.04 | 0.9 | 396 | 0 | 0.06 | 0.5 | 1.3 | -0.9 | -0.46 | -0.05 | 0.043 | 0.045 | 0
| 504 | 2008-03-21 | 230000 | 0 | 0 | 21.11 | 0.9 | 387.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0.045 | 0.048 | 0
| 505 | 2008-03-22 | 0 | 0 | 0 | 21.11 | 0.9 | 375.1 | 0 | 0.06 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.046 | 0.049 | 0
| 506 | 2008-03-22 | 10000 | 0 | 0 | 21.1 | 0.8 | 366.2 | 0 | 0.12 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0.047 | 0.05 | 0
| 507 | 2008-03-22 | 20000 | 0 | 0 | 21.1 | 0.9 | 359 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0.048 | 0.051 | 0
| 508 | 2008-03-22 | 30000 | 0 | 0 | 21.09 | 0.9 | 352.8 | 0 | 0.19 | 0.5 | 1.3 | -1 | -0.46 | -0.07 | 0.05 | 0.054 | 0
| 509 | 2008-03-22 | 40000 | 0 | 0 | 21 | 0.8 | 343.8 | 0 | 0.14 | 0.5 | 1.3 | -0.9 | -0.46 | -0.06 | 0.054 | 0.057 | 0
| 510 | 2008-03-22 | 50000 | 0 | 0 | 21.07 | 0.9 | 332.3 | 0 | 0.12 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0.056 | 0.06 | 0
| 511 | 2008-03-22 | 60000 | 0 | 0 | 21.06 | 0.9 | 324.4 | 0 | 0.1 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0.058 | 0.062 | 0
| 512 | 2008-03-22 | 70000 | 0 | 0 | 21.06 | 0.8 | 318.8 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0.061 | 0.065 | 0
| 513 | 2008-03-22 | 80000 | 0 | 0 | 21.05 | 0.8 | 314.1 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.45 | -0.06 | 0.061 | 0.065 | 0
| 514 | 2008-03-22 | 90000 | 0 | 0 | 21.04 | 0.8 | 310 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.44 | 2.11 | 0.064 | 0.068 | 0
| 515 | 2008-03-22 | 100000 | 0 | 0 | 21.03 | 0.8 | 306.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.42 | -0.04 | 0.068 | 0.073 | 0
| 516 | 2008-03-22 | 110000 | 0 | 0 | 20.94 | 0.9 | 302.9 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.44 | -0.03 | 0.084 | 0.087 | 0
| 517 | 2008-03-22 | 120000 | 0 | 0 | 20.99 | 0.8 | 299.4 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.45 | -0.06 | 0.112 | 0.118 | 0
| 518 | 2008-03-22 | 130000 | 0 | 0 | 20.89 | 0.8 | 296.3 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.46 | -0.06 | 0.172 | 0.177 | 0
| 519 | 2008-03-22 | 140000 | 0 | 0 | 20.95 | 0.9 | 292.7 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.206 | 0.211 | 0
| 520 | 2008-03-22 | 150000 | 3.1 | -3.3 | 20.95 | 0.9 | 289.3 | -15.2 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.242 | 0.242 | -2.3
| 521 | 2008-03-22 | 160000 | 4.5 | -3.4 | 20.93 | 0.9 | 286 | -19.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.07 | 0.314 | 0.321 | -3.2
| 522 | 2008-03-22 | 170000 | 42 | -30.8 | 20.91 | 1 | 282.9 | -196.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.229 | 0.242 | -30.5
| 523 | 2008-03-22 | 180000 | 133 | -94.8 | 20.89 | 0.9 | 279.6 | -603.7 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.043 | 0.049 | -96.1
| 524 | 2008-03-22 | 190000 | 142.4 | -94.9 | 20.88 | 1 | 276.2 | -520.2 | 0.04 | 0.5 | 1.3 | -0.9 | -0.46 | -0.07 | 0.009 | 0.01 | -101.6
| 525 | 2008-03-22 | 200000 | 151.1 | -98.1 | 20.88 | 1 | 272.6 | -753.3 | 0.04 | 0.5 | 1.3 | -0.9 | -0.46 | -0.06 | 0.026 | 0.031 | -107.4
| 526 | 2008-03-22 | 210000 | 149.6 | -91.2 | 20.88 | 0.9 | 269.2 | -616.9 | 0.04 | 0.5 | 1.3 | -0.9 | -0.46 | -0.06 | 0.02 | 0.022 | -96.8
| 527 | 2008-03-22 | 220000 | 136.1 | -88.3 | 20.89 | 1 | 266 | -623.7 | 0.04 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0.05 | 0.062 | -92.1
| 528 | 2008-03-22 | 230000 | 153.2 | -97.4 | 20.88 | 0.9 | 262.4 | -586.3 | 0.04 | 0.5 | 1.3 | -1 | -0.46 | -0.07 | 0.014 | 0.016 | -106.6
| 529 | 2008-03-23 | 0 | 146.9 | -89.5 | 20.87 | 1 | 259.1 | -537.2 | 0.04 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0.009 | 0.011 | -98.9
| 530 | 2008-03-23 | 10000 | 138.6 | -87.6 | 20.87 | 0.9 | 255.8 | -542 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0.001 | 0.001 | -96.2
| 531 | 2008-03-23 | 20000 | 109.2 | -66 | 20.85 | 0.9 | 252.4 | -419.9 | 0.04 | 0.5 | 1.3 | -1 | -0.46 | -0.07 | 0 | 0 | -70.8
| 532 | 2008-03-23 | 30000 | 70.1 | -41 | 20.83 | 0.9 | 244.6 | -253.4 | 0.04 | 0.5 | 1.3 | -0.9 | -0.46 | -0.07 | 0 | 0 | -44.9
| 533 | 2008-03-23 | 40000 | 64.4 | -39 | 20.83 | 0.9 | 231.9 | -244 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0 | 0 | -42.5
| 534 | 2008-03-23 | 50000 | 50.3 | -30.4 | 20.81 | 0.9 | 223.3 | -193.1 | 0.04 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0 | 0 | -33
| 535 | 2008-03-23 | 60000 | 41.2 | -25.5 | 20.8 | 1 | 217.3 | -170.1 | 0.25 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0 | 0 | -27.5
| 536 | 2008-03-23 | 70000 | 34.4 | -21.1 | 20.78 | 0.9 | 213.2 | -146.7 | 0.26 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0 | 0 | -22.3
| 537 | 2008-03-23 | 80000 | 32.7 | -19.6 | 20.77 | 0.8 | 210.1 | -145.7 | 0.21 | 0.5 | 1.3 | -1 | -0.45 | -0.05 | 0 | 0 | -20.9
| 538 | 2008-03-23 | 90000 | 32.5 | -19.2 | 20.77 | 0.9 | 207.5 | -120.1 | 0.04 | 0.5 | 1.3 | -1 | -0.45 | 2.13 | 0 | 0 | -20.5
| 539 | 2008-03-23 | 100000 | 30 | -17.8 | 20.69 | 0.8 | 205 | -111.5 | 0.04 | 0.5 | 1.3 | -1 | -0.45 | -0.04 | 0 | 0 | -19.4
| 540 | 2008-03-23 | 110000 | 27.8 | -17.2 | 20.75 | 0.9 | 202.9 | -124.1 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.04 | 0 | 0 | -18.5
| 541 | 2008-03-23 | 120000 | 26.5 | -16.5 | 20.74 | 0.8 | 201.1 | -98.9 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0 | 0 | -17.6
| 542 | 2008-03-23 | 130000 | 26 | -16.7 | 20.74 | 0.8 | 198.6 | -102.1 | 0.04 | 0.5 | 1.3 | -1 | -0.46 | -0.07 | 0 | 0 | -17.4
| 543 | 2008-03-23 | 140000 | 28.1 | -18.1 | 20.68 | 0.9 | 196.5 | -128.1 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.07 | 0 | 0 | -18.9
| 544 | 2008-03-23 | 150000 | 35.7 | -23.4 | 20.78 | 0.9 | 194.2 | -148.2 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0 | 0 | -24.5
| 545 | 2008-03-23 | 160000 | 48.8 | -32.1 | 20.74 | 0.9 | 191.4 | -190.5 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0 | 0 | -33.3
| 546 | 2008-03-23 | 170000 | 62.9 | -41.1 | 20.83 | 0.9 | 188.9 | -222.9 | 0.06 | 0.5 | 1.2 | -1 | -0.47 | -0.07 | 0 | 0 | -42.8
| 547 | 2008-03-23 | 180000 | 79.9 | -52.8 | 20.84 | 0.9 | 185.7 | -359.6 | 0.24 | 0.5 | 1.2 | -1 | -0.47 | -0.06 | 0 | 0 | -54.9
| 548 | 2008-03-23 | 190000 | 98.7 | -66.9 | 20.85 | 0.9 | 183.7 | -363.8 | 0.21 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0 | 0 | -69.5
| 549 | 2008-03-23 | 200000 | 137.5 | -92.3 | 20.87 | 0.9 | 181.3 | -458.3 | 0.04 | 0.5 | 1.3 | -1 | -0.48 | -0.06 | 0.004 | 0.004 | -96.2
| 550 | 2008-03-23 | 210000 | 161.4 | -108.2 | 20.8 | 0.9 | 178.9 | -663.7 | 0.04 | 0.5 | 1.3 | -1 | -0.48 | -0.07 | 0.008 | 0.009 | -114.5
| 551 | 2008-03-23 | 220000 | 142.3 | -99.2 | 20.88 | 0.9 | 176.9 | -576.2 | 0.04 | 0.5 | 1.3 | -1 | -0.48 | -0.07 | 0.025 | 0.028 | -100.8
| 552 | 2008-03-23 | 230000 | 130.2 | -89.5 | 20.89 | 0.8 | 174.8 | -586.8 | 0.04 | 0.5 | 1.3 | -1 | -0.48 | -0.06 | 0.047 | 0.051 | -91.5
| 553 | 2008-03-24 | 0 | 135.1 | -92.6 | 20.89 | 0.9 | 172.7 | -499.5 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0.044 | 0.05 | -92.7
| 554 | 2008-03-24 | 10000 | 135.3 | -82 | 20.89 | 0.8 | 170 | -520.8 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0.07 | 0.083 | -89.2
| 555 | 2008-03-24 | 20000 | 87.5 | -57.6 | 20.9 | 0.8 | 168 | -355.1 | 0.07 | 0.5 | 1.3 | -1 | -0.47 | -0.07 | 0.125 | 0.141 | -58.6
| 556 | 2008-03-24 | 30000 | 42.2 | -27.7 | 20.91 | 0.8 | 166 | -150.6 | 0.07 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0.224 | 0.243 | -27.7
| 557 | 2008-03-24 | 40000 | 29.7 | -18.7 | 20.92 | 0.8 | 163.8 | -71.8 | 0.06 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.251 | 0.268 | -19.3
| 558 | 2008-03-24 | 50000 | 35.9 | -23.1 | 20.84 | 0.8 | 161.8 | -103.1 | 0.08 | 0.5 | 1.3 | -1 | -0.46 | -0.06 | 0.254 | 0.283 | -22.7
| 559 | 2008-03-24 | 60000 | 13.1 | -8.1 | 20.93 | 0.8 | 159.9 | -55.6 | 0.04 | 0.5 | 1.3 | -1 | -0.45 | -0.06 | 0.259 | 0.273 | -8.1
| 560 | 2008-03-24 | 70000 | 0 | 0 | 20.94 | 0.8 | 157.7 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.45 | -0.07 | 0.254 | 0.269 | 0
| 561 | 2008-03-24 | 80000 | 0 | 0 | 20.95 | 0.8 | 155.9 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | -0.44 | -0.04 | 0.208 | 0.215 | 0
| 562 | 2008-03-24 | 90000 | 0 | 0 | 20.95 | 0.8 | 154 | 0 | 0.05 | 0.5 | 1.3 | -1 | -0.43 | -6.77 | 0.196 | 0.211 | 0
| 563 | 2008-03-24 | 100000 | 1.3 | -0.8 | 20.95 | 0.8 | 152.3 | 0.8 | 0.04 | 0.5 | 1.3 | -1 | -0.44 | -7.49 | 0.222 | 0.227 | -0.7
| 564 | 2008-03-24 | 110000 | 1.1 | -0.8 | 20.95 | 0.9 | 150.5 | -3.9 | 0.04 | 0.5 | 1.3 | -1 | -0.45 | -3.32 | 0.215 | 0.22 | -0.7
| 565 | 2008-03-24 | 120000 | 0 | 0 | 20.96 | 0.9 | 149.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | 1.72 | 0.194 | 0.205 | 0
| 566 | 2008-03-24 | 130000 | 0 | 0 | 20.95 | 0.9 | 147.4 | 0 | 0.17 | 0.5 | 1.3 | -0.9 | -0.47 | -0.04 | 0.225 | 0.231 | 0
| 567 | 2008-03-24 | 140000 | 4 | -3 | 20.93 | 0.9 | 146 | -31.2 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.03 | 0.274 | 0.281 | -2.8
| 568 | 2008-03-24 | 150000 | 14 | -10.1 | 20.92 | 1 | 144.6 | -49.9 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.03 | 0.296 | 0.312 | -9.3
| 569 | 2008-03-24 | 160000 | 48.4 | -32.3 | 20.91 | 0.9 | 142.8 | -176 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.03 | 0.222 | 0.239 | -32.7
| 570 | 2008-03-24 | 170000 | 95.7 | -65.5 | 20.9 | 0.8 | 137.1 | -343.5 | 0.04 | 0.5 | 1.3 | -0.9 | -0.48 | -0.06 | 0.113 | 0.125 | -65.5
| 571 | 2008-03-24 | 180000 | 126.3 | -85.6 | 20.89 | 0.9 | 132.8 | -396.4 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.069 | 0.077 | -86.5
| 572 | 2008-03-24 | 190000 | 100.5 | -68.8 | 20.9 | 0.9 | 130.3 | -502.9 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.132 | 0.144 | -68.1
| 573 | 2008-03-24 | 200000 | 131.1 | -89.8 | 20.89 | 0.9 | 128.3 | -550.6 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.062 | 0.071 | -89.7
| 574 | 2008-03-24 | 210000 | 117.3 | -80.1 | 20.89 | 0.8 | 126.8 | -497.4 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.082 | 0.093 | -80.1
| 575 | 2008-03-24 | 220000 | 109.5 | -75 | 20.9 | 0.9 | 126 | -347.5 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.1 | 0.107 | -75.3
| 576 | 2008-03-24 | 230000 | 145.7 | -93.2 | 20.89 | 0.9 | 123.8 | -435.1 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.069 | 0.074 | -94.7
| 577 | 2008-03-25 | 0 | 95.6 | -61.1 | 20.82 | 1 | 120.7 | -298.7 | 0.04 | 0.5 | 1.3 | -0.9 | -0.47 | -0.06 | 0.109 | 0.124 | -61
| 578 | 2008-03-25 | 10000 | 106.8 | -65.5 | 20.9 | 0.9 | 118.4 | -433.7 | 0.04 | 0.5 | 1.3 | -1 | -0.47 | -0.06 | 0.109 | 0.119 | -68.1
| 579 | 2008-03-25 | 20000 | 110.5 | -55.4 | 20.57 | 0.9 | 118 | -271 | 0.58 | 1 | 1.8 | -1 | 0.45 | 2.18 | 0.099 | 0.107 | -56.8
| 580 | 2008-03-25 | 30000 | 20.4 | 77.5 | 16.96 | 0.9 | 468 | 32.5 | 7.15 | 19.4 | 19.8 | -0.9 | 10.29 | 30.01 | 0.286 | 0.057 | 15.4
| 581 | 2008-03-25 | 40000 | 18.2 | 79.6 | 16.79 | 0.8 | 583.8 | 15.3 | 7.44 | 23 | 23.4 | -1 | 10.29 | 30.01 | 0.293 | 0.055 | 14.9
| 582 | 2008-03-25 | 50000 | 18 | 60.9 | 15.12 | 8.7 | 600.7 | 23.3 | 11.14 | 60 | 89.7 | -0.9 | 9.5 | 27.55 | 0.224 | 0.037 | 9.9
| 583 | 2008-03-25 | 60000 | 0.6 | 2 | 13.82 | 65 | 625.7 | -2.3 | 18.05 | 137.3 | 200.2 | -0.9 | 2.39 | 8.68 | 0.007 | 0.007 | 2
| 584 | 2008-03-25 | 70000 | 5.9 | -1.1 | 13.31 | 96.6 | 652.8 | -14.5 | 22.38 | 184.4 | 261.9 | -0.9 | 2.64 | 10 | 0.007 | 0.007 | -1.2
| 585 | 2008-03-25 | 80000 | 15.1 | 6.7 | 11.11 | 107.2 | 661.5 | 24 | 22.84 | 188.9 | 269.5 | -1 | 5.11 | 12.11 | 7.947 | 0.018 | 2.5
| 586 | 2008-03-25 | 90000 | 0.5 | 2 | 13.7 | 128.2 | 668.8 | -2.1 | 22.76 | 187.8 | 268.5 | -1 | 2.58 | 12.47 | 0.008 | 0.008 | 2.1
| 587 | 2008-03-25 | 100000 | 0.5 | 2 | 13.71 | 127.3 | 677 | -2.5 | 22.54 | 186.1 | 267.2 | -1 | 2.53 | 12.36 | 0.007 | 0.008 | 2.1
| 588 | 2008-03-25 | 110000 | 0.6 | 2.1 | 13.9 | 45.7 | 644.2 | -2.2 | 16.98 | 126.4 | 191.4 | -0.9 | 2.54 | 7.83 | 0.008 | 0.008 | 2.1
| 589 | 2008-03-25 | 120000 | 0.6 | 2 | 13.9 | 47.3 | 638.9 | -2.2 | 17.1 | 127.9 | 192.2 | -1 | 2.48 | 7.64 | 0.007 | 0.008 | 2.1
| 590 | 2008-03-25 | 130000 | 0.6 | 2.1 | 13.89 | 46.6 | 638.6 | -2.3 | 17.09 | 128.4 | 192.7 | -1 | 2.53 | 7.62 | 0.008 | 0.008 | 2.1
| 591 | 2008-03-25 | 140000 | 0.6 | 2 | 13.89 | 48.9 | 638 | -2.2 | 16.99 | 127.5 | 191.6 | -1 | 2.5 | 7.77 | 0.008 | 0.008 | 2.1
| 592 | 2008-03-25 | 150000 | 0.6 | 2 | 13.88 | 48.1 | 639.2 | -2.2 | 17.14 | 129 | 193.3 | -1 | 2.5 | 7.68 | 0.007 | 0.008 | 2.1
| 593 | 2008-03-25 | 160000 | 0.6 | 2 | 13.86 | 47.3 | 639.2 | -2.6 | 17.15 | 128.9 | 193.4 | -1 | 2.52 | 7.64 | 0.007 | 0.008 | 2.1
| 594 | 2008-03-25 | 170000 | 0.6 | 2 | 13.85 | 48.2 | 639.1 | -2.5 | 17.15 | 129.2 | 193.8 | -0.9 | 2.52 | 7.67 | 0.007 | 0.008 | 2.1
| 595 | 2008-03-25 | 180000 | 0.6 | 2.1 | 13.84 | 47.8 | 638.7 | -2.1 | 17.08 | 128.5 | 192.9 | -1 | 2.54 | 7.66 | 0.008 | 0.008 | 2.1
| 596 | 2008-03-25 | 190000 | 0.6 | 2 | 13.83 | 48.2 | 639.2 | -2.1 | 17.15 | 128.6 | 192.9 | -1 | 2.51 | 7.66 | 0.007 | 0.008 | 2.1
| 597 | 2008-03-25 | 200000 | 0.6 | 2 | 13.83 | 48 | 639.5 | -2.2 | 17.15 | 128.7 | 193 | -1 | 2.53 | 7.65 | 0.007 | 0.008 | 2.1
| 598 | 2008-03-25 | 210000 | 0.6 | 2 | 13.83 | 48.2 | 639.6 | -2.2 | 17.13 | 128.4 | 192.7 | -1 | 2.52 | 7.67 | 0.008 | 0.008 | 2.1
| 599 | 2008-03-25 | 220000 | 37.1 | -7.2 | 19.55 | 2.4 | 549.3 | -32.1 | 1.94 | 8.4 | 14.9 | -0.9 | 1.59 | 5.45 | 0.039 | 0.014 | -15
| 600 | 2008-03-25 | 230000 | 35.5 | -37.8 | 20.77 | 0.9 | 428.6 | -124.3 | 0.54 | 0.5 | 1.3 | -0.9 | -0.85 | 0.01 | 0 | 0 | -39.9
| 601 | 2008-03-26 | 0 | 33.5 | -36.4 | 20.77 | 1.1 | 404.1 | -127.2 | 0.3 | 0.5 | 1.3 | -1 | -0.85 | -0.04 | 0 | 0 | -38.6
| 602 | 2008-03-26 | 10000 | 31.5 | -35.2 | 20.76 | 0.9 | 391.2 | -116.3 | 0.27 | 0.5 | 1.3 | -1 | -0.86 | -0.03 | 0 | 0 | -37.4
| 603 | 2008-03-26 | 20000 | 31.3 | -35.1 | 20.76 | 0.9 | 380.6 | -113.6 | 0.21 | 0.5 | 1.3 | -0.9 | -0.86 | -0.03 | 0 | 0 | -37.6
| 604 | 2008-03-26 | 30000 | 28.1 | -22.2 | 20.23 | 0.9 | 396.1 | -90 | 0.88 | 1.6 | 2.4 | -1 | 0.84 | 3.97 | 0.027 | 0.01 | -28.4
| 605 | 2008-03-26 | 40000 | 32.9 | 41.5 | 18.37 | 0.9 | 557.3 | 8.6 | 3.89 | 9.2 | 9.8 | -0.9 | 6.43 | 18.35 | 0.162 | 0.042 | 8.7
| 606 | 2008-03-26 | 50000 | 32.5 | -28.7 | 20.75 | 0.9 | 432.1 | -87.7 | 0.04 | 0.5 | 1.3 | -0.9 | -0.77 | 0.14 | 0 | 0 | -30.5
| 607 | 2008-03-26 | 60000 | 29.8 | -17 | 20.01 | 0.8 | 417.6 | -85.1 | 1.3 | 2.7 | 3.4 | -1 | 1.53 | 5.85 | 0.045 | 0.014 | -27
| 608 | 2008-03-26 | 70000 | 19.3 | 56.3 | 15.38 | 42.2 | 603 | 30.3 | 10.5 | 54.5 | 67.5 | -0.9 | 9.57 | 28.42 | 0.207 | 0.039 | 10.6
| 609 | 2008-03-26 | 80000 | 5.6 | 4.4 | 10.79 | 131.4 | 654.1 | -38 | 22.3 | 183.8 | 261.8 | -0.9 | 4.09 | 12.06 | 0.023 | 0.008 | 0.7
| 610 | 2008-03-26 | 90000 | 1.6 | 4.3 | 13.47 | 140.3 | 670.1 | 4.8 | 22.53 | 185.3 | 265.7 | -0.9 | 2.92 | 12.35 | 0.016 | 0.014 | 3.6
| 611 | 2008-03-26 | 100000 | 0.5 | 5.5 | 13.88 | 52.3 | 644 | -1.9 | 16.58 | 121.7 | 186.8 | -1 | 2.87 | 9.14 | 0.02 | 0.009 | 2.4
| 612 | 2008-03-26 | 110000 | 26.2 | 5.2 | 20.21 | 1 | 544.5 | -136.7 | 0.64 | 2.3 | 4 | -1 | 1.42 | 3.36 | 0.03 | 0.016 | 1
| 613 | 2008-03-26 | 120000 | 8.7 | -7.2 | 20.81 | 0.9 | 448.6 | -176.5 | 0.04 | 0.5 | 1.3 | -0.9 | -0.12 | 0.01 | 0 | 0 | -8.6
| 614 | 2008-03-26 | 130000 | 7.2 | -8.8 | 20.81 | 0.9 | 432.6 | -204.5 | 0.19 | 0.5 | 1.3 | -1 | -0.13 | -0.03 | 0 | 0 | -9.1
| 615 | 2008-03-26 | 140000 | 8.9 | -8.7 | 20.81 | 0.9 | 425.7 | -206.2 | 0.1 | 0.5 | 1.3 | -1 | -0.13 | -0.03 | 0 | 0 | -9.1
| 616 | 2008-03-26 | 150000 | 9.1 | -8.7 | 20.81 | 0.8 | 419.6 | -169.8 | 0.42 | 0.5 | 1.3 | -1 | -0.13 | -0.03 | 0 | 0 | -8.9
| 617 | 2008-03-26 | 160000 | 8 | -9.4 | 20.82 | 0.9 | 414.8 | -206.1 | 0.16 | 0.5 | 1.3 | -0.9 | -0.13 | -0.03 | 0 | 0 | -10.3
| 618 | 2008-03-26 | 170000 | 16.6 | -19.5 | 20.86 | 0.8 | 409.2 | -451.9 | 0.07 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 0.004 | 0.004 | -23.3
| 619 | 2008-03-26 | 180000 | 11 | -13.5 | 20.91 | 0.8 | 403.2 | -292.7 | 0.04 | 0.5 | 1.2 | -1.1 | -0.14 | -0.03 | 22.207 | 0.063 | -13.9
| 620 | 2008-03-26 | 190000 | 0.3 | -0.4 | 20.95 | 0.9 | 397.5 | -32 | 0.04 | 0.5 | 1.2 | -1 | -0.14 | -0.03 | 0.064 | 0.071 | -0.6
| 621 | 2008-03-26 | 200000 | 0 | 0 | 20.97 | 0.7 | 392.4 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 0.041 | 0.045 | 0
| 622 | 2008-03-26 | 210000 | 0 | 0 | 20.99 | 0.9 | 377.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.05 | 0.031 | 0.034 | 0
| 623 | 2008-03-26 | 220000 | 0 | 0 | 21.01 | 0.8 | 350.4 | 0 | 0.09 | 0.5 | 1.3 | -1 | -0.14 | -0.06 | 0.026 | 0.029 | 0
| 624 | 2008-03-26 | 230000 | 0 | 0 | 21.03 | 0.8 | 338.7 | 0 | 0.12 | 0.5 | 1.3 | -1 | -0.14 | -0.05 | 0.022 | 0.024 | 0
| 625 | 2008-03-27 | 0 | 0 | 0 | 21.04 | 0.9 | 334 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.05 | 0.019 | 0.02 | 0
| 626 | 2008-03-27 | 10000 | 0 | 0 | 20.98 | 0.8 | 330.5 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.04 | 0.018 | 0.019 | 0
| 627 | 2008-03-27 | 20000 | 0 | 0 | 21.07 | 0.7 | 326.6 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 0.016 | 0.018 | 0
| 628 | 2008-03-27 | 30000 | 0 | 0 | 21.01 | 0.7 | 323.3 | 0 | 0.07 | 0.5 | 1.3 | -1 | -0.13 | -0.04 | 0.015 | 0.016 | 0
| 629 | 2008-03-27 | 40000 | 0 | 0 | 21.09 | 0.9 | 320.3 | 0 | 0.05 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 0.014 | 0.016 | 0
| 630 | 2008-03-27 | 50000 | 0 | 0 | 21.09 | 0.9 | 317.2 | 0 | 0.09 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 0.013 | 0.015 | 0
| 631 | 2008-03-27 | 60000 | 0 | 0 | 21.1 | 0.9 | 314.3 | 0 | 0.05 | 0.5 | 1.3 | -1 | -0.14 | -0.05 | 0.013 | 0.015 | 0
| 632 | 2008-03-27 | 70000 | 0 | 0 | 21.1 | 0.8 | 310.9 | 0 | 0.05 | 0.5 | 1.3 | -1 | -0.13 | -0.04 | 0.013 | 0.014 | 0
| 633 | 2008-03-27 | 80000 | 0 | 0 | 21.04 | 0.9 | 307.6 | 0 | 0.13 | 0.5 | 1.3 | -1 | -0.13 | -0.04 | 0.013 | 0.014 | 0
| 634 | 2008-03-27 | 90000 | 0 | 0 | 21.12 | 0.8 | 304.5 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | 2.09 | 0.012 | 0.013 | 0
| 635 | 2008-03-27 | 100000 | 0 | 0 | 21.13 | 0.9 | 301.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.03 | 0.012 | 0.013 | 0
| 636 | 2008-03-27 | 110000 | 0 | 0 | 21.13 | 0.7 | 297.7 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.04 | 0.012 | 0.013 | 0
| 637 | 2008-03-27 | 120000 | 0 | 0 | 21.12 | 0.8 | 294 | 0 | 0.17 | 0.5 | 1.3 | -1 | -0.14 | -0.05 | 0.011 | 0.013 | 0
| 638 | 2008-03-27 | 130000 | 0 | 0 | 21.12 | 0.8 | 290.3 | 0 | 0.1 | 0.5 | 1.3 | -1 | -0.13 | -0.07 | 0.013 | 0.014 | 0
| 639 | 2008-03-27 | 140000 | 0 | 0 | 21.04 | 0.9 | 286.7 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.07 | 0.011 | 0.014 | 0
| 640 | 2008-03-27 | 150000 | 0 | 0 | 21.11 | 0.9 | 283.3 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.06 | 0.012 | 0.014 | 0
| 641 | 2008-03-27 | 160000 | 0 | 0 | 21.08 | 0.9 | 280.1 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.07 | 0.014 | 0.016 | 0
| 642 | 2008-03-27 | 170000 | 0 | 0 | 21.06 | 0.8 | 276.6 | 0 | 0.13 | 0.5 | 1.3 | -1 | -0.13 | -0.06 | 0.017 | 0.018 | 0
| 643 | 2008-03-27 | 180000 | 0 | 0 | 21.04 | 0.8 | 273.1 | 0 | 0.4 | 0.5 | 1.3 | -1 | -0.13 | -0.07 | 0.021 | 0.022 | 0
| 644 | 2008-03-27 | 190000 | 0 | 0 | 20.95 | 0.9 | 269.4 | 0 | 0.16 | 0.5 | 1.3 | -1 | -0.13 | -0.07 | 0.021 | 0.024 | 0
| 645 | 2008-03-27 | 200000 | 0 | 0 | 21.01 | 0.8 | 265.9 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.06 | 0.025 | 0.027 | 0
| 646 | 2008-03-27 | 210000 | 0 | 0 | 21 | 1 | 262.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.07 | 0.028 | 0.031 | 0
| 647 | 2008-03-27 | 220000 | 0 | 0 | 20.98 | 0.8 | 258.5 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.06 | 0.04 | 0.041 | 0
| 648 | 2008-03-27 | 230000 | 0 | 0 | 20.96 | 0.8 | 255 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.07 | 0.055 | 0.06 | 0
| 649 | 2008-03-28 | 0 | 3.7 | -5 | 20.92 | 0.8 | 251.6 | -95.4 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.07 | 11.147 | 0.079 | -4.3
| 650 | 2008-03-28 | 10000 | 23.6 | -22.4 | 20.89 | 0.8 | 248.2 | -519.4 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.06 | 12.676 | 0.019 | -26.6
| 651 | 2008-03-28 | 20000 | 23.6 | -19 | 20.86 | 1 | 244.8 | -474.1 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.06 | 0.003 | 0.001 | -23.2
| 652 | 2008-03-28 | 30000 | 16.4 | -13.9 | 20.84 | 0.8 | 236.2 | -287.2 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.07 | 0 | 0 | -16.1
| 653 | 2008-03-28 | 40000 | 9.9 | -9.8 | 20.82 | 0.8 | 219 | -219.2 | 0.04 | 0.5 | 1.3 | -0.9 | -0.14 | -0.07 | 0 | 0 | -11.3
| 654 | 2008-03-28 | 50000 | 7.6 | -7.4 | 20.8 | 0.8 | 208.1 | -180.3 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.06 | 0 | 0 | -9.1
| 655 | 2008-03-28 | 60000 | 6.2 | -5.3 | 20.7 | 0.7 | 202.4 | -125 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.05 | 0 | 0 | -6.7
| 656 | 2008-03-28 | 70000 | 5.6 | -4.9 | 20.75 | 0.8 | 198.5 | -109.5 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.07 | 0 | 0 | -5.6
| 657 | 2008-03-28 | 80000 | 5.3 | -4.1 | 20.73 | 0.8 | 196.1 | -108.7 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.07 | 0 | 0 | -4.9
| 658 | 2008-03-28 | 90000 | 4.1 | -4.1 | 20.73 | 0.8 | 195.1 | -109.9 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | 2.06 | 0 | 0 | -4.6
| 659 | 2008-03-28 | 100000 | 11.9 | 6.1 | 20.07 | 0.8 | 202.6 | 18.3 | 1.15 | 1.8 | 2.6 | -1 | 1.81 | 4.84 | 0.035 | 0.012 | -0.1
| 660 | 2008-03-28 | 110000 | 18 | 76.9 | 16.71 | 0.8 | 523.7 | 16.1 | 7.2 | 21 | 21.4 | -1 | 10.29 | 30.01 | 0.283 | 0.054 | 14.6
| 661 | 2008-03-28 | 120000 | 19 | 52.8 | 15.19 | 63.9 | 602.5 | 25 | 10.58 | 54.8 | 78.8 | -1 | 9.75 | 28.58 | 0.194 | 0.038 | 10.3
| 662 | 2008-03-28 | 130000 | 1.2 | 4.4 | 12.03 | 81.8 | 633.7 | 18.3 | 20.43 | 165 | 235.1 | -1 | 3.68 | 9.24 | 0.017 | 0.008 | 2
| 663 | 2008-03-28 | 140000 | 2.2 | 5.5 | 12.21 | 136.7 | 656.9 | 1.6 | 22.55 | 185.6 | 265.4 | -1 | 3.59 | 12.03 | 0.02 | 0.013 | 3.6
| 664 | 2008-03-28 | 150000 | 0 | 2.1 | 13.6 | 130.8 | 665.4 | -2.1 | 22.56 | 186 | 266.1 | -1 | 2.6 | 11.97 | 0.008 | 0.008 | 2.1
| 665 | 2008-03-28 | 160000 | 0 | 2 | 13.62 | 128.5 | 673.9 | -2.4 | 22.59 | 185.7 | 266.7 | -1 | 2.56 | 11.74 | 0.008 | 0.008 | 2.1
| 666 | 2008-03-28 | 170000 | 0 | 2.1 | 13.61 | 134.7 | 674.7 | -1.9 | 22.59 | 185.8 | 266.6 | -1 | 2.65 | 12.15 | 0.008 | 0.008 | 2.1
| 667 | 2008-03-28 | 180000 | 0 | 2.1 | 13.61 | 132.6 | 674.6 | -2 | 22.54 | 186.1 | 266.3 | -1 | 2.61 | 11.99 | 0.008 | 0.008 | 2.1
| 668 | 2008-03-28 | 190000 | 0 | 2.1 | 13.62 | 133.7 | 675.6 | -2.3 | 22.56 | 186.3 | 266.6 | -1 | 2.61 | 11.83 | 0.008 | 0.008 | 2.1
| 669 | 2008-03-28 | 200000 | 0 | 2.1 | 13.63 | 134.5 | 676.4 | -2.1 | 22.56 | 186.4 | 266.7 | -0.9 | 2.6 | 11.85 | 0.008 | 0.008 | 2.1
| 670 | 2008-03-28 | 210000 | 0 | 2.1 | 13.63 | 134.2 | 676.9 | -2.2 | 22.64 | 186.6 | 266.9 | -0.9 | 2.6 | 11.8 | 0.008 | 0.008 | 2.1
| 671 | 2008-03-28 | 220000 | 24.2 | 13.3 | 18.67 | 9.7 | 582.4 | -35.1 | 4.06 | 23.3 | 39.4 | -1 | 2.92 | 8 | 0.054 | 0.02 | 4.1
| 672 | 2008-03-28 | 230000 | 8.9 | -6.4 | 20.72 | 0.8 | 437.3 | -177.3 | 0.19 | 0.5 | 1.3 | -1 | -0.13 | 0.04 | 0 | 0 | -7.4
| 673 | 2008-03-29 | 0 | 9.9 | -9 | 20.82 | 0.8 | 407.2 | -230.3 | 0.27 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 0 | 0 | -10.4
| 674 | 2008-03-29 | 10000 | 12 | -11.1 | 20.83 | 0.8 | 396.4 | -297.5 | 0.26 | 0.5 | 1.3 | -1 | -0.14 | -0.04 | 0.001 | 0 | -13.3
| 675 | 2008-03-29 | 20000 | 17.2 | -13.7 | 20.85 | 0.7 | 387.9 | -388.5 | 0.24 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 0.001 | 0 | -17.5
| 676 | 2008-03-29 | 30000 | 25.3 | -19.8 | 20.86 | 0.8 | 387.4 | -459.9 | 0.23 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 0.001 | 0 | -24.3
| 677 | 2008-03-29 | 40000 | 27.3 | -22.9 | 20.87 | 0.8 | 388.1 | -459.3 | 0.15 | 0.5 | 1.3 | -1 | -0.14 | -0.04 | 3.168 | 0.002 | -27.7
| 678 | 2008-03-29 | 50000 | 28.8 | -27.5 | 20.88 | 0.7 | 385.2 | -514.6 | 0.12 | 0.5 | 1.3 | -1.1 | -0.14 | -0.04 | 0.008 | 0.01 | -29.8
| 679 | 2008-03-29 | 60000 | 25.9 | -25.9 | 20.89 | 0.6 | 380.2 | -506 | 0.06 | 0.5 | 1.3 | -1 | -0.14 | -0.04 | 7.935 | 0.029 | -27.5
| 680 | 2008-03-29 | 70000 | 9 | -10 | 20.91 | 0.8 | 374.5 | -160.4 | 0.16 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 22.216 | 0.073 | -8.5
| 681 | 2008-03-29 | 80000 | 1.8 | -1.5 | 20.93 | 0.9 | 369.2 | -38.4 | 0.1 | 0.5 | 1.3 | -1 | -0.14 | -0.04 | 11.159 | 0.091 | -1.4
| 682 | 2008-03-29 | 90000 | 1.4 | -1.4 | 20.94 | 0.8 | 364 | -24.3 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | 2.1 | 0.06 | 0.071 | -1.2
| 683 | 2008-03-29 | 100000 | 0 | 0 | 20.96 | 0.8 | 359 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.02 | 0.056 | 0.059 | 0
| 684 | 2008-03-29 | 110000 | 0 | 0 | 20.97 | 0.8 | 354.7 | 0 | 0.11 | 0.5 | 1.3 | -1 | -0.14 | -0.03 | 0.045 | 0.049 | 0
| 685 | 2008-03-29 | 120000 | 0 | 0 | 20.97 | 0.8 | 349.5 | 0 | 0.19 | 0.5 | 1.3 | -1 | -0.14 | -0.04 | 0.045 | 0.049 | 0
| 686 | 2008-03-29 | 130000 | 0 | 0 | 20.97 | 0.9 | 333.5 | 0 | 0.13 | 0.5 | 1.3 | -1 | -0.14 | -0.06 | 0.042 | 0.05 | 0
| 687 | 2008-03-29 | 140000 | 0 | 0 | 20.97 | 0.9 | 315.2 | 0 | 0.28 | 0.5 | 1.3 | -1 | -0.14 | -0.06 | 0.041 | 0.047 | 0
| 688 | 2008-03-29 | 150000 | 0 | 0 | 20.98 | 0.8 | 304 | 0 | 0.26 | 0.5 | 1.3 | -1 | -0.14 | -0.07 | 0.04 | 0.043 | 0
| 689 | 2008-03-29 | 160000 | 0 | 0 | 20.97 | 0.8 | 298 | 0 | 0.22 | 0.5 | 1.3 | -1 | -0.14 | -0.06 | 0.04 | 0.044 | 0
| 690 | 2008-03-29 | 170000 | 0 | 0 | 20.96 | 0.8 | 294 | 0 | 0.26 | 0.5 | 1.3 | -1 | -0.14 | -0.07 | 0.044 | 0.051 | 0
| 691 | 2008-03-29 | 180000 | 0 | 0 | 20.97 | 0.8 | 290.1 | 0 | 0.19 | 0.5 | 1.3 | -1 | -0.14 | -0.06 | 0.044 | 0.049 | 0
| 692 | 2008-03-29 | 190000 | 0 | 0 | 20.97 | 0.9 | 286.7 | 0 | 0.05 | 0.5 | 1.3 | -1 | -0.14 | -0.07 | 0.043 | 0.048 | 0
| 693 | 2008-03-29 | 200000 | 0 | 0 | 20.97 | 0.9 | 283.6 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.06 | 0.042 | 0.047 | 0
| 694 | 2008-03-29 | 210000 | 0 | 0 | 20.98 | 0.7 | 280.8 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.14 | -0.07 | 0.037 | 0.042 | 0
| 695 | 2008-03-29 | 220000 | 0 | 0 | 20.97 | 0.9 | 274.2 | 0 | 0.04 | 0.5 | 1.3 | -1 | -0.13 | -0.06 | 0.039 | 0.042 | 0
| 696 | 2008-03-29 | 230000 | 10.5 | 20.5 | 19.8 | 0.9 | 295.3 | 66.9 | 2.06 | 4.9 | 5.5 | -1 | 3.11 | 8.58 | 0.105 | 0.048 | 5.4
| 697 | 2008-03-30 | 0 | 15.2 | 82.5 | 16.98 | 0.9 | 576.7 | 10.1 | 7.12 | 20.4 | 20.8 | -1 | 10.29 | 30.01 | 0.304 | 0.057 | 15.5
| 698 | 2008-03-30 | 10000 | 24.6 | 61.5 | 16.75 | 0.9 | 599.2 | 65.6 | 7.67 | 23.7 | 24.1 | -1 | 10.29 | 30.01 | 0.227 | 0.054 | 14.7
| 699 | 2008-03-30 | 20000 | 25.3 | 56.9 | 16.23 | 0.8 | 598.1 | 56 | 8.49 | 32.7 | 33 | -1 | 10.26 | 30.01 | 0.209 | 0.048 | 13
| 700 | 2008-03-30 | 30000 | 20 | 58.9 | 15.5 | 0.8 | 601 | 31.3 | 10.49 | 54.1 | 69.7 | -1 | 10.17 | 28.29 | 0.217 | 0.042 | 11.3
| 701 | 2008-03-30 | 40000 | 0 | 5 | 13.95 | 47.7 | 638.6 | -2.6 | 21.71 | 178.4 | 241 | -1 | 5.87 | 9.78 | 0.018 | 0.018 | 5
| 702 | 2008-03-30 | 50000 | 5.7 | 6.9 | 10.69 | 155.5 | 636.8 | 28.7 | 18.77 | 147 | 214.3 | -1 | 4.11 | 8.3 | 0.031 | 0.015 | 2.6
| 703 | 2008-03-30 | 60000 | 0.1 | 1.9 | 13.86 | 112.2 | 667.6 | -2.6 | 22.46 | 185.6 | 264.8 | -0.9 | 2.35 | 10.68 | 0.007 | 0.007 | 2
| 704 | 2008-03-30 | 70000 | 0.1 | 2.2 | 13.94 | 52.7 | 642.7 | -2.6 | 17.09 | 126.7 | 192.6 | -1 | 2.57 | 7.82 | 0.008 | 0.008 | 2.2
| 705 | 2008-03-30 | 80000 | 0.1 | 2 | 13.94 | 58 | 637.9 | -2.1 | 17.44 | 131.7 | 197.2 | -1 | 2.47 | 7.73 | 0.008 | 0.008 | 2.1
| 706 | 2008-03-30 | 90000 | 0 | 2.1 | 13.76 | 138.6 | 673 | -2.3 | 22.81 | 188.7 | 269.1 | -1 | 2.53 | 11.97 | 0.008 | 0.008 | 2.1
| 707 | 2008-03-30 | 100000 | 0 | 2.1 | 13.81 | 131.6 | 676.1 | -2.5 | 22.68 | 187.4 | 267.5 | -0.9 | 2.52 | 11.51 | 0.008 | 0.008 | 2.1
| 708 | 2008-03-30 | 110000 | 0 | 2 | 13.8 | 136 | 676.7 | -2.3 | 22.5 | 185.7 | 266.3 | -1 | 2.47 | 11.74 | 0.007 | 0.008 | 2.1
| 709 | 2008-03-30 | 120000 | 0.1 | 2.1 | 13.95 | 51.9 | 641.8 | -2.2 | 16.98 | 126.9 | 192 | -1 | 2.49 | 7.67 | 0.008 | 0.008 | 2.1
| 710 | 2008-03-30 | 130000 | 0.1 | 2.1 | 13.95 | 52.1 | 638.4 | -2.1 | 17.16 | 129.2 | 194.2 | -1 | 2.48 | 7.48 | 0.008 | 0.008 | 2.1
| 711 | 2008-03-30 | 140000 | 0.1 | 2 | 13.95 | 53.9 | 637.3 | -2.4 | 17.11 | 128.7 | 193.5 | -1 | 2.39 | 7.54 | 0.007 | 0.008 | 2
| 712 | 2008-03-30 | 150000 | 0.1 | 2 | 13.96 | 53.9 | 636.9 | -2.4 | 17.13 | 128.9 | 193.9 | -1 | 2.37 | 7.54 | 0.007 | 0.007 | 2
| 713 | 2008-03-30 | 160000 | 0.1 | 2 | 13.95 | 60 | 636.3 | -2.1 | 17.54 | 132.6 | 197.8 | -1 | 2.37 | 7.72 | 0.007 | 0.007 | 2
| 714 | 2008-03-30 | 170000 | 0 | 2 | 13.87 | 117.8 | 670.2 | -2.1 | 22.44 | 184.8 | 263.8 | -1 | 2.42 | 10.33 | 0.007 | 0.007 | 2
| 715 | 2008-03-30 | 180000 | 0 | 2.1 | 13.78 | 139.7 | 670.4 | -2.3 | 22.79 | 187.2 | 268.3 | -0.9 | 2.55 | 12.08 | 0.008 | 0.008 | 2.1
| 716 | 2008-03-30 | 190000 | 0 | 2.1 | 13.78 | 139.7 | 677.4 | -2.1 | 22.81 | 187.6 | 268.6 | -1 | 2.54 | 12.08 | 0.008 | 0.008 | 2.1
| 717 | 2008-03-30 | 200000 | 0 | 2.1 | 13.79 | 138.1 | 678.3 | -2.4 | 22.83 | 188.3 | 269.5 | -1 | 2.54 | 11.94 | 0.008 | 0.008 | 2.1
| 718 | 2008-03-30 | 210000 | 0 | 2.1 | 13.79 | 136.8 | 678.5 | -2.4 | 22.93 | 188.8 | 270 | -1 | 2.52 | 11.78 | 0.008 | 0.008 | 2.1
| 719 | 2008-03-30 | 220000 | 0.1 | 2.1 | 13.98 | 53 | 645 | -2.3 | 16.88 | 124.1 | 189.2 | -1 | 2.54 | 8.07 | 0.008 | 0.008 | 2.2
| 720 | 2008-03-30 | 230000 | 0.1 | 2 | 13.99 | 52.6 | 639.2 | -2.6 | 17.23 | 128.5 | 193.3 | -0.9 | 2.44 | 7.58 | 0.008 | 0.008 | 2.1
| 721 | 2008-03-31 | 0 | 0.1 | 2.1 | 14 | 51.5 | 638.8 | -2.3 | 17.25 | 128.3 | 193.2 | -0.9 | 2.49 | 7.53 | 0.008 | 0.008 | 2.1
| 722 | 2008-03-31 | 10000 | 0.1 | 2.1 | 14.01 | 51.9 | 638.6 | -2.3 | 17.22 | 128.2 | 193.1 | -1 | 2.46 | 7.54 | 0.008 | 0.008 | 2.1
| 723 | 2008-03-31 | 20000 | 0.1 | 2.1 | 14 | 52.5 | 638.6 | -2.3 | 17.28 | 128.8 | 193.9 | -0.9 | 2.45 | 7.52 | 0.008 | 0.008 | 2.1
| 724 | 2008-03-31 | 30000 | 0.1 | 2.1 | 14.01 | 52 | 638.8 | -2.6 | 17.26 | 128.3 | 193.1 | -0.9 | 2.47 | 7.55 | 0.008 | 0.008 | 2.1
| 725 | 2008-03-31 | 40000 | 0.1 | 2.1 | 14.01 | 52.8 | 639.3 | -2.7 | 17.37 | 129.2 | 194.4 | -1 | 2.47 | 7.58 | 0.008 | 0.008 | 2.1
| 726 | 2008-03-31 | 50000 | 0.1 | 2.1 | 14 | 57.2 | 639.2 | -2.4 | 17.54 | 131.7 | 196.8 | -0.9 | 2.47 | 7.67 | 0.008 | 0.008 | 2.1
| 727 | 2008-03-31 | 60000 | 2.6 | 4.6 | 11.81 | 128.7 | 672.8 | 26.6 | 22.84 | 188 | 267.7 | -0.9 | 3.94 | 10.76 | 0.019 | 0.01 | 2.3
| 728 | 2008-03-31 | 70000 | 1.4 | 4 | 12.79 | 127 | 677.3 | 11.8 | 22.92 | 188.7 | 269.2 | -0.9 | 3.08 | 11.35 | 0.015 | 0.008 | 2.1
| 729 | 2008-03-31 | 80000 | 0 | 2 | 13.91 | 121.4 | 676.7 | -2.6 | 22.83 | 188 | 268.1 | -0.9 | 2.43 | 11.18 | 0.007 | 0.008 | 2.1
| 730 | 2008-03-31 | 90000 | 0 | 2.1 | 13.88 | 127.6 | 677.5 | -2.6 | 22.9 | 188.8 | 269.5 | -0.9 | 2.51 | 11.82 | 0.008 | 0.008 | 2.1
| 731 | 2008-03-31 | 100000 | 0 | 2.1 | 13.87 | 131.8 | 678.3 | -2.1 | 22.82 | 188.6 | 269.5 | -0.9 | 2.52 | 12.08 | 0.008 | 0.008 | 2.1
| 732 | 2008-03-31 | 110000 | 0 | 2.1 | 13.86 | 134.8 | 678.3 | -2.6 | 22.8 | 187.7 | 268.9 | -1 | 2.52 | 12.32 | 0.008 | 0.008 | 2.1
| 733 | 2008-03-31 | 120000 | 0 | 2.1 | 13.87 | 136.7 | 678.1 | -2.3 | 22.63 | 186.6 | 267.7 | -1 | 2.52 | 12.46 | 0.008 | 0.008 | 2.1
| 734 | 2008-03-31 | 130000 | 0 | 2.1 | 13.86 | 136 | 677.4 | -2.4 | 22.6 | 186.4 | 267.5 | -0.9 | 2.52 | 12.46 | 0.008 | 0.008 | 2.1
| 735 | 2008-03-31 | 140000 | 0 | 2.1 | 13.86 | 135.7 | 676.8 | -2 | 22.61 | 186.5 | 267.6 | -1 | 2.51 | 12.45 | 0.008 | 0.008 | 2.1
| 736 | 2008-03-31 | 150000 | 0 | 2.1 | 13.85 | 135.3 | 676.6 | -2.7 | 22.63 | 186.5 | 267.7 | -0.9 | 2.52 | 12.47 | 0.008 | 0.008 | 2.1
| 737 | 2008-03-31 | 160000 | 0 | 2.1 | 13.85 | 136.6 | 676.7 | -2.3 | 22.54 | 185.9 | 267.1 | -1 | 2.52 | 12.54 | 0.008 | 0.008 | 2.1
| 738 | 2008-03-31 | 170000 | 0 | 2.1 | 13.85 | 136.6 | 676.2 | -2.3 | 22.53 | 185.5 | 266.7 | -0.9 | 2.51 | 12.55 | 0.008 | 0.008 | 2.1
| 739 | 2008-03-31 | 180000 | 0 | 2.1 | 13.86 | 136 | 675 | -2.2 | 22.54 | 185.6 | 266.7 | -1 | 2.51 | 12.5 | 0.008 | 0.008 | 2.1
| 740 | 2008-03-31 | 190000 | 0.3 | 1.7 | 14.82 | 115.3 | 673.3 | -1.2 | 19.26 | 157.6 | 226.5 | -1 | 2.11 | 10.7 | 0.017 | 0.017 | 1.7
| 741 | 2008-03-31 | 200000 | 0 | 0 | 21.08 | 1 | 511 | 0 | 0.21 | 0.5 | 1.3 | -1 | -0.55 | 0 | 0.063 | 0.065 | 0
| 742 | 2008-03-31 | 210000 | 10.7 | 36.1 | 18.73 | 0.9 | 534.2 | 10.3 | 4.2 | 14.5 | 15 | -1 | 4.92 | 15.74 | 0.161 | 0.056 | 7.3
| 743 | 2008-03-31 | 220000 | 19.5 | 70.3 | 15.3 | 13.5 | 612.1 | 28.3 | 10.85 | 57.1 | 88.4 | -1 | 9.83 | 28.86 | 0.259 | 0.039 | 10.5
| 744 | 2008-03-31 | 230000 | 0.1 | 2 | 13.84 | 139.6 | 659.3 | -2.3 | 23.03 | 189.8 | 270.5 | -0.9 | 2.43 | 13.11 | 0.007 | 0.008 | 2
| 745 | / | /
| 746 | / | / | 452.921 | 5.246 | 4.73 | -0.953 | AVE | 12.081 | -81.922 | 7.563 | 57.484 | 84.265 | 34.678 | 1.437 | -2.396 | 19.159 | 18.003 | -6.078
[11 empty] | July Total MW-hr | 36379.4
Excluding non-op hours
Used gas use column to confirm operation

## CEM INCIDENTS
Turbine CEMS Downtime
NOx ppm @15% O2 NOx lb/hr CO ppm @15% O2 and CO lb/hr CEMS Downtime for 1/1/2008 thru 3/31/2008
Parameter | Date/Time | Duration | Duration (minutes) | Reason |  | Action
All | 2/28/08 2300 | Qtr |  | CEMS not certified |  | CEMS certification testing complete 3/1/08
Turbine Excess Emissions
NOx ppm @15% O2 24-Hr Rolling NOx lb/hr CO ppm @15% O2 and CO lb/hr Excess Emissions for 1/1/2008 thru 3/31/2008
Parameter | Date/Time | Duration | Duration (minutes) | Average | Min | Max | Limit | Reason | Action
NOx | 3/30/2008 0300 | 1 hr | 60 minutes | 58 ppm | 58 | 58 | 2.5 | Equipment malfunction | Incident report 2008_01
CO | 3/30/2008 0300 | 1 hr | 60 minutes | 28.8 | 28.8 | 28.8 | 6 | Equipment malfunction | Incident report 2008_01

## Cooling Tower Emissions
TDS Sampling
Cooling Tower Discharge Samples
Date Taken |  | Value (ppm)
2008-03-31 |  | 444
2008-03-31 |  | 421
2008-03-30 |  | 458
| Avg: | 441 | ppmw
PM Emission Rate
100% PM is PM10
|  | 5e-06 | Max drift rate (0.0005%)
|  | 8.34 | weight of water (lb/gal)
|  | 77000 | Water circulation rate (gpm)
| PM/PM10 = | 0.08496 | lb/hr
PM/PM10 Emissions
| Month | Hours | Emissions
| Jan | 579.2 | 49.2091 | lbs
| Feb | 333.93 | 28.3708 | lbs
| Mar | 313.72 | 26.6538 | lbs
|  | Total PM/PM10: | 0.052117 | tons

## Diesel Calcs
Mint Farm Generation |  |  |  | Facility ID # | 2111
Diesel Generator
| Operation: | 1 | Hours
Pollutant | Emission Factor |  |  | Emissions
NOx | 14.57 | lb/hr |  | 0.007285 | tons
CO | 0.55 | lb/hr |  | 0.000275 | tons
SOx | 0.29 | lb/hr |  | 0.000145 | tons
PM/PM10/PM2.5 | 0.68 | lb/hr |  | 0.00034 | tons
VOC | 0.06 | lb/hr |  | 3e-05 | tons
Emission Factors per ADP 04-2571R1 TSD, Section 6.e