## Sheet1
Wa. 25 Acquisition Commitment
Item
No. in Study | ACTION ITEMS
1 | Complete the installation of upgraded transformer primary protection for PacifiCorp transformers located in the “Kraft Substation.” Installing “Transruptors” in place of fuses; | This $600,000 project required PacifiCorp to install four transrupters in the Cascade Kraft substation to replace the high side fuses on each transformer in the substation. The project was approved in July 2005. High side fuses were replaced with transrupters at the time the transformer was replaced in July 2005. The project was completed in December 2007 with the installation of the fourth transrupters
2 | Replace the PacifiCorp fixed capacitor banks located in the “Kraft Substation” with units that do not cause voltage transients when switched on and in addition mitigate harmonic currents and voltage distortion; | The filter capacitor bank installation in the Cascade Kraft substation was completed March 21, 2008 but not put into service until April 1, 2008, at Boise's request because they did not want to take a paper machine down until that date. The cost to PacifiCorp was approximately $1,000,000.
3 | Prepare an engineering study analyzing the cost of installation of adequate lightning protection to the 69 kV sub-transmission system that is interconnected to the “Kraft Substation;” | Final study completed and provided to Boise Cascade and WUTC Staff on March 19, 2007. Additional discussions about cost effective solutions took place during the Joint Reliability Task Force meetings, which occurred semi-annually as agreed to by Boise.
4 | Prepare an engineering study analyzing the cost of installation of adequate lightning protection to the 230 kV transmission system that is interconnected to the “Wallula Substation; | The study prepared by the outside consultant and provided to Boise Cascade in March 2007 was a combined study of both the 69 kV and 230 kV transmission systems serving the Cascade Kraft substation. Additional discussions about cost effective solutions took place during the Joint Reliability Task Force meetings, which occurred semi-annually as agreed to by Boise.
5 | Control the vegetation near the 230 kV structures to prevent range fire damage to the structures; | Vegetation chemically treated in 2007 and has continued thereafter on a regular every other year schedule.
6 | Complete and continue the training of system operators to mitigate human errors | In 2005 operators were all trained and have been provided ongoing annual training. Errors are reviewed on monthly basis and coaching provided as appropriate. We have experienced no process interruptions at the Boise Paper Wallula plant associated with operator error since 2004.
7 | Upgrade Dodd Road Substation facilities to reduce the potential for faults on the secondary that pull the voltage down on the primary for extended time periods. | PacifiCorp insulated the bus at Dodd Road substation to prevent bus faults at the substation caused by animals and birds in the station. This work was completed in January 2006 with a total capital investment of $100,000.