Pacific Power Smart Grid

Report

September 1, 2016

- Table of Contents

Table of Contents	i

List of Tables	iii

List of Figures	iv

List of Acronyms	v

I.	Executive Summary	1

II.	Smart Grid Strategies, Objectives, and Goals	4

A.	Strategies	4

B.	Goals	4

III.	Projects Overview	6

IV.	Status of Grid Modernization and Smart Grid Investments	8

A.	Advanced Metering Infrastructure and Customer Communications	8

1.	Advanced Metering Infrastructure Background	8

2.	Oregon AMI Customer Communications and Programs	9

B.	Transmission Network and Operations Enhancements	9

1.	Dynamic Line Rating Background	9

2.	NERC Reliability Standard MOD-033	12

C.	Substation Operations Enhancements	13

1.	Distributed Energy Resources Template Deployment	14

2.	Wapato Circuit Analysis	15

3.	Distribution Substation Metering	15

4.	Washington Clean Energy Fund 2	17

D.	Distribution Automation and Reliability	17

1.	Distribution Automation Pilot Project – Walla Walla	18

2.	Distribution Automation Feasibility Study	18

3.	Communicating Faulted Circuit Indicators	19

4.	Distribution Management	20

5.	Outage Management	21

6.	Circuit Analysis Software (CYME)	21

E.	Demand Response	22

1.	2015 Integrated Resource Plan (IRP) Update	22

2.	Cool Keeper AC Direct Load Control	23

3.	Irrigation Load Control	24

4.	Time-Based Pricing	26

F.	Distributed and Renewable Resource Enhancements	31

1.	Distributed and Renewable Resources	31

2.	Interconnection Standards and Smart Inverters	31

3.	Electric Vehicle (EV) Charging Infrastructure	34

V.	Roadmap to Grid Modernization	36

VI.	Conclusion	37

Appendix A – Summary of Project Updates	38

Appendix B – Dynamic Line Rating	42

Appendix C – Locations of Equipment for MOD-033 Requirement	43

Appendix D – MOD-033 Model Validation	44

Appendix E – DER Example Template	46

Appendix F – Distribution Substation Metering Technical Requirements	64

Appendix G – Washington Clean Energy Fund 2 Grant Application	65

Appendix H – Pacific Power Net Metering and Customer Generation	70

- List of Tables

Table 1 – Fuse Saving Device Locations by District (Oregon and Washington)	20

Table 2 – Time-Based Rate Schedule Participation by State	30

Table 3 – Summary of Project Updates	38

Table 4 – Locations Identified for MOD-033 Requirement	43

- List of Figures

Figure 1 – PacifiCorp Grid Modernization Projects	6

Figure 2 – Select Smart Grid Components	7

Figure 3 – Representation of AMI technology to be deployed in Oregon.	9

Figure 4 – Simplified Transmission System near Populus Substation	11

Figure 5 – Smart Grid Roadmap	36

Figure 6 – Dynamic Line Rating for West of Populus	42

Figure 7 – PMU Input Data	44

Figure 8 – Actual PMU Data Validates Model	45

Figure 9 – Actual PMU Data Invalidates Model	45

- List of Acronyms

A/C	Air Conditioning

AMI	Advanced Metering Infrastructure

AMR	Automated Meter Reading

AMS	Advanced Metering System

BESS	Battery Energy Storage System

CADOPS	Computer Aided Distribution Operations System

CAIDI	Customer Average Interruption Duration Index

CES	Centralized Energy Storage

CFCI	Communicating Faulted Circuit Indicators

CI	Customer Interruptions

CIS	Customer Information System

CMI	Customer Minutes Interrupted

CPP	Critical Peak Pricing

CVR	Conservation Voltage Reduction

DA	Distribution Automation

DER	Distributed Energy Resources

DLC	Direct Load Control

DLR	Dynamic Line Rating

DMS	Distribution Management System

DSM	Demand-Side Management

DR	Demand Response

EIM	Energy Imbalance Market

EV	Electric Vehicle

FAN	Field Area Network

FDIR	Fault Detection, Isolation, and Restoration

FTA	Federal Transit Administration

HAN	Home Area Network

IEEE	Institute of Electrical and Electronics Engineers

IRP	Integrated Resource Plan

IVVO	Integrated Volt/VAr Optimization

kW	Kilowatt

kWh	Kilowatt-hour

M&V	Movement and Verification

MDMS	Meter Data Management System

MW	Megawatt

MWh	Megawatt-hour

NERC	North American Electric Reliability Corporation

O&M	Operations and Maintenance

OMS	Outage Management System

ODOE	Oregon Department of Energy

OPUC	Oregon Public Utilities Commission

PGE	Portland General Electric

PMU	Phasor Measurement Unit

PNNL	Pacific Northwest National Laboratory

RAS	Remedial Action Scheme

SAIDI	System Average Interruption Duration Index

SCADA	Supervisory Control and Data Acquisition

T&D	Transmission and Distribution

TOU	Time-of-Use

UL	Underwriters Laboratories

WAN	Wide Area Network

WECC	Western Electricity Coordinating Council

# Executive Summary

Pacific Power & Light Company (Pacific Power or Company), a division of PacifiCorp, submits this 2016 Smart grid report (Smart grid report or Report) to provide the Washington Utilities and Transportation Commission (Commission) an update on its grid modernization and smart grid initiatives and projects in compliance with WAC 480-100-505.

In a coordinated effort to align corporate initiatives with industry terminology, the evolution of smart grid technology has necessitated the clarification of vocabulary to properly define existing and future projects and initiatives. Smart grid is the application of advanced communications and controls to the power system, from generation, through transmission and distribution, to the customer. As a result, a wide array of applications can be defined under the smart grid umbrella. This smart grid report focuses on technologies and processes that can be readily integrated in an affordable manner with the existing electrical grid infrastructure.

Modernization of the grid is essential to effectively implement, or overlay, smart grid technologies. While “grid modernization” projects may or may not fall under the purview of the smart grid report, such projects or initiatives are considered essential to realizing a strong and robust smart grid. For this reason, Pacific Power continues to focus on effective key enhancements to form an affordable and proven foundation for existing and future smart grid projects. Pacific Power acknowledges that traditional infrastructure solutions can be the most affordable and beneficial solutions for Washington customers and will continue with a common sense approach in implementing smart grid technologies.

2016 key efforts specific to the state of Washington include:

- Developing transmission synchrophasor locations and modeling criteria

- Central energy storage evaluation at Grandview substation

- Implementation of a screening tool to analyze traditional versus DER solutions for system reinforcement issues

- Implementation of distribution system analysis application

- Initiation of distribution automation pilot project in Walla Walla

The Company’s investments in grid modernization and smart grid technologies are divided into various sections within the report for advanced metering infrastructure, transmission, substation, and distribution networks. A summary of projects and their status is provided in Appendix A. The Company has completed, is monitoring, or is developing grid enhancement initiatives that include projects and initiatives undertaken in its six state service territory and the potential benefits or opportunities specific to each individual state and its customers:

- Advanced Metering Infrastructure (AMI): Network and metering infrastructure to improve customer service and provide a platform for future smart grid applications. AMI initiatives include:

  - AMI in Oregon – Implementation in Oregon of an automated two-way metering infrastructure for network data and information about power consumption for customers. Designed to deliver customer benefits addressing safe, affordable, reliable, and flexible service

- Transmission Network Enhancements: Transmission system projects to improve grid reliability and monitoring. Transmission network enhancement initiatives include:

  - Dynamic Line Rating – Ongoing data analysis and assessment to increase the efficient use of existing transmission assets.

  - Transmission Synchrophasor (NERC Standard MOD-033) – Model validation evaluation for improved accuracy in system analysis resulting in improved system reliability.

- Substation Enhancement Projects: Substation investments that increase flexibility of distributed energy resource integration. Substation enhancement initiatives include:

  - Centralized Energy Storage ­ Utilization of a DER template to screen the feasibility of DER solutions as alternatives to traditional solutions for system reinforcement issues.

  - Distribution Substation Metering ­ Introduction of a pilot program to enhance monitoring of substation loading and power quality at non-SCADA substations.

- Distribution Automation and Reliability: Distribution automation investments in hardware and software that enable remote or automatic configuration of the distribution network. Distribution automation and reliability initiatives include:

  - Distribution Automation Feasibility Study – Development of criteria for targeted distribution automation, screening circuits with given developed criteria, and evaluating cost benefit.

  - Distribution Management – Offering a standard option of a Fuse Saving device and evaluating integration into SCADA management systems.

  - Outage Management – Bid event for recloser with bidirectional power flow in anticipation of higher penetration levels of DER.

  - Circuit Analysis Software – Implementation of a distribution system modeling application that will provide improved accuracy and higher functionality in distribution circuit analysis pertaining to DER interconnection and diverse load characteristics.

- Demand-Side Management: Initiatives offered that allow development of direct load control and time-of-use programs. Demand-side management initiatives include:

  - Cool Keeper AC Direct Load Control – Implementation of a two-way communication network to better manage air conditioner loads.

  - Irrigation Load Control – Pilot programs in Oregon and California to determine grower acceptance of load control programs and cost.

  - Time-Based Pricing –Increasing participation rates in irrigation time-of-use pilot in Oregon.

- Distribution Network Enhancements: Distribution system investments in technologies that improve system efficiency and distributed energy resource programs. Distributed network enhancement initiatives include:

  - IEEE 1547 Standard – An update on the IEEE process to introduce guidelines for smart inverter implementation.

Through its key grid modernization efforts in Washington, Pacific Power expects to provide tangible benefits to its customers. As examples, a quantifiable reduction in customer minutes lost is expected to be proven in the Walla Walla distribution automation pilot project. Future cost savings are expected due to improved accuracy in distribution system modeling allowing project deferrals and evaluating DER solutions as alternatives to traditional solutions. Also, the ongoing installation of bi-directional equipment as a standard in areas of anticipated high growth DER will avoid costly equipment replacements in the future.

In addition to Pacific Power’s smart grid efforts, Pacific Power remains committed to the communities it serves, providing valuable contributions to economic development and improving the environment through operating efficiently, responsibly, and safely.

# Smart Grid Strategies, Objectives, and Goals

The purpose of the smart grid report is to define the philosophy and scope for Pacific Power to deliver, develop and define the strategies, objectives, and financial characteristics required for the future roadmap. Additionally, to build on previous reports, which validate and align the relative start dates for various components to give an understanding of the progress required to reach any smart grid deployment. However, progression of any effort must be driven by the fundamental economics laid out in a financial analysis to protect the customers’ best interests.

## Strategies

Pacific Power considers the following strategies necessary to realizing a smart grid:

- Ensure that smart grid investments provide service at reasonable and fair prices by comparing products and solutions in a financial model that highlights the most beneficial solution configurations.

- Institute cost-effective standards and equipment specifications that enable implementation of smart grid-compatible devices, either through retrofitting where appropriate or through replacement due to equipment obsolescence or failure.

- Provide customers with tools and understanding to change usage for their benefit.

- Leverage broad resources at the Company’s disposal, including lessons learned regarding existing analysis and work from Berkshire Hathaway Energy, comprised of four investor-owned utilities.

- Research industry projects and work with organizations, such as the National Electric Energy Testing Research and Applications Center, to enhance the Company’s understanding of smart grid technologies.

## Goals

By implementing the objectives mentioned above, the Company continues to achieve the following smart grid goals that align with WAC 480-100-505:

- Enhance the reliability, safety, security, quality, and efficiency of the transmission and distribution network.

- Enhance customer service and lower the cost of utility operation.

- Enhance the ability to save energy and reduce peak demand.

- Enhance the ability to develop renewable resources and distributed generation.

The Company seeks to leverage smart grid technologies to optimize the electrical grid when and where it is economically feasible, operationally beneficial, and in the best interest of customers. This overall goal aligns with state commissions, whose goals include improving reliability, increasing energy efficiency, enhancing customer service, and integrating renewable resources. These goals will be met by utilizing strategies that analyze the total cost of ownership, performing well-researched cost-benefit analyses, and focusing on customer outreach.

# Projects Overview

The Company has implemented a number of grid modernization and smart grid-related projects and programs. Section IV describes the individual projects, programs, and efforts in detail. These projects are displayed in Figure 1. These projects are chosen based on an analysis of their potential ability to cost-effectively improve service to customers. While these projects are located throughout the Company’s service territory, lessons learned through positive business case analyses will then be applied as potential additions to the Washington power system and its customers. These projects may also apply to any sector of the power system, which synergistically supports the smart grid concept as depicted in Figure 2.

Figure 1 – PacifiCorp Grid Modernization Projects

Figure 2 – Select Smart Grid Components

Many of the smart grid technologies are dependent upon preceding technology deployment for the full benefit. For example, the Oregon AMI network is an essential component of the field area network in Oregon that will enable future utilization of smart grid technologies by establishing a communication backbone.

# Status of Grid Modernization and Smart Grid Investments

## Advanced Metering Infrastructure and Customer Communications

### Advanced Metering Infrastructure Background

Over 60 million smart meters have been deployed in the U.S. over the last ten years. Pacific Power’s decision in early 2016 to install two-way AMI in Oregon benefits from the lessons learned from earlier deployments, technology advancements and cost reductions.

The Company has installed and operated 1.2 million Automated Meter Reading (AMR) meters in its Utah, Washington, and Wyoming service territories. The AMR installations have been successful in reducing meter reading costs, reducing meter energy losses, improving employee safety, and increasing the overall quality of service to customers.

Pacific Power conducted research with other utilities to capture lessons learned from early adopters of AMI from a cost, benefit and risk mitigation standpoint (specifically, First Energy, Pacific Gas and Electric, NV Energy and Portland General Electric). In addition, a request for information (RFI) was conducted with major vendors and focused on evaluating advancements in technology and reviewing actual benefits obtained by other utilities. The RFI was followed by a formal request for proposals (RFP) that resulted in price reductions that, coupled with increasing O&M labor rates, resulted in a positive business case to implement AMI in Oregon. On April 8, 2016, the Company announced its intentions to install smart meter assets through a press release.

The key components in the AMI network include smart meters, the communications network, and related software/IT systems. A representation of the AMI technology that will be implemented in Oregon is shown in Figure 3.

Figure 3 – Representation of AMI technology to be deployed in Oregon.

### Oregon AMI Customer Communications and Programs

A web-based customer portal that provides customers with usage and billing information will be introduced as a component of Pacific Power’s Oregon AMI project. The portal is anticipated to allow customers to monitor and manage energy consumption utilizing near real-time usage measurements. Additional communication materials will be disseminated throughout the project to educate customers about upcoming changes.

## Transmission Network and Operations Enhancements

### Dynamic Line Rating Background

Dynamic line rating (DLR) systems utilize sensors to monitor the conditions that impact the real-time temperature of a transmission line or lines, and use this measured data to calculate the real-time thermal capability of the lines. Transmission lines are rated utilizing anticipated conductor temperatures, which are based on line loading and assumptions of worst-case ambient weather conditions for a given season (for example, the hottest anticipated summer day with the lowest anticipated wind speed). Since line loading is the primary driver of conductor heating, these ratings allow utilities to safely operate their systems through changing weather conditions. However, as worst-case loading conditions approach thermal limits, favorable ambient weather conditions may supply some margin for thermal capacity increase beyond the static rating, which is based on worst-case ambient weather conditions. Dynamic line rating systems allow utilities to utilize this available thermal capacity.

PacifiCorp Transmission is also evaluating a related technology known as thermal replicating relays. These devices monitor the thermal properties of the line, and if these devices sense the conductor thermal limits are being exceeded, they send a trip signal to open the line. Under NERC standard PRC-023, transmission lines meeting a certain criteria are required to have thermal trip settings equal to 150 percent of their emergency winter rating. This setting requirement enables manual emergency remedial action during contingency outages to prevent cascading outages, but can put the line at risk for conductor damage. PRC-023 allows thermal replicating relaying to be installed as an exception to this practice where line tripping will not cause cascading outages, thus eliminating the risk of conductor damage and associated repair costs.

#### Dynamic Line Rating Project Summary

Two dynamic line rating (DLR) projects were implemented in 2014 and a third thermal replicating relay project will be evaluated in 2016.

The first DLR project, the Minors-Platte line project, is complete and the rating of the line has been modified to reflect the correlation between wind generation in the area and the cooling effects of wind on the line. The second DLR project, the West-of-Populus project, is currently being monitored for effectiveness and application to real-time operations.

The Company is investigating the third project, which is the use of thermal replicating relaying devices in the Soda Springs area of Idaho. The loss of two transmission lines in this area would overload a third line until remedial action is taken.

#### Project Description and Analysis

West-of-Populus DLR Project

The West-of-Populus location is comprised of three 345 kV transmission lines west of the Populus substation in southeast Idaho with a combined length of 147 miles. In 2013, the West-of-Populus location was identified as needing transmission expansion during the Company’s normal transmission planning process, and dynamic line rating was determined to be an applicable solution, e.g., the transmission was thermally constrained, and the time periods and capacities required were coincidental with that made available with dynamic line rating.

The Company selected the CAT-1 line monitoring system offered by The Valley Group for the project. The CAT-1 system calculates real-time line ratings using line section tension readings from load cells installed on the lines. Measurement data is taken from multiple sensing locations throughout the lines and is then communicated via radio to a central master station. The 345 kV transmission system near Populus substation is shown in Figure 4, where the West-of-Populus DLR system was installed.

Figure 4 – Simplified Transmission System near Populus Substation

The DLR installation on the 345 kV West-of-Populus path is producing data for PacifiCorp grid operations. Processing this data is ongoing and remains inconclusive because the actual line loading has not approached the thermal capacity of the line and no clear correlation between the dynamic line rating, conductor temperature and the loading levels is apparent. Appendix B demonstrates a fluctuating conductor temperature; however, the fluctuation is being influenced by the ambient nighttime and daytime temperatures more than the line loading, which is typically the primary driver of conductor temperature. Because low and fairly consistent loading levels are having very little effect on the temperature fluctuation of the line, there are periods of increasing load but decreasing or steady conductor temperatures. The dynamic line rating system is expecting conductor temperature to increase with line loading, and when the inverse occurs the system calculates irregular line ratings. Given these irregularities associated with the low loading levels experienced over the last year, it is difficult to draw a conclusion on the effectiveness of dynamic line rating for the West-of-Populus lines.

Thermal Replicating Relay Evaluation

Thermal replicating relays were investigated for installation in conjunction with a DLR system on the Grace-Soda-Threemile Knoll 138 kV line. The thermal replicating relays would monitor the current flow on the Grace-Soda-Threemile Knoll 138 kV line when the Grace-Threemile Knoll 138 kV line is out of service. The relays would trigger to open the circuit breaker at Soda substation and the associated Grace-Soda-Threemile Knoll 138 kV line if the line overloads to 100 percent of its emergency rating calculated by a DLR system. Opening the line avoids a prolonged overload condition which would cause conductor damage and associated repair costs.

As both the Grace-Soda 138 kV and Soda-Threemile Knoll 138 kV lines are parts of the PRC-023 list, the thermal relays combined with a DLR system was proposed instead of generic overload protection. The thermal replicating relays operating to trip the circuit breaker at Soda substation would sectionalize the Goshen-Soda 138 kV line and Soda-Threemile Knoll 138 kV line without tripping any generation or load. The cost of the thermal replicating relaying including the DLR system was approximately $1.4 million.

As part of this evaluation, an alternative to thermal replicating relays, a Remedial Action Scheme (RAS) in the form of redundant relays could be installed to trip the circuit breaker at the Soda 138 kV switch yard if the Soda-Threemile Knoll 138 kV line or Soda-Grace 138 kV line overloads to 100 percent of its emergency rating. The cost of the RAS alternative was determined to be $115,000. Due to the cost advantage for customers, the Company will move forward with the RAS solution.

#### Future Actions and Timeline

West-of-Populus DLR Project

PacifiCorp Transmission will continue to monitor line loading on the West-of-Populus path. When line loading increases due to outage contingencies or high flow scenarios, PacifiCorp Transmission expects to see a better correlation between line temperature and line loading. Higher line loading will provide a better opportunity to draw conclusions on the effectiveness of the dynamic line rating.

Dynamic Line Rating and Thermal Replicating Relays

PacifiCorp Transmission will continue to look for transmission constraints and other opportunities where dynamic line rating and/or thermal replicating relays may be viable solutions. Possible locations for dynamic line rating applications include the major bulk transmission sources to load areas where planned and unplanned outages can place the system at risk for the next event. Examples for PacifiCorp Transmission in Washington include the Yakima load area and the transmission paths connecting to the Walla Walla area. As constraints are identified through ongoing transmission planning on PacifiCorp’s transmission system in Washington, and dynamic line rating is deemed a viable alternative solution, further evaluation will be provided in future smart grid reports.

### NERC Reliability Standard MOD-033

The Steady-State and Dynamic System Model Validation standard, also called NERC Reliability Standard MOD-033, is a new model validation standard proposed to establish consistent validation requirements to facilitate collecting accurate data and building planning models to analyze the reliability of the interconnected transmission system.

#### Project Description

Measurement data originating from PMUs will be necessary to satisfy the validation requirements expressed in MOD-033. The Company has determined locations throughout its service territory necessary for such data to be collected and is in the process of identifying existing equipment capabilities at selected locations. Locations determined throughout the Company’s service territory are based on criteria outlined in standard PRC-002 and are provided in Appendix C. Additional locations may be requested to satisfy MOD-033 requirements. Equipment deemed inadequate to provide required measurements may be upgraded on a site-by-site basis.

Model validation procedures are also being evaluated, in conjunction with data and equipment availability, to fulfill MOD-033 requirements. Creation of a documented process to validate data that includes the comparison of a planning power flow model to actual system behavior and the comparison of the planning dynamic model to actual system response is ongoing. Appendix D illustrates the validation analysis utilizing sample data between two separate models and the actual PMU data.

#### Future Actions and Timeline

The Company is in its initial stages of gathering information, assessing feasibility for this project, and documenting the validation process to meet requirements. Sites under consideration in Washington include Merwin, Pomona Heights, Swift 1, Union Gap, Wallula and Yale. PacifiCorp Transmission is planning to meet necessary requirements set forth by MOD-033 before the effective date of July 1, 2017.

## Substation Operations Enhancements

Substation and distribution projects include centralized energy storage, communicating faulted circuit indicators, distribution automation, operational management systems, conservation voltage reduction, and integrated volt/VAr optimization.

Centralized energy storage (CES) includes but is not limited to large, centralized storage resources, such as electrochemical batteries, pumped hydro, and electromechanical batteries (i.e., flywheels). One of the benefits of the smart grid is the ability to integrate renewable energy sources into an electricity delivery system. In contrast to dispatchable resources that are available on demand, such as most fossil fuel generation, some renewable energy resources have intermittent generation output due to their fuel source of wind or photovoltaic solar. The generation output of these resources cannot be increased and has high opportunity costs when generation is decreased. Providing service to the electrical grid becomes progressively more challenging as the grid’s energy requirements are increasingly served from these intermittent resources. Two methods to fill this generation gap without the use of dispatchable resources are demand response (DR) programs and centralized and/or localized energy storage.

### Distributed Energy Resources Template Deployment

Pacific Power has recognized the role that distributed energy resources (DER) may play in the deferral or offset of traditional poles and wires infrastructure investments. To that end, the Company commissioned an internal study investigating the potential use of DER to offset or defer a power transformer replacement project in Moab, Utah. One of the outcomes of the report was the recognition of a need for a tool for transmission and distribution planners to utilize in comparing alternative DERs solutions to traditional solutions.

#### Project Summary

Create a tool that can be used by transmission and distribution planners to screen system issues and quantify the feasibility and affordability of a DER alternative solution in comparison to traditional solutions.

#### Project Description and Analysis

A DER alternatives template was created in a Berkshire Hathaway Energy cross-platform initiative that, given a few input parameters common to traditional solution analysis and solar data, provides a feasibility assessment and cost comparison for solar, battery storage, and demand response solutions. The screening tool utilizes input parameters such as hourly facility load data, annual solar data obtained from National Renewable Energy Laboratory’s (NREL) PVWatts Calculator and cost estimates for battery storage and demand response solutions.

Costs in the alternatives template for solar installations are based on the results of recent RFPs at Rocky Mountain Power and NV Energy. Costs for battery storage are based on studies performed by an external contractor to inform the IRP process. A new study has been commissioned to refresh the battery storage costs and results are expected by the end of 2016. Once results are finalized, costs will be updated in the DER alternatives template.

The template has been deployed to area transmission and distribution planners throughout the Company through a series of training sessions that began in February 2016 and ended in May 2016. An example template is provided in Appendix E.

#### Future Actions and Timeline

It is anticipated that for future budget cycles, proposed system reinforcements will include DER solutions as part of the analysis and their documentation proposals. Where feasible and the most affordable option, DER solutions will supplant traditional solutions for implementation.

### Wapato Circuit Analysis

#### Project Description, and Analysis

In 2016, the Wapato 5Y202 circuit near Yakima, Washington was identified as a potential candidate for installation of an energy storage device to rectify projected thermal overload issues.

An analysis was performed utilizing the DER template to determine the feasibility and estimated cost of a DER solution. The analysis is provided in Appendix E. The feasible DER alternative to resolve the loading issue is the installation of an energy storage device with an estimated cost of $3.5 million.

#### Future Actions and Timelines

Further investigation into the loading issues on Wapato 5Y202 shows that the existing #2 copper can be replaced with 477 AAC to solve the loading issues through the five year planning horizon. Due to the low cost of a traditional solution, the DER alternative solution will not be implemented at this time. However, circuits in Washington will continue to be evaluated as potential candidates for energy storage.

### Distribution Substation Metering

Substation monitoring and measurement of various electrical quantities is seen as a necessity due to growing levels of distributed energy resources. Enhanced monitoring helps to resolve the following challenges:

Limited visibility on loading levels, load shape, and event information required to develop thorough interconnection studies, determining safe switching procedures, and cost effective capital improvement plans.

Single-phase DER have the ability to exacerbate load imbalance on a distribution circuit, and increases the potential for unintended circuit breaker operations from elevated neutral currents.

The growing interaction of DER on distribution system equipment has potentially detrimental impacts on transient and steady-state voltage levels. Understanding the production levels of DER on a distribution circuit should allow for the accurate determination of effective grounding requirements and fault clearing control schemes. These systems, if not appropriately installed, can result in temporary overvoltages to customers or leave circuits improperly protected during fault conditions.

Potential harmonic issues from inverter-based DER can result in customer motor damage and interfere with high-frequency communications.

The necessity for measurement of per-phase vector quantities to improve optimization opportunities for capital costs and system losses.

#### Project Summary, Description, and Analysis

Pacific Power plans to deploy an advanced substation metering pilot that includes installing advanced meters at distribution substations that have no existing communications. Remote communication paths will be installed with all meters. A data management and analytical tool will be purchased to automatically collect, analyze, interpret and report on available data.

SCADA has been the preferable form of gathering load profile data from distribution circuits; however, SCADA systems can be expensive to install and additional equipment is required to provide the data needed to perform analysis on harmonics issues. The advanced metering pilot may prove to provide an affordable option for gathering requisite substation data.

#### Project Description and Analysis

Purchase and install advanced substation meters at distribution substations with limited or no communications.

Ensure all substation meters installed as part of this program are enabled with remote communication capabilities.

Implement a data management system to automatically download, analyze and interpret data downloaded from all installed substation meters.

Develop a process to ensure all data collected is used to improve the interconnection study process in addition to improving long-term and short-term distribution and transmission planning studies.

#### Future Actions

Pacific Power has selected an advanced substation meter based on the requirements listed in Appendix F and is in the process of evaluating locations for the pilot program. The Wapato substation in Wapato, Washington and the Grandview substation in Grandview, Washington have been identified as potential candidates for the pilot due to the need for more granular loading data in these locations. A data management system is also under evaluation. It is anticipated the advanced meters will be installed, and the data management system will be gathering data by Q1 2017.

The cost to install an advanced substation meter is estimated to be $15,000 for this pilot with ongoing cellular data costs of $20 per month. Typical SCADA installations cost $100,000 or more depending on the site location and availability of nearby compatible communication networks.

Based on the success of the pilot installation, additional meters will be installed as needed to address increasing DER penetration issues.

### Washington Clean Energy Fund 2

Pacific Power participated in Phase 1 of the Washington Clean Energy Fund 2 (CEF2) grant program, sponsored by Washington Department of Commerce, to apply for funding of a battery energy storage system (BESS). The proposed project involved the installation and integration of a 2 MW, 8 MWh energy storage system to be located at the Grandview substation in Grandview, Washington. The proposed battery storage technology was an advanced vanadium redox flow battery to be supplied by Uni-Energy Technologies (UET), headquartered in Mukilteo, Washington. The Phase 1 grant application submitted to Washington Department of Commerce is provided in Appendix G.

The proposal supported Pacific Power’s commitment to exceptional customer service and good stewardship of the environment. The primary benefits to Pacific Power were initially anticipated to be:

Grid modernization in furtherance of Washington State having a 21st century grid

Deferral of the capital cost associated with a distribution system upgrade

Testing of renewable wind resource firming

On April 20, 2016, Pacific Power withdrew its submission for the 2016 Washington CEF2 grant program. It was determined that the potential benefits to our customers compared to the need for traditional network capacity increases in the Yakima area was not cost effective to favorably research and develop the technology at this time. Pacific Power has prioritized the system capacity requirements, ongoing equipment maintenance, and the corresponding reliability for the customers served from the Grandview substation. Based on the benefit valuation of the battery storage pilot compared to the traditional capacity increase, Pacific Power decided to postpone its plan to pursue a BESS through CEF2 during this biennium.

The evaluation process utilized in the Washington grant proposal provided an excellent learning opportunity to analyze the use of battery storage in lieu of traditional infrastructure solutions. The lessons learned in this evaluation will be applied to other system issue analyses going forward. Pacific Power will continue to look for opportunities to apply for future grants and deploy cost-effective battery storage technology as an integral clean energy alternative.

## Distribution Automation and Reliability

Distribution automation includes fault detection, isolation, and restoration (FDIR) and communicating faulted circuit indicators (CFCIs). FDIR utilizes strategically-placed, communication-enabled fault detection devices, distribution reclosers and motor-operated switches to automate restoration. These systems enable the energy company to remotely or automatically reconfigure the distribution network in response to an outage. The devices communicate their status to a distribution management system (DMS), which determines the fault location and then sends out a signal to open or close fault isolation devices and switches to restore the maximum number of customers in areas outside the fault zone. CFCIs are used to assist in field locating the faulted component of the system and help shorten the time needed for restoration.

### Distribution Automation Pilot Project – Walla Walla

A distribution automation pilot project for the downtown Walla Walla, Washington area has been initiated. The scope of the project is to install two new reclosers with distribution automation capability in a looped configuration on two 12.47 kV circuits and upgrade another recloser in the loop to enable distribution automation functionality. The project will also establish communications with the reclosers to supply data, open/close indication, and control to existing operations systems. A fault detection isolation and restoration (FDIR) scheme will be programmed and enabled once communications are established to provide a fully functional distribution automation system. Subsequent testing of the system and observation of any reliability improvement will help to inform future investment in distribution automation for other areas of Washington.

Future Actions and Timeline

The Walla Walla distribution automation pilot project will be built out in phases to allow for construction time and system integration. The phased approach will also allow operations personnel to become familiar with the new equipment and operating procedures. The first phase, planned for 2016, includes the installation of the two new reclosers. The second phase, planned for 2017, includes establishing communications with the reclosing devices to integrate data, open/close indication, and control into existing operations systems such as the outage management system. The final phase of the project, planned for 2018, is to program and enable the FDIR scheme to observe the distribution automation performance.

### Distribution Automation Feasibility Study

Prior smart grid reports have analyzed a holistic approach to distribution automation deployment and associated cost-benefit analysis. A new study of Pacific Power’s distribution automation potential has been initiated in Oregon to focus on areas where distribution automation may have an improved cost-benefit result over the previous holistic approach. The study will be based upon cost and distribution system assumptions that will enhance reliability and yield benefits to customers. Preliminary analysis shows that urbanized areas have the greatest probability of a positive cost benefit because existing infrastructure may already be conducive to switching requirements. For that reason, the urbanized areas of Oregon, as well as downtown Walla Walla, Washington are the focus of the Company’s initial studies into the application of distribution automation.

Multiple steps were identified to achieve a preferred outcome of such a study:

Key criteria and requirements for selection of potential locations.

Necessary communication equipment and protocols at a site need to be identified.

Switch types and operators to be installed will need to be defined.

Potential candidates would be screened based on determined criteria.

Requirements for system integration into SCADA or DMS will be documented.

Cost-benefit evaluation of screened candidates will be performed.

The key criteria and requirements for selection of potential DA locations have been determined, and are outlined as follows:

Circuits shall be looped to another circuit and the smallest conductor surrounding the open point between circuits shall be 4/0 AAC with increasing conductor size towards the substations.

Circuits shall have SCADA control and indication.

Circuits that were previously used for distribution automation pilots and could be re-commissioned.

Circuits shall possess the ability to locate a minimum of three gang-operated switching devices, including at the open point.

Circuits containing critical loads, defined as critical public infrastructure, e.g., hospitals, water processing facilities, and public relief centers, shall be identified.

#### Future Actions and Timeline

The remaining steps identified to perform the study are ongoing. A cost benefit analysis will be completed as the study develops. Verification of equipment existing on-site and equipment to be installed at potential locations will require additional time and resources and be based on availability of field personnel.

### Communicating Faulted Circuit Indicators

The new SCADA Monarch system was commissioned by PacifiCorp Transmission in April 2016. This new energy management system will enable the integration of CFCI data to a centralized location, where a quantifiable reliability analysis can be performed. To date, there is insufficient reliability data from a manual collection process to perform the reliability savings analyses.

#### Future Actions and Timeline

Implementation of CFCI data is expected to occur in 2016 and outage event data is possible for analysis. In addition, an evaluation of the backhaul of fault detector data over the AMI communication network is ongoing.

### Distribution Management

As an example of DA functionality included in current scoping processes, Fuse Saving devices are currently being deployed as a standard device option. Fuse Saving devices have a lower pickup value than breakers and have the ability for peer-to-peer operation to determine system functionality. Although not considered “smart devices” because of their autonomous functionality, their specifications do include two-way communication capability. There are currently more than forty Fuse Saving devices installed. Their locations are given in Table 1.

Table 1 – Fuse Saving Device Locations by District (Oregon and Washington)

| Districts | Number Installed |
| --- | --- |
| Astoria | 11 |
| Klamath Falls | 3 |
| Bend, Coos Bay, Medford, and Roseburg | 34 |
| Walla Walla | 3 |

Given the limited exposure, newly installed Fuse Saving devices have had two reliability events; therefore, a comprehensive qualitative analysis of their benefit is not available. However, based on an extremely limited dataset it appears that certain Fuse Saving devices have resulted in an 80 percent reduction in momentary outages for all customers upstream of the device and an 80 percent reduction in sustained interruptions for customers downstream. This is consistent with historic fault data showing that indicates only one of five fault events is permanent. More analysis is required to quantify the reliability impact for sustained interruptions upstream of the device.

The cost of each installed Fuse Saving device is $4,000. The Company will be able to establish a more concrete quantitative benefit from the use of these devices with the collection of more data over the next year.

Pacific Power launched an investigation to determine the feasibility and cost of establishing communications with Fuse Saving devices. The scope and cost of integration with the SCADA Monarch energy management system are also being investigated.

Regulator Bid Event

Stock item numbers were added to reflect reverse flow controls. Stock item numbers are now available for units with two potential transformers for use at locations where reverse power flow may exist due to a distributed energy resource. These items are not standard items for construction due to additional costs but are available for use where deemed necessary. For example, these special units would be used in areas with increasing levels of distributed energy resources and light load situations where reverse power flow is probable.

Communication Protocols

The communication protocols for the control devices of reclosers and regulators were evaluated. The devices are DNP 3.0 ready. These controls will be evaluated with the AMI network to be deployed in Oregon.

### Outage Management

Recloser Bid Event

A bid event for recloser devices launched in April 2016, with a completion date scheduled for September 2016. The event included triple-single reclosers that have voltage sensors on the load side of the bushing used for deadline checking in areas with distributed energy resources and potential bidirectional power flow. The units also include sensors on the source-side bushing to allow the unit to function for loop feed, or reverse power flow conditions. In addition to these sensors, reclosers are being purchased communications ready and shall be compatible with an available communication network. These functionalities will be a key element in future conversions to distribution automation schemes. The Company is installing four reclosers per year on average over the past five years, based on the previous five years, in Washington.

### Circuit Analysis Software (CYME)

Pacific Power is transitioning to a newer, more powerful distribution system analysis application called CYME. The application will allow better customer load modeling and time series analysis, and will help ensure future planning efforts and project definitions are as accurate as possible.

#### Project Description

Pacific Power began its transition from ABB FeederAll to CYME at the end of 2015. Pacific Power began utilizing FeederAll to model its distribution system in the 1990’s. Users within Pacific Power continue to gain a greater understanding in the basic and advanced functions available in this new software. Pacific Power anticipates that system planning results will become more accurate with the software’s advanced capabilities.

Since a distribution system’s response to a change in volt/VAr control schemes is complex, the conclusions drawn from a power flow model are only as valid as the inputs provided to the model. CYME and its GIS Gateway permit the inclusion of several details that were not part of the former ABB FeederAll model, and these advancements will allow Pacific Power to obtain a more accurate view of the system’s behavior in differing scenarios. Specifically, more than 20 different customer types are derived from source data, and each type definition contains voltage response characteristics, utilization and coincidence factors, and demand profiles over time. For example, an irrigation customer with time-of-use metering can be differentiated in the model from a commercial customer with on-site generation. Refinement of these definitions to improve modelling results is ongoing.

Additional functionality within CYME permits devices, such as regulators and capacitors, to be modeled with operational time delay. This functionality, which was not available in ABB FeederAll, allows a power flow analysis with a time profile to illustrate the state of the system between device operations. In CYME, customer generation modeling is also much more robust, so that the influence on one network from generators on a different network can be identified, along with their interaction with line devices over time. For example, the model is capable of identifying the locations of lowest voltage when the output of a chosen subset of solar generation falls by 50 percent over the time required for the regulating device to respond to the increase in load.

The additional functionality provided by CYME allows users to evaluate many complex scenarios, and furthers engineers’ ability to respond efficiently and effectively to proposed system changes while maintaining reliability and safe operation of the system.

#### Future Actions and Timeline

Several minor improvements remain to be implemented in the Gateway product, which generate the CYME model from Pacific Power’s GIS source system. These improvements are anticipated to be completed in late 2016. ABB FeederAll will be phased out and all subsequent planning studies will be completed in CYME.

## Demand Response

The Company offers two types of demand response programs to customers: direct load control and time-of-use rates. Direct load control programs include Cool Keeper air conditioner (AC) load control and irrigation load control, which are categorized as Class 1 demand-side management under Pacific Power’s integrated resource plan. Time-of-use programs offered to specific customer classes are classified as Class 3 demand side-management.

### 2015 Integrated Resource Plan (IRP) Update

Pacific Power’s least-cost, least-risk preferred portfolio remains composed of Class 2 demand-side management resources (energy efficiency) and front office transactions. These are representative of short-term firm forward market purchases through the front nine years of the IRP 20-year planning horizon. Pacific Power’s 2015 integrated resource plan update (IRP Update) modeling results did not select new Washington direct load control demand response until 2027 in the preferred portfolio. This indicates that Washington direct load control demand response is not a least-cost resource until 2027 or later.

Pacific Power’s 2015 IRP Update preferred portfolio does not include simple cycle combustion turbine plants until 2028 of the planning horizon. This planning date differs from the 2015 IRP that indicated 2022 as a potential date for simple cycle combustion turbine plants.

With further load reductions forecast in the 2015 IRP Update, as compared to the 2015 IRP, Class 1 demand-side management resources are not required in the 2015 IRP Update preferred portfolio until 2025 for Rocky Mountain Power and 2027 for Pacific Power.

### Cool Keeper AC Direct Load Control

#### Project Summary

Rocky Mountain Power has an existing direct load control demand response program in Utah known as Cool Keeper. Residential and small commercial customers can participate in the program allowing Pacific Power Energy Supply Management to manage air conditioning (AC) loads.

#### Project Description and Analysis

Pacific Power Energy Supply Management continues to utilize the Cool Keeper program in an effort to manage summer peaks in the Wasatch Front area. Customers are provided an annual credit on their bills for their participation. The Cool Keeper program directly controls customers’ AC units with a radio-enabled device that cycles the compressors on and off. Based on the current number of Cool Keeper participants and load calculations, the capacity of the controllable load is approximately 115 MW during peak times.

The communication network for the Cool Keeper devices was upgraded in 2014 to allow two-way functionality. The upgrade performed on the network increased bandwidth and allowed for direct monitoring of the Cool Keeper devices.

The upgrade improved the overall efficiency of the system through enhanced situational awareness of real-time operations and data analysis. Prior to the upgrade, the system was not capable of providing real-time information from the devices and the number of units providing data for analysis was limited to a small number of fixed devices.

After the upgrade, the system can provide operators with an accurate view of real time DR resource availability through the following mechanisms:

Daily Resource Analysis – The system sends a daily message to test connectivity of all enrolled devices and collects data from these devices to measure system availability. This allows the operator to be informed of how many devices are available to respond to a DR event.

Hourly Forecasting – The system uses local weather information, such as temperature and humidity, to estimate the anticipated KW savings from the Cool Keeper resources. This forecast is sent to the PacifiCorp Unit Commitment application for use in the reserves allocation calculation.

The system is now capable of advanced data analysis by collecting information from every enrolled Cool Keeper device, which allows the operators to perform a Measurement and Verification (M&V) analysis. An M&V analysis consists of the following:

Event Validation – Interval runtime data is collected from all of the devices in the network. Data is analyzed to determine the amount of reduction each device delivered following a DR event. The information allows the Company to target site inspections on any non-performing participants to increase participants during the next event.

Customer Segmentation – Collected interval data allows the Company to segment the Cool Keeper participants into groups: Single Family, Multi-Family, and Small Commercial. Analysis has shown that each group has a different load shape and usage pattern. By applying different load shapes and usage patterns based on these groups, the Company is able to provide a more accurate overall forecast.

Ad-Hoc Analysis – Reports can also be run for specific use-cases on interval data. For example, the number of Cool Keeper participants who activate their AC units only when they are in need of cooling were identified. The majority of customers leave AC units operational all day, which allows for their unit to participate during events. The contribution of this subgroup of intermittent participants was determined to analyze their overall performance in the program.

#### Future Actions and Timeline

Pacific Power Energy Supply Management will continue to leverage Cool Keeper for load management during summer peaking events along the Wasatch Front.

### Irrigation Load Control

#### Project Summary

The Company has offered an irrigation load control program in various configurations for several years. These programs have been designed to reduce load by allowing the Company to control participants’ irrigation loads during periods of peak demand.

#### Project Description

In 2013, the Company selected EnerNOC to manage a ten-year irrigation load control program through a pay-for-performance agreement. EnerNOC’s responsibilities include enrollment, equipment installation, dispatch management, performance calculations, and customer service. Under this program the Company only pays for capacity available during program hours, as measured by EnerNOC’s energy monitoring technology and adjusted through a performance factor to account for those sites that opt out of participation during specific dispatch events.

In Utah and Idaho, the irrigation load control program is currently available to customer sites on Tariff Schedule 10. Participating sites are compensated for shutting off irrigation load for specific time periods determined by Rocky Mountain Power, and are provided day-ahead notice of dispatch events. Customers have the opportunity to opt out of dispatch events as necessary for their operations. Customer incentives are based on a site’s average available load during load control program hours adjusted for the number of opt-outs or non-participation.

The 2015 Rocky Mountain Power Irrigation Load Control Program dispatched seven events for a total of 52 hours from June 1, 2015, through August 21, 2015. In Idaho, the load control events for 2015 ranged from 123 MW to 151 MW as recorded by SCADA/EMS. The median curtailed load dispatch was 141 MW.

Pacific Power’s Oregon Pilot Load Control Program (targeting 3MW) for the 2016-2020 irrigation seasons was filed on March 4, 2016, in Advice 16-04 and was approved on May 3, 2016, with an effective date of May 4, 2016. The filing requested authorization to implement a pilot irrigation load control program for irrigation customers near the Oregon and California border, specifically in the area comprising the Klamath Basin. The objective of the pilot program is to test the design characteristics of the Company’s existing irrigation load control program offered in Utah and Idaho for applicability to agricultural pumping operations in Pacific Power’s Oregon service areas. Pacific Power intends to test for grower acceptance, barriers to participation, and cost to deliver within the Klamath Basin area.

#### Future Actions and Timeline

The Public Utility Commission of Oregon (OPUC) approval incorporated several staff recommendations to help inform a common and consistent demand response proposal framework. A summary of the recommendations is as follows:

After the third irrigation season in 2018, Pacific Power will provide a recommendation to expand the program to all of its agricultural customers for the next irrigation season or explain in detail why the pilot program appears to be unsuccessful and what additional information would be obtained in the remaining years of the pilot that would justify its continuance.

Use the California Public Utilities Commission Distributed Energy Resource Avoided Cost Framework as a guide when conducting the post-season assessment of benefits and costs of the Irrigation Load Control Pilot.

Pacific Power will work with OPUC staff on the development of the filing framework for a demand response program proposal.

Pacific Power’s Oregon demand response activities for the remainder of 2016 will consist of participant selection and enrollment, equipment installation, triggering management, and post season reporting.

Utilizing the same design as the approved Oregon program, Pacific Power expects to file a 2 MW irrigation load control pilot program for California customers in 2016 and, if approved, commence initial program roll-out for the 2017 irrigation season. It is expected the results and lessons learned from the pilot program will be utilized in meeting the Washington irrigation DSM resource need forecasted for 2027 in the 2015 IRP update.

### Time-Based Pricing

#### Project Summary

The Company has existing time-of-use rates for various customer classes within each of its six states.

#### Project Description

Time-based pricing can encourage customers to change energy usage patterns. The most common price signals in the industry today are time-of-use, critical peak pricing and critical peak rebate programs. A combination of time-of-use and critical peak pricing, or time-of-use and critical peak rebate pricing programs, are the most prevalent. If designed and implemented appropriately, these rate structures can present opportunities for creating reductions in energy usage during critical periods when system peaks are present.

Currently, the Company utilizes time-of-use programs where the price for broad blocks of hours is predetermined and constant. However, the Oregon AMI system will be installed with consideration that near real-time programs, such as critical peak pricing, may be pursued in the future. The Oregon AMI system will seamlessly handle existing time-of-use programs.

In Oregon, a two year time-of-use pilot program for irrigation customers was placed in-service beginning with the 2014 irrigation season. The program implemented on-peak energy surcharges and off-peak energy credits. A report on the pilot was filed with the OPUC in December 2014. An additional report was filed with the OPUC in December 2015.

The 2014 Pacific Power time-of-use irrigation pilot was implemented to assess the interest, willingness, and ability of Oregon irrigation customers to shift their energy usage away from designated on-peak periods. Although the potential savings for the customer through shifting usage was significant, customer participation was below the necessary threshold for conducting a successful pilot. In 2015, Pacific Power solicited input from irrigators to improve participation in the pilot. Surveys and in-person meetings were conducted to better understand the needs of irrigators in the area. Interest in the pilot and its potential for savings were highest in the Klamath Falls area. Based on feedback provided from those meetings, Pacific Power modified its pilot for 2015 to include a greater on-peak to off-peak rate ratio for increased potential savings and concentrated the location of potential participants to the Klamath Falls area.

In 2015, Pacific Power sent materials regarding the pilot and enrollment information to all irrigation customers in the Klamath Basin area to encourage customer participation. Invitations to participate in an irrigation workshop were also sent to Klamath Basin irrigators in Oregon and California. The workshop was attended by more than 200 participants.

The irrigation workshop was sponsored by Pacific Power, Energy Trust of Oregon, irrigation districts, and water user associations in the area with the intent to inform customers about energy and saving programs available to irrigators. Pacific Power gave a presentation at the workshop to describe the time-of-use pilot along with potential benefits to participants and customers were able to ask questions. Customer service and billing personnel were available at the workshop to discuss the pilot further and to enroll customers for the pilot. The majority of customers enrolled in the pilot attended the workshop. Interest in the pilot increased significantly in 2015 and the participation cap was expanded to include all of the approximately 95 meters that signed up in 2015.

In February 2016, Pacific Power filed Advice No. 16-03 describing the results of a post-season survey of pilot participants along with a request to extend and expand the pilot for two additional years. The single year of data obtained in 2015 was unlikely to be representative of typical usage data for the area because it was a low water year. Pacific Power proposed no changes to the time-of-use periods or on-peak and off-peak rate adders but proposed to open the pilot up to 75 new participants in the Klamath Basin area. At OPUC staff’s request, the number of new participants was lowered to 25. On April 21, 2016, the proposed filing was approved by the OPUC with additional reporting requirements due after the end of the 2016 irrigation season, including an estimate of the capacity reduction related to the pilot and an estimate of potential cost savings, both near-term and long-term.

#### Lessons Learned from the Irrigation Time-of-Use Pilot

Pacific Power learned from its time-of-use pilot that it was able to increase participation in the irrigation Time-of-Use program through three methods:

Increasing the potential for customer bill savings.

In 2015, the Company increased the ratio between on- and off-peak rates under the pilot to five-to-one. With this ratio a customer shifting 100 percent of their energy usage to off-peak could achieve a 33 percent savings on of their summer bills. This significant percentage likely encouraged more irrigators to participate because the potential for savings was great enough to offset the cost of operational efforts and/or equipment changes that would allow them to shift energy usage.

Concentrating the pilot in a location where customers were more acutely aware of the cost of electricity.

Many customers in the Klamath Basin were served under extremely low rate energy contracts through 2006. These irrigators experienced significant rate increases as they transitioned over seven years from the contract rates of less than one-cent per kilowatt-hour to the standard irrigation rates. The electric bill became a much more significant cost to the business for these irrigators and therefore they were receptive to the opportunity to achieve bill savings.

Conducting in-person outreach with the opportunity for potential participants to ask questions.

Pacific Power held a workshop in the Klamath Basin area to present energy and cost saving programs available to irrigation customers. Customers were able to ask questions about the time-of-use pilot in person to customer service and billing personnel at the meeting. Communications regarding the pilot were sent to all customers eligible to participate and were also available at the workshop. Approximately 95 customers signed up for the pilot in 2015, the majority of which signed up at the workshop.

Regarding residential time-based pricing, as of December 31, 2015, there were 1,130 Oregon residential customers participating in the residential time-of-use pricing. The Company communicates residential time-of-use information on its website (www.pacificpower.net/tou) which contains links to frequently asked questions, and on-peak and off-peak hours and pricing charts. Customers have the ability to enroll in the program online and by phone. Additionally, Pacific Power includes time-of-use program information in customer bills at least twice a year.

Table 2 is an updated summary of Pacific Power’s price schedules by state and shows current levels of participation in mandatory and voluntary programs.

The Company’s Idaho Schedule 36 Optional Time of Day has a higher participation rate than optional residential time of use tariffs in Oregon and Utah because its structure generally provides a greater benefit for customers, especially higher usage customers. Along with a higher basic charge, Schedule 36 customers are not subject to tier block pricing used for standard residential customers on Schedule 1.

In contrast, Oregon optional residential time-of-use rates are based upon applying credits and surcharges to the standard rates for those customers. As a result, time-of-use customers on portfolio Schedule 210 have a higher effective rate during on-peak times compared to standard Oregon residential customers on Schedule 4.

In Washington, large general service customers whose electric service load exceeds 999 kW are automatically enrolled in a metered time of use schedule.

Table 2 – Time-Based Rate Schedule Participation by State

| Description | State | Schedule | Participating Customers (Dec. 31, 2014) | Eligible Customers | Participating Eligible Customers | Voluntary or Mandatory |
| --- | --- | --- | --- | --- | --- | --- |
| Residential Time-of-Use Pricing | Idaho | 36 | 12,770 | 60,556 | 21.09% | Voluntary |
|  | Oregon | 4/210 | 1,130 | 487,060 | 0.23% | Voluntary |
|  | Utah | 2 | 424 | 755,425 | 0.06% | Voluntary |
| General Service (Business Sector and Irrigation) Time-of-Use Pricing, Either Energy or Demand | California | AT48 | 19 | 19 | 100% | Mandatory |
|  | Idaho | 35/35A | 3 | 10,544 | 0.03% | Voluntary |
|  | Oregon | 23/210 | 263 | 77,345 | 0.34% | Voluntary |
|  | Oregon | 41/210 | 60 | 5,509 | 1.09% | Voluntary |
|  | Oregon | 41/215 | 90 | 100 | 90% | Voluntary (Pilot) |
|  | Oregon | 47 | 7 | 7 | 100% | Mandatory |
|  | Oregon | 48 | 196 | 196 | 100% | Mandatory |
|  | Utah | 6A/6B | 2,455 | 100,517 | 2.44% | Voluntary |
|  | Utah | 8 | 244 | 244 | 100% | Mandatory |
|  | Utah | 9/9A | 164 | 164 | 100% | Mandatory |
|  | Utah | 10 | 240 | 3,127 | 7.68% | Voluntary |
|  | Utah | 31 | 7 | 7 | 100% | Mandatory |
|  | Washington | 47T | 1 | 1 | 100% | Mandatory |
|  | Washington | 48T | 66 | 66 | 100% | Mandatory |
|  | Wyoming | 33 | 10 | 10 | 100% | Mandatory |
|  | Wyoming | 46 | 83 | 83 | 100% | Mandatory |
|  | Wyoming | 48T | 29 | 29 | 100% | Mandatory |

## Distributed and Renewable Resource Enhancements

### Distributed and Renewable Resources

Pacific Power monitors customer generation and net metering customers throughout its service territory in an effort to ensure participation figures and generation capacities correspond with projected trends. Pacific Power has seen an increase in net metering customers across all of its service territory for the 2016 calendar year compared to previous years. A monthly report for July 2016 that indicates net metering and customer generation is provided in Appendix H.

### Interconnection Standards and Smart Inverters

Inverters with advanced functionalities, referred to as smart inverters, allow for conversion of DC to AC for grid connectivity, as well as providing advanced capabilities to support the stability, reliability, and efficiency of the electric grid. Such capabilities are imperative with penetration levels of inverter-based DER projected to increase through 2040 and necessitate standards be identified and followed to ensure a unified system.

Pacific Power’s interconnection standards and policies are based on the following standards, as well as other national, state, and local jurisdictional guidelines:

IEEE 1547 – Standard for Interconnecting Distributed Resources with Electric Power Systems

UL 1741 – Standard for Inverters, Converters, Controllers and Interconnection System Equipment for Use with Distributed Energy Resources

#### Background of IEEE 1547

The IEEE 1547 (2003) Standard for Interconnecting Distributed Resources with Electric Power Systems is a family of standards that serve as the interconnection standards for DER and address the technical and test requirements for systems less than 10 MW. The IEEE 1547 standard was published in 2003 and focuses on the technical specifications for, and testing of, the interconnection. The requirements are universally needed for interconnection of distributed energy resources, including synchronous machines, induction machines, and power inverters/converters, and will be sufficient for most installations.

The IEEE 1547 interconnection suite contains requirements pertinent to interconnection, control, operation, intentional islanding, and conducting impact studies of DER with electric power systems. IEEE 1547 is comprised of the following standards:

IEEE 1547 (2003 and 2014 Amendment 1) – Standard for Interconnecting Distributed Resources with Electric Power Systems

IEEE 1547.1 (2005 and 2015 Amendment 1) – Standard for Conformance Tests Procedures for Equipment Interconnecting Distributed Energy Resources with Electric Power Systems and Associated Interfaces

IEEE 1547.2 (2008) – Application Guide for IEEE 1547 Standard for Interconnecting Distributed Resources with Electric Power Systems

IEEE 1547.3 (2007) – Guide for Monitoring Information Exchange, and Control of Distributed Resources with Electric Power Systems

IEEE 1547.4 (2011) – Guide for Design, Operation, and Integration of Distributed Resources Island Systems with Electric Power Systems

IEEE 1547.6 (2011) – Recommended Practice for Interconnecting Distributed Resources with Electric Power Systems Distribution Secondary Networks

IEEE 1547.7 (2013) – Guide to Conducting Distribution Impact Studies for Distributed Resource Interconnection

IEEE P1547.8 – Draft Recommended Practice for Establishing Methods and Procedures that Provide Supplemental Support for Implementation Strategies for Expanded use of IEEE 1547-2003

#### Amendment to IEEE 1547

In mid-2013, members of the IEEE 1547 standards community initiated a “fast-track” amendment to IEEE 1547, labeled IEEE 1547a. Published by the standards organization in May 2014, IEEE 1547a is a “permissive” update to the existing IEEE 1547 whose main purpose is to permit some functionalities not currently allowed in IEEE 1547. The amendment has initiated a full revision of IEEE 1547 in consideration of evolving use-cases of modern inverter-based distributed energy resource systems.

#### Company Participation

Pacific Power is an active member of the IEEE 1547 working group and continues to support the standards’ revision process. Currently, the working group is in the process of drafting a complete revision of the standard that will allow distributed energy resources to have a more significant contribution to the local energy company’s electric power system. The fully revised standard will be technology agnostic with the requirements focusing on functionality. Prescriptive updates to the standard, such as to how to implement a solution to satisfy the requirement, will be omitted. The working group is also investigating processes to adopt prudent smart inverter functionalities as standard features to enable higher penetrations of distributed generation.

Traditionally, energy grids were not designed to accommodate active generation and storage at the distribution level. IEEE 1547 is being updated due to an increase of DER penetration to reflect corresponding increase in technology and use-cases of DER integration.

In addition to modifications throughout the standard, three sections of IEEE 1547 are undergoing significant changes:

Clause 4.1.1 – Voltage Regulation

Clause 4.2.3 – Voltage Response to Area Abnormal Voltage Conditions

Clause 4.2.4 – Frequency Response to Area Abnormal Voltage Conditions

The main intent of these changes is to clearly define and understand the challenges of integrating smart inverters into the suite of interconnection standards. The changes are anticipated to address general technical specifications, performance categories, and default equipment settings. The final draft of IEEE 1547 is expected to be balloted in Q4 2016, published in Q2 2017, and approved in 2018.

Since UL 1741 will not be testing the amended interconnection standard, any revisions made to IEEE 1547.1 must be modified to identify the test procedures to ensure conformance with the requirements listed in the full revision. The standards committee of IEEE is working expeditiously towards revising IEEE 1547.1, which will provide testing requirements for the new IEEE 1547 standard. Coordination between the UL 1741 testing and certification requirements and the new IEEE 1547.1 testing requirements is currently in process.

IEEE 1547 was established as the national standard for the interconnection of distributed energy resources by the Energy Policy Act of 2005. Individual states have the ability to enforce such industry standards. WAC 480-108-020 specifies technical requirements for Tier 1, Tier 2, and Tier 3 interconnections, where each tier is defined by nameplate capacity. A technical requirement for Tier 2 and Tier 3 interconnections is for the generating facility to comply with the IEEE 1547 standard. For this reason, the Company will continue to adhere to IEEE 1547 as currently written along with any future revision of the standard.

#### Future Actions

Pacific Power will await a revised IEEE 1547 standard to update internal interconnection standards and policies due to the existing effort to revise IEEE 1547, which is anticipated to encapsulate requirements found in IEEE 1547a. Pacific Power intends to implement the advanced inverter functionality recommendations to be defined in the IEEE 1547 standard. Until publishing of the new standard occurs, it is Pacific Power’s practice to require advanced inverter functionalities under circumstances where distribution system constraints warrant their use. For instance, a distribution circuit with voltage regulation issues may require additional VAR support from a distributed energy resource interconnection to accommodate the interconnection. Advanced inverter functionalities can provide the additional VAR support.

### Electric Vehicle (EV) Charging Infrastructure

Pacific Power continues to experience slower-than-anticipated growth of EVs in its service territory. Based on projected growth, large-scale deployment of EVs is expected to have limited impact to the Company’s distribution network.

Pacific Power continues to engage with its stakeholders to facilitate public charging infrastructure development and opportunities and is participating in the Commission staff investigation in Docket UE-160799.

In Oregon, Senate Bill 1547, known as the Clean Electricity and Coal Transition Act, reaffirms the state’s commitment to transportation electrification. The bill encourages developing programs and infrastructure necessary for increased usage of electricity to provide power to all or part of a vehicle for energy efficiency and carbon reduction purposes.

In California, the Company provided letters of support to applicants seeking funding from the California Public Utilities Commission (CPUC) for the purpose of establishing EV charging infrastructure. If successful, the additional EV infrastructure investments would further efforts to complete the West Coast Green Highway. Funding from CPUC would also support programs and planning efforts related to the implementation of EV infrastructure.

In Washington, RCW 80.28.360 authorizes the Utilities and Transportation Commission to allow an incentive rate of return on electric utility investment in electric vehicle supply equipment that is deployed for the benefit of ratepayers. On June 24, 2016, the Commission issued a Notice of Inquiry into Issuing a Policy-Interpretive Statement Describing Commission Policy Related to Utility Investment in Electric Vehicle Supply Equipment. The Company submitted comments in response to the questions posed by the Commission and will continue to monitor developments in this docket and form its Washington electric vehicle strategy accordingly.

In Utah, Senate Bill 115, known as the Sustainable Transportation and Energy Plan Act (STEP), is an effort to reduce emissions from fossil-fuel power plants, explore new methods to utilize battery storage and solar systems, and expand EV charging stations. Some primary goals of STEP include:

Reduced emissions through increased EV usage in the Utah market.

Continued investments in energy efficiency measures that deliver energy savings.

Maintain stable and low electricity prices for Utah customers through a proactive approach.

Increased cognizance of customer charging patterns in relation to coincident system peaks for operational considerations within the distribution network

#### Future Actions

The Company is researching the feasibility of transportation electrification programs throughout its service territories.

# Roadmap to Grid Modernization

Development of an objective roadmap must consider the economic value of individual components, technology maturity and interdependencies. Although funding levels will vary, the Company’s 10-year capital plan provides for investment for the current roadmap. In addition, funding is planned for smart grid technologies expected to be leveraged by the implementation of AMI, such as data analytics, outage management, and distribution automation.

A roadmap of Pacific Power’s current and anticipated grid modernization investments is shown in Figure 5. The distribution automation pilot project in Walla Walla will begin with recloser installation in 2016, followed by communications and system integration in 2017, and FDIR enabled in 2018. Oregon AMI network build-out and meter deployment begins in Q2 2016 with expected completion in 2019. CYME circuit analysis software implementation will be complete by Q4 2016. NERC MOD-33 requirements will be met by enforcement date of May 2017. A transportation electrification initiative will be proposed to satisfy Oregon Senate Bill 1547 by the end of 2016. Oregon irrigation load control programs will continue through 2020. Participation in the IEEE 1547 working group will continue with an anticipated balloting in Q4 2016, publication in Q2 2017 and approval in 2018.

Figure 5 – Smart Grid Roadmap

# Conclusion

Pacific Power continues to develop a strategy to attain long-term goals for grid modernization and smart grid related activities to continually improve system efficiency, reliability, and safety, while providing a cost-effective service to customers. Pacific Power continues to monitor smart grid technologies and determine viability and applicability of implementation to the Company’s system.

# Appendix A – Summary of Project Updates

Project status and timeline is summarized in Table 3.

Table 3 – Summary of Project Updates

| Topic | Project | Status | Cost | Benefit | Future Actions and Timeline |
| --- | --- | --- | --- | --- | --- |
| Dynamic Line Rating | West-of-Populus | Deployed. Evaluation ongoing | Installed cost of $2.37m Ongoing engineering costs for evaluation | Increased line capacity based on ambient weather conditions | West-of-Populus project fully functional. |
| Transmission synchrophasors | Evaluation of model validation process (NERC MOD-033). | In progress | Ongoing engineering costs. Estimated costs of $67,000 per identified | Improved planning dynamic model with actual system response data | Model validation evaluation process; expected 2017. |
| Centralized Energy Storage Assessment | Washington Clean Energy Fund 2 | Cancelled | Estimated installed cost of $10.1m for 8MWh BESS system | Offset of T&D deferral, Improved reliability and resiliency. | Project cancelled |
|  | DER Alternatives Template | Complete | Internal engineering costs to develop template | Potential use of DER to offset or defer traditional transformer upgrade or replacement | Deployed for use throughout Company. |
|  | Wapato Circuit Analysis | Complete | Internal engineering study costs | Potential use of DER to offset or defer traditional system reinforcement project | Additional details on analysis and cost comparisons provided in Appendix E. |
|  | Distribution Substation Metering | Pilot | $15k per meter. Ongoing $20 per month per meter for cellular connection | Enhanced monitoring capabilities for increased visibility of loading and voltage levels on high DER penetration circuits | Under evaluation; expected deployment by end of 2016. |
| Communicating Faulted Circuit Indicators | Cost-benefit analysis | In progress | Installed cost $40k (16 sites) Ongoing $15 per month per site for data | Quantifiable reliability analysis of CFCI deployment | Expected 2017. |
|  | SCADA integration | Delayed deployment | Estimated $55k for integration cost | Improved visibility of fault and outage events for further analysis and potential reliability enhancement | Dependent on Monarch implementation; expected 2017. |
| Distribution Automation and Reliability Analysis | Walla Walla DA Pilot Project | In Progress | Estimated $60k for recloser installation. Communications and system integration scoping in progress | Estimated 10-15% improvement in reliability | Recloser installation in 2016, communications and integration in 2017, and FDIR enabled in 2018. |
|  | Fuse Saving device deployment and SCADA integration. | Complete. SCADA integration launched. | $4000 per installed device | 80% reduction in MAIFI. Impact to other customers still under investigation | Offered as standard device option. SCADA integration dependent on Monarch implementation; expected 2017. |
|  | Feasibility of conducting study to determine DA device implementation | In progress | Estimated $30k per switching device. Additional costs, including communications and OMS integration, are being investigated. | Improved reliability (SAIDI, SAIFI) and potential reduction in avoided CMI and CI costs. Based on 2016 reliability project costs, $26 per avoided CMI and $125 per avoided CI are thresholds for DA evaluation. | Feasibility study will analyze reduction in SAIDI/SAIFI and associated costs. |
| Circuit Analysis Software (CYME) | Ongoing software deployment | In progress | Confidential and proprietary | Improved customer load modeling and time series analysis to provide more accurate planning scenarios. Varied cost savings from potential enhanced utilization of existing assets. | Complete integration expected by end of 2016. |
| Advanced Metering Infrastructure for Oregon Customers | Implementation of Advanced Metering Infrastructure in Oregon | In progress | Confidential and proprietary | Improved customer service, reduced O&M expenses, and provides platform for future Smart Grid applications. | Anticipated project completion date 2019. See Table 2. |
| Customer Communications and Programs | Lessons learned from irrigation pilot program | Complete | N/A | Potential increased participation in future irrigation pilot programs | See Section IV.E.4. |
|  | Customer web portal | In progress | Cost included in AMI total capital cost | Allow customers to monitor and manage energy consumption | Released with AMI project completion. See Table 2. |
| Demand Response - Irrigation Load Control | Initiation of pilot program in California and Oregon | Active deployment in Oregon | Confidential and proprietary. Aggregated costs may be available post-irrigation season. | Reduced load during periods of peak demands | California deployment expected 2017. |
| Demand Response - Cool Keeper AC Direct Load Control | Network upgrade complete | Complete | Confidential and proprietary | Increased bandwidth and direct monitoring for enhanced situational awareness of real-time operations and resource availability | No planned updates at this time. |
| Smart Inverters | Ongoing development of standards | In progress | Ongoing engineering costs | Improved system stability and reliability with increasing levels of DER. | Continued participation in workgroup. Publication of IEEE 1547 expected 2018. |
| Electric Vehicle Infrastructure | Initiation of Oregon SB 1547-B - Clean Electricity and Coal Transition Plan | In progress | Ongoing engineering costs to develop Transportation Electrification proposal | Development of programs and infrastructure necessary to provide power to electric vehicles | Ongoing development and coordination with OPUC. |
|  | Initiation of Utah Senate Bill 115 - Sustainable Transportation and Energy Program | In progress | Ongoing engineering costs to develop proposal | Reduced emissions from fossil-fuel plants and increased EV charging stations | Ongoing development and coordination with Utah PSC. |

# Appendix B – Dynamic Line Rating

Line flow, ratings, and conductor temperature for the Populus-Kinport 345 kV line on the West-of-Populus path are shown in Figure 6.

Figure 6 – Dynamic Line Rating for West of Populus

# Appendix C – Locations of Equipment for MOD-033 Requirement

Locations considered for equipment to provide the data necessary to satisfy MOD-033 requirement are listed in Table 4.

Table 4 – Locations Identified for MOD-033 Requirement

| Pacific Power | Rocky Mountain Power |
| --- | --- |
| Burns | 90th South |
| Dixonville 500 | Ben Lomond |
| Fry | Camp Williams |
| Hermiston Plant | Clover |
| JC Boyle | Dave Johnston |
| Klamath Co-Gen | Emery |
| Knott | Goshen |
| Leaning Juniper | Huntington |
| Malin | Jim Bridger |
| Meridian | Midvalley |
| Merwin | Mona/Current Creek |
| Pomona Heights | Naughton |
| Swift 1 | Oquirrh |
| Troutdale | Pinto |
| Union Gap | Point of Rocks |
| Wallula | Populus |
| Yale | Red Butte |
|  | Sigurd |
|  | Spanish Fork |
|  | Steel Mill/Lakeside 2 |
|  | Terminal |
|  | Windstar |

# Appendix D – MOD-033 Model Validation

Figure 7 shows the input PMU voltage data of actual system voltage compared against a power flow model. Figures 8 and 9 show the actual PMU data and model responses with respective validated and non-validated models. The combination of these comparisons, accompanied by guidelines for unacceptable results, is essential to satisfying the requirements.

Figure 7 – PMU Input Data

Figure 8 – Actual PMU Data Validates Model

Figure 9 – Actual PMU Data Invalidates Model

# Appendix E – DER Example Template

The following DER alternative solutions template was applied to the Wapato 5Y202 circuit:

# Appendix F – Distribution Substation Metering Technical Requirements

- All installations will be engineered, prints issued, and as-builts processed.

- Meters will use existing current and potential transformers.

- Meters will use existing meter panel cutouts if available. Panel modification will be limited to hole drilling only. New panels or panel cutting will be avoided to control costs.

- There will also be a design available where no convenient panel space is available, possible using transducer only versions of available meters.

- The number of meter styles used will be held to a minimum to reduce training costs of meter and relay technicians.

- Spares for the meters purchased will be available in stores for long-term support.

- All meters will be configured to measure and record all three-phase quantities.

- For installation without all three potentials available the meter will have ability to simulate the missing phases. The provided phase can be any phase available.

- Meters will be configured so that that the recorded phases are consistent with system vectors.

- Installed stand-alone meters will be easily upgradable so that they can be incorporated into SCADA if it becomes available at the metering point.

- The meters will support DNP, 61850 Ethernet as well as have analog outputs.

- Meters will have available at least six analog outputs.

  - Meters will read and store internally per phase: kW, kVAR, current, power factor, frequency, accumulated energy, harmonics, and recorded waveforms generated when programed limits are exceeded.

  - Meters need to have the ability to record waveforms of all phases at the same time.

- Meters will have the ability to be read by cellular phone.

- Stand-alone meters will have the ability to store all quantities for one a least one year. This is in case they are read on a periodic basis (i.e. monthly, quarterly, or yearly).

- Ideally the meters would have an adjustable storage rate to allow for different storage rates bases upon the expected read interval.

- Meters will have the ability for live and periodic data reads to be moved into MV90 so they can be transferred into the SCHOOL PI database.

# Appendix G – Washington Clean Energy Fund 2 Grant Application

Washington Clean Energy Fund 2 Phase 1 application for Grandview BESS project:

# Appendix H – Pacific Power Net Metering and Customer Generation

Monthly net metering and customer generation report for July 2016:

NERC. NERC: Project 2010-03 Modeling Data (MOD B) [Online]. Available:-http://www.nerc.com/pa/Stand/Pages/Project2010-03ModelingData(MOD-B).aspx

Standard PRC-002-NPCC-01 – Disturbance Monitoring. NERC Reliability Standards [Online]. Available: http://www.nerc.com/files/PRC-002-NPCC-01.pdf

NREL’s PVWatts Calculator. National Renewable Energy Laboratory [Online]. Available: http://pvwatts.nrel.gov/

Clean Energy Fund 2 (2015-2017 Biennium). State of Washington Department of Commerce [Online]. Available: http://www.commerce.wa.gov/Programs/Energy/Office/Pages/Clean-Energy-Funds-2.aspx

PacifiCorp, 2015 Integrated Resource Plan Update I [Online]. Page 50. Available:

http://www.pacificorp.com/content/dam/pacificorp/doc/Energy_Sources/Integrated_Resource_Plan/2015%20IRP%20Update/2015%20IRP%20Update_20160426.pdf

PacifiCorp Schedule 105, Docket No. ADV 242. Oregon Public Utility Commission [Online]. Available: http://apps.puc.state.or.us/edockets/docket.asp?DocketID=20031

U.S. Department of Energy. Time-Based Rate Programs [Online]. Available: http://www.smartgrid.gov/recovery_act/deployment_status/time_based_rate_programs

PacifiCorp Irrigation Time of Use Schedule 215, Docket No. RE 153. Oregon Public Utility Commission [Online]. Available: http://apps.puc.state.or.us/edockets/docket.asp?DocketID=19304

PacifiCorp Schedule 215 – Time-of-Use Pilot Supply Service. Docket No. ADV 224. Oregon Public Utility Commission [Online]. Available: http://apps.puc.state.or.us/edockets/docket.asp?DocketID=19999

Idaho Regulatory Information. Rocky Mountain Power [Online]. Available: https://www.rockymountainpower.net/about/rar/iri.html.

Oregon Regulatory Information. Pacific Power [Online]. Available: https://www.pacificpower.net/about/rr/ori.html

U.S. Energy Information Administration (2015). Annual Energy Outlook [Online]. Table A16 p A-31. Available: https://www.eia.gov/forecasts/aeo/pdf/tbla16.pdf

IEEE 1547 Standard for Interconnecting Distributed Resources with Electric Power Systems. IEEE [Online]. Available: http://grouper.ieee.org/groups/scc21/1547/1547_index.html

UL 1741 Standard for Inverters, Converters, Controllers and Interconnection System Equipment for Use With Distributed Energy Resources. Underwriters Laboratories [Online]. Available: http://ulstandards.ul.com/standard/?id=1741_2

Oregon Senate Bill 1547. Oregon State Legislature [Online]. Available: https://olis.leg.state.or.us/liz/2016R1/Measures/Overview/SB1547

Effected by Washington Laws 2015, c 220 § 2 (June 24, 2015).

Utah Senate Bill 1547. Utah State Legislature [Online]. Available: http://le.utah.gov/~2016/bills/static/SB0115.html