## QTRLY-SUM
Mint Farm Energy Center, LLC
2nd QUARTER 2008
CT/HRSG |  |  |  | Total
|  |  |  | THIS | PREV | 12 Mth
Month | Apr | May | Jun | QTR | 3 QTRs | RLG TOT
CT Hours | 638.93 | 52.18 | 0 | 691.11 | 1788.12 | 2479.23
HRSG - Duct Burners Hrs | 8.88 | 0 | 0 | 8.88 | 42.37 | 51.25
Fuel Use (KSCF) | 1080224 | 82183 | 0 | 1162407 | 2895979.7 | 4058386.7
BTU/SCF | 1033 | 1027
Heat Input (MMBTU) | 1115871.392 | 84401.941 | 0 | 1200273.333 | 2953899.2 | 4154172.533
Annual Capacity Factor |  | N/A
Factor (lb/MMBtu) |  | From CEMS
NOx (lbs) | 12000 | 1800 | 0 | 13800 | 47682.59 | 61482.59
Factor (lb/MMBtu) |  | From CEMS
CO (lbs) | 2000 | 1000 | 0 | 3000 | 83434.53 | 86434.53
Factor (lb/MMBtu) |  | 0.0006
SO2 (lbs) | 669.5228 | 50.6412 | 0 | 720.164 | 1772.34 | 2492.504
Factor (lb/MMBtu) |  | 0.0043
PM (lbs) | 4798.247 | 362.9283 | 0 | 5161.1753 | 15064.89 | 20226.0653
Factor (lb/MMBtu) |  | 0.0003
VOC (lbs) | 334.7614 | 25.3206 | 0 | 360.082 | 21302.6 | 21662.682
Factor (lb/MMBtu) |  | From PEMS
NH3 (lbs) | 733.0266 | 44.4101 | 0 | 777.4367 | 849.65 | 1627.0867
Cooling Tower Hrs* | 638.93 | 52.18 | 0 | 691.11 | 1788.12 | 2479.23
Diesel Fire Pump Hrs | N/A | N/A | N/A | N/A | N/A | N/A
Emergency Generator Hrs | 1 | 0 | 3 | 4 | 14 | 18
Fuel Preheater Hrs | N/A | N/A | N/A | N/A | N/A | N/A
*Assume Cooling Tower Operating hours equals Combustion Turbine operating hours
Note on D22: .0043 utilized based on Feb 08 stack testing
Note on D24: .0003 utilized based on Feb 08 stack testing

## Summary of CT hours
Summary of GT Fired Hours
Date | CT Fire St Hr | CT Fire St Min | Trip/End Hr | Trip/ End Min | Total Fired Hrs
2008-04-01 |  |  | 24 |  | -24
2008-04-02 |  |  | 24 |  | -24
2008-04-03 |  |  | 24 |  | -24
2008-04-04 |  |  | 24 |  | -24
2008-04-05 |  |  | 24 |  | -24
2008-04-06 |  |  | 6 | 35 | -6.5833
2008-04-06 | 8 | 48 | 23 | 19 | -14.5167
2008-04-07 | 8 | 22 | 24 |  | -15.6333
2008-04-08 |  |  | 24 |  | -24
2008-04-09 |  |  | 24 |  | -24
2008-04-10 |  |  | 24 |  | -24
2008-04-11 |  |  | 24 |  | -24
2008-04-12 |  |  | 24 |  | -24
2008-04-13 |  |  | 24 |  | -24
2008-04-14 |  |  | 24 |  | -24
2008-04-15 |  |  | 24 |  | -24
2008-04-16 |  |  | 0 | 20 | -0.33333
2008-04-16 | 4 | 0 | 24 |  | -20
2008-04-17 |  |  | 24 |  | -24
2008-04-18 |  |  | 24 |  | -24
2008-04-19 |  |  | 24 |  | -24
2008-04-20 |  |  | 1 | 18 | -1.3
2008-04-20 | 6 | 53 | 8 | 8 | -1.25
2008-04-20 | 10 | 3 | 12 | 5 | -2.0333
2008-04-20 | 12 | 5 | 24 |  | -11.9167
2008-04-21 |  |  | 24 |  | -24
2008-04-22 |  |  | 24 |  | -24
2008-04-23 |  |  | 22 | 15 | -22.25
2008-04-24 | 4 | 57 | 22 | 22 | -17.4167
2008-04-25 | 3 | 57 | 22 | 16 | -18.3167
2008-04-26 | 3 | 57 | 22 | 17 | -18.3333
2008-04-27 |  |  | 0 |  | 0
2008-04-28 | 2 | 59 | 23 | 22 | -20.3833
2008-04-29 | 3 | 57 | 22 | 16 | -18.3167
2008-04-30 | 4 | 1 | 22 | 22 | -18.35
-638.9333
| CT Fire St Hr | CT Fire St Min | Trip/End Hr | Trip/ End Min | Total Fired Hrs
2008-05-01 | 4 | 0 | 22 | 22 | -18.3667
2008-05-02 |  |  |  |  | 0
2008-05-03 |  |  |  |  | 0
2008-05-04 |  |  |  |  | 0
2008-05-05 | 1 | 53 | 22 | 19 | -20.4333
2008-05-06 | 4 | 53 | 18 | 16 | -13.3833
2008-05-07 |  |  |  |  | 0
2008-05-08 |  |  |  |  | 0
2008-05-09 |  |  |  |  | 0
2008-05-10 |  |  |  |  | 0
2008-05-11 |  |  |  |  | 0
2008-05-12 |  |  |  |  | 0
2008-05-13 |  |  |  |  | 0
2008-05-14 |  |  |  |  | 0
2008-05-15 |  |  |  |  | 0
2008-05-16 |  |  |  |  | 0
2008-05-17 |  |  |  |  | 0
2008-05-18 |  |  |  |  | 0
2008-05-19 |  |  |  |  | 0
2008-05-20 |  |  |  |  | 0
2008-05-21 |  |  |  |  | 0
2008-05-22 |  |  |  |  | 0
2008-05-23 |  |  |  |  | 0
2008-05-24 |  |  |  |  | 0
2008-05-25 |  |  |  |  | 0
2008-05-26 |  |  |  |  | 0
2008-05-27 |  |  |  |  | 0
2008-05-28 |  |  |  |  | 0
2008-05-29 |  |  |  |  | 0
2008-05-30 |  |  |  |  | 0
2008-05-31 |  |  |  |  | 0
0
-52.1833
| CT Fire St Hr | CT Fire St Min | Trip/End Hr | Trip/ End Min | Total Fired Hrs
2008-06-01 |  |  |  |  | 0
2008-06-02 |  |  |  |  | 0
2008-06-03 |  |  |  |  | 0
2008-06-04 |  |  |  |  | 0
2008-06-05 |  |  |  |  | 0
2008-06-06 |  |  |  |  | 0
2008-06-07 |  |  |  |  | 0
2008-06-08 |  |  |  |  | 0
2008-06-09 |  |  |  |  | 0
2008-06-10 |  |  |  |  | 0
2008-06-11 |  |  |  |  | 0
2008-06-12 |  |  |  |  | 0
2008-06-13 |  |  |  |  | 0
2008-06-14 |  |  |  |  | 0
2008-06-15 |  |  |  |  | 0
2008-06-16 |  |  |  |  | 0
2008-06-17 |  |  |  |  | 0
2008-06-18 |  |  |  |  | 0
2008-06-19 |  |  |  |  | 0
2008-06-20 |  |  |  |  | 0
2008-06-21 |  |  |  |  | 0
2008-06-22 |  |  |  |  | 0
2008-06-23 |  |  |  |  | 0
2008-06-24 |  |  |  |  | 0
2008-06-25 |  |  |  |  | 0
2008-06-26 |  |  |  |  | 0
2008-06-27 |  |  |  |  | 0
2008-06-28 |  |  |  |  | 0
2008-06-29 |  |  |  |  | 0
2008-06-30 |  |  |  |  | 0
Note on E3: GE Transportation: Time that flame is out.
Note on E42: GE Transportation: Time that flame is out.
Note on E82: GE Transportation: Time that flame is out.

## Summary of Duct burner hours
Duct Burner Operating Time
| DUCT BURNER |  | OPER
DATE | ON | OFF | TIME
2008-04-05 | 15:27 | 23:20 | 8.88
|  | Total: | 8.88

## April CEMS data
Note: NH3 data is not collected by the CEMS; please see monthly "PEMS" worksheets for calculated NH3 slip information
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-01
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 15.4 | 0.1 | 0.3 | 0 | 0.23181 | 0.55248 | 678 | 191.7
| 1 | 2.1 | 2.1 | 15.4 | 0.1 | 0.3 | 0 | 0.22114 | 0.52773 | 678 | 192
| 2 | 2.1 | 2.1 | 15.4 | 0.1 | 0.3 | 0 | 0.22824 | 0.5439 | 678 | 192.1
| 3 | 2.1 | 2.1 | 15.4 | 0 | 0 | 0 | 0.23537 | 0.55968 | 678 | 192.1
| 4 | 2.1 | 2.1 | 15.3 | 0 | 0 | 0 | 0.24657 | 0.58372 | 678 | 192
| 5 | 2.1 | 2.1 | 15.3 | 0.1 | 0.3 | 0 | 0.32582 | 0.76857 | 678 | 192
| 6 | 2.1 | 2.1 | 15.4 | 0.1 | 0.3 | 0 | 1.2663 | 2.321 | 678 | 192
| 7 | 2 | 2.1 | 15.3 | 0 | 0 | 0 | 1.1012 | 2.2343 | 678 | 192
| 8 | 2.1 | 2.1 | 15.3 | 0.1 | 0.3 | 0 | 0.4014 | 0.93168 | 678 | 191.1
| 9 | 2.1 | 2.1 | 15.1 | 0.1 | 0.3 | 0 | 0.44937 | 1.0359 | 678 | 188.4
| 10 | 2.1 | 2.1 | 15 | 0.1 | 0.3 | 0 | 0.48998 | 1.1166 | 676.8 | 186.5
| 11 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.49533 | 1.1269 | 676.1 | 185.2
| 12 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.52364 | 1.1806 | 675.3 | 184.4
| 13 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.55543 | 1.2444 | 674.9 | 183.6
| 14 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.56059 | 1.2559 | 673.7 | 182.9
| 15 | 2.1 | 2.1 | 14.7 | 0.1 | 0.3 | 0 | 0.5765 | 1.2886 | 672.5 | 182.6
| 16 | 2.1 | 2.1 | 14.7 | 0.1 | 0.3 | 0 | 0.5838 | 1.3008 | 672.5 | 182.2
| 17 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.56505 | 1.2607 | 672.5 | 182.8
| 18 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.56441 | 1.2592 | 672.9 | 183.5
| 19 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.53287 | 1.1953 | 674.9 | 184.7
| 20 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.48376 | 1.0934 | 675.7 | 185.5
| 21 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.40522 | 0.91629 | 676.8 | 186.4
| 22 | 2.1 | 2.1 | 15 | 0.1 | 0.3 | 0 | 0.39146 | 0.88873 | 676.5 | 186.9
| 23 | 2.2 | 2.1 | 11.1 | 0.1 | 0.2 | 0 | 0 | 0 | 642.9 | 124.6
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-02
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 11.4 | 0.1 | 0.2 | 0 | 0.098555 | 0.17451 | 639 | 128.4
| 1 | 2.1 | 2.1 | 11.4 | 0.1 | 0.2 | 0 | 0.10635 | 0.18777 | 639 | 128.6
| 2 | 2.1 | 2.1 | 11.4 | 0.2 | 0.5 | 0 | 0.13189 | 0.23388 | 639 | 129.4
| 3 | 2 | 2.1 | 15.3 | 0.1 | 0.3 | 0 | 0.38898 | 0.89708 | 672.1 | 189.6
| 4 | 2.1 | 2.1 | 15 | 0.1 | 0.3 | 0 | 0.30693 | 0.70791 | 673.7 | 187
| 5 | 1.7 | 2.1 | 11.3 | 0.1 | 0.3 | 0 | 0.34057 | 0.78751 | 674.1 | 187.6
| 6 | 1.8 | 2.1 | 11.3 | 3 | 12.6 | 0 | 1.9111 | 3.0668 | 674.5 | 187.9
| 7 | 2.1 | 2.1 | 15.2 | 0.1 | 0.3 | 0 | 0.3437 | 0.79366 | 677.2 | 188.7
| 8 | 2.1 | 2.1 | 15 | 0.1 | 0.3 | 0 | 0.4076 | 0.92624 | 677.6 | 187.2
| 9 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.51547 | 1.1662 | 676.5 | 185.8
| 10 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.51848 | 1.1669 | 674.5 | 184
| 11 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.56678 | 1.2698 | 674.9 | 183
| 12 | 1.5 | 2 | 8.3 | 0.1 | 0.2 | 0 | 0.090014 | 0.15592 | 642.9 | 124.7
| 13 | 2.1 | 2 | 11.3 | 0.1 | 0.2 | 0 | 0.096431 | 0.16963 | 637.8 | 128.4
| 14 | 2.1 | 2 | 11.3 | 0.1 | 0.2 | 0 | 0.10618 | 0.18677 | 637.4 | 128.6
| 15 | 2.1 | 2 | 11.3 | 0.1 | 0.2 | 0 | 0.10612 | 0.18739 | 637.8 | 129
| 16 | 2.1 | 2 | 11.3 | 0.1 | 0.2 | 0 | 0.10767 | 0.18891 | 637.4 | 128.5
| 17 | 2.1 | 2 | 11.3 | 0.1 | 0.2 | 0 | 0.10141 | 0.17854 | 637 | 128.5
| 18 | 2.1 | 2 | 11.3 | 0.2 | 0.5 | 0 | 0.08623 | 0.15095 | 636.6 | 127.9
| 19 | 2.1 | 2 | 11.3 | 0.2 | 0.5 | 0 | 0.064929 | 0.11416 | 636.6 | 128.1
| 20 | 2.1 | 2 | 11.4 | 0.2 | 0.5 | 0 | 0.047741 | 0.084429 | 635.4 | 128.3
| 21 | 2.1 | 2 | 11.4 | 0.2 | 0.5 | 0 | 0.030713 | 0.05427 | 635.8 | 128.4
| 22 | 2.1 | 2 | 11.4 | 0.2 | 0.5 | 0 | 0.043798 | 0.077572 | 636.2 | 128.9
| 23 | 2.1 | 2 | 11.4 | 0.2 | 0.5 | 0 | 0.036814 | 0.065088 | 636.6 | 128.6
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-03
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2 | 11.4 | 0.2 | 0.5 | 0 | 0.027306 | 0.048278 | 637 | 127.9
| 1 | 2.1 | 2 | 11.4 | 0.2 | 0.5 | 0 | 0.030047 | 0.053155 | 637 | 128
| 2 | 2.1 | 2 | 11.5 | 0.2 | 0.5 | 0 | 0.037846 | 0.067575 | 638.2 | 129.3
| 3 | 2.1 | 2 | 11.5 | 0.2 | 0.5 | 0 | 0.041374 | 0.073704 | 638.6 | 129.1
| 4 | 2.1 | 2 | 11.7 | 0.2 | 0.5 | 0 | 0.14085 | 0.25541 | 639 | 132.8
| 5 | 2 | 2.1 | 15.2 | 0.1 | 0.3 | 0 | 0.3757 | 0.86968 | 673.7 | 190.4
| 6 | 2.2 | 2.1 | 15.3 | 1.2 | 5.3 | 0 | 1.927 | 3.107 | 677.6 | 190.8
| 7 | 1.9 | 2.1 | 13.3 | 0.2 | 0.7 | 0 | 0.72251 | 1.6814 | 677.2 | 189.4
| 8 | 2.1 | 2.1 | 15.2 | 0.1 | 0.3 | 0 | 0.54811 | 1.2645 | 677.6 | 189.2
| 9 | 2.1 | 2.1 | 15.1 | 0.1 | 0.3 | 0 | 0.69557 | 1.5889 | 677.6 | 187.4
| 10 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.74393 | 1.6792 | 676.1 | 185.3
| 11 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.75917 | 1.6992 | 674.5 | 183.2
| 12 | 2.1 | 2.1 | 14.7 | 0.1 | 0.3 | 0 | 0.77354 | 1.7236 | 672.9 | 181.8
| 13 | 2 | 2.1 | 14.5 | 0.1 | 0.3 | 0 | 0.72994 | 1.6171 | 671.7 | 179.8
| 14 | 2.2 | 2.1 | 14.5 | 0.1 | 0.3 | 0 | 0.84781 | 1.8661 | 672.1 | 179.8
| 15 | 2.1 | 2.1 | 14.5 | 0.1 | 0.3 | 0 | 0.84539 | 1.8489 | 669.7 | 179.1
| 16 | 2.1 | 2.1 | 14.5 | 0.1 | 0.3 | 0 | 0.83413 | 1.8217 | 669.3 | 179.1
| 17 | 2.1 | 2.1 | 14.6 | 0.1 | 0.3 | 0 | 0.80091 | 1.7595 | 671.3 | 180.4
| 18 | 2.1 | 2.1 | 14.6 | 0.1 | 0.3 | 0 | 0.73839 | 1.6289 | 671.7 | 181.3
| 19 | 2.1 | 2.1 | 14.7 | 0.1 | 0.3 | 0 | 0.75623 | 1.6772 | 672.9 | 183.3
| 20 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.74443 | 1.6495 | 673.3 | 184
| 21 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.70606 | 1.5687 | 674.5 | 184
| 22 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.70288 | 1.5685 | 674.9 | 185
| 23 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.68056 | 1.5193 | 674.9 | 185.3
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-04
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.68303 | 1.5255 | 674.5 | 185.3
| 1 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.67901 | 1.5158 | 674.9 | 185.3
| 2 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.68511 | 1.5294 | 674.5 | 185.3
| 3 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.6958 | 1.5533 | 675.7 | 185.3
| 4 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.70809 | 1.5751 | 675.3 | 185.2
| 5 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.65436 | 1.4707 | 674.5 | 185.2
| 6 | 1.9 | 2.1 | 12.9 | 0.4 | 1.7 | 0 | 2.0387 | 3.1244 | 674.9 | 184.8
| 7 | 2 | 2.1 | 12.9 | 0.1 | 0.3 | 0 | 0.5884 | 1.3015 | 674.1 | 183.4
| 8 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.59033 | 1.3098 | 674.1 | 184.1
| 9 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.72253 | 1.5943 | 674.1 | 185.2
| 10 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.65806 | 1.4528 | 674.5 | 184.7
| 11 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.64517 | 1.4243 | 672.9 | 184.2
| 12 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.61816 | 1.3689 | 673.3 | 184.7
| 13 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.66154 | 1.4598 | 673.3 | 183.6
| 14 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.65757 | 1.4563 | 672.5 | 184.3
| 15 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.64097 | 1.4157 | 672.9 | 184
| 16 | 2.1 | 2.1 | 14.7 | 0.1 | 0.3 | 0 | 0.64629 | 1.4255 | 672.5 | 183.5
| 17 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.63035 | 1.391 | 672.5 | 184
| 18 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.62473 | 1.3786 | 673.3 | 184.6
| 19 | 2.1 | 2.1 | 14.8 | 0.1 | 0.3 | 0 | 0.61837 | 1.3707 | 674.5 | 185.1
| 20 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.599 | 1.3361 | 674.5 | 185.2
| 21 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.58353 | 1.3063 | 674.5 | 185.6
| 22 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.58454 | 1.3085 | 675.3 | 186
| 23 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.59368 | 1.3272 | 676.5 | 185.8
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-05
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.6063 | 1.3535 | 676.5 | 186.2
| 1 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.57975 | 1.2948 | 676.5 | 186.2
| 2 | 2.1 | 2.1 | 14.9 | 0.1 | 0.3 | 0 | 0.59549 | 1.3294 | 676.5 | 186.3
| 3 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.59278 | 1.3215 | 676.5 | 186.8
| 4 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.60794 | 1.3559 | 677.2 | 187.1
| 5 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.30327 | 0.73277 | 677.2 | 187.2
| 6 | 2 | 2.1 | 13.1 | 0 | 0 | 0 | 2.1908 | 3.2694 | 677.2 | 186.9
| 7 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.64846 | 1.445 | 676.8 | 186
| 8 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.62036 | 1.3713 | 676.5 | 185.1
| 9 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.66342 | 1.4619 | 674.9 | 183.9
| 10 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.65595 | 1.4428 | 674.1 | 183.1
| 11 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.6356 | 1.3918 | 672.5 | 182.8
| 12 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.64347 | 1.4052 | 672.5 | 182.5
| 13 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.67171 | 1.4682 | 672.5 | 182.8
| 14 | 2.1 | 2.1 | 18.8 | 0.2 | 0.8 | 0 | 0.53001 | 1.1821 | 676.1 | 182.8
| 15 | 2.2 | 2.1 | 18.8 | 0 | 0 | 0 | 0.79401 | 1.6719 | 753.8 | 182.1
| 16 | 2.1 | 2.1 | 18.8 | 0 | 0 | 0 | 0.82692 | 1.741 | 758.5 | 181.8
| 17 | 2.1 | 2.1 | 18.8 | 0 | 0 | 0 | 0.83717 | 1.7596 | 755.8 | 181.8
| 18 | 2 | 2.1 | 16.4 | 0 | 0 | 0 | 0.89585 | 1.8796 | 758.5 | 181.9
| 19 | 2 | 2.1 | 16.4 | 0 | 0 | 0 | 0.89234 | 1.8737 | 758.5 | 182.4
| 20 | 2.1 | 2.1 | 18.8 | 0 | 0 | 0 | 0.89939 | 1.8848 | 758.5 | 182.3
| 21 | 2 | 2.1 | 16.4 | 0 | 0 | 0 | 0.93008 | 1.9559 | 758.2 | 182.5
| 22 | 2 | 2.1 | 16.4 | 0.1 | 0.4 | 0 | 0.74902 | 1.6043 | 684.3 | 182.7
| 23 | 2.1 | 2.1 | 14.6 | 0.2 | 0.6 | 0 | 0.70827 | 1.5252 | 672.9 | 182.6
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-06
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 14.6 | 0.2 | 0.6 | 0 | 0.71806 | 1.5477 | 672.5 | 182.7
| 1 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.71022 | 1.5329 | 672.9 | 182.9
| 2 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.69919 | 1.5145 | 672.9 | 182.8
| 3 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.68648 | 1.4944 | 672.9 | 183.1
| 4 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.67268 | 1.4663 | 673.3 | 183.3
| 5 | 2.2 | 2.1 | 13.9 | 0 | 0 | 0 | 0.76876 | 1.5103 | 673.3 | 169.8 |  |  |  | 5:30 | 5:30
| 6 | Offline
| 7 | 46.8 | 2.1 | 65.1 | 0 | 0 | 0 | 0 | 0 | 501.2 | 7.1 | HS | 7:48
| 8 | 55.9X | 2.1 | 176.3 | 0.0X | 0 | 0 | 0 | 0 | 605.8 | 52.1 | HS |  | 9:00 |  |  | Dur 73 min
| 9 | 1.6X | 2.1 | 10.3 | 0.0X | 0 | 0 | 1.6699 | 2.4632 | 644.1 | 169
| 10 | 2.2 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.86307 | 1.8479 | 667.8 | 182.3
| 11 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.77646 | 1.6972 | 672.5 | 182.9
| 12 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.78335 | 1.706 | 672.5 | 182.6
| 13 | 2 | 2.1 | 11 | 0.2 | 0.5 | 0 | 0.26954 | 0.45354 | 643.3 | 124.1
| 14 | 2.1 | 2.1 | 11.3 | 0.2 | 0.5 | 0 | 0.2938 | 0.50538 | 636.6 | 128.2
| 15 | 2.1 | 2.1 | 11.2 | 0.2 | 0.5 | 0 | 0.28637 | 0.49223 | 635.8 | 127.7
| 16 | 2.1 | 2.1 | 11.2 | 0.2 | 0.5 | 0 | 0.27623 | 0.47592 | 636.2 | 127.6
| 17 | 2.2 | 2.1 | 11.5 | 0.2 | 0.5 | 0 | 0.41063 | 0.72192 | 636.2 | 132.4
| 18 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.76405 | 1.6821 | 670.1 | 183.9
| 19 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.67867 | 1.5037 | 672.9 | 183.8
| 20 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.6927 | 1.5443 | 674.5 | 185.2
| 21 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.69376 | 1.544 | 674.9 | 184.1
| 22 | 31.8 | 2.1 | 85.9 | 0 | 0 | 0 | 0 | 0 | 650.4 | 48.3 | SD |  |  | 22:00 | 22:19
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-07
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | 62.2 | 2.1 | 111.6 | 0 | 0 | 0 | 0 | 0 | 502.8 | 12.5 | HS | 7:22
| 8 | 59.3 | 2.1 | 142.5 | 0 | 0 | 0 | 0 | 0 | 603.8 | 27.4 | HS
| 9 | 25.5 | 3.3 | 114.2 | 12.8 | 34.9 | 0 | 0 | 0 | 625.5 | 99.7 |  |  | 9:36 |  |  | Dur 134 min vs. 120 limit
| 10 | 2.1 | 3.3 | 14.9 | 0.2 | 0.6 | 0 | 0.50066 | 1.1209 | 662.6 | 184.7
| 11 | 1.7 | 3.3 | 11.1 | 0 | 0 | 0 | 2.2636 | 4.1557 | 669.7 | 184
| 12 | 2.2 | 3.3 | 14.8 | 0.2 | 0.6 | 0 | 0.5518 | 1.2356 | 672.5 | 183.6
| 13 | 2.1 | 3.3 | 14.8 | 0.2 | 0.6 | 0 | 0.61569 | 1.3755 | 672.5 | 183.8
| 14 | 2.1 | 3.3 | 14.8 | 0.2 | 0.6 | 0 | 0.60393 | 1.3511 | 672.5 | 184.4
| 15 | 2.1 | 3.2 | 14.8 | 0.2 | 0.6 | 0 | 0.61099 | 1.365 | 672.1 | 184
| 16 | 2.1 | 3.2 | 14.8 | 0.2 | 0.6 | 0 | 0.59123 | 1.3274 | 672.1 | 184.9
| 17 | 2.1 | 3.2 | 14.8 | 0.2 | 0.6 | 0 | 0.58875 | 1.3213 | 672.5 | 185
| 18 | 2.1 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 0.57871 | 1.3063 | 674.5 | 185.3
| 19 | 2.1 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 0.56683 | 1.2817 | 674.5 | 186
| 20 | 2 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 0.54673 | 1.2354 | 675.3 | 185.2
| 21 | 2.1 | 3.2 | 14.8 | 0.2 | 0.6 | 0 | 0.57425 | 1.2953 | 676.5 | 185.6
| 22 | 2.1 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 0.58268 | 1.3152 | 676.5 | 186.4
| 23 | 2.1 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 0.99008 | 2.2316 | 676.5 | 186.5
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-08
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 1.3732 | 3.091 | 676.8 | 186.4
| 1 | 2.1 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 1.3671 | 3.073 | 676.8 | 186.4
| 2 | 2.1 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 1.3528 | 3.0408 | 676.8 | 186.6
| 3 | 2.1 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 1.3503 | 3.0351 | 676.8 | 186.7
| 4 | 2.1 | 3.2 | 14.9 | 0.2 | 0.6 | 0 | 1.3476 | 3.0264 | 676.8 | 186.8
| 5 | 2.1 | 3.2 | 15 | 0.2 | 0.6 | 0 | 1.32 | 2.967 | 676.8 | 187.2
| 6 | 2.1 | 3.1 | 14.9 | 0.2 | 0.6 | 0 | 1.3328 | 2.9944 | 677.2 | 187.2
| 7 | 2.1 | 3.1 | 14.9 | 0.2 | 0.6 | 0 | 1.3489 | 3.0225 | 677.2 | 186.3
| 8 | 2.2 | 3.1 | 11.2 | 0.2 | 0.7 | 0 | 0.02987 | 0.042565 | 640.9 | 126.3
| 9 | 2.1 | 2.1 | 14.9 | 0 | 0 | 0 | 0.72062 | 1.5971 | 671.7 | 186
| 10 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.64074 | 1.4357 | 676.8 | 185.5
| 11 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.65234 | 1.4506 | 676.1 | 185.1
| 12 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.66849 | 1.4798 | 674.9 | 184
| 13 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.64243 | 1.4247 | 674.9 | 184.4
| 14 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.63087 | 1.3965 | 674.5 | 184.4
| 15 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.6457 | 1.423 | 672.9 | 183
| 16 | 2.2 | 2.1 | 11.2 | 0.2 | 0.7 | 0 | 0.18085 | 0.31099 | 642.5 | 126.4
| 17 | 2.1 | 2.1 | 11.5 | 0.2 | 0.8 | 0 | 0.35302 | 0.62397 | 639 | 131.8
| 18 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.65944 | 1.4558 | 670.5 | 184.1
| 19 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.61994 | 1.3748 | 674.5 | 185.2
| 20 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.55966 | 1.2491 | 674.9 | 184
| 21 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.59027 | 1.3202 | 675.7 | 185.6
| 22 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.59215 | 1.3261 | 676.8 | 186.2
| 23 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.59265 | 1.3273 | 673.7 | 186.3
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-09
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.59362 | 1.3276 | 676.5 | 186.4
| 1 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.59208 | 1.3242 | 676.5 | 186.7
| 2 | 2 | 2.1 | 12.9 | 0.2 | 0.6 | 0 | 0.55393 | 1.2296 | 676.5 | 184.5
| 3 | 2.2 | 2.1 | 11.5 | 0.2 | 0.8 | 0 | 0.28621 | 0.50671 | 644.5 | 131.3
| 4 | 2 | 2.1 | 13 | 0.2 | 0.6 | 0 | 0.60659 | 1.3561 | 673.3 | 186.6
| 5 | 2.2 | 2.1 | 11.2 | 0.2 | 0.7 | 0 | 0.15865 | 0.27278 | 643.3 | 125.5
| 6 | 2.1 | 2.1 | 14.4 | 0.2 | 0.9 | 0 | 0.67372 | 1.4653 | 666.2 | 179
| 7 | 2.1 | 2.1 | 15 | 0.2 | 0.6 | 0 | 0.55783 | 1.2538 | 676.5 | 187.2
| 8 | 2 | 2.1 | 13.1 | 0 | 0 | 0 | 1.4241 | 2.642 | 676.8 | 186.8
| 9 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.58454 | 1.3121 | 676.5 | 186
| 10 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.5712 | 1.2776 | 676.1 | 185.2
| 11 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.5851 | 1.2988 | 674.5 | 184.3
| 12 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.64685 | 1.4352 | 674.5 | 183.9
| 13 | 2.1 | 2.1 | 14.8 | 0.2 | 0.6 | 0 | 0.6948 | 1.5395 | 673.7 | 183.6
| 14 | 2.1 | 2.1 | 14.7 | 0.2 | 1 | 0 | 0.70792 | 1.5679 | 672.9 | 182.9
| 15 | 2.1 | 2.1 | 14.7 | 0.2 | 0.9 | 0 | 0.70469 | 1.5572 | 672.5 | 182.8
| 16 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.69079 | 1.5314 | 672.5 | 182.9
| 17 | 2.1 | 2.1 | 14.7 | 0.2 | 0.6 | 0 | 0.68005 | 1.5089 | 672.5 | 183
| 18 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.68873 | 1.5324 | 672.1 | 183.6
| 19 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.68708 | 1.5315 | 672.1 | 184.1
| 20 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.68403 | 1.5274 | 672.5 | 184.7
| 21 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.57616 | 1.2941 | 673.7 | 185.2
| 22 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.57802 | 1.3007 | 674.5 | 185.2
| 23 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.55293 | 1.2476 | 674.5 | 185.2
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-10
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.54379 | 1.2308 | 674.9 | 185.2
| 1 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.53452 | 1.2098 | 676.1 | 185.3
| 2 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.54406 | 1.2326 | 675.7 | 185.3
| 3 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.55391 | 1.2554 | 675.7 | 185.7
| 4 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.56906 | 1.288 | 676.5 | 186.1
| 5 | 1.9 | 2.1 | 13.1 | 0.2 | 0.9 | 0 | 1.0753 | 2.1462 | 676.5 | 186.2
| 6 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.57467 | 1.2935 | 676.5 | 186
| 7 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.54976 | 1.2466 | 676.1 | 185.9
| 8 | 2.1 | 2.1 | 14.9 | 0.2 | 0.6 | 0 | 0.36801 | 0.878 | 676.1 | 185.6
| 9 | 1.9 | 2.1 | 13.1 | 0 | 0 | 0 | 1.4761 | 2.6705 | 675.3 | 185.4
| 10 | 2 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.54238 | 1.2379 | 674.5 | 185.3
| 11 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.56447 | 1.2833 | 674.1 | 184.8
| 12 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.59366 | 1.3456 | 672.9 | 184.1
| 13 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.58593 | 1.328 | 672.5 | 183.9
| 14 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.59189 | 1.3434 | 672.5 | 183.9
| 15 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.59153 | 1.3426 | 672.5 | 184
| 16 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.57675 | 1.3127 | 672.9 | 184.1
| 17 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.63069 | 1.4373 | 672.5 | 184.6
| 18 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.65203 | 1.4966 | 673.3 | 185.4
| 19 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.65594 | 1.5083 | 674.9 | 186.4
| 20 | 2.1 | 2.1 | 15 | 0.2 | 1 | 0 | 0.63285 | 1.4604 | 676.1 | 186.9
| 21 | 2.1 | 2.1 | 15.1 | 0.2 | 1 | 0 | 0.6159 | 1.4313 | 676.8 | 187.6
| 22 | 2.1 | 2.1 | 15.1 | 0.2 | 1 | 0 | 0.61057 | 1.4214 | 678 | 188.7
| 23 | 2.1 | 2.1 | 15.2 | 0.2 | 1 | 0 | 0.5954 | 1.3917 | 678 | 189.3
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-11
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 15.3 | 0.2 | 1 | 0 | 0.5802 | 1.3657 | 679.2 | 190.1
| 1 | 2.1 | 2.1 | 15.3 | 0.2 | 1 | 0 | 0.5913 | 1.3898 | 679.6 | 190.6
| 2 | 2.1 | 2.1 | 15.3 | 0.2 | 1 | 0 | 0.58687 | 1.382 | 678.8 | 191
| 3 | 2.1 | 2.1 | 15.3 | 0.2 | 1 | 0 | 0.58437 | 1.3761 | 679.2 | 191.2
| 4 | 2.1 | 2.1 | 15.3 | 0.2 | 1 | 0 | 0.5996 | 1.4113 | 679.2 | 191.1
| 5 | 2.1 | 2.1 | 15.3 | 0.2 | 1 | 0 | 0.58983 | 1.3915 | 678.8 | 191.7
| 6 | 2.1 | 2.1 | 15.3 | 0.2 | 1 | 0 | 0.58588 | 1.3816 | 678.4 | 191.7
| 7 | 2 | 2.1 | 13.4 | 0 | 0 | 0 | 1.3932 | 2.6921 | 678 | 191
| 8 | 2.1 | 2.1 | 15.2 | 0.2 | 1 | 0 | 0.50693 | 1.1946 | 678 | 189.9
| 9 | 2.1 | 2.1 | 15.1 | 0.2 | 1 | 0 | 0.52606 | 1.2193 | 677.2 | 187.5
| 10 | 2.1 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.55632 | 1.2718 | 674.9 | 184.7
| 11 | 2.1 | 2.1 | 14.7 | 0.2 | 1 | 0 | 0.56757 | 1.2854 | 672.9 | 181.9
| 12 | 2.1 | 2.1 | 14.6 | 0.2 | 1 | 0 | 0.58878 | 1.3238 | 671.7 | 179.9
| 13 | 2.1 | 2.1 | 14.5 | 0.2 | 1 | 0 | 0.71156 | 1.5912 | 669.3 | 178.7
| 14 | 2.1 | 2.1 | 14.4 | 0.2 | 1 | 0 | 0.63408 | 1.4095 | 669.3 | 177.1
| 15 | 2.1 | 2.1 | 14.3 | 0.2 | 1 | 0 | 0.57872 | 1.2764 | 668.6 | 175.9
| 16 | 2.1 | 2.1 | 14.3 | 0.2 | 1 | 0 | 0.528 | 1.1592 | 667.8 | 174.3
| 17 | 2.1 | 2.1 | 14.3 | 0.2 | 1 | 0 | 0.51266 | 1.1239 | 667.8 | 174.2
| 18 | 2 | 2.1 | 12.4 | 0.2 | 0.9 | 0 | 0.50909 | 1.1177 | 668.2 | 174
| 19 | 2.1 | 2.1 | 14.3 | 0.2 | 1 | 0 | 0.5055 | 1.1139 | 669.7 | 175
| 20 | 2 | 2.1 | 14.5 | 0.2 | 1 | 0 | 0.63437 | 1.4015 | 671.7 | 178.6
| 21 | 2 | 2.1 | 12.7 | 0.2 | 1 | 0 | 0.56686 | 1.2593 | 671.3 | 179.1
| 22 | 2.1 | 2.1 | 14.7 | 0.2 | 1 | 0 | 0.571 | 1.2747 | 672.5 | 181.3
| 23 | 2 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.55364 | 1.2438 | 672.5 | 182.5
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-12
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.55045 | 1.2349 | 674.1 | 183.1
| 1 | 2 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.55723 | 1.2495 | 674.5 | 183.6
| 2 | 2 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.55615 | 1.2448 | 674.5 | 183.8
| 3 | 2 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.5532 | 1.2393 | 674.5 | 184.3
| 4 | 2 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.54947 | 1.2364 | 674.5 | 184.9
| 5 | 2 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.54522 | 1.2317 | 674.9 | 185.2
| 6 | 2 | 2.1 | 14.9 | 0.2 | 1 | 0 | 0.53529 | 1.2082 | 674.9 | 185
| 7 | 1.9 | 2 | 12.9 | 0 | 0 | 0 | 1.3947 | 2.5652 | 674.1 | 183.5
| 8 | 2 | 2 | 12.8 | 0.3 | 1.3 | 0 | 0.49413 | 1.1043 | 672.1 | 179.9
| 9 | 2 | 2 | 14.4 | 0.2 | 0.9 | 0 | 0.54313 | 1.1939 | 672.1 | 177.2
| 10 | 2.1 | 2 | 14.3 | 0.2 | 0.9 | 0 | 0.61585 | 1.3345 | 670.1 | 175.4
| 11 | 2 | 2 | 14.2 | 0.2 | 0.9 | 0 | 0.60893 | 1.3025 | 667 | 172.2
| 12 | 2 | 2 | 13.9 | 0.2 | 0.9 | 0 | 0.62711 | 1.3174 | 664.6 | 167.9
| 13 | 2 | 2 | 13.8 | 0.2 | 0.9 | 0 | 0.61383 | 1.2837 | 664.2 | 165.9
| 14 | 2 | 2 | 13.7 | 0.2 | 0.9 | 0 | 0.64922 | 1.348 | 663.8 | 165.5
| 15 | 2 | 2 | 11.7 | 0.2 | 0.9 | 0 | 0.45132 | 0.93341 | 663.4 | 160.5
| 16 | 2 | 2 | 11.5 | 0.3 | 0.9 | 0 | 0.41528 | 0.85218 | 662.2 | 158.7
| 17 | 2.1 | 2 | 13.7 | 0.2 | 0.9 | 0 | 0.50405 | 1.0665 | 664.6 | 167.2
| 18 | 2.1 | 2 | 14.2 | 0.2 | 0.9 | 0 | 0.63983 | 1.3718 | 668.6 | 173.6
| 19 | 2 | 2 | 14.4 | 0.2 | 0.9 | 0 | 0.65152 | 1.417 | 669 | 177
| 20 | 2 | 2 | 14.5 | 0.2 | 1 | 0 | 0.56168 | 1.2306 | 670.5 | 178.7
| 21 | 2.1 | 2 | 14.7 | 0.2 | 0.9 | 0 | 0.5784 | 1.2747 | 671.7 | 181.2
| 22 | 2 | 2 | 12.9 | 0.2 | 1 | 0 | 0.54842 | 1.2174 | 671.3 | 182.1
| 23 | 2 | 2 | 12.9 | 0.2 | 1 | 0 | 0.55032 | 1.2227 | 671.7 | 182.8
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-13
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2 | 2 | 12.9 | 0.2 | 1 | 0 | 0.54254 | 1.206 | 672.5 | 183.2
| 1 | 2 | 2 | 12.9 | 0.2 | 1 | 0 | 0.54317 | 1.209 | 672.9 | 183.9
| 2 | 2 | 2 | 13 | 0.2 | 1 | 0 | 0.52839 | 1.1824 | 672.5 | 184
| 3 | 2 | 2 | 13 | 0.2 | 1 | 0 | 0.52501 | 1.1764 | 672.9 | 184.2
| 4 | 2 | 2 | 13 | 0.2 | 1 | 0 | 0.54551 | 1.2218 | 673.7 | 184.4
| 5 | 1.9 | 2 | 9.8 | 0.3 | 1 | 0 | 0.1279 | 0.22098 | 642.5 | 125.1
| 6 | 2.1 | 2 | 11.2 | 0.3 | 1 | 0 | 0.19657 | 0.34142 | 637.4 | 126
| 7 | 1.9 | 2 | 9.8 | 0 | 0 | 0 | 0.80392 | 1.137 | 637.4 | 126.9
| 8 | 2 | 2 | 10.1 | 0.3 | 1 | 0 | 0.1518 | 0.27144 | 637.8 | 131.7
| 9 | 1.9 | 2 | 12.2 | 0.3 | 0.9 | 0 | 0.28393 | 0.61551 | 665.4 | 171.2
| 10 | 1.9 | 2 | 12.4 | 0.3 | 1 | 0 | 0.4348 | 0.95465 | 669.7 | 173.8
| 11 | 2.2 | 2 | 14.3 | 0.2 | 1 | 0 | 0.46 | 1.008 | 671.3 | 176.1
| 12 | 2 | 2 | 14.4 | 0.2 | 0.9 | 0 | 0.47672 | 1.0416 | 669.7 | 177
| 13 | 2 | 2 | 12.7 | 0.2 | 0.9 | 0 | 0.60088 | 1.3015 | 668.2 | 178
| 14 | 1.9 | 2 | 9.7 | 0.2 | 0.7 | 0 | 0.15631 | 0.26727 | 640.5 | 123.6
| 15 | 2.1 | 2 | 11.3 | 0.2 | 0.7 | 0 | 0.32854 | 0.57604 | 635.8 | 128.3
| 16 | 2 | 2 | 14.5 | 0.2 | 1 | 0 | 0.54608 | 1.2003 | 666.6 | 179.8
| 17 | 2 | 2 | 14.6 | 0.2 | 1 | 0 | 0.55025 | 1.2144 | 670.9 | 181.4
| 18 | 2 | 2 | 12.9 | 0.2 | 0.9 | 0 | 0.54678 | 1.2111 | 672.1 | 182.7
| 19 | 2.2 | 2 | 14.8 | 0.2 | 1 | 0 | 0.61103 | 1.3508 | 672.1 | 184
| 20 | 2 | 2 | 12.9 | 0.2 | 1 | 0 | 0.5702 | 1.2617 | 673.3 | 184.3
| 21 | 2.1 | 2 | 14.8 | 0.2 | 1 | 0 | 0.55485 | 1.2327 | 674.5 | 184.6
| 22 | 2 | 2 | 12.9 | 0.2 | 1 | 0 | 0.58423 | 1.2904 | 674.1 | 183.3
| 23 | 1.9 | 2 | 9.8 | 0.3 | 1 | 0 | 0.13424 | 0.23122 | 642.9 | 125.4
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-14
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2 | 11.3 | 0.3 | 1 | 0 | 0.19728 | 0.34322 | 638.2 | 127.4
| 1 | 2.1 | 2 | 11.3 | 0.3 | 1 | 0 | 0.22345 | 0.38776 | 638.2 | 127.6
| 2 | 2.1 | 2 | 11.3 | 0.3 | 1 | 0 | 0.2238 | 0.38827 | 638.6 | 127.6
| 3 | 2.1 | 2 | 11.3 | 0.3 | 1 | 0 | 0.24815 | 0.43254 | 639 | 128.2
| 4 | 2.1 | 2 | 11.3 | 0.3 | 1 | 0 | 0.21499 | 0.37452 | 638.6 | 128.1
| 5 | 2.1 | 2 | 11.6 | 0.3 | 1 | 0 | 0.37108 | 0.65894 | 639.4 | 132.2
| 6 | 2 | 2 | 13 | 0.2 | 1 | 0 | 0.53346 | 1.1868 | 671.7 | 183.5
| 7 | 2 | 2 | 13 | 0.2 | 1 | 0 | 0.5588 | 1.2426 | 674.9 | 183.8
| 8 | 2.2 | 2 | 14.9 | 0 | 0 | 0 | 1.4038 | 2.5869 | 674.9 | 184.9
| 9 | 2 | 2 | 13 | 0.3 | 1.3 | 0 | 0.62615 | 1.3987 | 674.5 | 184.6
| 10 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.65098 | 1.4378 | 673.3 | 183.8
| 11 | 2 | 2 | 12.9 | 0.2 | 1 | 0 | 0.58511 | 1.29 | 671.7 | 183.7
| 12 | 2 | 2 | 13 | 0.2 | 1 | 0 | 0.55951 | 1.239 | 671.7 | 184.4
| 13 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.57386 | 1.2663 | 672.1 | 183.9
| 14 | 2 | 2.1 | 12.9 | 0.2 | 1 | 0 | 0.57222 | 1.2633 | 671.3 | 183.8
| 15 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.58278 | 1.2877 | 671.3 | 183.7
| 16 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.60926 | 1.3463 | 670.9 | 183
| 17 | 2 | 2.1 | 12.9 | 0.2 | 1 | 0 | 0.66658 | 1.4756 | 671.3 | 183.8
| 18 | 2 | 2.1 | 12.9 | 0.2 | 1 | 0 | 0.67326 | 1.491 | 671.7 | 184.6
| 19 | 2 | 2.1 | 13 | 0.2 | 1 | 0 | 0.65327 | 1.4604 | 672.5 | 185.2
| 20 | 2 | 2.1 | 13.1 | 0.2 | 1 | 0 | 0.64821 | 1.4537 | 674.1 | 186.2
| 21 | 2.1 | 2.1 | 11.3 | 0.3 | 1 | 0 | 0.24078 | 0.41798 | 646.5 | 126.7
| 22 | 2 | 2.1 | 9.9 | 0.3 | 1 | 0 | 0.17127 | 0.29893 | 637 | 127.9
| 23 | 2.1 | 2.1 | 11.3 | 0.3 | 1 | 0 | 0.16952 | 0.29508 | 637.8 | 127.4
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-15
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 11.3 | 0.3 | 1 | 0 | 0.1696 | 0.29556 | 637.4 | 127.6
| 1 | 2.1 | 2.1 | 11.2 | 0.3 | 1 | 0 | 0.17292 | 0.29992 | 637.4 | 127
| 2 | 2.1 | 2.1 | 11.3 | 0.3 | 1 | 0 | 0.1651 | 0.28846 | 637.8 | 127.6
| 3 | 2.1 | 2.1 | 11.4 | 0.3 | 1 | 0 | 0.1861 | 0.32725 | 638.2 | 128.2
| 4 | 2 | 2.1 | 13.2 | 0.3 | 1.3 | 0 | 0.66661 | 1.5144 | 671.3 | 187.7
| 5 | 2.1 | 2.1 | 14.8 | 0.2 | 1 | 0 | 0.51186 | 1.1621 | 674.5 | 185.2
| 6 | 2 | 2.1 | 15.1 | 0.2 | 1 | 0 | 0.53429 | 1.2199 | 676.5 | 187.7
| 7 | 2.1 | 2.1 | 15 | 0 | 0 | 0 | 1.2868 | 2.4125 | 676.5 | 187.4
| 8 | 2 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.50641 | 1.1544 | 676.5 | 186.7
| 9 | 2 | 2.1 | 15 | 0.2 | 1 | 0 | 0.55825 | 1.2662 | 676.5 | 187
| 10 | 2 | 2 | 14.9 | 0.2 | 1 | 0 | 0.51338 | 1.1646 | 676.8 | 186.6
| 11 | 2 | 2 | 15 | 0.2 | 1 | 0 | 0.53448 | 1.2124 | 675.7 | 186.4
| 12 | 2 | 2 | 14.9 | 0.2 | 1 | 0 | 0.51336 | 1.1624 | 674.5 | 185.8
| 13 | 2 | 2 | 14.9 | 0.3 | 1.3 | 0 | 0.50918 | 1.153 | 673.7 | 185.3
| 14 | 2 | 2 | 14.9 | 0.2 | 1 | 0 | 0.58175 | 1.3161 | 672.9 | 185.4
| 15 | 2 | 2 | 14.9 | 0.3 | 1.3 | 0 | 0.59703 | 1.3513 | 672.9 | 185.2
| 16 | 2 | 2 | 14.9 | 0.3 | 1.3 | 0 | 0.58416 | 1.3246 | 672.9 | 185.3
| 17 | 2 | 2 | 14.9 | 0.3 | 1.3 | 0 | 0.60073 | 1.3622 | 674.1 | 185.8
| 18 | 2 | 2 | 14.9 | 0.3 | 1.3 | 0 | 0.59454 | 1.3481 | 674.5 | 185.7
| 19 | 2 | 2 | 14.9 | 0.3 | 1.3 | 0 | 0.60493 | 1.3693 | 674.5 | 184.9
| 20 | 2.1 | 2 | 11 | 0.4 | 1.3 | 0 | 0.0098133 | 0.016962 | 641.3 | 123
| 21 | 2 | 2 | 9.9 | 0.4 | 1.3 | 0 | 0.13794 | 0.24412 | 638.2 | 127.1
| 22 | 2 | 2 | 9.8 | 0.4 | 1.3 | 0 | 0.13274 | 0.2334 | 637.4 | 125.7
| 23 | 48.9 | 2 | 104.7 | 0 | 0 | 0 | 0 | 0 | 629.1 | 27.7 | SD |  |  | 2300 | 23:20
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-16
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 444.8 | 0.5 | HS | 3:00
| 3 | 54.7 | 2 | 120.2 | 0 | 0 | 0 | 0 | 0 | 580.9 | 21.2 | HS
| 4 | 38.4 | 3.8 | 149.8 | 23.4 | 55.6 | 0 | 0 | 0 | 631.5 | 78.8 |  |  | 4:43 |  |  | Dur. 103 min
| 5 | 2.1 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.27353 | 0.62665 | 670.5 | 185.4
| 6 | 2.1 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.4157 | 0.95293 | 676.1 | 185.2
| 7 | 2.1 | 3.8 | 14.9 | 0 | 0 | 0 | 1.2463 | 2.3364 | 676.5 | 184.5
| 8 | 2.2 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.41163 | 0.94695 | 677.6 | 185.8
| 9 | 2.1 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.4781 | 1.0927 | 676.5 | 186.1
| 10 | 2.2 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.45549 | 1.043 | 676.5 | 185.2
| 11 | 2.1 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.45756 | 1.0487 | 675.7 | 184.9
| 12 | 2.2 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.45227 | 1.0352 | 674.9 | 184
| 13 | 2.1 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.4569 | 1.0444 | 674.5 | 183.3
| 14 | 2.2 | 3.8 | 14.8 | 0.2 | 1 | 0 | 0.48335 | 1.0974 | 674.5 | 183
| 15 | 2.2 | 3.8 | 14.8 | 0.3 | 1.3 | 0 | 0.50231 | 1.1353 | 673.7 | 183
| 16 | 2.1 | 3.8 | 14.8 | 0.3 | 1.3 | 0 | 0.49679 | 1.1228 | 672.9 | 182.9
| 17 | 2.1 | 3.8 | 14.8 | 0.3 | 1.3 | 0 | 0.49571 | 1.1188 | 672.9 | 183
| 18 | 2.1 | 3.8 | 14.8 | 0.3 | 1.3 | 0 | 0.4878 | 1.1019 | 672.9 | 183.7
| 19 | 2.1 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.47611 | 1.0793 | 672.5 | 184
| 20 | 2.1 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.47694 | 1.0855 | 672.9 | 184.1
| 21 | 2.1 | 3.8 | 14.9 | 0.3 | 1.3 | 0 | 0.49145 | 1.119 | 673.7 | 185
| 22 | 2.1 | 3.8 | 11.9 | 0.3 | 1.1 | 0 | 0.26684 | 0.4957 | 652 | 136.8
| 23 | 2 | 3.8 | 9.9 | 0.3 | 1 | 0 | 0.14094 | 0.25016 | 637.4 | 127.6
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-17
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 3.8 | 11.4 | 0.3 | 1 | 0 | 0.13037 | 0.23295 | 637.8 | 128.1
| 1 | 2.1 | 3.8 | 11.3 | 0.3 | 1 | 0 | 0.13425 | 0.23856 | 637.8 | 127.3
| 2 | 2.1 | 3.7 | 11.4 | 0.3 | 1 | 0 | 0.15984 | 0.28447 | 637.8 | 127
| 3 | 2.1 | 3.6 | 11.4 | 0.3 | 1 | 0 | 0.1622 | 0.28976 | 638.2 | 127.7
| 4 | 2 | 2.1 | 15.1 | 0.3 | 1.3 | 0 | 0.48938 | 1.1235 | 670.9 | 186.2
| 5 | 2.1 | 2.1 | 15.1 | 0.3 | 1.3 | 0 | 0.45104 | 1.0355 | 675.7 | 186.4
| 6 | 2.1 | 2.1 | 15.1 | 0.3 | 1.3 | 0 | 0.61971 | 1.3694 | 676.5 | 186.6
| 7 | 1.9 | 2.1 | 13.2 | 0 | 0 | 0 | 1.1109 | 2.1788 | 676.8 | 186.1
| 8 | 2.1 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.45677 | 1.0423 | 675.3 | 185.2
| 9 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.55687 | 1.2633 | 674.5 | 184.1
| 10 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.55413 | 1.2565 | 672.9 | 183.3
| 11 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.56789 | 1.2837 | 671.3 | 182.8
| 12 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.56019 | 1.2646 | 669.3 | 182.9
| 13 | 2.1 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.57319 | 1.2882 | 669.3 | 182.1
| 14 | 2.1 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.58421 | 1.3094 | 669.7 | 181.8
| 15 | 2.1 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.5904 | 1.3233 | 669.3 | 181.9
| 16 | 2.1 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.57957 | 1.299 | 670.5 | 182.9
| 17 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.55056 | 1.2434 | 671.3 | 183.6
| 18 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.54442 | 1.2328 | 672.1 | 184
| 19 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.54456 | 1.2314 | 672.5 | 184.6
| 20 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.54161 | 1.2247 | 672.5 | 185.1
| 21 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.56927 | 1.2844 | 673.7 | 184.6
| 22 | 2.1 | 2.1 | 11 | 0.4 | 1.3 | 0 | 0 | 0 | 640.9 | 123.2
| 23 | 2.1 | 2.1 | 11.3 | 0.4 | 1.3 | 0 | 0.12698 | 0.22291 | 636.2 | 126.7
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-18
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 11.2 | 0.4 | 1.3 | 0 | 0.12452 | 0.21821 | 635.4 | 126.6
| 1 | 2.1 | 2.1 | 11.3 | 0.4 | 1.3 | 0 | 0.12163 | 0.21353 | 635.8 | 126.7
| 2 | 2.1 | 2.1 | 11.2 | 0.4 | 1.3 | 0 | 0.13577 | 0.23731 | 635.8 | 126.9
| 3 | 2.1 | 2.1 | 11.2 | 0.4 | 1.3 | 0 | 0.13399 | 0.23447 | 636.2 | 126.7
| 4 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.63896 | 1.4359 | 668.6 | 185
| 5 | 2 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.51461 | 1.1641 | 674.5 | 184.6
| 6 | 2.1 | 2.1 | 14.9 | 0 | 0 | 0 | 1.1645 | 2.1646 | 674.9 | 185.2
| 7 | 2 | 2.1 | 13 | 0.4 | 1.7 | 0 | 0.48715 | 1.1095 | 674.9 | 185.3
| 8 | 2 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.40028 | 0.90543 | 674.5 | 184.7
| 9 | 2 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.45408 | 1.028 | 674.5 | 185.4
| 10 | 2 | 2.1 | 13 | 0.3 | 1.3 | 0 | 0.56626 | 1.2782 | 674.5 | 185.3
| 11 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.46375 | 1.0439 | 674.9 | 185.5
| 12 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.45338 | 1.0211 | 673.3 | 185
| 13 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.54855 | 1.2342 | 672.5 | 185.8
| 14 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.53596 | 1.2042 | 672.5 | 185.4
| 15 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.54249 | 1.2199 | 672.9 | 186
| 16 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.53857 | 1.2089 | 672.9 | 185.9
| 17 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.54672 | 1.2266 | 674.5 | 186.4
| 18 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.54729 | 1.2273 | 674.5 | 186.4
| 19 | 2.1 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.54488 | 1.2268 | 674.5 | 187.1
| 20 | 2.1 | 2.1 | 15.1 | 0.3 | 1.3 | 0 | 0.5142 | 1.1643 | 674.1 | 187.9
| 21 | 2.1 | 2.1 | 15.1 | 0.3 | 1.3 | 0 | 0.46426 | 1.0494 | 675.3 | 187.6
| 22 | 2.1 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.48041 | 1.0787 | 676.5 | 187.3
| 23 | 2.1 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.48849 | 1.0983 | 676.8 | 187.4
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-19
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.47747 | 1.0706 | 676.8 | 187.5
| 1 | 2.1 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.49065 | 1.0967 | 676.5 | 187.4
| 2 | 2.1 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.48097 | 1.076 | 676.8 | 187.5
| 3 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.48876 | 1.0876 | 676.8 | 187
| 4 | 2.1 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.50643 | 1.1259 | 676.5 | 187.2
| 5 | 2.1 | 2.1 | 15 | 0.3 | 1.3 | 0 | 0.50631 | 1.1272 | 676.5 | 187.3
| 6 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.51155 | 1.1378 | 676.5 | 186.8
| 7 | 1.7 | 2.1 | 11.2 | 0 | 0 | 0 | 1.5783 | 2.9115 | 676.1 | 186.7
| 8 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.50443 | 1.1205 | 675.7 | 186
| 9 | 2.1 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.54701 | 1.2064 | 674.9 | 185.1
| 10 | 2.1 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.55859 | 1.2287 | 674.9 | 184.8
| 11 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.48133 | 1.0707 | 674.1 | 185.9
| 12 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.50661 | 1.1254 | 670.9 | 185.6
| 13 | 2.2 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.51623 | 1.1431 | 674.5 | 185.6
| 14 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.50358 | 1.1186 | 674.9 | 186.4
| 15 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.48694 | 1.0811 | 674.9 | 186
| 16 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.4675 | 1.0366 | 674.9 | 185.6
| 17 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.48645 | 1.0767 | 674.9 | 185.3
| 18 | 2.1 | 2.1 | 14.9 | 0.3 | 1.3 | 0 | 0.4814 | 1.0646 | 674.9 | 185.2
| 19 | 2.1 | 2.1 | 14.8 | 0.3 | 1.3 | 0 | 0.62844 | 1.3867 | 675.3 | 183.9
| 20 | 2 | 2.1 | 9.7 | 0.4 | 1.2 | 0 | 0.21158 | 0.36088 | 641.7 | 124.9
| 21 | 2.1 | 2.1 | 11.3 | 0.4 | 1.3 | 0 | 0.28801 | 0.49698 | 637.8 | 127
| 22 | 2.1 | 2.1 | 11.3 | 0.4 | 1.3 | 0 | 0.29428 | 0.51109 | 638.6 | 128
| 23 | 2.1 | 2.1 | 11.3 | 0.4 | 1.3 | 0 | 0.28011 | 0.48374 | 638.2 | 126.7
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-20
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 40.6 | 2.1 | 87.7 | 0 | 0 | 0 | 0 | 0 | 632.6 | 32.1 | SD |  |  | 0:00 | 0:18
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | 39.2 | 2.1 | 46.9 | 0 | 0 | 0 | 0 | 0 | 472 | 6.1 | HS | 5:53
| 6 | 59.3 | 2.1 | 112.5 | 0 | 0 | 0 | 0 | 0 | 617.6 | 11.8 | HS
| 7 | 54.5 | 4.6 | 93.9 | 27.7 | 29 | 0 | 0 | 0 | 632.6 | 6.6 |  |  |  |  | 7:08
| 8 | 0 | 4.5 | 0 | 1.2 | 0 | 0 | 0 | 0 | 417.5 | 0.5
| 9 | 68.2X | 7.6 | 132.7 | 15.2X | 18 | 0 | 0 | 0 | 556.9 | 16.5 |  | 9:03
| 10 | 45.3X | 9.7 | 152.1 | 17.3X | 35.2 | 0 | 0 | 0 | 629.9 | 60.8 |  |  | 10:51 |  |  | dur. 108 min
| 11 | 15.2X | 10.3 | 87.3 | 3.3X | 11.6 | 0 | 2.1189 | 3.3239 | 657.1 | 145.4 |  |  | 11:23 | 11:07 |  | dur. 140 min
| 12 | 1.8 | 10.3 | 12.8 | 0 | 0 | 0 | 0.46594 | 3.3239 | 670.1 | 182.3
| 13 | 1.8 | 10.3 | 12.8 | 0.3 | 1.3 | 0 | 0.64703 | 1.0604 | 672.5 | 181.2
| 14 | 2 | 10.3 | 12.8 | 0.3 | 1.3 | 0 | 0.63397 | 1.4474 | 673.7 | 182.8
| 15 | 2.1 | 10.3 | 14.8 | 0.3 | 1.3 | 0 | 0.5905 | 1.4107 | 675.3 | 184.5
| 16 | 2.1 | 10.3 | 11.4 | 0.4 | 1.3 | 0 | 0.30898 | 1.3156 | 648.4 | 129.5
| 17 | 1.9 | 10.3 | 13.1 | 0.3 | 1.3 | 0 | 0.63091 | 0.54261 | 670.5 | 186.5
| 18 | 2 | 10.3 | 14.9 | 0.3 | 1.3 | 0 | 0.54914 | 1.4181 | 675.7 | 186
| 19 | 2 | 10.3 | 14.9 | 0.3 | 1.3 | 0 | 0.55545 | 1.2351 | 674.1 | 185.4
| 20 | 2 | 10.3 | 13.2 | 0.3 | 1.3 | 0 | 0.62964 | 1.2551 | 676.5 | 187.6
| 21 | 2 | 10.3 | 13.2 | 0.3 | 1.3 | 0 | 0.62296 | 1.4272 | 676.8 | 187.7
| 22 | 2 | 10.3 | 13.2 | 0.3 | 1.3 | 0 | 0.62917 | 1.4101 | 677.2 | 187.3
| 23 | 2 | 10.2 | 9.7 | 0.5 | 1.5 | 0 | 0.11096 | 1.4236 | 643.3 | 123.6
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-21
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2.1 | 10.3 | 11.2 | 0.5 | 1.5 | 0 | 0.21324 | 0.36935 | 638.2 | 126.5
| 1 | 2.1 | 10.3 | 11.2 | 0.5 | 1.5 | 0 | 0.23943 | 0.41519 | 638.6 | 127.2
| 2 | 2.1 | 10.3 | 11.3 | 0.5 | 1.5 | 0 | 0.23105 | 0.40207 | 638.6 | 127.3
| 3 | 2.1 | 10.3 | 11.3 | 0.5 | 1.5 | 0 | 0.2357 | 0.41127 | 638.2 | 127.7
| 4 | 1.9 | 9.9 | 13.1 | 0.4 | 1.7 | 0 | 0.71671 | 1.6137 | 670.1 | 186.7
| 5 | 2 | 9.5 | 13.2 | 0.3 | 1.3 | 0 | 0.63087 | 1.4241 | 676.5 | 187.6
| 6 | 2 | 9.2 | 13.1 | 0.3 | 1.3 | 0 | 0.61616 | 1.3893 | 676.5 | 186.9
| 7 | 2 | 7 | 13.1 | 0.3 | 1.3 | 0 | 0.62408 | 1.4047 | 676.8 | 186.8
| 8 | 2.1 | 7.1 | 14.9 | 0 | 0 | 0 | 1.3694 | 2.551 | 676.8 | 186.2
| 9 | 2 | 4.4 | 14.9 | 0.4 | 1.7 | 0 | 0.64701 | 1.4577 | 676.8 | 186
| 10 | 2 | 2.6 | 13.1 | 0.3 | 1.3 | 0 | 0.64683 | 1.4546 | 676.1 | 185.8
| 11 | 2 | 2 | 13 | 0.3 | 1.3 | 0 | 0.65014 | 1.4568 | 675.7 | 185.4
| 12 | 2 | 2 | 13 | 0.3 | 1.3 | 0 | 0.64667 | 1.4444 | 674.9 | 185.1
| 13 | 2 | 2 | 13 | 0.3 | 1.3 | 0 | 0.651 | 1.4548 | 674.9 | 185
| 14 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.63919 | 1.4322 | 674.9 | 185.4
| 15 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.56717 | 1.2702 | 675.7 | 186.2
| 16 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.56212 | 1.2583 | 674.9 | 185.7
| 17 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.56462 | 1.2645 | 676.1 | 186.3
| 18 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.56408 | 1.2615 | 676.5 | 186.1
| 19 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.54677 | 1.2228 | 676.5 | 186.2
| 20 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.56156 | 1.2576 | 676.5 | 186.3
| 21 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.54118 | 1.212 | 675.3 | 186.2
| 22 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.55794 | 1.2478 | 675.7 | 186.3
| 23 | 2.1 | 2 | 14.9 | 0.4 | 1.7 | 0 | 0.56049 | 1.2535 | 675.7 | 186.3
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-22
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2 | 2 | 13.1 | 0.3 | 1.3 | 0 | 0.60723 | 1.3562 | 674.9 | 186.3
| 1 | 2.1 | 2 | 14.9 | 0.4 | 1.7 | 0 | 0.55741 | 1.2449 | 675.3 | 186.2
| 2 | 2.1 | 2 | 14.9 | 0.3 | 1.3 | 0 | 0.54819 | 1.2221 | 674.5 | 185.9
| 3 | 2.1 | 2 | 14.9 | 0.3 | 1.3 | 0 | 0.57085 | 1.2686 | 675.3 | 185.9
| 4 | 2.1 | 2 | 14.9 | 0.4 | 1.6 | 0 | 0.56513 | 1.2547 | 676.1 | 186
| 5 | 2.1 | 2 | 14.9 | 0.4 | 1.6 | 0 | 0.57387 | 1.2719 | 675.3 | 185.6
| 6 | 2.1 | 2 | 14.9 | 0.4 | 1.6 | 0 | 0.59444 | 1.3128 | 674.5 | 185.3
| 7 | 2.1 | 2 | 14.8 | 0.4 | 1.6 | 0 | 0.60747 | 1.3362 | 674.5 | 185.1
| 8 | 2.1 | 2 | 14.8 | 0.4 | 1.6 | 0 | 0.62063 | 1.3608 | 674.5 | 184.5
| 9 | 2 | 2 | 12.9 | 0 | 0 | 0 | 1.3799 | 2.5084 | 674.1 | 183.5
| 10 | 2.1 | 2 | 14.6 | 0.4 | 1.6 | 0 | 0.62884 | 1.3658 | 672.5 | 182.1
| 11 | 2.1 | 2 | 14.6 | 0.4 | 1.6 | 0 | 0.62374 | 1.3499 | 671.3 | 180.8
| 12 | 2.1 | 2.1 | 14.5 | 0.4 | 1.6 | 0 | 0.639 | 1.3741 | 671.3 | 180.1
| 13 | 2.1 | 2.1 | 14.5 | 0.4 | 1.6 | 0 | 0.65857 | 1.4078 | 669.7 | 179.2
| 14 | 2.1 | 2.1 | 14.5 | 0 | 0 | 0 | 1.4231 | 2.5565 | 669 | 179.1
| 15 | 2 | 2.1 | 14.5 | 0.1 | 0.3 | 0 | 0.63036 | 1.3811 | 670.5 | 179.8
| 16 | 2 | 2.1 | 14.5 | 0 | 0 | 0 | 0.65751 | 1.4353 | 670.5 | 179.4
| 17 | 2 | 2.1 | 12.7 | 0 | 0 | 0 | 0.63548 | 1.3891 | 670.5 | 179.9
| 18 | 2 | 2.1 | 12.8 | 0 | 0 | 0 | 0.59093 | 1.2994 | 671.3 | 180.5
| 19 | 2 | 2.1 | 12.8 | 0 | 0 | 0 | 0.59656 | 1.3112 | 671.3 | 180.5
| 20 | 2 | 2.1 | 12.8 | 0 | 0 | 0 | 0.62746 | 1.3785 | 671.3 | 180.9
| 21 | 2 | 2.1 | 12.8 | 0 | 0 | 0 | 0.62578 | 1.3747 | 671.3 | 181.1
| 22 | 2 | 2.1 | 12.7 | 0 | 0 | 0 | 0.62297 | 1.3643 | 671.7 | 180
| 23 | 2.1 | 2.1 | 11.1 | 0.1 | 0.2 | 0 | 0.17904 | 0.30947 | 642.1 | 126.3
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-23
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 2 | 2.1 | 9.9 | 0.1 | 0.2 | 0 | 0.29621 | 0.51901 | 639.4 | 128.6
| 1 | 2.1 | 2.1 | 11.3 | 0.1 | 0.2 | 0 | 0.2505 | 0.43815 | 638.6 | 128.6
| 2 | 2.1 | 2.1 | 11.3 | 0.1 | 0.2 | 0 | 0.28402 | 0.49782 | 639 | 128.8
| 3 | 2.1 | 2.1 | 11.3 | 0.1 | 0.2 | 0 | 0.31934 | 0.56085 | 639 | 128.9
| 4 | 2 | 2.1 | 14.7 | 0 | 0 | 0 | 0.68553 | 1.5178 | 668.2 | 182.5
| 5 | 2 | 2.1 | 14.7 | 0 | 0 | 0 | 0.6201 | 1.3742 | 672.5 | 182.6
| 6 | 2 | 2 | 14.7 | 0 | 0 | 0 | 0.59473 | 1.3245 | 672.5 | 182.9
| 7 | 2 | 2 | 14.7 | 0 | 0 | 0 | 0.59496 | 1.3262 | 672.9 | 182.9
| 8 | 1.9 | 2 | 9.8 | 0 | 0 | 0 | 0.72402 | 1.0354 | 644.5 | 127.7
| 9 | 2 | 2 | 9.9 | 0.1 | 0.2 | 0 | 0.29751 | 0.52364 | 638.2 | 128.1
| 10 | 2 | 2 | 9.9 | 0.1 | 0.2 | 0 | 0.30358 | 0.53406 | 638.6 | 128.7
| 11 | 2 | 2 | 9.8 | 0.1 | 0.2 | 0 | 0.30701 | 0.53578 | 637.8 | 126.9
| 12 | 2.1 | 2 | 11.2 | 0.1 | 0.2 | 0 | 0.30663 | 0.53671 | 637.8 | 128.3
| 13 | 2.1 | 2 | 11.2 | 0.1 | 0.2 | 0 | 0.30149 | 0.52802 | 638.2 | 128.3
| 14 | 2 | 2 | 9.8 | 0.1 | 0.2 | 0 | 0.30178 | 0.5251 | 637.8 | 126.8
| 15 | 2.1 | 2 | 11.2 | 0.1 | 0.2 | 0 | 0.29888 | 0.52389 | 638.6 | 128.3
| 16 | 2 | 2 | 9.8 | 0.1 | 0.2 | 0 | 0.29003 | 0.50881 | 637.4 | 127
| 17 | 2 | 2 | 9.8 | 0.1 | 0.2 | 0 | 0.28705 | 0.50358 | 637.8 | 127.7
| 18 | 2 | 2 | 9.8 | 0.1 | 0.2 | 0 | 0.28302 | 0.49793 | 637.8 | 127
| 19 | 2 | 2 | 9.8 | 0.1 | 0.2 | 0 | 0.27564 | 0.4868 | 638.2 | 128
| 20 | 2.1 | 2 | 11.2 | 0.1 | 0.2 | 0 | 0.21262 | 0.37547 | 639 | 126.6
| 21 | 52.8 | 2 | 96.8 | 0 | 0 | 0 | 0 | 0 | 632.2 | 22.5 | SD |  |  | 20:59 | 21:15
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-24
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | 2.2 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 443.6 | 0.5 | HS | 3:57
| 4 | 62.2 | 2 | 150.3 | 0 | 0 | 0 | 0 | 0 | 581.7 | 27.2 | HS
| 5 | 26.3 | 3.2 | 118.7 | 10 | 27.4 | 0 | 0 | 0 | 623.2 | 101.1 |  |  | 5:28 |  |  | dur. 91 min
| 6 | 2 | 3.2 | 9.9 | 0.2 | 0.5 | 0 | 0.11771 | 0.21365 | 635 | 127.2
| 7 | 2.1 | 3.2 | 11.2 | 0.2 | 0.5 | 0 | 0.15906 | 0.28726 | 635 | 126.1
| 8 | 1.9 | 3.2 | 9.8 | 0 | 0 | 0 | 0.6203 | 0.90554 | 636.6 | 126.4
| 9 | 2.1 | 3.2 | 11.2 | 0.2 | 0.5 | 0 | 0.65091 | 1.0142 | 637 | 126.3
| 10 | 1.6 | 3.2 | 8.4 | 0.1 | 0.3 | 0 | 0.57056 | 0.80514 | 637 | 126.6
| 11 | 2.1 | 3.2 | 11.2 | 0.1 | 0.2 | 0 | 0.037888 | 0.066278 | 637 | 126.6
| 12 | 2.1 | 3.2 | 11.2 | 0.2 | 0.5 | 0 | 2.01 | 1.4174 | 637 | 126.3
| 13 | 2.2I | 3.2 | 11.2 | 0.4I | 1.3 | 0 | 2.016 | 1.4483 | 636.2 | 126.1
| 14 | 2.1I | 3.2 | 11.4 | 0.2I | 0.5 | 0 | 1.7921 | 1.5292 | 635.8 | 129.4
| 15 | 2 | 3.2 | 12.9 | 0.1 | 0.3 | 0 | 1.1569 | 2.2757 | 669.7 | 183.8
| 16 | 1.7 | 3.2 | 11.1 | 0.1 | 0.3 | 0 | 1.1748 | 2.3817 | 672.5 | 183.9
| 17 | 2 | 3.2 | 14.8 | 0.1 | 0.3 | 0 | 0.57985 | 1.3081 | 672.5 | 184.1
| 18 | 2 | 3.2 | 14.9 | 0.1 | 0.3 | 0 | 0.54504 | 1.2394 | 673.7 | 185.1
| 19 | 2 | 3.2 | 14.9 | 0.1 | 0.3 | 0 | 0.55198 | 1.2581 | 674.5 | 185.9
| 20 | 2 | 3.2 | 13 | 0.1 | 0.3 | 0 | 0.53208 | 1.2102 | 676.1 | 184.9
| 21 | 34.1 | 3.2 | 94.3 | 0 | 0 | 0 | 0 | 0 | 650.4 | 48.2 | SD |  |  | 21:00 | 21:22
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-25
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | 7.1 | 3.3 | 3.6 | 0 | 0 | 0 | 0 | 0 | 459.8 | 0.5 | HS | 2:57
| 3 | 63.3 | 3.4 | 156 | 0 | 0 | 0 | 0 | 0 | 585.3 | 28.6 | HS
| 4 | 25.1 | 4.6 | 119.3 | 10.2 | 29.2 | 0 | 0 | 0 | 626.7 | 109 |  |  | 4:26 |  |  | Dur. 89 min
| 5 | 2 | 4.6 | 15.1 | 0.1 | 0.3 | 0 | 0.46413 | 1.0705 | 669.7 | 187.4
| 6 | 2 | 4.5 | 15.1 | 0.1 | 0.3 | 0 | 0.47721 | 1.1012 | 675.3 | 187.6
| 7 | 2 | 4.4 | 15.1 | 0.1 | 0.3 | 0 | 0.48225 | 1.1128 | 676.8 | 187.4
| 8 | 1.9 | 4.2 | 13.2 | 0 | 0 | 0 | 1.4169 | 2.6745 | 676.5 | 187
| 9 | 2 | 3.1 | 13.1 | 0.1 | 0.3 | 0 | 0.54827 | 1.2612 | 676.5 | 186.2
| 10 | 2.1 | 3.1 | 14.9 | 0.1 | 0.3 | 0 | 0.6297 | 1.4373 | 674.9 | 185
| 11 | 2 | 3.1 | 12 | 0 | 0 | 0 | 0.50589 | 1.084 | 665.8 | 167.9
| 12 | 2 | 3.1 | 12.9 | 0.1 | 0.3 | 0 | 0.64167 | 1.453 | 673.3 | 183.5
| 13 | 2.1 | 3.1 | 14.8 | 0.1 | 0.3 | 0 | 0.65227 | 1.4763 | 672.5 | 183.1
| 14 | 2.1 | 3.1 | 14.8 | 0.1 | 0.3 | 0 | 0.64305 | 1.4555 | 672.5 | 182.9
| 15 | 1.9 | 3.1 | 12.6 | 0 | 0 | 0 | 0.49863 | 1.1169 | 670.5 | 177.2
| 16 | 2.1 | 3.1 | 11.1 | 0.1 | 0.2 | 0 | 0.22499 | 0.39413 | 642.1 | 125.5
| 17 | 2.1 | 3.1 | 11.2 | 0.1 | 0.2 | 0 | 0.21714 | 0.38142 | 637.4 | 126.2
| 18 | 2.1 | 3.1 | 11.5 | 0.1 | 0.2 | 0 | 0.32628 | 0.58947 | 637.8 | 131.4
| 19 | 2 | 3.1 | 12.8 | 0.1 | 0.3 | 0 | 0.5795 | 1.298 | 670.5 | 181.3
| 20 | 2 | 3.1 | 9.8 | 0.2 | 0.5 | 0 | 0.079055 | 0.13875 | 642.5 | 125
| 21 | 48.4 | 3.2 | 97.2 | 0 | 0 | 0 | 0 | 0 | 631.9 | 26.7 | SD |  |  | 21:00 | 21:17
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-26
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | 4 | 3.2 | 2.3 | 0 | 0 | 0 | 0 | 0 | 466.5 | 0.4 | HS | 2:57
| 3 | 64.3 | 3.3 | 162.8 | 0 | 0 | 0 | 0 | 0 | 592.8 | 30.6 | HS
| 4 | 20 | 4.3 | 94.7 | 7 | 20 | 0 | 0 | 0 | 626.7 | 108.3 |  |  | 4:20 |  |  | Dur. 83 min
| 5 | 2 | 4.2 | 9.9 | 0 | 0 | 0 | 0.81801 | 1.1843 | 636.2 | 126.9
| 6 | 1.9 | 4.1 | 13.1 | 0.1 | 0.3 | 0 | 0.40025 | 0.93498 | 670.1 | 186.6
| 7 | 2.1 | 4 | 14.9 | 0.1 | 0.3 | 0 | 0.38564 | 0.89306 | 676.5 | 185.5
| 8 | 2.1 | 2.9 | 15 | 0.1 | 0.3 | 0 | 0.42474 | 0.97565 | 678 | 185.5
| 9 | 2 | 2.9 | 14.9 | 0.1 | 0.3 | 0 | 0.54824 | 1.2484 | 676.8 | 185
| 10 | 2 | 2.9 | 14.7 | 0.1 | 0.3 | 0 | 0.52521 | 1.1801 | 674.5 | 182.1
| 11 | 2 | 2.9 | 14.6 | 0.1 | 0.3 | 0 | 0.55097 | 1.2228 | 673.3 | 179.4
| 12 | 2 | 2.9 | 14.4 | 0.1 | 0.3 | 0 | 0.56079 | 1.2299 | 671.7 | 176.4
| 13 | 2.1 | 2.9 | 14.2 | 0.1 | 0.3 | 0 | 0.56693 | 1.2348 | 669.7 | 174.1
| 14 | 2.1 | 2.9 | 14.1 | 0.1 | 0.3 | 0 | 0.58814 | 1.2738 | 669 | 173.1
| 15 | 2.1 | 2.9 | 14.1 | 0.1 | 0.3 | 0 | 0.55605 | 1.2049 | 669 | 172.4
| 16 | 1.9 | 2.9 | 9.6 | 0.1 | 0.2 | 0 | 0.17637 | 0.30476 | 644.5 | 123.4
| 17 | 2 | 2.9 | 9.8 | 0.1 | 0.2 | 0 | 0.22017 | 0.38599 | 639.4 | 126.2
| 18 | 2 | 2.9 | 9.7 | 0.1 | 0.2 | 0 | 0.23542 | 0.40954 | 639.4 | 125.4
| 19 | 2 | 2.9 | 9.8 | 0.1 | 0.2 | 0 | 0.25019 | 0.43721 | 639.4 | 126.8
| 20 | 2 | 2.9 | 9.8 | 0.1 | 0.2 | 0 | 0.22517 | 0.3932 | 639 | 126.8
| 21 | 42.7 | 2.9 | 89 | 0 | 0 | 0 | 0 | 0 | 632.2 | 30.1 | SD |  |  | 21:00 | 21:17
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-27
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-28
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | 13.4X | 3 | 6.3 | 0.0X | 0 | 0 | 0 | 0 | 287.7 | 0.5 | WS | 1:59
| 2 | 63.8X | 3 | 141.8 | 0.0X | 0 | 0 | 0 | 0 | 525.3 | 21.4 | WS
| 3 | 59.7X | 3.1 | 176.3 | 0.0X | 0 | 0 | 0 | 0 | 612.5 | 44.8 | WS
| 4 | 10.1X | 3.5 | 55.5 | 0.0X | 0 | 0 | 0 | 0 | 635 | 139.5 |  |  | 4:13 |  |  | Dur. 134 min vs. 240 limit for WS
| 5 | 2 | 3.4 | 12.8 | 0 | 0 | 0 | 1.3038 | 2.3439 | 665.8 | 180.1
| 6 | 2 | 3.3 | 14.5 | 0.1 | 0.3 | 0 | 0.45049 | 0.9879 | 671.3 | 179.3
| 7 | 2.1 | 2.4 | 14.5 | 0.1 | 0.3 | 0 | 0.53617 | 1.1704 | 671.7 | 179.5
| 8 | 2 | 2.4 | 12.8 | 0.1 | 0.3 | 0 | 0.5281 | 1.1528 | 670.1 | 179.2
| 9 | 2.1 | 2.4 | 14.5 | 0.1 | 0.3 | 0 | 0.5447 | 1.1815 | 669.3 | 178.4
| 10 | 2 | 2.4 | 12.6 | 0.1 | 0.3 | 0 | 0.54936 | 1.191 | 669 | 177.1
| 11 | 2 | 2.4 | 12.5 | 0.1 | 0.3 | 0 | 0.58006 | 1.2426 | 668.2 | 176.8
| 12 | 2 | 2.4 | 12.5 | 0.1 | 0.3 | 0 | 0.58106 | 1.2441 | 667.4 | 176.4
| 13 | 2 | 2.4 | 12.5 | 0.1 | 0.3 | 0 | 0.56773 | 1.2156 | 667.8 | 175.7
| 14 | 1.9 | 2.4 | 12.4 | 0.1 | 0.3 | 0 | 0.62012 | 1.3234 | 667 | 174.5
| 15 | 2 | 2.4 | 12.4 | 0.1 | 0.3 | 0 | 0.58056 | 1.2378 | 666.2 | 174.9
| 16 | 2 | 2.4 | 12.4 | 0.1 | 0.3 | 0 | 0.61117 | 1.3109 | 667 | 175.1
| 17 | 2.1 | 2.4 | 14.4 | 0.1 | 0.3 | 0 | 0.53809 | 1.1618 | 667.8 | 177.7
| 18 | 2 | 2.4 | 12.6 | 0.1 | 0.3 | 0 | 0.4803 | 1.0432 | 667.4 | 178.1
| 19 | 2 | 2.4 | 14.4 | 0.1 | 0.3 | 0 | 0.42691 | 0.93585 | 670.5 | 178.3
| 20 | 2.1 | 2.4 | 11.8 | 0.1 | 0.2 | 0 | 0.21094 | 0.38337 | 647.2 | 137.2
| 21 | 2.1 | 2.4 | 11.2 | 0.1 | 0.2 | 0 | 0.19777 | 0.34165 | 637 | 126.7
| 22 | 40.9 | 2.4 | 92.1 | 0 | 0 | 0 | 0 | 0 | 630.3 | 31.9 | SD |  |  | 22:02 | 22:22
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-29
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0.5 | HS | 2:57
| 3 | 62.5 | 2.5 | 128.3 | 0 | 0 | 0 | 0 | 0 | 563.6 | 18 | HS
| 4 | 49 | 4.9 | 176.1 | 13.7 | 29.9 | 0 | 0 | 0 | 622 | 67.8 |  |  | 4:52 |  |  | Dur. 115 min
| 5 | 2 | 4.8 | 10.1 | 0.1 | 0.2 | 0 | 0.13939 | 0.2461 | 631.5 | 132
| 6 | 1.8 | 4.6 | 12.9 | 0 | 0 | 0 | 1.5226 | 2.7765 | 659.9 | 183
| 7 | 2 | 4.2 | 12.9 | 0.1 | 0.3 | 0 | 0.51867 | 1.143 | 674.1 | 183.8
| 8 | 2 | 4.2 | 12.9 | 0.1 | 0.3 | 0 | 0.59032 | 1.2991 | 675.7 | 183.2
| 9 | 2 | 4.2 | 12.9 | 0.1 | 0.3 | 0 | 0.63444 | 1.3968 | 674.5 | 183
| 10 | 2 | 4.2 | 12.9 | 0.1 | 0.3 | 0 | 0.63207 | 1.3897 | 673.7 | 182.5
| 11 | 2 | 4.2 | 12.8 | 0.1 | 0.3 | 0 | 0.66319 | 1.451 | 672.5 | 181.5
| 12 | 2 | 4.2 | 12.8 | 0.1 | 0.3 | 0 | 0.64923 | 1.4237 | 672.1 | 182
| 13 | 2 | 4.2 | 12.8 | 0.1 | 0.3 | 0 | 0.64136 | 1.407 | 671.3 | 181.5
| 14 | 2 | 4.2 | 12.8 | 0.1 | 0.3 | 0 | 0.65 | 1.428 | 671.3 | 181.1
| 15 | 2 | 4.2 | 12.8 | 0.1 | 0.3 | 0 | 0.66563 | 1.4623 | 671.3 | 180.8
| 16 | 2 | 4.2 | 12.8 | 0.1 | 0.3 | 0 | 0.64116 | 1.4105 | 670.9 | 181.6
| 17 | 2 | 4.2 | 12.8 | 0.1 | 0.3 | 0 | 0.62185 | 1.373 | 671.3 | 182.1
| 18 | 2 | 4.2 | 12.9 | 0.1 | 0.3 | 0 | 0.52924 | 1.177 | 671.7 | 182.9
| 19 | 2 | 4.2 | 12.9 | 0.1 | 0.3 | 0 | 0.57872 | 1.2859 | 672.9 | 183
| 20 | 3.1 | 4.3 | 15 | 0.2 | 0.7 | 0 | 0 | 0 | 641.3 | 121.3
| 21 | 51.2 | 4.4 | 106.3 | 0 | 0 | 0 | 0 | 0 | 628.3 | 23.6 | SD |  |  | 21:00 | 21:16
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-04-30
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 434.9 | 0.4 | HS | 2:58
| 3 | 58.6 | 4.7 | 126.9 | 0 | 0 | 0 | 0 | 0 | 576.6 | 19.9 | HS
| 4 | 39.9 | 6.8 | 156.9 | 13.7 | 32.6 | 0 | 0 | 0 | 618.8 | 80.3 |  |  | 4:38 |  |  | Dur. 100 min
| 5 | 2 | 6.5 | 10.2 | 0.2 | 0.5 | 0 | 0.26197 | 0.47641 | 631.9 | 134.4
| 6 | 1.9 | 6.3 | 12.9 | 0.1 | 0.3 | 0 | 0.32271 | 0.7536 | 659.5 | 183.9
| 7 | 2.1 | 6.1 | 14.7 | 0 | 0 | 0 | 1.1551 | 2.0955 | 673.3 | 183.6
| 8 | 2 | 3.8 | 12.7 | 0.1 | 0.3 | 0 | 0.39012 | 0.8715 | 675.7 | 180.5
| 9 | 1.9 | 3.8 | 9.8 | 0.2 | 0.5 | 0 | 0.1504 | 0.26385 | 641.3 | 126.8
| 10 | 2 | 3.9 | 9.8 | 0.2 | 0.5 | 0 | 0.19131 | 0.33514 | 637.4 | 127
| 11 | 2 | 3.9 | 9.8 | 0.2 | 0.5 | 0 | 0.20645 | 0.36239 | 636.2 | 127.1
| 12 | 2 | 3.9 | 10.1 | 0.2 | 0.5 | 0 | 0.35431 | 0.63865 | 636.2 | 132.6
| 13 | 1.9 | 3.8 | 12.9 | 0.2 | 0.6 | 0 | 0.60869 | 1.3625 | 669.3 | 181.8
| 14 | 2 | 3.8 | 14.7 | 0.2 | 0.6 | 0 | 0.55958 | 1.255 | 671.3 | 181.7
| 15 | 2 | 3.8 | 12.9 | 0.2 | 0.6 | 0 | 0.5398 | 1.2134 | 670.9 | 182.1
| 16 | 2 | 3.8 | 12.9 | 0.1 | 0.3 | 0 | 0.52635 | 1.1858 | 670.9 | 182.8
| 17 | 2 | 3.8 | 12.9 | 0.1 | 0.3 | 0 | 0.50527 | 1.1383 | 671.3 | 183
| 18 | 2 | 3.8 | 12.9 | 0.1 | 0.3 | 0 | 0.49495 | 1.1172 | 671.3 | 183.3
| 19 | 2 | 3.8 | 12.9 | 0.1 | 0.3 | 0 | 0.46599 | 1.0593 | 673.3 | 182.8
| 20 | 1.9 | 3.8 | 12.7 | 0.1 | 0.3 | 0 | 0.41388 | 0.93374 | 674.1 | 180.2
| 21 | 42.8 | 3.9 | 102.1 | 0 | 0 | 0 | 0 | 0 | 644.5 | 36.6 | SD |  |  | 21:00 | 21:22
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
Note on C1105: Analyzer offline for quarterly linearity checks
Note on C1106: Analyzer offline for quarterly linearity checks
Note on F1105: Analyzer offline for quarterly linearity checks
Note on F1106: Analyzer offline for quarterly linearity checks
Note on O915: High HP steam temperature condition cleared and unit was brought back to mode 6 operation.
Note on P915: Unit began auto shutdown runback due to high HP steam temperature

## April CEMS Raw data
This data is raw hourly CEMs database data which may include invalid data such as values obtained during calibration checks.
2008-04-01
| Record# | DATE | TIME | CATTMP12 | COH13 | CO_14 | CO_COR15 | CO_HCOR16 | GAS17 | GEN18 | GEN29 | HGAS110 | NH3FLO112 | NOX113 | NOX1I14 | NOXCOR115 | NOXH116 | NOXHCOR117 | NOXHRT118 | NOXRT119 | OXY120
| 1 | 2008-04-01 | 0 | 675.3 | -2.6 | 0.07 | 0.1 | -2.4 | 23.05 | 190.8 | 272.4 | -1 | 133.8 | 2.52 | 12.37 | 2.1 | 2.47 | 2.1 | 0.008 | 0.008 | 13.84
| 2 | 2008-04-01 | 10000 | 678.3 | -2.8 | 0.06 | 0 | -2.3 | 23.23 | 191.7 | 273.9 | -1 | 132.4 | 2.53 | 12.17 | 2.1 | 2.48 | 2.1 | 0.008 | 0.008 | 13.84
| 3 | 2008-04-01 | 20000 | 678.2 | -2.7 | 0.05 | 0 | -2.2 | 23.26 | 192 | 274.3 | -1 | 131.5 | 2.52 | 12.11 | 2.1 | 2.48 | 2.1 | 0.008 | 0.008 | 13.84
| 4 | 2008-04-01 | 30000 | 678.4 | -3 | 0.05 | 0 | -2.3 | 23.26 | 192.1 | 274.3 | -1 | 129.7 | 2.53 | 11.97 | 2.1 | 2.49 | 2.1 | 0.008 | 0.008 | 13.83
| 5 | 2008-04-01 | 40000 | 678.2 | -2.5 | 0.05 | 0 | -2.1 | 23.21 | 192.1 | 274.2 | -1 | 129.2 | 2.53 | 11.93 | 2.1 | 2.49 | 2.1 | 0.008 | 0.008 | 13.83
| 6 | 2008-04-01 | 50000 | 678.3 | -2.7 | 0.05 | 0 | -2.3 | 23.14 | 192 | 274.1 | -0.9 | 129.6 | 2.53 | 11.97 | 2.1 | 2.49 | 2.1 | 0.008 | 0.008 | 13.82
| 7 | 2008-04-01 | 60000 | 678.2 | -2.6 | 0.06 | 0.1 | -2.1 | 23.09 | 192 | 274.1 | -1 | 131.2 | 2.54 | 11.89 | 2.1 | 2.49 | 2.1 | 0.008 | 0.008 | 13.81
| 8 | 2008-04-01 | 70000 | 678.3 | 44.3 | 3.99 | 3.8 | -2.7 | 23.18 | 192 | 273.3 | -0.9 | 130.5 | 3.78 | 11.87 | 0.7 | 10.34 | 2.9 | 0.047 | 0.043 | 11.74
| 9 | 2008-04-01 | 80000 | 678.3 | 92.9 | 2.32 | 4.2 | 0.8 | 23.11 | 192 | 273.2 | -1 | 136 | 3.44 | 11.88 | 5.1 | 11.3 | 7.1 | 177.291 | 197.86 | 12.65
| 10 | 2008-04-01 | 90000 | 678.3 | -2.7 | 0.09 | 0.1 | -2.1 | 23.04 | 191.1 | 272 | -1 | 133.8 | 2.58 | 12.05 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.71
| 11 | 2008-04-01 | 100000 | 678.4 | -2.9 | 0.08 | 0.1 | -2.5 | 22.85 | 188.5 | 269.3 | -0.9 | 138.1 | 2.58 | 12.32 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.72
| 12 | 2008-04-01 | 110000 | 677 | -2.6 | 0.07 | 0.1 | -2.1 | 22.59 | 186.5 | 267.4 | -1 | 140.2 | 2.57 | 12.48 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.72
| 13 | 2008-04-01 | 120000 | 676.3 | -2.7 | 0.07 | 0.1 | -2.2 | 22.52 | 185.3 | 265.8 | -1 | 139.9 | 2.57 | 12.46 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.73
| 14 | 2008-04-01 | 130000 | 675.3 | -2.5 | 0.06 | 0 | -2 | 22.38 | 184.4 | 264.9 | -1 | 139.8 | 2.58 | 12.47 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.71
| 15 | 2008-04-01 | 140000 | 675.1 | -2.7 | 0.06 | 0.1 | -2.3 | 22.27 | 183.6 | 264 | -1 | 140.9 | 2.58 | 12.53 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.7
| 16 | 2008-04-01 | 150000 | 674 | -3 | 0.06 | 0.1 | -2.5 | 22.27 | 182.9 | 263.2 | -1 | 141.7 | 2.58 | 12.58 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.7
| 17 | 2008-04-01 | 160000 | 672.8 | -2.6 | 0.07 | 0.1 | -2.2 | 22.25 | 182.6 | 262.9 | -1 | 143.1 | 2.58 | 12.67 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.69
| 18 | 2008-04-01 | 170000 | 672.8 | -2.6 | 0.06 | 0.1 | -2.1 | 22.21 | 182.2 | 262.5 | -1 | 142.6 | 2.58 | 12.64 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.68
| 19 | 2008-04-01 | 180000 | 672.8 | -2.5 | 0.06 | 0 | -2 | 22.27 | 182.8 | 263 | -1 | 140.3 | 2.57 | 12.48 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.67
| 20 | 2008-04-01 | 190000 | 673.1 | -2.6 | 0.06 | 0 | -2.2 | 22.27 | 183.5 | 263.9 | -0.9 | 139.2 | 2.58 | 12.4 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.67
| 21 | 2008-04-01 | 200000 | 675.1 | -2.9 | 0.06 | 0.1 | -2.4 | 22.39 | 184.7 | 265.1 | -1 | 138 | 2.58 | 12.34 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.67
| 22 | 2008-04-01 | 210000 | 675.7 | -2.8 | 0.06 | 0.1 | -2.4 | 22.53 | 185.6 | 266.1 | -1 | 137.1 | 2.58 | 12.34 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.68
| 23 | 2008-04-01 | 220000 | 676.9 | -2.7 | 0.07 | 0.1 | -2.2 | 22.54 | 186.4 | 266.9 | -1 | 134.2 | 2.57 | 12.34 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.68
| 24 | 2008-04-01 | 230000 | 676.8 | -2.7 | 0.07 | 0.1 | -2 | 22.63 | 187 | 267.5 | -1 | 133.1 | 2.57 | 12.25 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.68
| 25 | 2008-04-02 | 0 | 643.1 | -2.7 | 0.14 | 0.1 | -2.5 | 16.83 | 124.7 | 189.3 | -1 | 51 | 2.56 | 8.09 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.87
| 26 | 2008-04-02 | 10000 | 639 | -2.5 | 0.14 | 0.1 | -1.9 | 17.21 | 128.4 | 192.8 | -1 | 53.3 | 2.5 | 7.81 | 2.1 | 2.35 | 2 | 0.007 | 0.008 | 13.86
| 27 | 2008-04-02 | 20000 | 639.3 | -2.5 | 0.15 | 0.1 | -2.2 | 17.16 | 128.6 | 192.9 | -1 | 53 | 2.52 | 7.79 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.86
| 28 | 2008-04-02 | 30000 | 639 | -2.8 | 0.16 | 0.1 | -2.4 | 17.26 | 129.3 | 193.7 | -1 | 54.1 | 2.53 | 7.81 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.85
| 29 | 2008-04-02 | 40000 | 672.3 | -2.7 | 0.1 | 0.1 | -2.2 | 23.02 | 189.5 | 269.3 | -0.9 | 133.4 | 2.54 | 12.08 | 2.1 | 2.39 | 1.9 | 0.007 | 0.008 | 13.67
| 30 | 2008-04-02 | 50000 | 673.9 | -2.9 | 0.08 | 0.1 | -2.4 | 22.64 | 187 | 266.1 | -0.9 | 110.9 | 2.48 | 10.48 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.79
| 31 | 2008-04-02 | 60000 | 674.3 | -2.8 | 0.08 | 0.1 | -2.1 | 22.73 | 187.6 | 266.5 | -1 | 121.2 | 2 | 10.7 | 1.7 | 1.88 | 1.6 | 0.006 | 0.006 | 13.78
| 32 | 2008-04-02 | 70000 | 674.6 | 142.3 | 6.23 | 10.4 | -18.8 | 22.82 | 187.8 | 267.2 | -0.9 | 130.4 | 4.54 | 10.88 | -3.3 | 19.36 | 1.2 | 0.029 | 0.013 | 10.6
| 33 | 2008-04-02 | 80000 | 677.3 | -2.9 | 0.11 | 0.1 | -2.4 | 22.89 | 188.8 | 269.3 | -0.9 | 132.4 | 2.56 | 12.16 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.72
| 34 | 2008-04-02 | 90000 | 677.8 | -2.9 | 0.08 | 0.1 | -2.2 | 22.62 | 187.3 | 268.1 | -1 | 135.3 | 2.59 | 12.39 | 2.1 | 2.45 | 2 | 0.007 | 0.008 | 13.69
| 35 | 2008-04-02 | 100000 | 676.6 | -2.8 | 0.09 | 0.1 | -2.2 | 22.52 | 185.8 | 266.7 | -1 | 139.9 | 2.59 | 12.47 | 2.1 | 2.45 | 2 | 0.007 | 0.008 | 13.69
| 36 | 2008-04-02 | 110000 | 674.7 | -2.9 | 0.08 | 0.1 | -2.4 | 22.31 | 184 | 264.4 | -0.9 | 137.4 | 2.57 | 12.3 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.72
| 37 | 2008-04-02 | 120000 | 674.9 | -2.8 | 0.08 | 0.1 | -2.4 | 22.27 | 183.1 | 263.7 | -1 | 141.1 | 2.59 | 12.52 | 2.1 | 2.45 | 2 | 0.007 | 0.008 | 13.7
| 38 | 2008-04-02 | 130000 | 643.3 | -2.9 | 0.1 | 0.1 | -2.3 | 16.74 | 124.9 | 189.8 | -0.9 | 61.8 | 1.82 | 8.2 | 1.5 | 1.71 | 1.4 | 0.005 | 0.006 | 13.9
| 39 | 2008-04-02 | 140000 | 638.2 | -2.6 | 0.11 | 0.1 | -2.2 | 17 | 128.4 | 192.9 | -0.9 | 52.4 | 2.48 | 7.74 | 2.1 | 2.34 | 2 | 0.007 | 0.008 | 13.9
| 40 | 2008-04-02 | 150000 | 637.4 | -2.4 | 0.11 | 0.1 | -2.2 | 17 | 128.6 | 193.1 | -1 | 52.5 | 2.51 | 7.75 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.9
| 41 | 2008-04-02 | 160000 | 638 | -3.4 | 0.11 | 0.1 | -2.7 | 17.09 | 129 | 193.7 | -0.9 | 52.8 | 2.5 | 7.75 | 2.1 | 2.35 | 2 | 0.007 | 0.008 | 13.89
| 42 | 2008-04-02 | 170000 | 637.5 | -2.9 | 0.12 | 0.1 | -2.4 | 16.98 | 128.5 | 193.1 | -1 | 52.6 | 2.51 | 7.77 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.89
| 43 | 2008-04-02 | 180000 | 637.4 | -2.7 | 0.12 | 0.1 | -2.4 | 17.04 | 128.5 | 193.1 | -0.9 | 52.6 | 2.51 | 7.77 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.89
| 44 | 2008-04-02 | 190000 | 637 | -2.6 | 0.15 | 0.1 | -2.3 | 16.99 | 127.9 | 192.3 | -1 | 51.2 | 2.5 | 7.69 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.87
| 45 | 2008-04-02 | 200000 | 636.7 | -2.4 | 0.18 | 0.2 | -2.1 | 17.04 | 128.2 | 192.5 | -1 | 50.6 | 2.51 | 7.68 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.88
| 46 | 2008-04-02 | 210000 | 635.7 | -2.7 | 0.16 | 0.1 | -2.3 | 17.14 | 128.3 | 192.7 | -1 | 50.1 | 2.49 | 7.63 | 2.1 | 2.35 | 2 | 0.007 | 0.008 | 13.88
| 47 | 2008-04-02 | 220000 | 636 | -2.7 | 0.16 | 0.1 | -2.3 | 17.15 | 128.5 | 193.2 | -1 | 48.7 | 2.52 | 7.57 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.87
| 48 | 2008-04-02 | 230000 | 636.3 | -2.8 | 0.16 | 0.1 | -2.3 | 17.19 | 128.9 | 193.6 | -1 | 49.3 | 2.51 | 7.57 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.87
| 49 | 2008-04-03 | 0 | 636.8 | -3.2 | 0.17 | 0.1 | -2.8 | 17.16 | 128.6 | 193.3 | -1 | 49.1 | 2.52 | 7.59 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.87
| 50 | 2008-04-03 | 10000 | 637.3 | -2.9 | 0.18 | 0.2 | -2.5 | 17.16 | 128 | 192.5 | -1 | 49.1 | 2.52 | 7.62 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.87
| 51 | 2008-04-03 | 20000 | 637 | -2.8 | 0.19 | 0.2 | -2.3 | 17.17 | 128.1 | 192.7 | -1 | 49.4 | 2.52 | 7.64 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.87
| 52 | 2008-04-03 | 30000 | 638.5 | -3.1 | 0.19 | 0.2 | -2.5 | 17.33 | 129.3 | 194.1 | -1 | 50 | 2.5 | 7.61 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.87
| 53 | 2008-04-03 | 40000 | 638.8 | -2.7 | 0.19 | 0.2 | -2.3 | 17.29 | 129.1 | 193.8 | -0.9 | 49.8 | 2.52 | 7.61 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.87
| 54 | 2008-04-03 | 50000 | 639.3 | -2.8 | 0.19 | 0.2 | -2.3 | 17.6 | 132.7 | 197.7 | -1 | 55.1 | 2.5 | 7.73 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.87
| 55 | 2008-04-03 | 60000 | 673.9 | -2.6 | 0.12 | 0.1 | -2.1 | 23.01 | 190.4 | 270.7 | -1 | 124.5 | 2.46 | 11.29 | 2 | 2.32 | 1.9 | 0.007 | 0.008 | 13.7
| 56 | 2008-04-03 | 70000 | 677.7 | 139.7 | 6.23 | 10.7 | 1.9 | 23.04 | 190.8 | 271.5 | -1 | 134.1 | 4.9 | 11.48 | 5.6 | 19.57 | 9.7 | 49.105 | 49.09 | 10.55
| 57 | 2008-04-03 | 80000 | 677.6 | -2.7 | 0.16 | 0.1 | -2.2 | 22.94 | 189.4 | 270 | -1 | 143 | 2.37 | 11.53 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.76
| 58 | 2008-04-03 | 90000 | 677.7 | -2.6 | 0.12 | 0.1 | -2.1 | 22.9 | 189.2 | 269.7 | -1 | 137.6 | 2.62 | 11.99 | 2.1 | 2.55 | 2.1 | 0.008 | 0.008 | 13.71
| 59 | 2008-04-03 | 100000 | 677.9 | -2.8 | 0.14 | 0.1 | -2.2 | 22.77 | 187.5 | 268.5 | -1 | 146.1 | 2.6 | 12.29 | 2.1 | 2.53 | 2.1 | 0.008 | 0.008 | 13.68
| 60 | 2008-04-03 | 110000 | 676.3 | -3 | 0.14 | 0.1 | -2.5 | 22.5 | 185.3 | 266.5 | -1 | 148.8 | 2.59 | 12.49 | 2.1 | 2.52 | 2.1 | 0.008 | 0.008 | 13.68
| 61 | 2008-04-03 | 120000 | 674.6 | -2.8 | 0.13 | 0.1 | -2.3 | 22.28 | 183.3 | 264.4 | -1 | 148.7 | 2.59 | 12.54 | 2.1 | 2.52 | 2.1 | 0.008 | 0.008 | 13.69
| 62 | 2008-04-03 | 130000 | 673.2 | -2.7 | 0.13 | 0.1 | -2.2 | 22.18 | 181.8 | 262.9 | -1 | 149.9 | 2.59 | 12.65 | 2.1 | 2.52 | 2.1 | 0.008 | 0.008 | 13.69
| 63 | 2008-04-03 | 140000 | 672.1 | -2.8 | 0.12 | 0.1 | -2.1 | 21.93 | 179.8 | 260.1 | -1 | 142.7 | 2.49 | 12.17 | 2 | 2.41 | 2 | 0.007 | 0.008 | 13.73
| 64 | 2008-04-03 | 150000 | 672.1 | -2.8 | 0.12 | 0.1 | -2.2 | 21.94 | 179.8 | 260.5 | -1 | 152.6 | 2.68 | 12.88 | 2.2 | 2.6 | 2.1 | 0.008 | 0.008 | 13.68
| 65 | 2008-04-03 | 160000 | 670 | -2.8 | 0.12 | 0.1 | -2.2 | 21.83 | 179.1 | 259.9 | -0.9 | 153.1 | 2.58 | 12.91 | 2.1 | 2.51 | 2 | 0.008 | 0.008 | 13.67
| 66 | 2008-04-03 | 170000 | 669.7 | -2.9 | 0.12 | 0.1 | -2.2 | 21.83 | 179.1 | 259.7 | -1 | 150.4 | 2.58 | 12.73 | 2.1 | 2.5 | 2 | 0.007 | 0.008 | 13.66
| 67 | 2008-04-03 | 180000 | 671.4 | -2.4 | 0.12 | 0.1 | -1.9 | 22.02 | 180.5 | 261.1 | -1 | 147.4 | 2.58 | 12.5 | 2.1 | 2.5 | 2 | 0.007 | 0.008 | 13.64
| 68 | 2008-04-03 | 190000 | 671.9 | -2.7 | 0.12 | 0.1 | -2.2 | 22.02 | 181.4 | 261.4 | -1 | 138.4 | 2.58 | 11.9 | 2.1 | 2.51 | 2 | 0.008 | 0.008 | 13.67
| 69 | 2008-04-03 | 200000 | 673.2 | -2.7 | 0.12 | 0.1 | -2 | 22.26 | 183.3 | 264.3 | -1 | 144.5 | 2.59 | 12.29 | 2.1 | 2.51 | 2 | 0.007 | 0.008 | 13.63
| 70 | 2008-04-03 | 210000 | 673.5 | -3.2 | 0.12 | 0.1 | -2.5 | 22.27 | 184 | 265 | -1 | 143 | 2.6 | 12.22 | 2.1 | 2.52 | 2 | 0.008 | 0.008 | 13.62
| 71 | 2008-04-03 | 220000 | 674.8 | -2.9 | 0.13 | 0.1 | -2.4 | 22.3 | 184 | 264.6 | -0.9 | 139.6 | 2.59 | 12.02 | 2.1 | 2.51 | 2 | 0.007 | 0.008 | 13.63
| 72 | 2008-04-03 | 230000 | 675 | -2.6 | 0.12 | 0.1 | -2.1 | 22.49 | 185.1 | 266.1 | -0.9 | 140.2 | 2.61 | 12.04 | 2.1 | 2.54 | 2 | 0.007 | 0.008 | 13.6
| 73 | 2008-04-04 | 0 | 675 | -2.8 | 0.12 | 0.1 | -2.2 | 22.53 | 185.3 | 266.1 | -1 | 139.3 | 2.61 | 12.03 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.59
| 74 | 2008-04-04 | 10000 | 674.9 | -2.7 | 0.12 | 0.1 | -2.2 | 22.54 | 185.4 | 266.2 | -1 | 139.1 | 2.62 | 12.01 | 2.1 | 2.54 | 2.1 | 0.008 | 0.008 | 13.59
| 75 | 2008-04-04 | 20000 | 675.1 | -2.8 | 0.12 | 0.1 | -2.2 | 22.53 | 185.4 | 266.2 | -1 | 139 | 2.61 | 12.01 | 2.1 | 2.54 | 2 | 0.008 | 0.008 | 13.59
| 76 | 2008-04-04 | 30000 | 674.9 | -3 | 0.11 | 0.1 | -2.5 | 22.53 | 185.4 | 266.3 | -0.9 | 139 | 2.61 | 11.99 | 2.1 | 2.54 | 2.1 | 0.008 | 0.008 | 13.59
| 77 | 2008-04-04 | 40000 | 675.7 | -3.1 | 0.12 | 0.1 | -2.5 | 22.53 | 185.3 | 266.1 | -0.9 | 139.3 | 2.62 | 11.99 | 2.1 | 2.55 | 2.1 | 0.008 | 0.008 | 13.59
| 78 | 2008-04-04 | 50000 | 675.4 | -2.8 | 0.11 | 0.1 | -2.2 | 22.48 | 185.3 | 266 | -0.9 | 139.2 | 2.61 | 11.97 | 2.1 | 2.53 | 2 | 0.008 | 0.008 | 13.58
| 79 | 2008-04-04 | 60000 | 674.9 | -2.8 | 0.12 | 0.1 | -2.3 | 22.31 | 185.2 | 265.7 | -0.9 | 137.7 | 2.55 | 11.88 | 2 | 2.48 | 2 | 0.007 | 0.008 | 13.71
| 80 | 2008-04-04 | 70000 | 675 | 141.2 | 6.26 | 4 | 30.9 | 22.28 | 184.9 | 265.2 | -0.9 | 136.6 | 4.99 | 12 | 4.1 | 19.52 | 8.3 | 0.031 | 0.015 | 10.37
| 81 | 2008-04-04 | 80000 | 674.4 | -2.8 | 0.14 | 0.1 | -2.3 | 22.17 | 183.4 | 263.2 | -0.9 | 126.7 | 2.51 | 11.29 | 2 | 2.44 | 2 | 0.007 | 0.008 | 13.64
| 82 | 2008-04-04 | 90000 | 674.2 | -3.1 | 0.11 | 0.1 | -2.5 | 22.3 | 184.1 | 263.9 | -0.9 | 128.3 | 2.58 | 11.45 | 2.1 | 2.5 | 2 | 0.007 | 0.008 | 13.62
| 83 | 2008-04-04 | 100000 | 674.4 | -2.5 | 0.12 | 0.1 | -2 | 22.3 | 185.2 | 265.3 | -0.9 | 140.3 | 2.57 | 12.07 | 2.1 | 2.5 | 2 | 0.007 | 0.008 | 13.58
| 84 | 2008-04-04 | 110000 | 674.7 | -3 | 0.11 | 0.1 | -2.4 | 22.28 | 184.8 | 265.3 | -1 | 138.3 | 2.63 | 12.17 | 2.1 | 2.55 | 2.1 | 0.008 | 0.008 | 13.59
| 85 | 2008-04-04 | 120000 | 673 | -2.6 | 0.11 | 0.1 | -2.2 | 22.28 | 184.2 | 264.6 | -1 | 137.8 | 2.62 | 12.16 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.59
| 86 | 2008-04-04 | 130000 | 673.5 | -3 | 0.11 | 0.1 | -2.5 | 22.38 | 184.7 | 265.2 | -1 | 136.5 | 2.61 | 12.09 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.58
| 87 | 2008-04-04 | 140000 | 673.4 | -2.9 | 0.11 | 0.1 | -2.3 | 22.27 | 183.6 | 264.1 | -1 | 139.2 | 2.64 | 12.25 | 2.1 | 2.56 | 2.1 | 0.008 | 0.008 | 13.59
| 88 | 2008-04-04 | 150000 | 672.8 | -2.6 | 0.12 | 0.1 | -2.2 | 22.32 | 184.3 | 264.7 | -0.9 | 140.7 | 2.59 | 12.3 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.6
| 89 | 2008-04-04 | 160000 | 672.9 | -2.8 | 0.13 | 0.1 | -2.3 | 22.29 | 184.1 | 264.5 | -0.9 | 139 | 2.63 | 12.28 | 2.1 | 2.55 | 2.1 | 0.008 | 0.008 | 13.59
| 90 | 2008-04-04 | 170000 | 672.5 | -2.3 | 0.12 | 0.1 | -1.8 | 22.26 | 183.5 | 264 | -0.9 | 140.2 | 2.61 | 12.36 | 2.1 | 2.54 | 2 | 0.008 | 0.008 | 13.59
| 91 | 2008-04-04 | 180000 | 672.7 | -3 | 0.13 | 0.1 | -2.5 | 22.27 | 184.1 | 264.5 | -0.9 | 138.7 | 2.6 | 12.27 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.59
| 92 | 2008-04-04 | 190000 | 673.7 | -2.6 | 0.14 | 0.1 | -2.1 | 22.27 | 184.6 | 265.2 | -1 | 138.6 | 2.61 | 12.29 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.59
| 93 | 2008-04-04 | 200000 | 674.9 | -3 | 0.14 | 0.1 | -2.5 | 22.37 | 185.2 | 265.8 | -1 | 138.5 | 2.61 | 12.25 | 2.1 | 2.54 | 2.1 | 0.008 | 0.008 | 13.59
| 94 | 2008-04-04 | 210000 | 674.8 | -3 | 0.13 | 0.1 | -2.6 | 22.48 | 185.2 | 266 | -1 | 138.7 | 2.62 | 12.27 | 2.1 | 2.54 | 2.1 | 0.008 | 0.008 | 13.6
| 95 | 2008-04-04 | 220000 | 674.7 | -3 | 0.14 | 0.1 | -2.2 | 22.53 | 185.6 | 266.3 | -1 | 138.8 | 2.6 | 12.27 | 2.1 | 2.53 | 2 | 0.008 | 0.008 | 13.61
| 96 | 2008-04-04 | 230000 | 675.4 | -2.9 | 0.15 | 0.1 | -2.3 | 22.53 | 186 | 266.8 | -1 | 138.6 | 2.61 | 12.26 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.61
| 97 | 2008-04-05 | 0 | 676.7 | -2.5 | 0.15 | 0.1 | -2.1 | 22.53 | 185.8 | 266.6 | -1 | 138.8 | 2.61 | 12.26 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.6
| 98 | 2008-04-05 | 10000 | 676.8 | -2.9 | 0.15 | 0.1 | -2.3 | 22.53 | 186.2 | 266.9 | -1 | 138.3 | 2.61 | 12.19 | 2.1 | 2.55 | 2.1 | 0.008 | 0.008 | 13.59
| 99 | 2008-04-05 | 20000 | 676.8 | -2.4 | 0.15 | 0.1 | -2 | 22.54 | 186.3 | 267 | -1 | 137.2 | 2.61 | 12.18 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.59
| 100 | 2008-04-05 | 30000 | 676.7 | -2.8 | 0.15 | 0.1 | -2.2 | 22.53 | 186.3 | 267 | -1 | 136.8 | 2.62 | 12.11 | 2.1 | 2.54 | 2.1 | 0.008 | 0.008 | 13.59
| 101 | 2008-04-05 | 40000 | 676.8 | -2.8 | 0.16 | 0.1 | -2.4 | 22.53 | 186.8 | 267.6 | -1 | 136.3 | 2.62 | 12.09 | 2.1 | 2.54 | 2 | 0.007 | 0.008 | 13.58
| 102 | 2008-04-05 | 50000 | 677.4 | -3.1 | 0.17 | 0.1 | -2.4 | 22.54 | 187.1 | 267.9 | -1 | 136 | 2.62 | 12.01 | 2.1 | 2.55 | 2.1 | 0.008 | 0.008 | 13.58
| 103 | 2008-04-05 | 60000 | 677.4 | -2.5 | 0.17 | 0.7 | -7.8 | 22.55 | 187.2 | 268 | -1 | 136.5 | 2.4 | 12.03 | 2 | 2.33 | 1.9 | 0.007 | 0.008 | 14.14
| 104 | 2008-04-05 | 70000 | 677.5 | 140.2 | 6.37 | 4.4 | 32.7 | 22.54 | 186.9 | 267.6 | -0.9 | 142.3 | 5.03 | 12.08 | 3.2 | 19.51 | 7.3 | 0.027 | 0.012 | 9.96
| 105 | 2008-04-05 | 80000 | 676.9 | -2.7 | 0.2 | 0.2 | -2.1 | 22.52 | 186 | 266.6 | -0.9 | 138.9 | 2.6 | 12.11 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.58
| 106 | 2008-04-05 | 90000 | 676.8 | -3 | 0.17 | 0.1 | -2.5 | 22.37 | 185.1 | 265.6 | -0.9 | 137.2 | 2.62 | 12.17 | 2.1 | 2.54 | 2 | 0.008 | 0.008 | 13.57
| 107 | 2008-04-05 | 100000 | 675 | -2.6 | 0.16 | 0.1 | -2.1 | 22.27 | 184 | 264.4 | -0.9 | 139 | 2.63 | 12.23 | 2.1 | 2.56 | 2.1 | 0.008 | 0.008 | 13.58
| 108 | 2008-04-05 | 110000 | 674.4 | -2.8 | 0.16 | 0.1 | -2.4 | 22.26 | 183.1 | 263.4 | -1 | 139.2 | 2.62 | 12.28 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.57
| 109 | 2008-04-05 | 120000 | 672.9 | -2.5 | 0.17 | 0.1 | -2.1 | 22.16 | 182.8 | 262.7 | -0.9 | 136.5 | 2.63 | 12.18 | 2.1 | 2.56 | 2.1 | 0.008 | 0.008 | 13.57
| 110 | 2008-04-05 | 130000 | 672.6 | -2.9 | 0.17 | 0.1 | -2.4 | 22.13 | 182.6 | 262.5 | -0.9 | 136.7 | 2.63 | 12.2 | 2.1 | 2.55 | 2 | 0.008 | 0.008 | 13.56
| 111 | 2008-04-05 | 140000 | 672.8 | -3.1 | 0.17 | 0.1 | -2.3 | 22.18 | 182.8 | 262.7 | -1 | 139 | 2.63 | 12.29 | 2.1 | 2.55 | 2 | 0.008 | 0.008 | 13.55
| 112 | 2008-04-05 | 150000 | 676.1 | -3 | 0.17 | 0.1 | -2.2 | 22.18 | 182.8 | 264.3 | 113.9 | 136.2 | 2.7 | 12.33 | 2.1 | 2.62 | 2.1 | 0.008 | 0.008 | 13.44
| 113 | 2008-04-05 | 160000 | 753.7 | -2.6 | -0.02 | 0 | -1.9 | 22.06 | 182.1 | 295.2 | 463.2 | 169 | 3.18 | 15.1 | 2.2 | 3.09 | 2.1 | 0.008 | 0.008 | 12.29
| 114 | 2008-04-05 | 170000 | 758.6 | -3.1 | -0.02 | 0 | -2 | 22.06 | 181.8 | 295.4 | 463.2 | 169.5 | 3.07 | 14.92 | 2.1 | 2.98 | 2 | 0.008 | 0.008 | 12.32
| 115 | 2008-04-05 | 180000 | 756.1 | -3.2 | -0.02 | 0 | -2.3 | 22.05 | 181.8 | 294.5 | 463.2 | 168.4 | 3.06 | 14.81 | 2.1 | 2.97 | 2 | 0.008 | 0.008 | 12.35
| 116 | 2008-04-05 | 190000 | 758.6 | -2.9 | -0.03 | 0 | -2 | 22.05 | 181.9 | 296 | 463.2 | 173.6 | 2.95 | 14.94 | 2 | 2.86 | 2 | 0.007 | 0.007 | 12.29
| 117 | 2008-04-05 | 200000 | 758.9 | -2.8 | -0.03 | 0 | -1.9 | 22.06 | 182.5 | 296.7 | 463.2 | 172.8 | 2.94 | 14.86 | 2 | 2.86 | 2 | 0.007 | 0.007 | 12.29
| 118 | 2008-04-05 | 210000 | 758.6 | -3 | -0.03 | 0 | -1.9 | 22.06 | 182.4 | 296.4 | 463.2 | 172.7 | 2.96 | 14.87 | 2 | 2.89 | 2 | 0.007 | 0.007 | 12.28
| 119 | 2008-04-05 | 220000 | 758.1 | -2.8 | -0.03 | 0 | -2.1 | 22.06 | 182.5 | 294.3 | 463.2 | 175.4 | 2.9 | 14.89 | 2 | 2.82 | 1.9 | 0.007 | 0.007 | 12.31
| 120 | 2008-04-05 | 230000 | 684.7 | -2.5 | 0.14 | 0.1 | -2.2 | 22.06 | 182.7 | 265.4 | 29.6 | 139.1 | 2.47 | 12.09 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.44
| 121 | 2008-04-06 | 0 | 673.1 | -3.1 | 0.16 | 0.1 | -2.4 | 22.06 | 182.6 | 262.6 | -1 | 136.4 | 2.6 | 12.07 | 2.1 | 2.51 | 2 | 0.007 | 0.008 | 13.48
| 122 | 2008-04-06 | 10000 | 672.8 | -3.2 | 0.17 | 0.1 | -2.3 | 22.08 | 182.7 | 262.6 | -1 | 136.9 | 2.59 | 12.06 | 2.1 | 2.51 | 2 | 0.007 | 0.008 | 13.48
| 123 | 2008-04-06 | 20000 | 673 | -2.7 | 0.16 | 0.1 | -2.1 | 22.11 | 182.9 | 262.6 | -1 | 136.9 | 2.59 | 12.07 | 2.1 | 2.51 | 2 | 0.007 | 0.008 | 13.48
| 124 | 2008-04-06 | 30000 | 673 | -2.8 | 0.16 | 0.1 | -2.2 | 22.16 | 182.8 | 262.7 | -1 | 136.7 | 2.59 | 12.05 | 2.1 | 2.53 | 2 | 0.007 | 0.008 | 13.49
| 125 | 2008-04-06 | 40000 | 673.1 | -2.7 | 0.15 | 0.1 | -2 | 22.24 | 183.1 | 263.1 | -1 | 137.2 | 2.58 | 12.07 | 2.1 | 2.5 | 2 | 0.007 | 0.008 | 13.5
| 126 | 2008-04-06 | 50000 | 673.6 | -2.5 | 0.16 | 0.1 | -2.1 | 22.27 | 183.4 | 263.5 | -0.9 | 136.5 | 2.59 | 12.05 | 2.1 | 2.51 | 2 | 0.007 | 0.008 | 13.5
| 127 | 2008-04-06 | 60000 | 619.4 | -1.1 | 1.36 | 9.8 | -16.8 | 10.09 | 82 | 120.4 | -0.9 | 64 | 1.42 | 6.22 | 1.5 | 1.4 | 1.6 | 0.006 | 0.006 | 17.18
| 128 | 2008-04-06 | 70000 | 441 | -2.6 | 0.29 | 6.2 | -54 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.01 | 0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.62
| 129 | 2008-04-06 | 80000 | 438.2 | -0.7 | 2.43 | 7.6 | -53.2 | 1.15 | 2.1 | 2.9 | -1 | 0.9 | 1.73 | 5.37 | 2.7 | 5.78 | 9 | 0.034 | 0.01 | 19.97
| 130 | 2008-04-06 | 90000 | 605.7 | 21 | 18.08 | 18.8 | 21.6 | 10.29 | 51.7 | 64.1 | -1 | 56.9 | 9.98 | 26.23 | 10.3 | 55.08 | 56.6 | 0.208 | 0.038 | 15.1
| 131 | 2008-04-06 | 100000 | 644.2 | 132 | 5.57 | 3.9 | 27.4 | 20.65 | 169 | 241.5 | -1 | 96.6 | 4.52 | 9.15 | 4.3 | 17.8 | 8 | 0.03 | 0.016 | 10.76
| 132 | 2008-04-06 | 110000 | 668.1 | 8 | 0.98 | 0.9 | 1.2 | 22.14 | 182.3 | 262.2 | -1 | 139.2 | 3.06 | 12.3 | 2.5 | 4.54 | 2.9 | 0.011 | 0.009 | 13.41
| 133 | 2008-04-06 | 120000 | 672.7 | -3 | 0.18 | 0.1 | -2.3 | 22.18 | 182.9 | 263.8 | -1 | 144.8 | 2.56 | 12.37 | 2.1 | 2.48 | 2 | 0.007 | 0.008 | 13.55
| 134 | 2008-04-06 | 130000 | 672.7 | -2.6 | 0.17 | 0.1 | -2 | 22.13 | 182.6 | 263.5 | -0.9 | 144.7 | 2.57 | 12.39 | 2.1 | 2.5 | 2 | 0.007 | 0.008 | 13.54
| 135 | 2008-04-06 | 140000 | 643.5 | -2.9 | 0.19 | 0.2 | -2.2 | 16.68 | 124.3 | 189.9 | -0.9 | 62.7 | 2.53 | 8.62 | 2.1 | 2.45 | 2 | 0.007 | 0.008 | 13.72
| 136 | 2008-04-06 | 150000 | 636.9 | -2.4 | 0.19 | 0.2 | -2.2 | 16.98 | 128.2 | 193 | -1 | 55.2 | 2.46 | 7.51 | 2 | 2.39 | 2 | 0.007 | 0.008 | 13.75
| 137 | 2008-04-06 | 160000 | 636.2 | -2.6 | 0.2 | 0.2 | -2.2 | 16.92 | 127.8 | 192.7 | -1 | 55.1 | 2.51 | 7.58 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.77
| 138 | 2008-04-06 | 170000 | 636.6 | -2.6 | 0.2 | 0.2 | -2.2 | 16.96 | 127.6 | 192.5 | -1 | 55.3 | 2.52 | 7.63 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.77
| 139 | 2008-04-06 | 180000 | 636.4 | -2.7 | 0.2 | 0.2 | -2.4 | 17.33 | 132.2 | 197.8 | -1 | 62 | 2.57 | 7.84 | 2.1 | 2.49 | 2.1 | 0.008 | 0.008 | 13.76
| 140 | 2008-04-06 | 190000 | 670.2 | -2.9 | 0.19 | 0.2 | -2.3 | 22.28 | 184 | 264.9 | -1 | 143.4 | 2.59 | 12.24 | 2.1 | 2.52 | 2 | 0.007 | 0.008 | 13.57
| 141 | 2008-04-06 | 200000 | 673.1 | -2.9 | 0.18 | 0.1 | -2.2 | 22.3 | 183.7 | 264.5 | -1 | 135.5 | 2.6 | 11.8 | 2.1 | 2.52 | 2 | 0.007 | 0.008 | 13.61
| 142 | 2008-04-06 | 210000 | 674.7 | -3.3 | 0.18 | 0.1 | -2.5 | 22.5 | 185.2 | 266.6 | -1 | 141.5 | 2.62 | 12.2 | 2.1 | 2.54 | 2.1 | 0.008 | 0.008 | 13.59
| 143 | 2008-04-06 | 220000 | 674.9 | -2.3 | 0.17 | 0.1 | -2.1 | 22.43 | 184.3 | 265.7 | -1 | 140.9 | 2.58 | 12.13 | 2.1 | 2.51 | 2 | 0.007 | 0.008 | 13.6
| 144 | 2008-04-06 | 230000 | 572.2 | 3.7 | 4.46 | 21.2 | -37.2 | 2.56 | 14.2 | 24.8 | -1 | 9.1 | 1.86 | 5.71 | 2.9 | 7.82 | 9.2 | 0.035 | 0.011 | 19.18
| 145 | 2008-04-07 | 0 | 449.5 | -3 | 0.32 | 12 | -112.8 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | 0.01 | 0.03 | 0.4 | 0.01 | 0.4 | 0.004 | 0.001 | 20.66
| 146 | 2008-04-07 | 10000 | 430.8 | -3 | 0.31 | 12.2 | -111.4 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0.01 | -0.03 | 0.5 | 0.01 | 0.3 | 0.004 | 0.002 | 20.75
| 147 | 2008-04-07 | 20000 | 421 | -2.6 | 0.32 | 12.4 | -104.9 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0.02 | -0.03 | 0.6 | 0.02 | 0.9 | 0.005 | 0.002 | 20.75
| 148 | 2008-04-07 | 30000 | 410.5 | -2.4 | 0.31 | 12 | -97.2 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0.01 | -0.03 | 0.3 | 0.01 | 0.3 | 0.005 | 0.001 | 20.75
| 149 | 2008-04-07 | 40000 | 402.7 | -2.6 | 0.32 | 12.1 | -98.7 | 0.16 | 0.5 | 1.3 | -1 | 1 | 0 | -0.05 | 0.2 | 0.01 | 0.3 | 0.004 | 0.001 | 20.74
| 150 | 2008-04-07 | 50000 | 392.4 | -3 | 0.33 | 12.7 | -118 | 0.35 | 0.5 | 1.3 | -1 | 0.9 | 0.01 | -0.06 | 0.5 | 0.01 | 0.3 | 0.004 | 0.002 | 20.74
| 151 | 2008-04-07 | 60000 | 381.8 | -3.1 | 0.31 | 12.4 | -125.8 | 0.26 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0.1 | 0.01 | 0.3 | 0.004 | 0.001 | 20.75
| 152 | 2008-04-07 | 70000 | 374.2 | -2.8 | 0.33 | 14 | -117 | 0.26 | 0.5 | 1.3 | -0.9 | 0.9 | 0.02 | -0.06 | 0.7 | 0.02 | 0.9 | 0.006 | 0.003 | 20.76
| 153 | 2008-04-07 | 80000 | 465.4 | 6.2 | 9.24 | 17.8 | -36.3 | 4.05 | 8.6 | 9.1 | -1 | 0.8 | 6.11 | 17.93 | 9.5 | 24.78 | 38.6 | 0.143 | 0.035 | 18.53
| 154 | 2008-04-07 | 90000 | 604.2 | 20 | 15.58 | 20 | 24.4 | 7.88 | 27.3 | 27.7 | -1 | 40.3 | 10.26 | 27.22 | 13.7 | 45.25 | 61 | 0.225 | 0.05 | 16.38
| 155 | 2008-04-07 | 100000 | 625.5 | 13.8 | 10.11 | 11 | 15.6 | 14.63 | 99.4 | 141.2 | -1 | 103.4 | 6.59 | 21.45 | 6.8 | 27.3 | 28.4 | 0.105 | 0.025 | 14.61
| 156 | 2008-04-07 | 110000 | 662.9 | -2.6 | 0.21 | 0.2 | -2.2 | 22.44 | 184.7 | 264.8 | -0.9 | 141 | 2.59 | 12.72 | 2.1 | 2.51 | 2 | 0.008 | 0.008 | 13.64
| 157 | 2008-04-07 | 120000 | 669.8 | 92.2 | 3.3 | 5 | -10.1 | 22.28 | 184 | 265.5 | -1 | 180.5 | 3.14 | 12.57 | 2.1 | 9.8 | 3.8 | 22.173 | 12.67 | 12.11
| 158 | 2008-04-07 | 130000 | 672.7 | -2.6 | 0.24 | 0.2 | -2.2 | 22.29 | 183.6 | 265.1 | -1 | 140.6 | 2.65 | 12.59 | 2.2 | 2.47 | 2 | 0.007 | 0.008 | 13.69
| 159 | 2008-04-07 | 140000 | 672.5 | -3 | 0.21 | 0.2 | -2.4 | 22.27 | 183.7 | 265.1 | -1 | 144.7 | 2.58 | 12.68 | 2.1 | 2.39 | 1.9 | 0.007 | 0.008 | 13.68
| 160 | 2008-04-07 | 150000 | 672.6 | -3 | 0.21 | 0.2 | -2.5 | 22.3 | 184.4 | 265.9 | -1 | 143.6 | 2.57 | 12.6 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.68
| 161 | 2008-04-07 | 160000 | 672.4 | -2.7 | 0.21 | 0.2 | -2.2 | 22.27 | 184 | 265.4 | -1 | 143.8 | 2.59 | 12.63 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.68
| 162 | 2008-04-07 | 170000 | 672.4 | -2.9 | 0.22 | 0.2 | -2.5 | 22.38 | 185 | 266.4 | -1 | 143.5 | 2.58 | 12.6 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.68
| 163 | 2008-04-07 | 180000 | 672.7 | -2.6 | 0.22 | 0.2 | -2.1 | 22.37 | 185 | 266.3 | -1 | 143.7 | 2.58 | 12.63 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.68
| 164 | 2008-04-07 | 190000 | 674.6 | -2.6 | 0.22 | 0.2 | -2.2 | 22.5 | 185.3 | 266.3 | -1 | 143.9 | 2.58 | 12.61 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.68
| 165 | 2008-04-07 | 200000 | 674.6 | -2.5 | 0.22 | 0.2 | -2.1 | 22.54 | 186 | 266.9 | -1 | 142.6 | 2.58 | 12.52 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.68
| 166 | 2008-04-07 | 210000 | 675.6 | -3 | 0.22 | 0.2 | -2.4 | 22.43 | 185.3 | 265.8 | -1 | 136.9 | 2.53 | 12.08 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.71
| 167 | 2008-04-07 | 220000 | 676.6 | -2.7 | 0.22 | 0.2 | -2.3 | 22.39 | 185.7 | 266 | -1 | 136.4 | 2.6 | 12.04 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.71
| 168 | 2008-04-07 | 230000 | 676.6 | -3 | 0.23 | 0.2 | -2.4 | 22.53 | 186.5 | 267.5 | -1 | 141.3 | 2.58 | 12.38 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.67
| 169 | 2008-04-08 | 0 | 676.7 | -2.6 | 0.22 | 0.2 | -2.2 | 22.53 | 186.5 | 267.4 | -1 | 140.7 | 2.59 | 11.03 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.66
| 170 | 2008-04-08 | 10000 | 677 | -2.8 | 0.22 | 0.2 | -2.3 | 22.53 | 186.5 | 267.2 | -1 | 140.4 | 2.6 | 9.78 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.65
| 171 | 2008-04-08 | 20000 | 677 | -3.1 | 0.22 | 0.2 | -2.6 | 22.53 | 186.5 | 267.3 | -1 | 139.8 | 2.59 | 9.75 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.64
| 172 | 2008-04-08 | 30000 | 676.9 | -3 | 0.22 | 0.2 | -2.5 | 22.53 | 186.6 | 267.2 | -0.9 | 139.6 | 2.6 | 9.79 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.64
| 173 | 2008-04-08 | 40000 | 677 | -2.7 | 0.23 | 0.2 | -2.3 | 22.53 | 186.7 | 267.3 | -0.9 | 139.5 | 2.6 | 9.79 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.64
| 174 | 2008-04-08 | 50000 | 676.8 | -2.8 | 0.21 | 0.2 | -2.4 | 22.54 | 186.8 | 267.6 | -0.9 | 139.1 | 2.6 | 9.77 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.63
| 175 | 2008-04-08 | 60000 | 677.2 | -2.8 | 0.21 | 0.2 | -2.2 | 22.56 | 187.2 | 268 | -0.9 | 138.5 | 2.6 | 9.8 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.63
| 176 | 2008-04-08 | 70000 | 677.5 | -2.7 | 0.21 | 0.2 | -2.1 | 22.55 | 187.2 | 268 | -1 | 138.7 | 2.6 | 9.78 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.63
| 177 | 2008-04-08 | 80000 | 677.4 | -2.9 | 0.21 | 0.2 | -2.3 | 22.49 | 186.4 | 267.1 | -1 | 138.6 | 2.59 | 9.74 | 2.1 | 2.4 | 1.9 | 0.007 | 0.008 | 13.63
| 178 | 2008-04-08 | 90000 | 641.2 | 75.9 | 2.6 | 2.2 | 10.3 | 16.88 | 126.3 | 190.9 | -1 | 53.3 | 3.47 | 10.34 | 2.2 | 8.33 | 3.5 | 0.013 | 0.008 | 12.32
| 179 | 2008-04-08 | 100000 | 672 | 15 | 1.07 | 1.2 | 2.1 | 22.52 | 186 | 265.7 | -0.9 | 140.4 | 2.92 | 12.37 | 2.4 | 3.88 | 2.6 | 0.009 | 0.009 | 13.54
| 180 | 2008-04-08 | 110000 | 676.9 | -3.3 | 0.23 | 0.2 | -2.6 | 22.52 | 185.5 | 266.1 | -1 | 143.3 | 2.6 | 12.45 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.62
| 181 | 2008-04-08 | 120000 | 676.4 | -2.6 | 0.23 | 0.2 | -2 | 22.38 | 185.1 | 265.5 | -1 | 142.7 | 2.61 | 12.46 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.61
| 182 | 2008-04-08 | 130000 | 675.2 | -3.1 | 0.22 | 0.2 | -2.5 | 22.28 | 184 | 264.5 | -0.9 | 143.4 | 2.62 | 12.53 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.61
| 183 | 2008-04-08 | 140000 | 675 | -3 | 0.22 | 0.2 | -2.5 | 22.35 | 184.4 | 264.8 | -0.9 | 142.2 | 2.59 | 12.46 | 2.1 | 2.4 | 1.9 | 0.007 | 0.008 | 13.6
| 184 | 2008-04-08 | 150000 | 674.7 | -2.8 | 0.23 | 0.2 | -2.3 | 22.31 | 184.4 | 264.8 | -1 | 139.6 | 2.63 | 12.34 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.6
| 185 | 2008-04-08 | 160000 | 673.2 | -2.8 | 0.22 | 0.2 | -2.3 | 22.21 | 183.1 | 263.5 | -1 | 141.2 | 2.59 | 12.44 | 2.1 | 2.4 | 1.9 | 0.007 | 0.008 | 13.6
| 186 | 2008-04-08 | 170000 | 642.8 | -2.9 | 0.3 | 0.2 | -2.3 | 16.88 | 126.5 | 191.1 | -0.9 | 52 | 2.59 | 7.66 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.79
| 187 | 2008-04-08 | 180000 | 639.1 | -3 | 0.29 | 0.2 | -2.2 | 17.35 | 131.7 | 196.2 | -1 | 59.5 | 2.54 | 7.7 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.79
| 188 | 2008-04-08 | 190000 | 670.5 | -3.1 | 0.24 | 0.2 | -2.5 | 22.28 | 184.1 | 264.2 | -0.9 | 141.9 | 2.58 | 12.42 | 2.1 | 2.4 | 1.9 | 0.007 | 0.008 | 13.59
| 189 | 2008-04-08 | 200000 | 674.8 | -2.4 | 0.24 | 0.2 | -1.9 | 22.35 | 185.2 | 265.6 | -1 | 139.9 | 2.6 | 12.35 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.6
| 190 | 2008-04-08 | 210000 | 675 | -2.7 | 0.23 | 0.2 | -2.1 | 22.31 | 184.1 | 263.7 | -0.9 | 129.9 | 2.59 | 11.64 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.66
| 191 | 2008-04-08 | 220000 | 676 | -2.7 | 0.23 | 0.2 | -2.4 | 22.51 | 185.6 | 266.1 | -1 | 139.3 | 2.6 | 12.3 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.61
| 192 | 2008-04-08 | 230000 | 677 | -2.7 | 0.23 | 0.2 | -2.3 | 22.54 | 186.2 | 266.8 | -1 | 139.2 | 2.61 | 12.28 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.61
| 193 | 2008-04-09 | 0 | 673.9 | -3 | 0.23 | 0.2 | -2.3 | 22.54 | 186.3 | 266.9 | -1 | 138.5 | 2.61 | 12.22 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.61
| 194 | 2008-04-09 | 10000 | 676.7 | -3 | 0.23 | 0.2 | -2.4 | 22.54 | 186.4 | 267 | -0.9 | 138.5 | 2.61 | 12.23 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.6
| 195 | 2008-04-09 | 20000 | 676.6 | -2.6 | 0.23 | 0.2 | -2 | 22.54 | 186.8 | 267.4 | -0.9 | 138.2 | 2.61 | 12.21 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.6
| 196 | 2008-04-09 | 30000 | 676.8 | -3 | 0.23 | 0.2 | -2.6 | 22.31 | 184.7 | 265.2 | -0.9 | 133.6 | 2.51 | 11.94 | 2 | 2.34 | 1.9 | 0.007 | 0.008 | 13.62
| 197 | 2008-04-09 | 40000 | 644.6 | -2.8 | 0.33 | 0.3 | -2.2 | 17.33 | 131.2 | 196.1 | -1 | 56.7 | 2.66 | 7.73 | 2.2 | 2.48 | 2.1 | 0.008 | 0.008 | 13.81
| 198 | 2008-04-09 | 50000 | 673.3 | -2.8 | 0.24 | 0.2 | -2.3 | 22.5 | 186.7 | 266.8 | -1 | 138.8 | 2.55 | 12.16 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.61
| 199 | 2008-04-09 | 60000 | 643.6 | -2.9 | 0.34 | 0.3 | -2.5 | 16.83 | 125.6 | 190.2 | -1 | 52.8 | 2.63 | 7.86 | 2.2 | 2.44 | 2 | 0.007 | 0.008 | 13.81
| 200 | 2008-04-09 | 70000 | 666.3 | -2.4 | 0.26 | 0.2 | -1.9 | 21.77 | 178.9 | 255.9 | -0.9 | 130.7 | 2.56 | 11.59 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.65
| 201 | 2008-04-09 | 80000 | 676.8 | -2.7 | 0.24 | 0.2 | -2.2 | 22.59 | 187.2 | 268 | -1 | 138.8 | 2.59 | 12.3 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.62
| 202 | 2008-04-09 | 90000 | 676.9 | 94 | 3.38 | 3 | 14 | 22.54 | 186.8 | 267.3 | -1 | 143.4 | 3.48 | 12.29 | 2.3 | 9.47 | 3.9 | 0.015 | 0.009 | 12.1
| 203 | 2008-04-09 | 100000 | 676.7 | -2.3 | 0.27 | 0.2 | -1.9 | 22.53 | 186 | 266.6 | -1 | 140 | 2.61 | 12.35 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.63
| 204 | 2008-04-09 | 110000 | 676.2 | -2.8 | 0.25 | 0.2 | -2.1 | 22.45 | 185.2 | 265.7 | -1 | 139.7 | 2.59 | 12.39 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.63
| 205 | 2008-04-09 | 120000 | 674.9 | -2.7 | 0.25 | 0.2 | -2.4 | 22.28 | 184.3 | 264.7 | -1 | 139.3 | 2.61 | 12.42 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.63
| 206 | 2008-04-09 | 130000 | 674.8 | -2.7 | 0.25 | 0.2 | -2.3 | 22.27 | 183.9 | 264.4 | -1 | 140.8 | 2.61 | 12.35 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.63
| 207 | 2008-04-09 | 140000 | 673.7 | -2.6 | 0.24 | 0.2 | -2.2 | 22.27 | 183.7 | 264.1 | -1 | 142.5 | 2.61 | 12.35 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.62
| 208 | 2008-04-09 | 150000 | 673.1 | -2.8 | 0.27 | 0.2 | -2.4 | 22.26 | 183 | 263.2 | -1 | 143.3 | 2.6 | 12.37 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.62
| 209 | 2008-04-09 | 160000 | 672.7 | -2.9 | 0.27 | 0.2 | -2.3 | 22.21 | 182.8 | 263 | -1 | 143.8 | 2.6 | 12.45 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.62
| 210 | 2008-04-09 | 170000 | 672.8 | -2.6 | 0.25 | 0.2 | -2.1 | 22.25 | 182.9 | 263.1 | -1 | 143.8 | 2.6 | 12.46 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.63
| 211 | 2008-04-09 | 180000 | 672.6 | -2.6 | 0.25 | 0.2 | -2.1 | 22.27 | 183 | 263.3 | -1 | 142.8 | 2.6 | 12.4 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.63
| 212 | 2008-04-09 | 190000 | 672.4 | -2.7 | 0.26 | 0.2 | -2.1 | 22.27 | 183.6 | 264 | -1 | 143.1 | 2.59 | 12.36 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.65
| 213 | 2008-04-09 | 200000 | 672.5 | -2.8 | 0.26 | 0.2 | -2.2 | 22.28 | 184.1 | 264.6 | -1 | 143.5 | 2.59 | 12.38 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.66
| 214 | 2008-04-09 | 210000 | 672.8 | -3 | 0.27 | 0.2 | -2.4 | 22.32 | 184.7 | 265.4 | -1 | 143.4 | 2.58 | 12.35 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.66
| 215 | 2008-04-09 | 220000 | 674 | -2.7 | 0.26 | 0.2 | -2.1 | 22.42 | 185.2 | 265.8 | -1 | 142.4 | 2.58 | 12.55 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.67
| 216 | 2008-04-09 | 230000 | 674.6 | -2.6 | 0.27 | 0.2 | -2 | 22.43 | 185.2 | 265.8 | -0.9 | 142.1 | 2.58 | 12.5 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.68
| 217 | 2008-04-10 | 0 | 674.7 | -3 | 0.26 | 0.2 | -2.6 | 22.46 | 185.2 | 265.9 | -0.9 | 142.2 | 2.58 | 12.56 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.69
| 218 | 2008-04-10 | 10000 | 675.1 | -2.8 | 0.26 | 0.2 | -2.2 | 22.53 | 185.3 | 266.1 | -1 | 141.8 | 2.58 | 12.52 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.69
| 219 | 2008-04-10 | 20000 | 676.2 | -2.8 | 0.26 | 0.2 | -2.2 | 22.53 | 185.3 | 266.1 | -1 | 141.8 | 2.58 | 12.55 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.69
| 220 | 2008-04-10 | 30000 | 675.9 | -2.5 | 0.27 | 0.2 | -2.2 | 22.52 | 185.3 | 266.1 | -1 | 142.4 | 2.57 | 12.55 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.7
| 221 | 2008-04-10 | 40000 | 675.7 | -2.7 | 0.26 | 0.2 | -2.3 | 22.53 | 185.8 | 266.5 | -0.9 | 142 | 2.57 | 12.48 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.7
| 222 | 2008-04-10 | 50000 | 676.5 | -2.8 | 0.28 | 0.2 | -2.2 | 22.53 | 186.1 | 266.9 | -0.9 | 141.7 | 2.58 | 12.43 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.69
| 223 | 2008-04-10 | 60000 | 676.5 | -2.2 | 1.08 | 0.5 | -2.1 | 22.54 | 186.2 | 266.9 | -1 | 141.8 | 3.02 | 12.34 | 2.1 | 2.8 | 2 | 0.007 | 0.008 | 12.72
| 224 | 2008-04-10 | 70000 | 676.6 | -2.8 | 0.31 | 0.2 | -2.3 | 22.53 | 186 | 266.7 | -1 | 140.9 | 2.59 | 12.41 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.65
| 225 | 2008-04-10 | 80000 | 676.1 | -2.7 | 0.26 | 0.2 | -2.3 | 22.54 | 185.9 | 266.7 | -0.9 | 141.9 | 2.57 | 12.48 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.7
| 226 | 2008-04-10 | 90000 | 676.2 | -2.2 | 0.49 | 1.5 | -0.7 | 22.53 | 185.6 | 266.5 | -1 | 142.7 | 2.47 | 12.51 | 2.4 | 2.28 | 2.2 | 0.009 | 0.009 | 14.06
| 227 | 2008-04-10 | 100000 | 675.4 | 93.7 | 3.2 | 1.8 | 26.5 | 22.53 | 185.4 | 266.3 | -0.9 | 144.6 | 3.61 | 12.56 | 2.3 | 9.59 | 3.9 | 0.014 | 0.009 | 11.88
| 228 | 2008-04-10 | 110000 | 674.9 | -2.8 | 0.26 | 0.2 | -2.2 | 22.53 | 185.4 | 266.6 | -0.9 | 145.2 | 2.5 | 12.64 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.75
| 229 | 2008-04-10 | 120000 | 674.4 | -2.4 | 0.26 | 0.2 | -2 | 22.38 | 184.8 | 266.1 | -1 | 146.9 | 2.5 | 12.76 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.77
| 230 | 2008-04-10 | 130000 | 673 | -2.8 | 0.27 | 0.2 | -2.3 | 22.28 | 184.1 | 266.9 | -1 | 148.4 | 2.49 | 12.82 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.78
| 231 | 2008-04-10 | 140000 | 672.9 | -2.8 | 0.27 | 0.2 | -2.3 | 22.28 | 184 | 266.9 | -0.9 | 148.1 | 2.49 | 12.82 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.78
| 232 | 2008-04-10 | 150000 | 672.9 | -3.1 | 0.27 | 0.2 | -2.6 | 22.28 | 183.9 | 265.4 | -0.9 | 147.9 | 2.49 | 12.77 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.79
| 233 | 2008-04-10 | 160000 | 672.9 | -2.9 | 0.27 | 0.2 | -2.4 | 22.28 | 184 | 265.2 | -0.9 | 147.4 | 2.48 | 12.72 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.79
| 234 | 2008-04-10 | 170000 | 672.9 | -3 | 0.27 | 0.2 | -2.4 | 22.31 | 184.1 | 265.3 | -1 | 147.2 | 2.48 | 12.72 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.8
| 235 | 2008-04-10 | 180000 | 672.8 | -2.9 | 0.27 | 0.2 | -2.4 | 22.37 | 184.6 | 266 | -1 | 148.3 | 2.48 | 12.62 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.79
| 236 | 2008-04-10 | 190000 | 673.3 | -2.7 | 0.27 | 0.2 | -2.3 | 22.53 | 185.4 | 266.9 | -0.9 | 148.6 | 2.48 | 12.49 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.79
| 237 | 2008-04-10 | 200000 | 675.1 | -2.2 | 0.27 | 0.2 | -1.9 | 22.54 | 186.4 | 267.9 | -0.9 | 148.5 | 2.48 | 12.45 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.8
| 238 | 2008-04-10 | 210000 | 676.3 | -3 | 0.27 | 0.2 | -2.5 | 22.62 | 186.9 | 268.3 | -1 | 147.5 | 2.48 | 12.4 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.8
| 239 | 2008-04-10 | 220000 | 677.2 | -2.7 | 0.28 | 0.2 | -2.3 | 22.78 | 187.6 | 269.1 | -0.9 | 147 | 2.48 | 12.33 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.8
| 240 | 2008-04-10 | 230000 | 678 | -3 | 0.28 | 0.2 | -2.6 | 22.82 | 188.7 | 270.3 | -1 | 145.8 | 2.48 | 12.23 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.8
| 241 | 2008-04-11 | 0 | 678.3 | -2.2 | 0.27 | 0.2 | -1.8 | 22.88 | 189.3 | 270.9 | -1 | 145 | 2.47 | 12.16 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.81
| 242 | 2008-04-11 | 10000 | 679.4 | -2.8 | 0.27 | 0.2 | -2.5 | 23.04 | 190.1 | 271.8 | -1 | 144.9 | 2.48 | 12.13 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.81
| 243 | 2008-04-11 | 20000 | 679.9 | -2.5 | 0.26 | 0.2 | -2 | 23.04 | 190.7 | 272.3 | -1 | 145.3 | 2.48 | 12.14 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.8
| 244 | 2008-04-11 | 30000 | 679.1 | -3.3 | 0.27 | 0.2 | -2.7 | 23.05 | 191.1 | 272.7 | -1 | 144.6 | 2.48 | 12.08 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.81
| 245 | 2008-04-11 | 40000 | 679.3 | -2.5 | 0.27 | 0.2 | -2 | 23.05 | 191.3 | 272.9 | -1 | 144.5 | 2.47 | 12.07 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.81
| 246 | 2008-04-11 | 50000 | 679.3 | -2.5 | 0.26 | 0.2 | -2 | 23.04 | 191.2 | 272.8 | -1 | 145.3 | 2.48 | 12.1 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.81
| 247 | 2008-04-11 | 60000 | 679 | -2.5 | 0.27 | 0.2 | -2.1 | 23.06 | 191.7 | 273.4 | -1 | 144.7 | 2.47 | 12.05 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.82
| 248 | 2008-04-11 | 70000 | 678.4 | -2.9 | 0.28 | 0.2 | -2.4 | 23.05 | 191.7 | 273.3 | -1 | 144.1 | 2.47 | 12.02 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.82
| 249 | 2008-04-11 | 80000 | 678.3 | 93.4 | 3.43 | 2.3 | 24.5 | 23.05 | 191 | 272.7 | -1 | 145.2 | 3.45 | 12.08 | 2.1 | 9.39 | 3.7 | 0.014 | 0.008 | 12.26
| 250 | 2008-04-11 | 90000 | 678.2 | -2.8 | 0.35 | 0.3 | -2.3 | 22.97 | 189.9 | 272.8 | -1 | 145.2 | 2.46 | 12.36 | 2.1 | 2.27 | 1.9 | 0.007 | 0.008 | 13.84
| 251 | 2008-04-11 | 100000 | 677.5 | -2.8 | 0.29 | 0.2 | -2.2 | 22.72 | 187.5 | 270.6 | -1 | 147.9 | 2.49 | 12.73 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.8
| 252 | 2008-04-11 | 110000 | 675.1 | -3.1 | 0.3 | 0.2 | -2.5 | 22.44 | 184.7 | 267.7 | -0.9 | 151 | 2.49 | 13.05 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.79
| 253 | 2008-04-11 | 120000 | 673 | -2.7 | 0.3 | 0.2 | -2.2 | 22.2 | 182 | 265.1 | -1 | 150 | 2.49 | 13.05 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.8
| 254 | 2008-04-11 | 130000 | 671.7 | -2.8 | 0.3 | 0.2 | -2.4 | 22.04 | 179.9 | 263.2 | -0.9 | 151.9 | 2.49 | 13.23 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.8
| 255 | 2008-04-11 | 140000 | 669.5 | -2.7 | 0.32 | 0.3 | -2.3 | 21.92 | 178.7 | 261.5 | -0.9 | 154.8 | 2.49 | 13.15 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.8
| 256 | 2008-04-11 | 150000 | 669.5 | -2.7 | 0.31 | 0.3 | -2.1 | 21.79 | 177.2 | 259.8 | -0.9 | 151.3 | 2.48 | 13.17 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.8
| 257 | 2008-04-11 | 160000 | 668.9 | -2.8 | 0.3 | 0.2 | -2.5 | 21.62 | 175.9 | 258.3 | -0.9 | 147.8 | 2.48 | 13.15 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.8
| 258 | 2008-04-11 | 170000 | 667.8 | -2.7 | 0.29 | 0.2 | -2.3 | 21.52 | 174.3 | 256.3 | -0.9 | 143.1 | 2.47 | 12.96 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.8
| 259 | 2008-04-11 | 180000 | 668 | -2.4 | 0.28 | 0.2 | -2 | 21.52 | 174.2 | 256 | -0.9 | 142 | 2.48 | 12.94 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.79
| 260 | 2008-04-11 | 190000 | 668.4 | -2.9 | 0.28 | 0.2 | -2.5 | 21.43 | 174.1 | 255.1 | -0.9 | 133.5 | 2.39 | 12.13 | 2 | 2.21 | 1.8 | 0.007 | 0.008 | 13.83
| 261 | 2008-04-11 | 200000 | 669.9 | -3.1 | 0.28 | 0.2 | -2.6 | 21.54 | 175 | 256 | -0.9 | 132 | 2.45 | 12.03 | 2 | 2.27 | 1.9 | 0.007 | 0.008 | 13.82
| 262 | 2008-04-11 | 210000 | 671.7 | -2.9 | 0.34 | 0.3 | -2.4 | 21.87 | 178.6 | 261.2 | -1 | 149.2 | 2.56 | 13.13 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.73
| 263 | 2008-04-11 | 220000 | 671.4 | -2.6 | 0.31 | 0.3 | -2.2 | 21.96 | 179.1 | 261.6 | -1 | 146.1 | 2.4 | 12.86 | 2 | 2.22 | 1.8 | 0.007 | 0.007 | 13.74
| 264 | 2008-04-11 | 230000 | 672.6 | -2.8 | 0.34 | 0.3 | -2.2 | 22.13 | 181.3 | 264.1 | -1 | 147.4 | 2.59 | 13.08 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.72
| 265 | 2008-04-12 | 0 | 672.9 | -2.9 | 0.33 | 0.3 | -2.4 | 22.27 | 182.5 | 265.4 | -0.9 | 147.9 | 2.5 | 13.01 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.72
| 266 | 2008-04-12 | 10000 | 674.2 | -2.4 | 0.31 | 0.3 | -2 | 22.27 | 183.1 | 266.1 | -0.9 | 147 | 2.5 | 12.96 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.71
| 267 | 2008-04-12 | 20000 | 674.8 | -2.8 | 0.32 | 0.3 | -2.2 | 22.29 | 183.6 | 266.6 | -0.9 | 146.5 | 2.51 | 12.91 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.7
| 268 | 2008-04-12 | 30000 | 674.8 | -3.1 | 0.33 | 0.3 | -2.5 | 22.28 | 183.8 | 266.8 | -0.9 | 145.5 | 2.51 | 12.85 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.69
| 269 | 2008-04-12 | 40000 | 674.8 | -2.8 | 0.32 | 0.3 | -2.3 | 22.33 | 184.3 | 267.3 | -1 | 145.3 | 2.52 | 12.84 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.68
| 270 | 2008-04-12 | 50000 | 674.7 | -2.8 | 0.34 | 0.3 | -2.3 | 22.43 | 184.9 | 267.9 | -1 | 144.6 | 2.52 | 12.74 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.68
| 271 | 2008-04-12 | 60000 | 675 | -2.8 | 0.32 | 0.3 | -2.3 | 22.55 | 185.2 | 268.3 | -1 | 143.1 | 2.52 | 12.58 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.67
| 272 | 2008-04-12 | 70000 | 675.1 | -2.6 | 0.32 | 0.3 | -2.2 | 22.53 | 185 | 268 | -1 | 142.1 | 2.53 | 12.55 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.67
| 273 | 2008-04-12 | 80000 | 674.3 | 94.2 | 3.43 | 6.1 | 10 | 22.32 | 183.5 | 266.1 | -0.9 | 144.8 | 3.49 | 12.69 | 2.2 | 9.41 | 4.2 | 7.93 | 0.008 | 12.11
| 274 | 2008-04-12 | 90000 | 672.1 | -2.6 | 0.35 | 0.3 | -2.2 | 22.03 | 180 | 261.9 | -1 | 131.8 | 2.43 | 11.86 | 2 | 2.25 | 1.9 | 0.007 | 0.008 | 13.76
| 275 | 2008-04-12 | 100000 | 672.4 | -3.1 | 0.3 | 0.2 | -2.6 | 21.79 | 177.2 | 258.8 | -1 | 129.6 | 2.48 | 11.74 | 2 | 2.3 | 1.9 | 0.007 | 0.008 | 13.72
| 276 | 2008-04-12 | 110000 | 670.2 | -2.6 | 0.32 | 0.3 | -2.1 | 21.6 | 175.4 | 257.3 | -1 | 137.8 | 2.59 | 12.47 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.68
| 277 | 2008-04-12 | 120000 | 667 | -3.1 | 0.32 | 0.3 | -2.4 | 21.38 | 172.3 | 253.9 | -1 | 137.2 | 2.53 | 12.53 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.66
| 278 | 2008-04-12 | 130000 | 665 | -2.4 | 0.31 | 0.3 | -2 | 20.94 | 168 | 248.7 | -1 | 132.2 | 2.53 | 12.25 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.68
| 279 | 2008-04-12 | 140000 | 664.3 | -2.5 | 0.29 | 0.2 | -2 | 20.76 | 165.9 | 246.1 | -1 | 130.7 | 2.52 | 12.21 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.71
| 280 | 2008-04-12 | 150000 | 664.2 | -2.8 | 0.3 | 0.2 | -2.3 | 20.64 | 165.5 | 245.7 | -0.9 | 131.4 | 2.51 | 12.23 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.7
| 281 | 2008-04-12 | 160000 | 663.6 | -3.1 | 0.28 | 0.2 | -2.4 | 20.13 | 160.6 | 238.3 | -1 | 98.1 | 2.36 | 9.79 | 2 | 2.18 | 1.8 | 0.007 | 0.007 | 13.85
| 282 | 2008-04-12 | 170000 | 662.4 | -2.7 | 0.26 | 0.2 | -2.3 | 19.86 | 158.7 | 234.2 | -1 | 78.2 | 2.43 | 8.24 | 2.1 | 2.26 | 1.9 | 0.007 | 0.008 | 13.89
| 283 | 2008-04-12 | 180000 | 664.9 | -3.1 | 0.27 | 0.2 | -2.5 | 20.74 | 167.2 | 245.4 | -1 | 100 | 2.49 | 9.71 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.8
| 284 | 2008-04-12 | 190000 | 668.9 | -2.4 | 0.29 | 0.2 | -2.1 | 21.43 | 173.6 | 254.9 | 3.1 | 131.9 | 2.57 | 11.98 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.66
| 285 | 2008-04-12 | 200000 | 669.3 | -3.1 | 0.28 | 0.2 | -2.5 | 21.74 | 177 | 258.9 | -1 | 134.6 | 2.51 | 11.95 | 2 | 2.32 | 1.9 | 0.007 | 0.008 | 13.66
| 286 | 2008-04-12 | 210000 | 670.7 | -2.7 | 0.29 | 0.2 | -2.2 | 21.9 | 178.7 | 260.8 | -1 | 132.4 | 2.53 | 11.99 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.66
| 287 | 2008-04-12 | 220000 | 671.9 | -2.8 | 0.29 | 0.2 | -2.4 | 22.12 | 181.2 | 264.1 | -0.9 | 141.7 | 2.57 | 12.69 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.63
| 288 | 2008-04-12 | 230000 | 671.7 | -2.7 | 0.3 | 0.2 | -2.3 | 22.28 | 182.1 | 265.1 | -0.9 | 141.8 | 2.54 | 12.68 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.63
| 289 | 2008-04-13 | 0 | 671.8 | -2.8 | 0.31 | 0.2 | -2.2 | 22.27 | 182.8 | 265.8 | -1 | 141.5 | 2.53 | 12.63 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.64
| 290 | 2008-04-13 | 10000 | 672.6 | -2.8 | 0.31 | 0.3 | -2.2 | 22.28 | 183.2 | 266.3 | -1 | 141.5 | 2.53 | 12.65 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.64
| 291 | 2008-04-13 | 20000 | 672.9 | -2.4 | 0.3 | 0.2 | -2.2 | 22.31 | 183.9 | 267 | -0.9 | 141 | 2.54 | 12.6 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.64
| 292 | 2008-04-13 | 30000 | 672.8 | -2.6 | 0.31 | 0.3 | -2 | 22.43 | 184.1 | 267.3 | -1 | 141.9 | 2.54 | 12.66 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.64
| 293 | 2008-04-13 | 40000 | 672.9 | -2.6 | 0.31 | 0.3 | -2.2 | 22.49 | 184.2 | 267.5 | -0.9 | 142.1 | 2.53 | 12.66 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.63
| 294 | 2008-04-13 | 50000 | 673.8 | -2.8 | 0.31 | 0.3 | -2.1 | 22.48 | 184.5 | 267.8 | -0.9 | 141.4 | 2.53 | 12.54 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.63
| 295 | 2008-04-13 | 60000 | 642.8 | -3.1 | 0.36 | 0.3 | -2.7 | 16.84 | 125.2 | 191.7 | -0.9 | 53.8 | 2.34 | 7.75 | 2 | 2.16 | 1.8 | 0.007 | 0.007 | 13.84
| 296 | 2008-04-13 | 70000 | 637.7 | -3.1 | 0.37 | 0.3 | -2.8 | 16.93 | 126 | 191.6 | -0.9 | 53.6 | 2.46 | 7.6 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.84
| 297 | 2008-04-13 | 80000 | 637.5 | 94.5 | 3.51 | 7.8 | -9.2 | 16.93 | 126.9 | 192.4 | -0.9 | 55.2 | 3.37 | 7.53 | 2.2 | 9.36 | 3.8 | 7.929 | 0.008 | 12.23
| 298 | 2008-04-13 | 90000 | 637.8 | -3 | 0.4 | 0.3 | -2.6 | 17.38 | 131.6 | 197.4 | -1 | 65.3 | 2.41 | 8.75 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.86
| 299 | 2008-04-13 | 100000 | 665.7 | -2.3 | 0.31 | 0.3 | -1.9 | 21.01 | 171.3 | 247.8 | -1 | 83.4 | 2.33 | 8.62 | 2 | 2.16 | 1.8 | 0.007 | 0.007 | 13.88
| 300 | 2008-04-13 | 110000 | 669.8 | -2.5 | 0.3 | 0.3 | -2 | 21.34 | 173.8 | 252.3 | -1 | 96.1 | 2.34 | 9.14 | 2 | 2.17 | 1.8 | 0.007 | 0.007 | 13.86
| 301 | 2008-04-13 | 120000 | 671.4 | -2.7 | 0.3 | 0.2 | -2.2 | 21.6 | 176.2 | 256.2 | -0.9 | 111.4 | 2.56 | 10.58 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.76
| 302 | 2008-04-13 | 130000 | 669.9 | -2.4 | 0.31 | 0.3 | -2.1 | 21.78 | 177 | 258.4 | -1 | 125.6 | 2.48 | 11.67 | 2 | 2.29 | 1.9 | 0.007 | 0.008 | 13.68
| 303 | 2008-04-13 | 140000 | 668.2 | -2.9 | 0.32 | 0.3 | -2.4 | 21.83 | 178 | 260.3 | -0.9 | 142.3 | 2.53 | 12.83 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.6
| 304 | 2008-04-13 | 150000 | 640.9 | -2.5 | 0.32 | 0.3 | -2.2 | 16.69 | 123.8 | 190.4 | -1 | 54.9 | 2.32 | 7.82 | 1.9 | 2.14 | 1.8 | 0.007 | 0.007 | 13.83
| 305 | 2008-04-13 | 160000 | 635.8 | -2.7 | 0.33 | 0.3 | -2.2 | 17.09 | 128.2 | 194.5 | -1 | 57 | 2.46 | 7.49 | 2.1 | 2.27 | 1.9 | 0.007 | 0.008 | 13.84
| 306 | 2008-04-13 | 170000 | 666.6 | -2.3 | 0.33 | 0.3 | -2 | 21.94 | 179.8 | 260.5 | -1 | 132.2 | 2.48 | 11.94 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.67
| 307 | 2008-04-13 | 180000 | 671 | -2.6 | 0.32 | 0.3 | -2.2 | 22.09 | 181.4 | 263.6 | -1 | 136.5 | 2.51 | 12.27 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.65
| 308 | 2008-04-13 | 190000 | 672.1 | -2.6 | 0.32 | 0.3 | -2.2 | 22.17 | 182.7 | 265 | -1 | 135.2 | 2.45 | 12.07 | 2 | 2.27 | 1.8 | 0.007 | 0.007 | 13.65
| 309 | 2008-04-13 | 200000 | 672.3 | -2.9 | 0.32 | 0.3 | -2.4 | 22.28 | 184 | 266.2 | -1 | 140.3 | 2.66 | 12.51 | 2.2 | 2.45 | 2 | 0.007 | 0.008 | 13.6
| 310 | 2008-04-13 | 210000 | 673.4 | -2.6 | 0.31 | 0.3 | -2.3 | 22.3 | 184.3 | 266.6 | -1 | 140.5 | 2.55 | 12.54 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.6
| 311 | 2008-04-13 | 220000 | 674.7 | -2.9 | 0.31 | 0.3 | -2.3 | 22.36 | 184.6 | 266.9 | -1 | 140.8 | 2.55 | 12.57 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.61
| 312 | 2008-04-13 | 230000 | 674.3 | -2.9 | 0.33 | 0.3 | -2.4 | 22.26 | 183.4 | 265.7 | -1 | 140.2 | 2.52 | 12.46 | 2 | 2.34 | 1.9 | 0.007 | 0.008 | 13.6
| 313 | 2008-04-14 | 0 | 643.1 | -2.6 | 0.37 | 0.3 | -2.2 | 16.86 | 125.5 | 191.4 | -1 | 53.1 | 2.35 | 7.68 | 2 | 2.17 | 1.8 | 0.007 | 0.007 | 13.81
| 314 | 2008-04-14 | 10000 | 638.2 | -2.7 | 0.37 | 0.3 | -2.3 | 17.03 | 127.4 | 192.8 | -1 | 54.2 | 2.45 | 7.64 | 2 | 2.27 | 1.9 | 0.007 | 0.008 | 13.81
| 315 | 2008-04-14 | 20000 | 638.2 | -2.7 | 0.37 | 0.3 | -2.2 | 17.01 | 127.7 | 193.3 | -1 | 54.1 | 2.49 | 7.6 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.8
| 316 | 2008-04-14 | 30000 | 638.6 | -2.6 | 0.38 | 0.3 | -2.2 | 17.03 | 127.6 | 193.1 | -1 | 54.2 | 2.5 | 7.62 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.79
| 317 | 2008-04-14 | 40000 | 639 | -2.9 | 0.38 | 0.3 | -2.3 | 17.11 | 128.2 | 193.7 | -1 | 56.3 | 2.47 | 7.71 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.79
| 318 | 2008-04-14 | 50000 | 638.9 | -3 | 0.39 | 0.3 | -2.5 | 17.1 | 128.1 | 193.7 | -1 | 55 | 2.49 | 7.7 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.79
| 319 | 2008-04-14 | 60000 | 639.3 | -2.5 | 0.39 | 0.3 | -2 | 17.48 | 132.2 | 198.2 | -1 | 63.4 | 2.5 | 7.98 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.77
| 320 | 2008-04-14 | 70000 | 671.9 | -2.7 | 0.33 | 0.3 | -2.3 | 22.33 | 183.5 | 264.3 | -1 | 130.1 | 2.49 | 11.67 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.63
| 321 | 2008-04-14 | 80000 | 675.1 | -2.5 | 0.33 | 0.3 | -2.1 | 22.35 | 183.8 | 265.4 | -1 | 132.6 | 2.52 | 11.83 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.62
| 322 | 2008-04-14 | 90000 | 675 | 94.7 | 3.5 | 3.4 | 18.7 | 22.49 | 185 | 267.3 | -1 | 141.5 | 3.6 | 12.37 | 2.2 | 9.5 | 3.9 | 0.015 | 0.008 | 12.06
| 323 | 2008-04-14 | 100000 | 674.5 | -2.5 | 0.37 | 0.3 | -1.8 | 22.39 | 184.6 | 266.5 | -1 | 138.4 | 2.54 | 12.07 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.64
| 324 | 2008-04-14 | 110000 | 673.6 | -2.8 | 0.34 | 0.3 | -2.1 | 22.29 | 183.8 | 265.9 | -1 | 142.7 | 2.55 | 12.48 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.59
| 325 | 2008-04-14 | 120000 | 672.1 | -2.7 | 0.33 | 0.3 | -2.2 | 22.28 | 183.7 | 265.7 | -1 | 142.4 | 2.55 | 12.69 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.58
| 326 | 2008-04-14 | 130000 | 672 | -2.7 | 0.32 | 0.3 | -2.2 | 22.38 | 184.4 | 266.5 | -1 | 140.5 | 2.55 | 12.56 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.58
| 327 | 2008-04-14 | 140000 | 672.3 | -2.9 | 0.33 | 0.3 | -2.3 | 22.27 | 184 | 266.1 | -1 | 141 | 2.56 | 12.61 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.59
| 328 | 2008-04-14 | 150000 | 671.6 | -2.9 | 0.34 | 0.3 | -2.3 | 22.28 | 183.8 | 265.9 | -1 | 142.3 | 2.55 | 12.71 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.59
| 329 | 2008-04-14 | 160000 | 671.6 | -2.7 | 0.34 | 0.3 | -2.2 | 22.27 | 183.7 | 265.8 | -1 | 142.1 | 2.55 | 12.65 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.6
| 330 | 2008-04-14 | 170000 | 671.3 | -2.7 | 0.34 | 0.3 | -2.1 | 22.27 | 183.1 | 265.1 | -1 | 143.6 | 2.56 | 12.7 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.6
| 331 | 2008-04-14 | 180000 | 671.6 | -2.8 | 0.34 | 0.3 | -2.2 | 22.28 | 183.8 | 266 | -1 | 143.8 | 2.54 | 12.49 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.61
| 332 | 2008-04-14 | 190000 | 672 | -2.5 | 0.33 | 0.3 | -2.1 | 22.32 | 184.6 | 266.9 | -1 | 143.8 | 2.54 | 12.46 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.6
| 333 | 2008-04-14 | 200000 | 672.9 | -3.1 | 0.34 | 0.3 | -2.5 | 22.5 | 185.2 | 267.7 | -1 | 144.1 | 2.55 | 12.45 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.61
| 334 | 2008-04-14 | 210000 | 674.3 | -2.7 | 0.33 | 0.3 | -2.3 | 22.54 | 186.2 | 268.8 | -1 | 143 | 2.53 | 12.32 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.62
| 335 | 2008-04-14 | 220000 | 646.7 | -2.5 | 0.42 | 0.4 | -2.1 | 17.04 | 126.9 | 194.3 | -1 | 68.4 | 2.53 | 9.12 | 2.1 | 2.35 | 2 | 0.007 | 0.008 | 13.79
| 336 | 2008-04-14 | 230000 | 637.1 | -2.7 | 0.43 | 0.4 | -2.3 | 17.06 | 127.9 | 193.5 | -1 | 54.9 | 2.44 | 7.77 | 2 | 2.26 | 1.9 | 0.007 | 0.008 | 13.82
| 337 | 2008-04-15 | 0 | 638 | -2.7 | 0.44 | 0.4 | -2.3 | 16.99 | 127.5 | 193 | -1 | 54.6 | 2.45 | 7.77 | 2.1 | 2.26 | 1.9 | 0.007 | 0.008 | 13.83
| 338 | 2008-04-15 | 10000 | 637.4 | -2.7 | 0.43 | 0.4 | -2.2 | 17.01 | 127.6 | 193.2 | -1 | 54.2 | 2.48 | 7.75 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.83
| 339 | 2008-04-15 | 20000 | 637.6 | -2.8 | 0.45 | 0.4 | -2.4 | 16.93 | 127 | 192.4 | -1 | 54.6 | 2.46 | 7.79 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.83
| 340 | 2008-04-15 | 30000 | 638.1 | -2.6 | 0.45 | 0.4 | -2.2 | 17.03 | 127.6 | 193 | -0.9 | 54.2 | 2.46 | 7.73 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.84
| 341 | 2008-04-15 | 40000 | 638.4 | -2.7 | 0.45 | 0.4 | -2.1 | 17.14 | 128.1 | 193.5 | -0.9 | 54.8 | 2.47 | 7.7 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.84
| 342 | 2008-04-15 | 50000 | 671.6 | -2.8 | 0.36 | 0.3 | -2.2 | 22.74 | 187.6 | 268.9 | -0.9 | 140.5 | 2.5 | 11.88 | 2 | 2.31 | 1.9 | 0.007 | 0.008 | 13.65
| 343 | 2008-04-15 | 60000 | 674.7 | -3 | 0.34 | 0.3 | -2.4 | 22.38 | 185.2 | 265.7 | -1 | 117.2 | 2.5 | 10.5 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.76
| 344 | 2008-04-15 | 70000 | 676.7 | -2.8 | 0.35 | 0.3 | -2.3 | 22.79 | 187.7 | 270 | -1 | 142.6 | 2.53 | 12.46 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.67
| 345 | 2008-04-15 | 80000 | 676.7 | 94.7 | 3.53 | 7.3 | -3 | 22.7 | 187.4 | 270.1 | -1 | 140.5 | 3.57 | 12.5 | 2.3 | 9.5 | 4 | 0.016 | 0.009 | 12.13
| 346 | 2008-04-15 | 90000 | 676.7 | -3 | 0.37 | 0.3 | -2.4 | 22.66 | 186.8 | 269.3 | -1 | 141.8 | 2.5 | 12.48 | 2 | 2.31 | 1.9 | 0.007 | 0.008 | 13.7
| 347 | 2008-04-15 | 100000 | 676.7 | -2.8 | 0.34 | 0.3 | -2.2 | 22.64 | 187 | 269.9 | -0.9 | 148.8 | 2.54 | 12.98 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.67
| 348 | 2008-04-15 | 110000 | 676.9 | -2.8 | 0.34 | 0.3 | -2.4 | 22.55 | 186.6 | 269 | -1 | 142.6 | 2.52 | 12.6 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.7
| 349 | 2008-04-15 | 120000 | 675.9 | -2.4 | 0.34 | 0.3 | -2 | 22.58 | 186.5 | 269.3 | -0.9 | 146 | 2.5 | 12.79 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.69
| 350 | 2008-04-15 | 130000 | 674.8 | -2.5 | 0.34 | 0.3 | -2.2 | 22.54 | 185.8 | 268.5 | -0.9 | 143.7 | 2.52 | 12.71 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.69
| 351 | 2008-04-15 | 140000 | 673.8 | -2.4 | 0.35 | 0.3 | -2 | 22.54 | 185.3 | 267.9 | -1 | 143.9 | 2.52 | 12.74 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.69
| 352 | 2008-04-15 | 150000 | 673.2 | -2.4 | 0.35 | 0.3 | -1.9 | 22.52 | 185.4 | 268.1 | -1 | 144.8 | 2.52 | 12.59 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.69
| 353 | 2008-04-15 | 160000 | 673.2 | -2.3 | 0.36 | 0.3 | -1.9 | 22.53 | 185.3 | 268 | -1 | 145.1 | 2.52 | 12.56 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.69
| 354 | 2008-04-15 | 170000 | 673 | -2.6 | 0.36 | 0.3 | -2.1 | 22.54 | 185.4 | 268.1 | -1 | 145.8 | 2.51 | 12.63 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.7
| 355 | 2008-04-15 | 180000 | 674.1 | -2.8 | 0.36 | 0.3 | -2.4 | 22.54 | 185.8 | 268.7 | -1 | 145.6 | 2.51 | 12.56 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.7
| 356 | 2008-04-15 | 190000 | 674.8 | -2.9 | 0.37 | 0.3 | -2.3 | 22.54 | 185.7 | 268.6 | -1 | 145.6 | 2.52 | 12.59 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.7
| 357 | 2008-04-15 | 200000 | 674.7 | -2.4 | 0.38 | 0.3 | -2 | 22.5 | 185 | 267.7 | -1 | 144.9 | 2.5 | 12.5 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.7
| 358 | 2008-04-15 | 210000 | 641.8 | -2.9 | 0.49 | 0.4 | -2.5 | 16.68 | 123.1 | 188.7 | -1 | 52.3 | 2.47 | 8.09 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.91
| 359 | 2008-04-15 | 220000 | 638.5 | -2.4 | 0.46 | 0.4 | -2.2 | 17.03 | 127.1 | 192.7 | -1 | 54.6 | 2.43 | 7.76 | 2.1 | 2.26 | 1.9 | 0.007 | 0.008 | 13.93
| 360 | 2008-04-15 | 230000 | 637.4 | -2.8 | 0.46 | 0.4 | -2.3 | 16.92 | 125.8 | 191.3 | -1 | 54 | 2.45 | 7.77 | 2.1 | 2.26 | 1.9 | 0.007 | 0.008 | 13.93
| 361 | 2008-04-16 | 0 | 555.1 | 8.9 | 6.37 | 62.5 | -46.2 | 2.17 | 8.3 | 16.2 | -1 | 8.9 | 2.45 | 7.38 | 4.7 | 10.12 | 13.8 | 229.551 | 58.578 | 19.53
| 362 | 2008-04-16 | 10000 | 428.7 | -2.8 | 0.49 | 0.9 | -8 | 0.24 | 0.5 | 1.3 | -1 | 1 | 0 | 0 | 0 | 0.02 | 0.1 | 444.757 | 12.663 | 20.93
| 363 | 2008-04-16 | 20000 | 402.2 | -3.2 | 0.47 | 0 | 0 | 0.18 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.05 | 0 | 0.01 | 0 | 98.137 | 0.001 | 20.95
| 364 | 2008-04-16 | 30000 | 399.2 | -2.8 | 0.43 | 0 | 0 | 0.08 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.01 | 0 | 30.078 | 0.001 | 20.95
| 365 | 2008-04-16 | 40000 | 580.8 | 30.8 | 16.61 | 23.9 | 42.4 | 7.16 | 21 | 21.4 | -1 | 15 | 9.67 | 28.85 | 14 | 37.01 | 53.5 | 0.197 | 0.052 | 16.92
| 366 | 2008-04-16 | 50000 | 631.6 | 23.8 | 14.75 | 16.2 | 26.5 | 12.78 | 78.4 | 106.4 | -1 | 91.9 | 8.34 | 26.08 | 9 | 38.5 | 41 | 0.151 | 0.033 | 15.04
| 367 | 2008-04-16 | 60000 | 670.7 | -2.7 | 0.39 | 0.3 | -2.2 | 22.52 | 185.4 | 267.6 | -1 | 133.4 | 2.53 | 12.53 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.78
| 368 | 2008-04-16 | 70000 | 676.3 | -2.4 | 0.37 | 0.3 | -1.9 | 22.47 | 185.2 | 269.4 | -1 | 134.1 | 2.52 | 12.12 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.8
| 369 | 2008-04-16 | 80000 | 676.7 | 93.7 | 3.52 | 10.3 | 31.8 | 22.44 | 184.6 | 268.1 | -1 | 130.7 | 3.55 | 11.72 | 2.2 | 9.49 | 4 | 0.015 | 3.174 | 12.23
| 370 | 2008-04-16 | 90000 | 677.7 | -2.9 | 0.41 | 0.3 | -2.4 | 22.55 | 185.8 | 269.2 | -1 | 140.7 | 2.58 | 12.69 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.8
| 371 | 2008-04-16 | 100000 | 676.7 | -2.6 | 0.37 | 0.3 | -2.1 | 22.53 | 186.1 | 269.5 | -1 | 145.3 | 2.55 | 12.89 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.76
| 372 | 2008-04-16 | 110000 | 676.6 | -2.7 | 0.37 | 0.3 | -2.3 | 22.54 | 185.2 | 267.9 | -1 | 144.9 | 2.55 | 12.91 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.77
| 373 | 2008-04-16 | 120000 | 675.7 | -2.5 | 0.37 | 0.3 | -2 | 22.53 | 184.9 | 267.7 | -1 | 146.2 | 2.55 | 13 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.78
| 374 | 2008-04-16 | 130000 | 675 | -2.9 | 0.36 | 0.3 | -2.5 | 22.53 | 184 | 266.6 | -0.9 | 145.2 | 2.56 | 12.96 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.77
| 375 | 2008-04-16 | 140000 | 674.7 | -2.5 | 0.35 | 0.3 | -2.1 | 22.5 | 183.3 | 265 | -1 | 145.8 | 2.55 | 13 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.77
| 376 | 2008-04-16 | 150000 | 674.8 | -3.1 | 0.35 | 0.3 | -2.4 | 22.35 | 183 | 264.6 | -1 | 146.1 | 2.55 | 13.02 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.77
| 377 | 2008-04-16 | 160000 | 674.1 | -2.6 | 0.35 | 0.3 | -2.2 | 22.28 | 183 | 264.6 | -1 | 146.2 | 2.55 | 13.02 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.76
| 378 | 2008-04-16 | 170000 | 673 | -2.4 | 0.35 | 0.3 | -2 | 22.31 | 182.9 | 264.5 | -1 | 145.4 | 2.55 | 12.97 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.75
| 379 | 2008-04-16 | 180000 | 673.1 | -2.7 | 0.36 | 0.3 | -2.3 | 22.28 | 183.1 | 264.9 | -1 | 144.8 | 2.56 | 12.95 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.75
| 380 | 2008-04-16 | 190000 | 672.9 | -2.6 | 0.35 | 0.3 | -2.2 | 22.33 | 183.7 | 265.8 | -1 | 144.4 | 2.56 | 12.93 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.74
| 381 | 2008-04-16 | 200000 | 672.9 | -2.8 | 0.36 | 0.3 | -2.3 | 22.44 | 184 | 266.3 | -1 | 144.6 | 2.56 | 12.94 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.73
| 382 | 2008-04-16 | 210000 | 673.1 | -2.9 | 0.36 | 0.3 | -2.4 | 22.53 | 184.1 | 266.4 | -0.9 | 145.7 | 2.57 | 12.99 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.73
| 383 | 2008-04-16 | 220000 | 674.1 | -2.9 | 0.36 | 0.3 | -2.4 | 22.54 | 185 | 267.5 | -1 | 146.7 | 2.56 | 13.01 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.73
| 384 | 2008-04-16 | 230000 | 652.2 | -2.8 | 0.42 | 0.4 | -2.3 | 18.03 | 137 | 206.8 | -1 | 79.5 | 2.55 | 9.7 | 2.1 | 2.35 | 2 | 0.007 | 0.008 | 13.87
| 385 | 2008-04-17 | 0 | 637.6 | -2.8 | 0.44 | 0.4 | -2.5 | 17.08 | 127.7 | 193.1 | -1 | 55.8 | 2.44 | 7.87 | 2.1 | 2.26 | 1.9 | 0.007 | 0.008 | 13.93
| 386 | 2008-04-17 | 10000 | 638.1 | -3.1 | 0.44 | 0.4 | -2.6 | 17.17 | 128.1 | 193.8 | -1 | 54.8 | 2.49 | 7.81 | 2.1 | 2.31 | 2 | 0.007 | 0.008 | 13.94
| 387 | 2008-04-17 | 20000 | 638.1 | -2.8 | 0.44 | 0.4 | -2.3 | 17.1 | 127.3 | 192.6 | -0.9 | 55 | 2.52 | 7.88 | 2.1 | 2.33 | 2 | 0.007 | 0.008 | 13.93
| 388 | 2008-04-17 | 30000 | 637.9 | -2.8 | 0.44 | 0.4 | -2.3 | 17.15 | 127 | 192.1 | -0.9 | 56.9 | 2.46 | 7.93 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.92
| 389 | 2008-04-17 | 40000 | 638.3 | -2.7 | 0.44 | 0.4 | -2.2 | 17.19 | 127.7 | 192.9 | -1 | 56.7 | 2.5 | 7.92 | 2.1 | 2.31 | 2 | 0.007 | 0.008 | 13.93
| 390 | 2008-04-17 | 50000 | 671 | -2.9 | 0.37 | 0.3 | -2.5 | 22.79 | 186.1 | 267.4 | -1 | 142.6 | 2.55 | 12.57 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.71
| 391 | 2008-04-17 | 60000 | 676 | -2.7 | 0.37 | 0.3 | -2.2 | 22.82 | 186.4 | 268.7 | -1 | 142.2 | 2.57 | 12.68 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.7
| 392 | 2008-04-17 | 70000 | 676.7 | -1.9 | 1.11 | 0.6 | -2.4 | 22.82 | 186.6 | 268.7 | -1 | 142 | 2.77 | 12.69 | 2 | 2.56 | 1.9 | 19 | 0.008 | 13.42
| 393 | 2008-04-17 | 80000 | 676.9 | 93 | 2.84 | 1.9 | 26.9 | 22.8 | 186.1 | 269.3 | -1 | 142.5 | 3.33 | 12.7 | 2.2 | 9.27 | 3.9 | 11.093 | 19.001 | 12.48
| 394 | 2008-04-17 | 90000 | 675.5 | -2.7 | 0.37 | 0.3 | -2.3 | 22.62 | 185.2 | 268.2 | -0.9 | 142.5 | 2.57 | 12.76 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.72
| 395 | 2008-04-17 | 100000 | 674.6 | -2.8 | 0.36 | 0.3 | -2.3 | 22.55 | 184.1 | 267.4 | -0.9 | 143.7 | 2.58 | 12.61 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.7
| 396 | 2008-04-17 | 110000 | 673.1 | -2.4 | 0.36 | 0.3 | -2 | 22.54 | 183.4 | 266.4 | -0.9 | 144.5 | 2.58 | 12.69 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.7
| 397 | 2008-04-17 | 120000 | 671.5 | -2.8 | 0.36 | 0.3 | -2.1 | 22.47 | 182.8 | 265.7 | -1 | 145.8 | 2.57 | 12.78 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.7
| 398 | 2008-04-17 | 130000 | 669.7 | -2.7 | 0.36 | 0.3 | -2.3 | 22.44 | 182.9 | 265.3 | -1 | 144.7 | 2.57 | 12.73 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.7
| 399 | 2008-04-17 | 140000 | 669.6 | -2.5 | 0.37 | 0.3 | -2 | 22.34 | 182.1 | 264.7 | -0.9 | 144.2 | 2.58 | 12.71 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.7
| 400 | 2008-04-17 | 150000 | 669.8 | -2.7 | 0.37 | 0.3 | -2.3 | 22.28 | 181.8 | 264.3 | -1 | 144 | 2.57 | 12.68 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.7
| 401 | 2008-04-17 | 160000 | 669.5 | -2.7 | 0.37 | 0.3 | -2.1 | 22.28 | 182 | 264.4 | -1 | 144.6 | 2.58 | 12.72 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.7
| 402 | 2008-04-17 | 170000 | 670.5 | -2.6 | 0.36 | 0.3 | -2.1 | 22.28 | 182.9 | 265.3 | -1 | 144.3 | 2.56 | 12.71 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.7
| 403 | 2008-04-17 | 180000 | 671.5 | -2.5 | 0.36 | 0.3 | -2.1 | 22.45 | 183.6 | 266.4 | -1 | 143.3 | 2.56 | 12.63 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.7
| 404 | 2008-04-17 | 190000 | 672.1 | -2.9 | 0.37 | 0.3 | -2.2 | 22.54 | 184.1 | 266.9 | -1 | 143.1 | 2.58 | 12.62 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.69
| 405 | 2008-04-17 | 200000 | 672.7 | -2.7 | 0.38 | 0.3 | -2.3 | 22.54 | 184.6 | 267.4 | -1 | 143.3 | 2.57 | 12.64 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.68
| 406 | 2008-04-17 | 210000 | 672.9 | -2.8 | 0.38 | 0.3 | -2.3 | 22.54 | 185.1 | 268.2 | -1 | 142.7 | 2.58 | 12.61 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.68
| 407 | 2008-04-17 | 220000 | 673.7 | -2.8 | 0.38 | 0.3 | -2.1 | 22.49 | 184.7 | 267.8 | -1 | 142.5 | 2.57 | 12.52 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.68
| 408 | 2008-04-17 | 230000 | 641 | -2.6 | 0.5 | 0.4 | -2.1 | 16.64 | 123.3 | 189.1 | -1 | 51.3 | 2.55 | 8.13 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.88
| 409 | 2008-04-18 | 0 | 636.4 | -2.9 | 0.49 | 0.4 | -2.4 | 16.99 | 126.8 | 192.3 | -1 | 54.8 | 2.5 | 7.93 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.89
| 410 | 2008-04-18 | 10000 | 635.6 | -2.6 | 0.49 | 0.4 | -2.2 | 16.96 | 126.6 | 192.2 | -1 | 55.1 | 2.51 | 7.99 | 2.1 | 2.33 | 2 | 0.007 | 0.008 | 13.89
| 411 | 2008-04-18 | 20000 | 635.9 | -2.3 | 0.52 | 0.4 | -1.9 | 16.99 | 126.8 | 192.4 | -1 | 55.3 | 2.5 | 8 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.89
| 412 | 2008-04-18 | 30000 | 636 | -2.8 | 0.52 | 0.4 | -2.2 | 16.94 | 126.9 | 192.6 | -1 | 55.2 | 2.52 | 7.99 | 2.1 | 2.33 | 2 | 0.007 | 0.008 | 13.88
| 413 | 2008-04-18 | 40000 | 636.5 | -3 | 0.53 | 0.5 | -2.5 | 16.96 | 126.7 | 192.3 | -1 | 55.4 | 2.51 | 8 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.88
| 414 | 2008-04-18 | 50000 | 668.6 | -2.9 | 0.42 | 0.3 | -2.3 | 22.4 | 184.9 | 265.9 | -1 | 142 | 2.56 | 12.29 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.68
| 415 | 2008-04-18 | 60000 | 674.7 | -2.8 | 0.4 | 0.3 | -2.3 | 22.33 | 184.7 | 266.3 | -1 | 126.6 | 2.5 | 11.3 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.75
| 416 | 2008-04-18 | 70000 | 675.1 | 94.2 | 3.56 | 10.2 | -7.4 | 22.43 | 185.2 | 266.9 | -1 | 125.2 | 3.65 | 11.66 | 2.5 | 9.49 | 4 | 11.095 | 0.009 | 12.16
| 417 | 2008-04-18 | 80000 | 675.3 | -2.8 | 0.46 | 0.4 | -2.1 | 22.42 | 185.4 | 267.1 | -1 | 133.9 | 2.44 | 11.86 | 2 | 2.26 | 1.9 | 0.007 | 0.008 | 13.77
| 418 | 2008-04-18 | 90000 | 674.6 | -2.7 | 0.41 | 0.3 | -2.1 | 22.36 | 184.8 | 266.4 | -1 | 127.5 | 2.54 | 11.78 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.74
| 419 | 2008-04-18 | 100000 | 674.7 | -2.5 | 0.4 | 0.3 | -2.1 | 22.41 | 185.4 | 267.1 | -1 | 129 | 2.48 | 11.66 | 2 | 2.3 | 1.9 | 0.007 | 0.007 | 13.73
| 420 | 2008-04-18 | 110000 | 674.5 | -2.8 | 0.4 | 0.3 | -2 | 22.47 | 185.3 | 267.3 | -1 | 139.4 | 2.41 | 12.11 | 2 | 2.23 | 1.8 | 0.007 | 0.007 | 13.69
| 421 | 2008-04-18 | 120000 | 674.9 | -2.7 | 0.41 | 0.3 | -2.2 | 22.47 | 185.5 | 268 | -1 | 138.2 | 2.58 | 12.54 | 2.1 | 2.39 | 1.9 | 0.007 | 0.008 | 13.67
| 422 | 2008-04-18 | 130000 | 673.5 | -2.4 | 0.4 | 0.3 | -2.1 | 22.48 | 185.1 | 267.3 | -1 | 138.7 | 2.61 | 12.64 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.67
| 423 | 2008-04-18 | 140000 | 672.7 | -2.8 | 0.41 | 0.3 | -2.3 | 22.52 | 185.8 | 268.5 | -1 | 141.5 | 2.58 | 12.54 | 2.1 | 2.39 | 1.9 | 0.007 | 0.008 | 13.65
| 424 | 2008-04-18 | 150000 | 672.6 | -2.6 | 0.41 | 0.3 | -2.3 | 22.49 | 185.5 | 268.1 | -1.1 | 141.3 | 2.59 | 12.59 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.65
| 425 | 2008-04-18 | 160000 | 673 | -2.8 | 0.41 | 0.3 | -2.4 | 22.54 | 186 | 268.7 | -1.1 | 140.5 | 2.59 | 12.49 | 2.1 | 2.4 | 1.9 | 0.007 | 0.008 | 13.64
| 426 | 2008-04-18 | 170000 | 672.8 | -2.6 | 0.41 | 0.3 | -2.1 | 22.53 | 185.9 | 268.6 | -1 | 140 | 2.6 | 12.49 | 2.1 | 2.4 | 1.9 | 0.007 | 0.008 | 13.63
| 427 | 2008-04-18 | 180000 | 674.6 | -2.7 | 0.41 | 0.3 | -2.2 | 22.55 | 186.5 | 269.2 | -1 | 139.8 | 2.6 | 12.45 | 2.1 | 2.4 | 1.9 | 0.007 | 0.008 | 13.62
| 428 | 2008-04-18 | 190000 | 674.7 | -2.8 | 0.41 | 0.3 | -2.2 | 22.54 | 186.5 | 269.1 | -1 | 139.4 | 2.61 | 12.43 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.62
| 429 | 2008-04-18 | 200000 | 674.7 | -2.9 | 0.41 | 0.3 | -2.4 | 22.63 | 187.2 | 269.7 | -1 | 139.5 | 2.6 | 12.39 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.62
| 430 | 2008-04-18 | 210000 | 674.5 | -2.7 | 0.4 | 0.3 | -2.1 | 22.79 | 187.9 | 270.5 | -1 | 138.5 | 2.61 | 12.35 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.61
| 431 | 2008-04-18 | 220000 | 675.6 | -2.2 | 0.41 | 0.3 | -1.7 | 22.75 | 187.6 | 270.1 | -1 | 138.7 | 2.61 | 12.55 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.61
| 432 | 2008-04-18 | 230000 | 676.5 | -2.8 | 0.41 | 0.3 | -2.2 | 22.63 | 187.3 | 269.8 | -1 | 138.2 | 2.61 | 12.53 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.6
| 433 | 2008-04-19 | 0 | 676.9 | -2.7 | 0.41 | 0.3 | -2.1 | 22.66 | 187.5 | 270 | -1 | 138.1 | 2.61 | 12.48 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.6
| 434 | 2008-04-19 | 10000 | 676.9 | -2.4 | 0.4 | 0.3 | -2 | 22.66 | 187.5 | 269.9 | -1 | 135.9 | 2.61 | 12.36 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.58
| 435 | 2008-04-19 | 20000 | 676.8 | -2.4 | 0.41 | 0.3 | -2 | 22.62 | 187.5 | 269.7 | -1 | 135.9 | 2.61 | 12.35 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.57
| 436 | 2008-04-19 | 30000 | 676.9 | -2.8 | 0.4 | 0.3 | -2.1 | 22.64 | 187.5 | 269.8 | -1 | 134.8 | 2.62 | 12.29 | 2.1 | 2.42 | 1.9 | 0.007 | 0.008 | 13.57
| 437 | 2008-04-19 | 40000 | 676.9 | -2.6 | 0.4 | 0.3 | -2.1 | 22.55 | 187 | 269.3 | -1 | 136.2 | 2.63 | 12.45 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.56
| 438 | 2008-04-19 | 50000 | 676.8 | -2.7 | 0.4 | 0.3 | -2.1 | 22.56 | 187.2 | 269.6 | -0.9 | 136.2 | 2.62 | 12.39 | 2.1 | 2.43 | 1.9 | 0.007 | 0.008 | 13.55
| 439 | 2008-04-19 | 60000 | 676.8 | -2.7 | 0.4 | 0.3 | -2.1 | 22.56 | 187.3 | 269.7 | -0.9 | 135.4 | 2.63 | 12.32 | 2.1 | 2.42 | 1.9 | 0.007 | 0.008 | 13.56
| 440 | 2008-04-19 | 70000 | 676.7 | -2.9 | 0.41 | 0.3 | -2.3 | 22.54 | 186.8 | 268.9 | -1 | 136.2 | 2.63 | 12.38 | 2.1 | 2.43 | 1.9 | 0.007 | 0.008 | 13.56
| 441 | 2008-04-19 | 80000 | 676.4 | 95.4 | 3.58 | 2.9 | 23.4 | 22.54 | 186.8 | 268.8 | -1 | 153.5 | 3.18 | 12.45 | 1.7 | 9.04 | 3.4 | 0.013 | 0.007 | 12.05
| 442 | 2008-04-19 | 90000 | 676.1 | -2.8 | 0.43 | 0.3 | -2.3 | 22.51 | 186 | 268 | -1 | 138 | 2.64 | 12.58 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.56
| 443 | 2008-04-19 | 100000 | 675.1 | -2.8 | 0.43 | 0.3 | -2.3 | 22.38 | 185.1 | 267.2 | -0.9 | 141.3 | 2.63 | 12.79 | 2.1 | 2.44 | 1.9 | 0.007 | 0.008 | 13.55
| 444 | 2008-04-19 | 110000 | 675 | -2.7 | 0.42 | 0.3 | -2.2 | 22.32 | 184.8 | 267 | -1 | 140.9 | 2.62 | 12.74 | 2.1 | 2.42 | 1.9 | 0.007 | 0.008 | 13.55
| 445 | 2008-04-19 | 120000 | 674.3 | -2.7 | 0.4 | 0.3 | -2.3 | 22.45 | 185.9 | 267.6 | -0.9 | 130.9 | 2.57 | 11.98 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.59
| 446 | 2008-04-19 | 130000 | 671.4 | -3.3 | 0.41 | 0.3 | -2.7 | 22.45 | 185.6 | 267.2 | -0.9 | 133.4 | 2.61 | 12.16 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.58
| 447 | 2008-04-19 | 140000 | 674.8 | -2.5 | 0.42 | 0.3 | -2 | 22.47 | 185.6 | 267.5 | -0.9 | 137.7 | 2.68 | 12.59 | 2.1 | 2.48 | 2 | 0.007 | 0.008 | 13.55
| 448 | 2008-04-19 | 150000 | 674.9 | -2.7 | 0.41 | 0.3 | -2.3 | 22.54 | 186.4 | 268.6 | -1 | 136.8 | 2.61 | 12.45 | 2.1 | 2.42 | 1.9 | 0.007 | 0.008 | 13.55
| 449 | 2008-04-19 | 160000 | 674.9 | -2.6 | 0.42 | 0.3 | -2.1 | 22.53 | 186 | 268.2 | -1 | 136.8 | 2.63 | 12.53 | 2.1 | 2.43 | 1.9 | 0.007 | 0.008 | 13.55
| 450 | 2008-04-19 | 170000 | 674.9 | -2.9 | 0.42 | 0.3 | -2.2 | 22.5 | 185.6 | 267.7 | -1 | 135.5 | 2.63 | 12.5 | 2.1 | 2.43 | 1.9 | 0.007 | 0.008 | 13.55
| 451 | 2008-04-19 | 180000 | 674.9 | -2.6 | 0.41 | 0.3 | -1.9 | 22.46 | 185.3 | 267.4 | -1 | 136 | 2.62 | 12.49 | 2.1 | 2.44 | 1.9 | 0.007 | 0.008 | 13.55
| 452 | 2008-04-19 | 190000 | 674.9 | -2.5 | 0.41 | 0.3 | -2 | 22.44 | 185.3 | 267.3 | -1 | 135.8 | 2.63 | 12.51 | 2.1 | 2.44 | 1.9 | 0.007 | 0.008 | 13.55
| 453 | 2008-04-19 | 200000 | 675.5 | -3.1 | 0.43 | 0.3 | -2.4 | 22.36 | 184.1 | 266.3 | -0.9 | 134.7 | 2.56 | 11.89 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.56
| 454 | 2008-04-19 | 210000 | 642 | -2.9 | 0.54 | 0.4 | -2.2 | 16.79 | 124.9 | 190.5 | -0.9 | 54.5 | 2.41 | 7.7 | 2 | 2.22 | 1.8 | 0.007 | 0.007 | 13.77
| 455 | 2008-04-19 | 220000 | 638 | -2.8 | 0.54 | 0.4 | -2.2 | 17.01 | 127 | 192.2 | -1 | 56.3 | 2.47 | 7.64 | 2 | 2.28 | 1.9 | 0.007 | 0.008 | 13.76
| 456 | 2008-04-19 | 230000 | 638.7 | -2.9 | 0.53 | 0.4 | -2.4 | 17.12 | 128 | 193.3 | -1 | 56.2 | 2.5 | 7.6 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.76
| 457 | 2008-04-20 | 0 | 638.3 | -2.4 | 0.53 | 0.4 | -2.1 | 17 | 126.8 | 191.6 | -0.9 | 56.1 | 2.49 | 7.66 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.77
| 458 | 2008-04-20 | 10000 | 559.3 | 4.2 | 4.83 | 23.2 | -22 | 1.85 | 7.9 | 13.9 | -1 | 2.6 | 2.1 | 5.25 | 4.4 | 7.7 | 10 | 0.038 | 0.016 | 19.49
| 459 | 2008-04-20 | 20000 | 449.2 | -2.9 | 0.56 | 15.3 | -79.5 | 0.26 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.01 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.68
| 460 | 2008-04-20 | 30000 | 429.6 | -2.6 | 0.54 | 15.4 | -76.1 | 0.26 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.69
| 461 | 2008-04-20 | 40000 | 421.8 | -2.9 | 0.54 | 16.5 | -85.2 | 0.23 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0 | 0.1 | 0.003 | 0 | 20.63
| 462 | 2008-04-20 | 50000 | 413.2 | -2.7 | 0.55 | 17.2 | -82.2 | 0.15 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0.1 | 0.01 | 0.2 | 0.004 | 0 | 20.71
| 463 | 2008-04-20 | 60000 | 423.5 | -0.9 | 2.05 | 16.3 | -70.8 | 0.8 | 1.5 | 2.2 | -0.9 | 0.9 | 1.11 | 3 | 1.9 | 2.79 | 4.4 | 0.018 | 0.007 | 20.32
| 464 | 2008-04-20 | 70000 | 617.8 | 11 | 14.17 | 23.1 | 17.8 | 6.21 | 11.8 | 12.3 | -1 | 0.9 | 10.26 | 30.01 | 16.7 | 37.26 | 59.8 | 0.22 | 0.061 | 17.25
| 465 | 2008-04-20 | 80000 | 509.3 | -0.9 | 2.16 | 21.9 | -83.8 | 0.5 | 1.1 | 1.8 | -1 | 0.8 | 1.18 | 3.26 | 4.5 | 3.24 | 8 | 0.031 | 0.016 | 20.4
| 466 | 2008-04-20 | 90000 | 386 | -2.8 | 0.51 | 18.6 | -99.6 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0.02 | 2.05 | 0.6 | 0.02 | 0.5 | 0.005 | 0.002 | 20.74
| 467 | 2008-04-20 | 100000 | 556.5 | 9.7 | 13.05 | 20.2 | 8.2 | 6.37 | 16.5 | 16.9 | -1 | 0.9 | 9.78 | 28.03 | 14.9 | 43.79 | 64.2 | 0.237 | 0.055 | 17.11
| 468 | 2008-04-20 | 110000 | 629.9 | 16.2 | 12.21 | 14.5 | 19.4 | 10.97 | 60.6 | 65.6 | -1 | 36.3 | 8.37 | 25.1 | 9.9 | 42.38 | 50.1 | 0.184 | 0.037 | 15.39
| 469 | 2008-04-20 | 120000 | 657.3 | 97.6 | 5.94 | 6 | 23.4 | 18.82 | 145.4 | 209.5 | -1 | 155.1 | 4.73 | 14.93 | 3.6 | 20 | 13.7 | 0.051 | 0.013 | 12.21
| 470 | 2008-04-20 | 130000 | 670.5 | -1 | 0.88 | 1.5 | -0.5 | 22.12 | 182.2 | 263.3 | -1 | 135.3 | 2.21 | 11.84 | 1.9 | 2.13 | 1.8 | 0.007 | 0.007 | 13.86
| 471 | 2008-04-20 | 140000 | 672.5 | -2.7 | 0.45 | 0.4 | -2.2 | 22.02 | 181.2 | 262.3 | -1 | 126.5 | 2.24 | 10.73 | 1.8 | 2.07 | 1.7 | 0.006 | 0.007 | 13.77
| 472 | 2008-04-20 | 150000 | 674 | -2.6 | 0.44 | 0.4 | -2.1 | 22.12 | 182.9 | 265 | -1 | 133.8 | 2.41 | 11.59 | 2 | 2.23 | 1.8 | 0.007 | 0.007 | 13.7
| 473 | 2008-04-20 | 160000 | 675.4 | -3 | 0.44 | 0.4 | -2.4 | 22.27 | 184.4 | 266.2 | -1 | 134.8 | 2.58 | 11.96 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.66
| 474 | 2008-04-20 | 170000 | 648.7 | -2.8 | 0.51 | 0.4 | -2.1 | 17.19 | 129.5 | 195.9 | -1 | 63.6 | 2.5 | 8.28 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.81
| 475 | 2008-04-20 | 180000 | 670.8 | -2.9 | 0.45 | 0.4 | -2.3 | 22.53 | 186.5 | 267.5 | -1 | 142.1 | 2.44 | 12.19 | 2 | 2.25 | 1.8 | 0.007 | 0.007 | 13.64
| 476 | 2008-04-20 | 190000 | 675.8 | -2.5 | 0.44 | 0.4 | -2 | 22.45 | 186.1 | 268 | -1 | 131.9 | 2.5 | 11.67 | 2 | 2.32 | 1.9 | 0.007 | 0.008 | 13.67
| 477 | 2008-04-20 | 200000 | 674.1 | -2.8 | 0.44 | 0.4 | -2.3 | 22.43 | 185.5 | 266.6 | -1 | 122.6 | 2.51 | 10.85 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.71
| 478 | 2008-04-20 | 210000 | 676.5 | -2.7 | 0.44 | 0.4 | -2.2 | 22.72 | 187.6 | 270 | -1 | 139 | 2.52 | 11.92 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.64
| 479 | 2008-04-20 | 220000 | 676.8 | -2.9 | 0.45 | 0.4 | -2.4 | 22.72 | 187.7 | 270.2 | -1 | 138.7 | 2.55 | 11.96 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.63
| 480 | 2008-04-20 | 230000 | 677.3 | -2.6 | 0.44 | 0.4 | -2.1 | 22.71 | 187.5 | 270 | -0.9 | 138.4 | 2.52 | 11.89 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.63
| 481 | 2008-04-21 | 0 | 643.5 | -2.9 | 0.58 | 0.5 | -2.3 | 16.72 | 123.7 | 189.3 | -0.9 | 52.6 | 2.38 | 7.77 | 2 | 2.2 | 1.8 | 0.007 | 0.007 | 13.82
| 482 | 2008-04-21 | 10000 | 638.6 | -2.7 | 0.56 | 0.5 | -2.3 | 16.93 | 126.5 | 191.7 | -1 | 53.4 | 2.46 | 7.54 | 2 | 2.26 | 1.9 | 0.007 | 0.008 | 13.82
| 483 | 2008-04-21 | 20000 | 638.8 | -2.7 | 0.56 | 0.5 | -2.3 | 16.95 | 127.2 | 192.5 | -1 | 53.4 | 2.48 | 7.47 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.82
| 484 | 2008-04-21 | 30000 | 638.6 | -3 | 0.56 | 0.5 | -2.5 | 17.01 | 127.3 | 192.5 | -1 | 53.9 | 2.47 | 7.52 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.82
| 485 | 2008-04-21 | 40000 | 638.4 | -2.4 | 0.57 | 0.5 | -2 | 17.08 | 127.7 | 192.9 | -1 | 54.1 | 2.48 | 7.52 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.81
| 486 | 2008-04-21 | 50000 | 670.4 | -2.6 | 0.45 | 0.4 | -2.1 | 22.63 | 186.6 | 267.2 | -1 | 140 | 2.43 | 11.7 | 2 | 2.25 | 1.8 | 0.007 | 0.007 | 13.62
| 487 | 2008-04-21 | 60000 | 676.8 | -2.6 | 0.45 | 0.4 | -2.1 | 22.72 | 187.6 | 269.9 | -0.9 | 138.7 | 2.54 | 11.95 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.61
| 488 | 2008-04-21 | 70000 | 676.6 | -2.5 | 0.44 | 0.4 | -2 | 22.6 | 186.9 | 269 | -1 | 135.2 | 2.55 | 11.74 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.64
| 489 | 2008-04-21 | 80000 | 676.8 | -2.6 | 0.44 | 0.4 | -2.1 | 22.56 | 186.8 | 269.1 | -1 | 137.2 | 2.5 | 11.85 | 2 | 2.31 | 1.9 | 0.007 | 0.008 | 13.64
| 490 | 2008-04-21 | 90000 | 677 | 94.7 | 3.62 | 3.9 | 18.5 | 22.53 | 186.2 | 268.2 | -1 | 137.8 | 3.53 | 11.96 | 2.2 | 9.34 | 3.7 | 0.014 | 0.008 | 12.14
| 491 | 2008-04-21 | 100000 | 677.1 | -2.9 | 0.49 | 0.4 | -2.3 | 22.52 | 186.1 | 268.4 | -1 | 140.7 | 2.52 | 12.08 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.66
| 492 | 2008-04-21 | 110000 | 676.3 | -2.4 | 0.45 | 0.4 | -2 | 22.54 | 185.8 | 268.3 | -1 | 140.5 | 2.53 | 12.09 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.64
| 493 | 2008-04-21 | 120000 | 675.9 | -2.8 | 0.45 | 0.4 | -2.3 | 22.49 | 185.4 | 267.7 | -1 | 139.8 | 2.54 | 12.07 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.63
| 494 | 2008-04-21 | 130000 | 674.9 | -2.8 | 0.44 | 0.4 | -2.2 | 22.45 | 185.1 | 267.3 | -1 | 138.9 | 2.54 | 12.04 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.62
| 495 | 2008-04-21 | 140000 | 675 | -2.9 | 0.45 | 0.4 | -2.3 | 22.43 | 185.1 | 267.3 | -1 | 139.7 | 2.54 | 12.09 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.63
| 496 | 2008-04-21 | 150000 | 675.1 | -2.7 | 0.44 | 0.4 | -2.1 | 22.52 | 185.4 | 267.7 | -1 | 138.8 | 2.54 | 12.02 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.62
| 497 | 2008-04-21 | 160000 | 675.7 | -2.8 | 0.43 | 0.3 | -2.3 | 22.54 | 186.3 | 268.7 | -0.9 | 137.5 | 2.54 | 12.15 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.61
| 498 | 2008-04-21 | 170000 | 675 | -2.5 | 0.43 | 0.3 | -2.1 | 22.53 | 185.7 | 268.1 | -1 | 138.2 | 2.54 | 12.23 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.61
| 499 | 2008-04-21 | 180000 | 676.4 | -3 | 0.44 | 0.4 | -2.4 | 22.54 | 186.3 | 268.8 | -1 | 137.4 | 2.55 | 12.16 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.61
| 500 | 2008-04-21 | 190000 | 676.6 | -2.8 | 0.44 | 0.4 | -2.4 | 22.54 | 186.1 | 268.5 | -1 | 137.7 | 2.55 | 12.2 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.6
| 501 | 2008-04-21 | 200000 | 676.7 | -2.3 | 0.44 | 0.4 | -1.9 | 22.54 | 186.2 | 268.6 | -1 | 137.5 | 2.55 | 12.24 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.6
| 502 | 2008-04-21 | 210000 | 676.8 | -2.5 | 0.45 | 0.4 | -2.1 | 22.54 | 186.3 | 268.7 | -1 | 137.4 | 2.54 | 12.16 | 2.1 | 2.34 | 1.9 | 0.007 | 0.008 | 13.61
| 503 | 2008-04-21 | 220000 | 675.6 | -2.7 | 0.45 | 0.4 | -2.1 | 22.54 | 186.2 | 268.5 | -1 | 137.2 | 2.54 | 12.21 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.61
| 504 | 2008-04-21 | 230000 | 676 | -2.6 | 0.45 | 0.4 | -2.1 | 22.54 | 186.3 | 268.7 | -1 | 137.1 | 2.55 | 12.17 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.6
| 505 | 2008-04-22 | 0 | 675.9 | -2.8 | 0.46 | 0.4 | -2.2 | 22.54 | 186.3 | 268.7 | -1 | 137.2 | 2.55 | 12.17 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.6
| 506 | 2008-04-22 | 10000 | 675.2 | -2.5 | 0.45 | 0.4 | -2.1 | 22.54 | 186.3 | 268.7 | -1 | 137.8 | 2.55 | 12.08 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.59
| 507 | 2008-04-22 | 20000 | 675.3 | -3 | 0.45 | 0.4 | -2.4 | 22.54 | 186.3 | 268.5 | -1 | 137.4 | 2.55 | 12.21 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.59
| 508 | 2008-04-22 | 30000 | 674.8 | -2.6 | 0.45 | 0.4 | -2.2 | 22.53 | 185.9 | 268.2 | -0.9 | 136.7 | 2.56 | 12.21 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.58
| 509 | 2008-04-22 | 40000 | 675.6 | -2.7 | 0.45 | 0.4 | -2 | 22.52 | 185.9 | 268.2 | -0.9 | 136.5 | 2.56 | 12.15 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.56
| 510 | 2008-04-22 | 50000 | 676.3 | -2.8 | 0.45 | 0.4 | -2.3 | 22.53 | 186.1 | 268.3 | -1 | 136.3 | 2.56 | 12.16 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.55
| 511 | 2008-04-22 | 60000 | 675.5 | -2.9 | 0.46 | 0.4 | -2 | 22.49 | 185.7 | 267.8 | -0.9 | 136.4 | 2.58 | 12.18 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.55
| 512 | 2008-04-22 | 70000 | 674.8 | -2.8 | 0.46 | 0.4 | -2.1 | 22.41 | 185.4 | 267.4 | -1 | 137.9 | 2.57 | 12.27 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.55
| 513 | 2008-04-22 | 80000 | 674.8 | -3 | 0.46 | 0.4 | -2.5 | 22.35 | 185.2 | 267.1 | -1 | 138 | 2.57 | 12.28 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.54
| 514 | 2008-04-22 | 90000 | 674.9 | -2.6 | 0.46 | 0.4 | -2 | 22.28 | 184.5 | 266.4 | -1 | 138.9 | 2.57 | 12.35 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.54
| 515 | 2008-04-22 | 100000 | 674.2 | 94.7 | 3.65 | 3.1 | 22.8 | 22.26 | 183.6 | 265.4 | -1 | 140.2 | 3.49 | 12.4 | 2.1 | 9.32 | 3.7 | 0.014 | 0.008 | 12.03
| 516 | 2008-04-22 | 110000 | 672.8 | -2.9 | 0.48 | 0.4 | -2.3 | 22.1 | 182.1 | 263.9 | -1 | 139.8 | 2.58 | 12.52 | 2.1 | 2.39 | 1.9 | 0.007 | 0.008 | 13.53
| 517 | 2008-04-22 | 120000 | 671.6 | -2.8 | 0.47 | 0.4 | -2.1 | 22.05 | 180.8 | 262.3 | -1 | 138.9 | 2.58 | 12.5 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.52
| 518 | 2008-04-22 | 130000 | 671.4 | -2.8 | 0.47 | 0.4 | -2.3 | 21.91 | 180.1 | 261.3 | -1 | 138.6 | 2.58 | 12.5 | 2.1 | 2.39 | 1.9 | 0.007 | 0.008 | 13.52
| 519 | 2008-04-22 | 140000 | 670.1 | -3.2 | 0.48 | 0.4 | -2.6 | 21.81 | 179.2 | 260.4 | -1 | 138.9 | 2.58 | 12.53 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.51
| 520 | 2008-04-22 | 150000 | 669.2 | 93.1 | 3.36 | 3.1 | 14.7 | 21.8 | 179.1 | 260.2 | -1 | 140.1 | 3.54 | 12.49 | 2.4 | 9.85 | 4.3 | 0.016 | 0.009 | 12.11
| 521 | 2008-04-22 | 160000 | 670.8 | -2.4 | 0.06 | 0 | -2 | 21.84 | 179.8 | 261 | -1 | 140 | 2.52 | 12.41 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.68
| 522 | 2008-04-22 | 170000 | 670.8 | -2.5 | 0.04 | 0 | -2.2 | 21.82 | 179.4 | 260.5 | -1 | 140.7 | 2.53 | 12.43 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.66
| 523 | 2008-04-22 | 180000 | 670.9 | -3.1 | 0.03 | 0 | -2.6 | 21.88 | 179.9 | 261 | -1 | 138.8 | 2.52 | 12.31 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.65
| 524 | 2008-04-22 | 190000 | 671.4 | -2.5 | 0.03 | 0 | -2 | 22.01 | 180.5 | 261.6 | -1 | 137.8 | 2.53 | 12.31 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.65
| 525 | 2008-04-22 | 200000 | 671.5 | -2.5 | 0.03 | 0 | -2 | 22.03 | 180.6 | 261.7 | -0.9 | 138.1 | 2.54 | 12.33 | 2.1 | 2.39 | 1.9 | 0.007 | 0.008 | 13.64
| 526 | 2008-04-22 | 210000 | 671.6 | -2.8 | 0.04 | 0 | -2.3 | 22.05 | 181 | 262.2 | -1 | 138.9 | 2.53 | 12.29 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.63
| 527 | 2008-04-22 | 220000 | 671.6 | -2.7 | 0.04 | 0 | -2.2 | 22.05 | 181.1 | 262.4 | -1 | 138.6 | 2.54 | 12.28 | 2.1 | 2.39 | 1.9 | 0.007 | 0.008 | 13.63
| 528 | 2008-04-22 | 230000 | 672 | -2.6 | 0.04 | 0 | -2.2 | 21.92 | 180.2 | 261.6 | -1 | 136.7 | 2.49 | 12.12 | 2 | 2.35 | 1.9 | 0.007 | 0.008 | 13.65
| 529 | 2008-04-23 | 0 | 642.5 | -2.9 | 0.14 | 0.1 | -2.4 | 16.8 | 126.3 | 191.8 | -1 | 51.7 | 2.52 | 7.54 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.86
| 530 | 2008-04-23 | 10000 | 639.5 | -2.6 | 0.13 | 0.1 | -2.1 | 17.03 | 128.7 | 193.9 | -1 | 55.6 | 2.44 | 7.43 | 2 | 2.3 | 1.9 | 0.007 | 0.008 | 13.86
| 531 | 2008-04-23 | 20000 | 638.9 | -2.7 | 0.13 | 0.1 | -2.2 | 17 | 128.6 | 193.7 | -0.9 | 53.4 | 2.46 | 7.37 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.86
| 532 | 2008-04-23 | 30000 | 639 | -2.8 | 0.13 | 0.1 | -2.3 | 17.06 | 128.9 | 194.1 | -1 | 54.8 | 2.46 | 7.4 | 2.1 | 2.32 | 1.9 | 0.007 | 0.008 | 13.85
| 533 | 2008-04-23 | 40000 | 639.1 | -2.5 | 0.12 | 0.1 | -2.1 | 17.07 | 128.8 | 194 | -1 | 56.7 | 2.48 | 7.5 | 2.1 | 2.33 | 1.9 | 0.007 | 0.008 | 13.86
| 534 | 2008-04-23 | 50000 | 668.4 | -2.7 | 0.05 | 0 | -2.1 | 22.13 | 182.5 | 262.8 | -1 | 142 | 2.5 | 12.25 | 2 | 2.36 | 1.9 | 0.007 | 0.008 | 13.66
| 535 | 2008-04-23 | 60000 | 672.8 | -2.6 | 0.04 | 0 | -1.8 | 22.12 | 182.7 | 264.1 | -1 | 141 | 2.53 | 12.4 | 2.1 | 2.37 | 1.9 | 0.007 | 0.008 | 13.67
| 536 | 2008-04-23 | 70000 | 672.9 | -2.6 | 0.04 | 0 | -2.2 | 22.23 | 182.9 | 264.4 | -1 | 140.6 | 2.52 | 12.38 | 2.1 | 2.36 | 1.9 | 0.007 | 0.008 | 13.67
| 537 | 2008-04-23 | 80000 | 672.9 | -2.7 | 0.04 | 0 | -2.3 | 22.25 | 182.9 | 264.5 | -1 | 139.9 | 2.53 | 12.32 | 2.1 | 2.38 | 1.9 | 0.007 | 0.008 | 13.67
| 538 | 2008-04-23 | 90000 | 644.9 | 94.9 | 3.32 | 2.7 | -2.9 | 17 | 127.9 | 194.4 | -1 | 60.1 | 3.42 | 8.47 | 2.1 | 9.65 | 3.8 | 0.015 | 0.008 | 12.29
| 539 | 2008-04-23 | 100000 | 638.4 | -2.6 | 0.13 | 0.1 | -2.1 | 17.01 | 128.2 | 193.3 | -1 | 56.5 | 2.42 | 7.48 | 2 | 2.28 | 1.9 | 0.007 | 0.008 | 13.9
| 540 | 2008-04-23 | 110000 | 638.6 | -2.4 | 0.09 | 0.1 | -2.1 | 17.05 | 128.7 | 193.9 | -1 | 56.3 | 2.45 | 7.47 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.88
| 541 | 2008-04-23 | 120000 | 638 | -2.4 | 0.09 | 0.1 | -2 | 16.89 | 126.9 | 191.7 | -1 | 56.5 | 2.44 | 7.52 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.89
| 542 | 2008-04-23 | 130000 | 638 | -2.8 | 0.09 | 0.1 | -2.3 | 16.94 | 128.3 | 193.7 | -0.9 | 56 | 2.45 | 7.46 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.89
| 543 | 2008-04-23 | 140000 | 638.3 | -2.6 | 0.1 | 0.1 | -2.1 | 16.95 | 128.4 | 193.5 | -0.9 | 55.6 | 2.46 | 7.44 | 2.1 | 2.31 | 1.9 | 0.007 | 0.008 | 13.89
| 544 | 2008-04-23 | 150000 | 638.1 | -3.1 | 0.12 | 0.1 | -2.8 | 16.84 | 126.8 | 191.7 | -0.9 | 55.9 | 2.43 | 7.48 | 2 | 2.27 | 1.9 | 0.007 | 0.008 | 13.89
| 545 | 2008-04-23 | 160000 | 638.8 | -2.8 | 0.09 | 0.1 | -2.4 | 16.94 | 128.3 | 193.5 | -0.9 | 54.9 | 2.47 | 7.38 | 2.1 | 2.32 | 2 | 0.007 | 0.008 | 13.9
| 546 | 2008-04-23 | 170000 | 637.5 | -2.8 | 0.1 | 0.1 | -2.4 | 16.93 | 127.1 | 192.1 | -1 | 55.8 | 2.44 | 7.47 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.91
| 547 | 2008-04-23 | 180000 | 638.1 | -2.7 | 0.1 | 0.1 | -2.2 | 16.93 | 127.8 | 192.9 | -1 | 55.9 | 2.44 | 7.49 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.91
| 548 | 2008-04-23 | 190000 | 638.2 | -2.5 | 0.11 | 0.1 | -2 | 16.93 | 127 | 192.2 | -1 | 56.2 | 2.44 | 7.52 | 2.1 | 2.3 | 1.9 | 0.007 | 0.008 | 13.93
| 549 | 2008-04-23 | 200000 | 638.4 | -2.7 | 0.11 | 0.1 | -2.3 | 16.97 | 128 | 193.3 | -1 | 55.9 | 2.42 | 7.47 | 2.1 | 2.28 | 1.9 | 0.007 | 0.008 | 13.94
| 550 | 2008-04-23 | 210000 | 639.2 | -2.7 | 0.11 | 0.1 | -2.2 | 16.92 | 126.7 | 192 | -0.9 | 54.3 | 2.45 | 7.53 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.96
| 551 | 2008-04-23 | 220000 | 548.1 | 4.8 | 4.67 | 36.8 | 4.1 | 1.23 | 4.9 | 9.4 | -1 | 13.6 | 1.69 | 5.04 | 4 | 7.29 | 10 | 6.37 | 49.079 | 19.99
| 552 | 2008-04-23 | 230000 | 435.4 | -2.8 | 0.16 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 1.1 | 0 | 0.01 | 0 | 0 | 0 | 0.004 | 0 | 21.01
| 553 | 2008-04-24 | 0 | 414.3 | -2.5 | 0.11 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.05 | 0 | 0 | 0 | 0.003 | 0 | 21.04
| 554 | 2008-04-24 | 10000 | 405.4 | -2.9 | 0.11 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.02 | 0 | 0.002 | 0 | 21.06
| 555 | 2008-04-24 | 20000 | 397.3 | -2.7 | 0.12 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.01 | 0 | 0.002 | 0 | 21.08
| 556 | 2008-04-24 | 30000 | 391.5 | -2.5 | 0.13 | 0 | 0 | 0.17 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.002 | 0 | 21.1
| 557 | 2008-04-24 | 40000 | 399.4 | -2.3 | 0.38 | 0.7 | -1.4 | 0.25 | 0.5 | 1.3 | -1 | 1 | 0.06 | 0.83 | 0.1 | 0.06 | 0.2 | 0.002 | 0.001 | 20.91
| 558 | 2008-04-24 | 50000 | 581.3 | 30.4 | 18.84 | 26.4 | 41.1 | 7.91 | 27.1 | 28.1 | -1 | 2.8 | 10.23 | 29.86 | 14.5 | 45.08 | 62 | 0.228 | 0.053 | 16.61
| 559 | 2008-04-24 | 60000 | 623.4 | 11.1 | 8.06 | 8.7 | 12.5 | 14.75 | 100.8 | 149.7 | -1 | 66.8 | 5.54 | 18.39 | 5.7 | 28.3 | 29.5 | 0.109 | 0.021 | 14.59
| 560 | 2008-04-24 | 70000 | 635 | -2.7 | 0.19 | 0.2 | -2.3 | 17.04 | 127.2 | 193.4 | -1 | 58.6 | 2.28 | 7.95 | 2 | 2.15 | 1.9 | 0.007 | 0.007 | 14.1
| 561 | 2008-04-24 | 80000 | 635.4 | -2.6 | 0.2 | 0.2 | -2.1 | 16.93 | 126.1 | 193 | -0.9 | 57.2 | 2.37 | 7.8 | 2.1 | 2.22 | 1.9 | 0.007 | 0.008 | 14.11
| 562 | 2008-04-24 | 90000 | 636.9 | 94 | 3.36 | 1.6 | 27.8 | 16.93 | 126.4 | 193.6 | -1 | 59.4 | 3.38 | 8.64 | 2.1 | 9.5 | 3.9 | 0.014 | 0.008 | 12.5
| 563 | 2008-04-24 | 100000 | 637.3 | 77.8 | 2.38 | 0.8 | 20.5 | 16.93 | 126.4 | 193.4 | -1 | 59.4 | 3.09 | 7.91 | 2.2 | 8.67 | 3.6 | 0.014 | 0.008 | 13.03
| 564 | 2008-04-24 | 110000 | 637.2 | 1.7 | 2.58 | 2.8 | -21.5 | 16.93 | 126.6 | 193 | -1 | 58.3 | 1.9 | 7.39 | 1.5 | 2.01 | 1.6 | 39.575 | 11.085 | 12.21
| 565 | 2008-04-24 | 120000 | 637.2 | -2.9 | 0.11 | 0.7 | -15.1 | 16.93 | 126.7 | 192.7 | -1 | 59.1 | 1.75 | 7.94 | 1.4 | 1.67 | 1.5 | 0.006 | 0.006 | 13.89
| 566 | 2008-04-24 | 130000 | 637.2 | 381.7 | 11.54 | 3.3 | 107.1 | 16.93 | 126.3 | 192.1 | -1 | 57.2 | 8.44 | 7.9 | 2.8 | 39.73 | 11.6 | 0.043 | 0.01 | 3.51
| 567 | 2008-04-24 | 140000 | 636.6 | 660.7 | 16.88 | 9.8 | 192.9 | 16.93 | 126.1 | 191.9 | -1 | 56.8 | 8.48 | 7.8 | 3.7 | 56.08 | 17.3 | 31.718 | 33.251 | 3.83
| 568 | 2008-04-24 | 150000 | 635.9 | 21.5 | 5.62 | 5.1 | 3.2 | 17.2 | 129.2 | 195.1 | -1 | 59.6 | 6.52 | 7.82 | 3.6 | 11.25 | 4.9 | 3.183 | 11.092 | 6.3
| 569 | 2008-04-24 | 160000 | 670 | -0.7 | 2.46 | 1.4 | -32.7 | 22.27 | 183.8 | 266.1 | -1 | 146.5 | 3.2 | 12.85 | 2 | 3.07 | 2.1 | 6.34 | 6.338 | 12.7
| 570 | 2008-04-24 | 170000 | 672.6 | -2.1 | 1.06 | 1 | -1.9 | 22.28 | 184 | 266.9 | -1 | 157.6 | 2.52 | 12.84 | 1.9 | 2.44 | 1.9 | 0.008 | 1.59 | 12.94
| 571 | 2008-04-24 | 180000 | 672.7 | -3.1 | 0.07 | 0.1 | -2.5 | 22.3 | 184.1 | 267 | -1 | 147.9 | 2.52 | 12.9 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.74
| 572 | 2008-04-24 | 190000 | 674 | -3 | 0.07 | 0.1 | -2.5 | 22.51 | 185.1 | 268.1 | -1 | 146.9 | 2.5 | 12.81 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.73
| 573 | 2008-04-24 | 200000 | 674.7 | -2.5 | 0.06 | 0 | -2.2 | 22.53 | 185.9 | 269.1 | -1 | 147.6 | 2.5 | 12.82 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.74
| 574 | 2008-04-24 | 210000 | 676.2 | -3 | 0.06 | 0 | -2.5 | 22.42 | 185.1 | 268 | -1 | 142.8 | 2.42 | 12.44 | 2 | 2.31 | 1.9 | 0.007 | 0.008 | 13.76
| 575 | 2008-04-24 | 220000 | 576.4 | 6.7 | 5.22 | 45.4 | -122.4 | 2.9 | 15.8 | 27.5 | -1 | 7.9 | 2.25 | 6.9 | 3.8 | 9.04 | 11.8 | 178.899 | 25.338 | 19.17
| 576 | 2008-04-24 | 230000 | 443.1 | -2.6 | 0.18 | 8.8 | -152.9 | 0.45 | 0.5 | 1.3 | -1 | 1 | 0 | 0 | 0 | 0.01 | 2 | 728.08 | 42.734 | 20.84
| 577 | 2008-04-25 | 0 | 417.1 | -3.2 | 0.2 | 3.8 | -52.2 | 0.28 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.9 | 593.542 | 14.246 | 20.92
| 578 | 2008-04-25 | 10000 | 407.3 | -2.8 | 0.23 | 5.7 | -50.6 | 0.26 | 0.5 | 1.3 | -1 | 0.9 | 0.01 | -0.07 | 0.1 | 0.01 | 2.2 | 449.517 | 44.317 | 20.93
| 579 | 2008-04-25 | 20000 | 399.2 | -2.6 | 0.2 | 4 | -69.7 | 0.26 | 0.5 | 1.3 | -1 | 1 | 0.01 | -0.06 | 0.2 | 0.02 | 1.3 | 751.812 | 79.137 | 20.92
| 580 | 2008-04-25 | 30000 | 408.1 | -2.5 | 0.39 | 1 | -15.4 | 0.38 | 0.5 | 1.3 | -1 | 0.8 | 0.2 | 0.87 | 0.4 | 0.2 | 0.6 | 295.984 | 14.246 | 20.8
| 581 | 2008-04-25 | 40000 | 584.9 | 24.5 | 18.54 | 25.2 | 31.7 | 8.08 | 28.5 | 30.9 | -1 | 2.8 | 10.29 | 29.86 | 14.2 | 48.24 | 64.1 | 0.236 | 0.052 | 16.45
| 582 | 2008-04-25 | 50000 | 626.7 | 11.4 | 7.48 | 7.9 | 12.5 | 15.45 | 108.7 | 163.8 | -1 | 60.5 | 5.57 | 17.98 | 5.5 | 27.86 | 28.2 | 0.104 | 0.02 | 14.4
| 583 | 2008-04-25 | 60000 | 670 | -3 | 0.1 | 0.1 | -2.4 | 22.8 | 187.5 | 271.6 | -1 | 144.4 | 2.46 | 12.66 | 2 | 2.35 | 1.9 | 0.007 | 0.008 | 13.74
| 584 | 2008-04-25 | 70000 | 675.5 | -2.5 | 0.08 | 0.1 | -2.1 | 22.81 | 187.6 | 272.8 | -1 | 143.5 | 2.5 | 12.58 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.74
| 585 | 2008-04-25 | 80000 | 676.9 | -2.9 | 0.07 | 0.1 | -2.4 | 22.81 | 187.4 | 272.2 | -1 | 143.7 | 2.5 | 12.58 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.74
| 586 | 2008-04-25 | 90000 | 676.8 | 92.5 | 3.24 | 2.1 | 20.2 | 22.75 | 187 | 270.7 | -1 | 148.8 | 3.45 | 12.62 | 2.1 | 9.76 | 3.7 | 0.015 | 0.008 | 12.17
| 587 | 2008-04-25 | 100000 | 676.5 | -2.4 | 0.14 | 0.1 | -2 | 22.58 | 186.2 | 269.4 | -1 | 148.3 | 2.43 | 12.72 | 2 | 2.31 | 1.9 | 0.007 | 0.008 | 13.79
| 588 | 2008-04-25 | 110000 | 674.9 | -3.1 | 0.07 | 0.1 | -2.6 | 22.5 | 185.1 | 268 | -1 | 148.6 | 2.49 | 12.63 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.76
| 589 | 2008-04-25 | 120000 | 666.1 | -2.7 | 0.05 | 0 | -2.2 | 20.62 | 167.9 | 243.6 | -1 | 96.3 | 2.42 | 9.23 | 2 | 2.31 | 1.9 | 0.007 | 0.008 | 13.93
| 590 | 2008-04-25 | 130000 | 673.7 | -2.7 | 0.07 | 0.1 | -2.3 | 22.29 | 183.6 | 266.8 | -1 | 152.7 | 2.41 | 12.95 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.77
| 591 | 2008-04-25 | 140000 | 672.8 | -2.7 | 0.06 | 0.1 | -2.4 | 22.28 | 183.1 | 266 | -1 | 152.8 | 2.49 | 13.01 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.77
| 592 | 2008-04-25 | 150000 | 672.7 | -2.6 | 0.06 | 0 | -2.2 | 22.28 | 182.9 | 265.7 | -0.9 | 152.2 | 2.49 | 12.99 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.77
| 593 | 2008-04-25 | 160000 | 670.8 | -2.8 | 0.05 | 0 | -2.3 | 21.71 | 177.5 | 258 | -1 | 124.4 | 2.33 | 11.13 | 2 | 2.21 | 1.9 | 0.007 | 0.007 | 13.88
| 594 | 2008-04-25 | 170000 | 642.4 | -2.7 | 0.11 | 0.1 | -2.3 | 16.76 | 125.5 | 191.8 | -1 | 59 | 2.42 | 8.01 | 2.1 | 2.29 | 1.9 | 0.007 | 0.008 | 13.97
| 595 | 2008-04-25 | 180000 | 637.8 | -2.8 | 0.12 | 0.1 | -2.2 | 16.83 | 126.2 | 192 | -1 | 58 | 2.43 | 7.92 | 2.1 | 2.3 | 2 | 0.007 | 0.008 | 13.96
| 596 | 2008-04-25 | 190000 | 638.1 | -2.7 | 0.14 | 0.1 | -2.3 | 17.36 | 131.3 | 197.6 | -1 | 65.1 | 2.47 | 8.18 | 2.1 | 2.35 | 2 | 0.007 | 0.008 | 13.94
| 597 | 2008-04-25 | 200000 | 670.8 | -2.7 | 0.09 | 0.1 | -2.2 | 22.11 | 181.5 | 264 | -1 | 147.4 | 2.38 | 12.81 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.75
| 598 | 2008-04-25 | 210000 | 642.8 | -2.9 | 0.17 | 0.1 | -2.6 | 16.84 | 125.2 | 191.5 | -1 | 54.1 | 2.37 | 7.88 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.95
| 599 | 2008-04-25 | 220000 | 556.2 | 5.3 | 4.7 | 47.9 | -173.6 | 1.6 | 6.4 | 12.2 | -0.9 | 8.3 | 1.82 | 5.55 | 3.8 | 7.86 | 10.4 | 170.983 | 52.244 | 19.81
| 600 | 2008-04-25 | 230000 | 445.1 | -2.8 | 0.2 | 5.8 | -88.7 | 0.04 | 0.5 | 1.3 | -0.9 | 1 | 0 | 0.01 | 0.1 | 0 | 1.8 | 642.608 | 37.986 | 20.92
| 601 | 2008-04-26 | 0 | 423.1 | -2.8 | 0.21 | 5.2 | -55.1 | 0.17 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.03 | 0.1 | 0.01 | 1.3 | 398.865 | 30.072 | 20.92
| 602 | 2008-04-26 | 10000 | 413.6 | -2.7 | 0.22 | 5.6 | -59.8 | 0.35 | 0.5 | 1.3 | -0.9 | 0.9 | 0 | -0.06 | 0 | 0 | 1.3 | 666.345 | 42.734 | 20.92
| 603 | 2008-04-26 | 20000 | 405.6 | -2.6 | 0.19 | 3.6 | -23.4 | 0.26 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0 | 1.1 | 528.648 | 7.914 | 20.93
| 604 | 2008-04-26 | 30000 | 414.7 | -2.6 | 0.43 | 3.6 | -63.3 | 0.29 | 0.5 | 1.3 | -1 | 1 | 0.12 | 1.06 | 0.2 | 0.12 | 1.4 | 210.523 | 3.168 | 20.78
| 605 | 2008-04-26 | 40000 | 592.8 | 24.6 | 18.58 | 24.6 | 30.7 | 8.29 | 30.5 | 33.4 | -1 | 1.3 | 10.29 | 29.91 | 13.9 | 49.96 | 64.1 | 0.236 | 0.051 | 16.32
| 606 | 2008-04-26 | 50000 | 626.7 | 8.2 | 5.5 | 5.7 | 9 | 15.44 | 108.1 | 165.5 | -1 | 47.1 | 4.92 | 15.42 | 4.7 | 22.56 | 22.3 | 0.082 | 0.017 | 14.27
| 607 | 2008-04-26 | 60000 | 636.5 | 92.7 | 3.4 | 2 | 27.6 | 17.11 | 126.8 | 193.6 | -1 | 61.5 | 3.41 | 8.2 | 2.1 | 9.74 | 3.9 | 0.015 | 0.008 | 12.34
| 608 | 2008-04-26 | 70000 | 670.3 | -2.8 | 0.13 | 0.1 | -2.4 | 22.64 | 186.6 | 269.4 | -1 | 123.6 | 2.32 | 10.94 | 1.9 | 2.2 | 1.9 | 0.007 | 0.007 | 13.88
| 609 | 2008-04-26 | 80000 | 676.5 | -2.8 | 0.07 | 0.1 | -2.4 | 22.54 | 185.5 | 268.8 | -1 | 121.9 | 2.48 | 11.09 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.85
| 610 | 2008-04-26 | 90000 | 678 | -2.7 | 0.11 | 0.1 | -2.2 | 22.58 | 185.5 | 268.9 | -1 | 138.1 | 2.53 | 12.4 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.78
| 611 | 2008-04-26 | 100000 | 677.2 | -2.6 | 0.1 | 0.1 | -2.2 | 22.51 | 185.1 | 268.5 | -1 | 152.2 | 2.52 | 13.24 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.74
| 612 | 2008-04-26 | 110000 | 674.8 | -2.3 | 0.08 | 0.1 | -1.9 | 22.21 | 182.1 | 265.1 | -0.9 | 148.8 | 2.52 | 13.2 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.74
| 613 | 2008-04-26 | 120000 | 673.6 | -2.4 | 0.08 | 0.1 | -2 | 21.97 | 179.4 | 262.2 | -1 | 148 | 2.51 | 13.19 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.73
| 614 | 2008-04-26 | 130000 | 672 | -2.9 | 0.1 | 0.1 | -2.3 | 21.68 | 176.5 | 259 | -1 | 145.3 | 2.51 | 13.08 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.74
| 615 | 2008-04-26 | 140000 | 670.1 | -2.8 | 0.09 | 0.1 | -2.4 | 21.47 | 174.2 | 256.3 | -1 | 144 | 2.51 | 13.04 | 2.1 | 2.39 | 2 | 0.007 | 0.008 | 13.76
| 616 | 2008-04-26 | 150000 | 669.2 | -3 | 0.1 | 0.1 | -2.6 | 21.32 | 173.1 | 255.2 | -0.7 | 144.3 | 2.48 | 13.04 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.77
| 617 | 2008-04-26 | 160000 | 669 | -3 | 0.1 | 0.1 | -2.4 | 21.33 | 172.4 | 254.1 | 0.4 | 141.9 | 2.49 | 12.94 | 2.1 | 2.36 | 2 | 0.007 | 0.008 | 13.77
| 618 | 2008-04-26 | 170000 | 644.6 | -2.2 | 0.1 | 0.1 | -1.9 | 16.58 | 123.6 | 190.9 | -1 | 60.7 | 2.3 | 8.31 | 2 | 2.19 | 1.9 | 0.007 | 0.007 | 13.95
| 619 | 2008-04-26 | 180000 | 639.4 | -2.6 | 0.11 | 0.1 | -2.2 | 16.87 | 126.2 | 192.8 | -1 | 55 | 2.41 | 7.58 | 2 | 2.29 | 1.9 | 0.007 | 0.008 | 13.93
| 620 | 2008-04-26 | 190000 | 639.4 | -2.7 | 0.12 | 0.1 | -2.2 | 16.74 | 125.5 | 192 | -1 | 55.3 | 2.44 | 7.64 | 2.1 | 2.32 | 2 | 0.007 | 0.008 | 13.93
| 621 | 2008-04-26 | 200000 | 639.4 | -2.4 | 0.13 | 0.1 | -2 | 16.84 | 126.8 | 193.6 | -1 | 55.9 | 2.42 | 7.61 | 2 | 2.3 | 1.9 | 0.007 | 0.008 | 13.92
| 622 | 2008-04-26 | 210000 | 639.3 | -2.6 | 0.15 | 0.1 | -2.3 | 16.9 | 126.9 | 193.5 | -1 | 54.5 | 2.45 | 7.57 | 2.1 | 2.33 | 2 | 0.007 | 0.008 | 13.89
| 623 | 2008-04-26 | 220000 | 556.3 | 4.2 | 4.32 | 27.5 | -87.7 | 1.59 | 7.2 | 13.2 | -1 | 2.7 | 2.08 | 5.08 | 5.9 | 7.57 | 11.5 | 0.045 | 0.022 | 19.59
| 624 | 2008-04-26 | 230000 | 448.5 | -3 | 0.22 | 17.8 | -246.9 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.01 | 0.3 | 0 | -0.5 | 0.006 | 0.001 | 20.82
| 625 | 2008-04-27 | 0 | 433.7 | -2.8 | 0.22 | 18.5 | -221 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0.1 | 0 | -0.6 | 0.007 | 0.001 | 20.82
| 626 | 2008-04-27 | 10000 | 425.6 | -2.9 | 0.23 | 19.7 | -229.2 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0 | -0.2 | 0.006 | 0 | 20.75
| 627 | 2008-04-27 | 20000 | 419.4 | -2.9 | 0.24 | 17.8 | -217.8 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | 0 | -0.06 | 0.1 | 0 | -0.5 | 0.006 | 0.001 | 20.82
| 628 | 2008-04-27 | 30000 | 414.2 | -2.6 | 0.22 | 15.2 | -173.4 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0 | -0.1 | 0.006 | 0 | 20.81
| 629 | 2008-04-27 | 40000 | 408.7 | -2.7 | 0.2 | 13.8 | -188.6 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | -0.1 | 0 | -0.2 | 0.006 | 0 | 20.74
| 630 | 2008-04-27 | 50000 | 404.1 | -2 | 0.2 | 13.5 | -158.8 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.1 | 0.01 | -0.1 | 0.006 | 0 | 20.81
| 631 | 2008-04-27 | 60000 | 399 | -2.8 | 0.21 | 13.8 | -184.9 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | -0.1 | 0.01 | 0.1 | 0.006 | 0 | 20.81
| 632 | 2008-04-27 | 70000 | 392.4 | -2.8 | 0.21 | 15.5 | -201 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0 | -0.1 | 0.006 | 0 | 20.81
| 633 | 2008-04-27 | 80000 | 369.2 | -2.7 | 0.2 | 14.7 | -206 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | 0 | -0.06 | 0.1 | 0.01 | 0.1 | 0.007 | 0.001 | 20.82
| 634 | 2008-04-27 | 90000 | 354 | -2.6 | 0.23 | 16.8 | -176.9 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0.02 | 2.08 | 1.5 | 0.02 | 0.9 | 0.009 | 0.005 | 20.82
| 635 | 2008-04-27 | 100000 | 346.6 | -2.6 | 0.23 | 16.1 | -184.2 | 0.05 | 0.5 | 1.3 | -1 | 0.9 | 0.02 | -0.06 | 1.6 | 0.03 | 1.6 | 0.01 | 0.006 | 20.81
| 636 | 2008-04-27 | 110000 | 342.6 | -3 | 0.22 | 14.5 | -185.3 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.3 | 0.01 | 0.4 | 0.007 | 0.001 | 20.81
| 637 | 2008-04-27 | 120000 | 339.6 | -2.8 | 0.24 | 14 | -167.6 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0.01 | -0.06 | 0.4 | 0.01 | 0.3 | 0.005 | 0.001 | 20.72
| 638 | 2008-04-27 | 130000 | 336.5 | -2.9 | 0.25 | 13.7 | -169.7 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | 0.3 | 0 | -0.1 | 0.005 | 0.001 | 20.79
| 639 | 2008-04-27 | 140000 | 333.7 | -2.6 | 0.26 | 13.7 | -136.5 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | 0.01 | -0.07 | 0.5 | 0 | -0.1 | 0.004 | 0.002 | 20.78
| 640 | 2008-04-27 | 150000 | 331.1 | -2.6 | 0.18 | 8.8 | -128.9 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0 | -0.3 | 0.004 | 0 | 20.78
| 641 | 2008-04-27 | 160000 | 327.7 | -2.9 | 0.18 | 8.1 | -130.5 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | -0.1 | 0.004 | 0 | 20.69
| 642 | 2008-04-27 | 170000 | 324.7 | -2.6 | 0.18 | 8.2 | -120.5 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.004 | 0 | 20.77
| 643 | 2008-04-27 | 180000 | 321.6 | -2.8 | 0.19 | 8.2 | -116.9 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0 | -0.1 | 0.004 | 0 | 20.76
| 644 | 2008-04-27 | 190000 | 318.6 | -2.8 | 0.18 | 7.4 | -114 | 0.04 | 0.5 | 1.3 | -1 | 1.1 | 0 | -0.07 | 0 | 0 | 0.1 | 0.004 | 0 | 20.76
| 645 | 2008-04-27 | 200000 | 315.3 | -2.6 | 0.18 | 7.7 | -113.4 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0 | 0 | 0.004 | 0 | 20.76
| 646 | 2008-04-27 | 210000 | 312.3 | -2.9 | 0.17 | 7 | -123 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | -0.1 | 0.004 | 0 | 20.75
| 647 | 2008-04-27 | 220000 | 308.8 | -2.6 | 0.17 | 6.6 | -110.4 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0 | -0.2 | 0.003 | 0 | 20.75
| 648 | 2008-04-27 | 230000 | 305.1 | -3 | 0.17 | 6.1 | -109.7 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0.004 | 0 | 20.74
| 649 | 2008-04-28 | 0 | 301.7 | -2.9 | 0.19 | 6.5 | -102.7 | 0.04 | 0.5 | 1.2 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.003 | 0 | 20.73
| 650 | 2008-04-28 | 10000 | 295.1 | -3.1 | 0.19 | 6.3 | -105 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | 0 | 0.003 | 0 | 20.72
| 651 | 2008-04-28 | 20000 | 283.8 | 15.7 | 1.19 | 8.2 | -49.9 | 0.19 | 0.5 | 1.3 | -1 | 1 | 0.39 | 0.71 | 0.9 | 0.42 | 0.8 | 0.006 | 0.003 | 20.58
| 652 | 2008-04-28 | 30000 | 525 | 27.6 | 14.39 | 19.8 | 42.4 | 7.27 | 21.4 | 21.9 | -1 | 1 | 10.29 | 29.76 | 14.3 | 46.34 | 63.7 | 0.235 | 0.053 | 16.6
| 653 | 2008-04-28 | 40000 | 612.7 | 29.5 | 20.03 | 20.5 | 30.2 | 9.67 | 44.8 | 54.6 | -1 | 6 | 10.29 | 30.01 | 10.5 | 58.75 | 60.2 | 0.222 | 0.039 | 15.15
| 654 | 2008-04-28 | 50000 | 635 | 0.6 | 2.17 | 2.1 | 0.9 | 18.06 | 139.1 | 204.8 | -1 | 75.7 | 3.61 | 12.2 | 3.1 | 12.41 | 11.2 | 0.041 | 0.011 | 13.8
| 655 | 2008-04-28 | 60000 | 666.2 | 92.9 | 3.22 | 3.1 | 2.9 | 22.04 | 180.2 | 262.8 | -1 | 138.3 | 3.46 | 12.63 | 2.4 | 9.72 | 4.1 | 0.015 | 0.009 | 12.02
| 656 | 2008-04-28 | 70000 | 671.5 | -2.8 | 0.15 | 0.1 | -2.1 | 21.92 | 179.4 | 262.7 | -1 | 129.1 | 2.49 | 12.02 | 2 | 2.37 | 1.9 | 0.007 | 0.008 | 13.66
| 657 | 2008-04-28 | 80000 | 672 | -2.7 | 0.08 | 0.1 | -2 | 21.94 | 179.5 | 262.1 | -1 | 136.2 | 2.56 | 12.46 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.62
| 658 | 2008-04-28 | 90000 | 670.3 | -2.8 | 0.08 | 0.1 | -2.3 | 22 | 179.3 | 261.6 | -1 | 138.4 | 2.54 | 12.65 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.6
| 659 | 2008-04-28 | 100000 | 669.4 | -2.5 | 0.09 | 0.1 | -2.1 | 21.83 | 178.5 | 260.6 | -1 | 139.4 | 2.56 | 12.78 | 2.1 | 2.44 | 2 | 0.007 | 0.008 | 13.61
| 660 | 2008-04-28 | 110000 | 669 | -2.6 | 0.08 | 0.1 | -2.2 | 21.79 | 177.1 | 259.1 | -1 | 139.6 | 2.54 | 12.77 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.62
| 661 | 2008-04-28 | 120000 | 668.4 | -2.6 | 0.08 | 0.1 | -2.1 | 21.56 | 176.8 | 258.8 | -1 | 138.2 | 2.54 | 12.69 | 2.1 | 2.41 | 1.9 | 0.007 | 0.008 | 13.61
| 662 | 2008-04-28 | 130000 | 667.8 | -2.9 | 0.08 | 0.1 | -2.4 | 21.55 | 176.4 | 257.5 | -1 | 137.6 | 2.52 | 12.62 | 2 | 2.41 | 1.9 | 0.007 | 0.008 | 13.61
| 663 | 2008-04-28 | 140000 | 668 | -2.8 | 0.08 | 0.1 | -2.2 | 21.55 | 175.7 | 257.4 | -1 | 137.1 | 2.55 | 12.65 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.61
| 664 | 2008-04-28 | 150000 | 667.1 | -2.7 | 0.09 | 0.1 | -2.2 | 21.42 | 174.5 | 255.8 | -1 | 141.4 | 2.43 | 12.78 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.63
| 665 | 2008-04-28 | 160000 | 666.3 | -2.9 | 0.08 | 0.1 | -2.5 | 21.43 | 174.9 | 256.1 | -1 | 138.8 | 2.53 | 12.79 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.62
| 666 | 2008-04-28 | 170000 | 667.1 | -2.6 | 0.06 | 0 | -2 | 21.44 | 175.1 | 255.6 | -1 | 132.5 | 2.35 | 11.9 | 1.9 | 2.24 | 1.8 | 0.007 | 0.007 | 13.66
| 667 | 2008-04-28 | 180000 | 667.9 | -2.6 | 0.06 | 0 | -2.1 | 21.76 | 177.8 | 259.5 | -1 | 137.5 | 2.55 | 12.68 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.6
| 668 | 2008-04-28 | 190000 | 667.7 | -3.1 | 0.06 | 0 | -2.4 | 21.74 | 178.1 | 258.9 | -1 | 123.2 | 2.4 | 11.43 | 1.9 | 2.3 | 1.9 | 0.007 | 0.007 | 13.65
| 669 | 2008-04-28 | 200000 | 670.8 | -2.9 | 0.06 | 0 | -2.4 | 21.73 | 178.4 | 258.5 | -1 | 111.7 | 2.47 | 10.61 | 2 | 2.35 | 1.9 | 0.007 | 0.008 | 13.72
| 670 | 2008-04-28 | 210000 | 647.5 | -3 | 0.07 | 0.1 | -2.5 | 17.84 | 137.3 | 206 | -1 | 55.6 | 2.47 | 7.51 | 2.1 | 2.35 | 1.9 | 0.007 | 0.008 | 13.79
| 671 | 2008-04-28 | 220000 | 637.3 | -2.4 | 0.11 | 0.1 | -1.9 | 16.91 | 126.7 | 192.1 | -1 | 53 | 2.5 | 7.6 | 2.1 | 2.38 | 2 | 0.007 | 0.008 | 13.81
| 672 | 2008-04-28 | 230000 | 556.5 | 6.6 | 5.89 | 23.3 | -28.5 | 2.38 | 10 | 17.5 | -1 | 13 | 2.43 | 7.34 | 3.5 | 9.76 | 11.4 | 0.043 | 0.013 | 19.22
| 673 | 2008-04-29 | 0 | 427.4 | -2.7 | 0.22 | 7.7 | -92.4 | 0.27 | 0.5 | 1.3 | -1 | 0.9 | 0 | 0.03 | 0 | 0 | -0.1 | 0.003 | 0 | 20.73
| 674 | 2008-04-29 | 10000 | 403.4 | -2.8 | 0.19 | 6.2 | -98 | 0.25 | 0.5 | 1.3 | -1 | 1.1 | 0 | -0.05 | -0.1 | 0 | 0.1 | 0.003 | 0 | 20.72
| 675 | 2008-04-29 | 20000 | 393.9 | -2.8 | 0.19 | 6.2 | -93 | 0.26 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.1 | 0 | 0 | 0.003 | 0 | 20.72
| 676 | 2008-04-29 | 30000 | 395.8 | -2.7 | 0.14 | 4.5 | -86.3 | 0.07 | 0.5 | 1.3 | -1 | 1 | 0 | 0.04 | -0.1 | 0 | 0 | 0.003 | 0 | 20.71
| 677 | 2008-04-29 | 40000 | 563.2 | 10.4 | 13.28 | 19.2 | 13.3 | 6.71 | 17.9 | 18.3 | -1 | 1.8 | 9.79 | 29.22 | 14.2 | 42.22 | 60.9 | 0.224 | 0.052 | 16.88
| 678 | 2008-04-29 | 50000 | 622.3 | 14.5 | 15.06 | 15.4 | 15 | 11.74 | 67.8 | 94.5 | -1 | 35.3 | 8.41 | 25.82 | 8.4 | 50.72 | 50.8 | 0.187 | 0.031 | 14.76
| 679 | 2008-04-29 | 60000 | 631.7 | -2.8 | 0.13 | 0.1 | -2.3 | 17.38 | 131.8 | 197.9 | 1.5 | 61.7 | 2.35 | 8.43 | 1.9 | 2.24 | 1.9 | 0.007 | 0.007 | 13.77
| 680 | 2008-04-29 | 70000 | 659.9 | 93.8 | 3.32 | 2.6 | 18.7 | 22.18 | 183.1 | 265.1 | -0.6 | 145.5 | 3.19 | 12.07 | 1.9 | 9.43 | 3.7 | 0.014 | 0.007 | 12.09
| 681 | 2008-04-29 | 80000 | 674.2 | -2.5 | 0.11 | 0.1 | -2 | 22.27 | 183.8 | 267.5 | -1 | 137.4 | 2.48 | 12.42 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.58
| 682 | 2008-04-29 | 90000 | 675.8 | -2.6 | 0.09 | 0.1 | -2.3 | 22.27 | 183.2 | 266.7 | -1 | 139.9 | 2.5 | 12.43 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.57
| 683 | 2008-04-29 | 100000 | 674.7 | -2.4 | 0.09 | 0.1 | -1.8 | 22.25 | 183.1 | 265.4 | -0.9 | 140.7 | 2.5 | 12.35 | 2 | 2.39 | 1.9 | 0.007 | 0.007 | 13.58
| 684 | 2008-04-29 | 110000 | 673.8 | -3 | 0.1 | 0.1 | -2.5 | 22.19 | 182.5 | 264.4 | -1 | 141.8 | 2.5 | 12.47 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.59
| 685 | 2008-04-29 | 120000 | 672.6 | -2.9 | 0.1 | 0.1 | -2.4 | 22.05 | 181.6 | 263.4 | -1 | 143.9 | 2.49 | 12.6 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.6
| 686 | 2008-04-29 | 130000 | 672.2 | -2.9 | 0.1 | 0.1 | -2.4 | 22.07 | 182 | 263.8 | -1 | 142.6 | 2.49 | 12.51 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.61
| 687 | 2008-04-29 | 140000 | 671.4 | -2.7 | 0.1 | 0.1 | -2.2 | 22.05 | 181.5 | 263.4 | -1 | 142.8 | 2.48 | 12.54 | 2 | 2.37 | 1.9 | 0.007 | 0.007 | 13.62
| 688 | 2008-04-29 | 150000 | 671.5 | -2.9 | 0.1 | 0.1 | -2.3 | 22.05 | 181.1 | 262.8 | -1 | 144 | 2.48 | 12.6 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.63
| 689 | 2008-04-29 | 160000 | 671.3 | -2.4 | 0.1 | 0.1 | -1.9 | 22.05 | 180.9 | 262.6 | -1 | 144.6 | 2.47 | 12.59 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.63
| 690 | 2008-04-29 | 170000 | 671.3 | -2.6 | 0.1 | 0.1 | -2.2 | 22.05 | 181.6 | 263.3 | -1 | 143 | 2.47 | 12.52 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.64
| 691 | 2008-04-29 | 180000 | 671.5 | -2.7 | 0.1 | 0.1 | -2.2 | 22.1 | 182.1 | 264 | -1 | 143.1 | 2.46 | 12.54 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.65
| 692 | 2008-04-29 | 190000 | 672 | -2.7 | 0.1 | 0.1 | -2.3 | 22.26 | 182.9 | 264.7 | -1 | 141.5 | 2.47 | 12.63 | 2 | 2.36 | 1.9 | 0.007 | 0.007 | 13.65
| 693 | 2008-04-29 | 200000 | 673.2 | -2.9 | 0.1 | 0.1 | -2.4 | 22.21 | 183.2 | 265.2 | -1 | 143.5 | 2.45 | 12.63 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.66
| 694 | 2008-04-29 | 210000 | 641.6 | -2.5 | 0.3 | 0.2 | -2 | 16.49 | 121.5 | 186.7 | -1 | 53.9 | 2.49 | 8.48 | 2.1 | 3.5 | 2.7 | 0.01 | 0.008 | 13.85
| 695 | 2008-04-29 | 220000 | 544.2 | 5.6 | 4.68 | 29.1 | -91.8 | 1.34 | 4.6 | 9.3 | -1 | 3.2 | 1.82 | 5.16 | 3.1 | 7.35 | 9.8 | 0.038 | 0.011 | 19.89
| 696 | 2008-04-29 | 230000 | 424.9 | -2.9 | 0.21 | 11.6 | -157.4 | 0.51 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.01 | -0.1 | 0.01 | 0.1 | 0.005 | 0 | 20.72
| 697 | 2008-04-30 | 0 | 401.7 | -2.6 | 0.2 | 12.6 | -165.2 | 0.3 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.1 | 0.01 | 0.4 | 0.005 | 0 | 20.8
| 698 | 2008-04-30 | 10000 | 393.4 | -2.8 | 0.2 | 13.8 | -186.2 | 0.27 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.006 | 0 | 20.81
| 699 | 2008-04-30 | 20000 | 386.6 | -2.8 | 0.21 | 14.7 | -183.5 | 0.26 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | -0.2 | 0 | -0.2 | 0.005 | 0 | 20.81
| 700 | 2008-04-30 | 30000 | 390.9 | -2.6 | 0.16 | 11.6 | -200.7 | 0.29 | 0.5 | 1.3 | -1 | 1 | 0 | 0.14 | -0.2 | 0 | -0.2 | 0.006 | 0 | 20.82
| 701 | 2008-04-30 | 40000 | 576.4 | 30.1 | 16.6 | 23.8 | 41.1 | 7.08 | 19.9 | 20.3 | -1 | 0.8 | 10.13 | 29.31 | 14.7 | 40.63 | 58.7 | 0.216 | 0.054 | 16.83
| 702 | 2008-04-30 | 50000 | 619 | 15 | 12.03 | 12.4 | 15.7 | 12.86 | 80.1 | 111.4 | -1 | 28.8 | 7.32 | 22.5 | 7.3 | 42.7 | 42.8 | 0.158 | 0.027 | 14.63
| 703 | 2008-04-30 | 60000 | 632.2 | -2.6 | 0.24 | 0.2 | -2.1 | 17.65 | 134.2 | 197.9 | -1 | 65.6 | 2.37 | 8.28 | 2 | 2.25 | 1.9 | 0.007 | 0.007 | 13.87
| 704 | 2008-04-30 | 70000 | 659.5 | -2.3 | 0.46 | 0.5 | -12.2 | 22.31 | 184 | 265.4 | -1 | 127.2 | 2.31 | 11.48 | 1.8 | 2.21 | 2 | 42.742 | 14.251 | 13.98
| 705 | 2008-04-30 | 80000 | 673.3 | 93.7 | 3.03 | 4 | 12.7 | 22.24 | 183.6 | 266 | -1 | 120.2 | 3.45 | 11.22 | 2.7 | 9.71 | 4.4 | 0.016 | 0.01 | 12.02
| 706 | 2008-04-30 | 90000 | 675.8 | -2.9 | 0.13 | 0.1 | -2.4 | 21.99 | 180.7 | 262.6 | -1 | 126.9 | 2.43 | 11.79 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.77
| 707 | 2008-04-30 | 100000 | 641.5 | -2.5 | 0.24 | 0.2 | -2.1 | 16.93 | 126.8 | 192.7 | -1 | 56.1 | 2.32 | 7.82 | 2 | 2.21 | 1.9 | 0.007 | 0.007 | 13.91
| 708 | 2008-04-30 | 110000 | 637.5 | -2.6 | 0.24 | 0.2 | -2.2 | 16.93 | 127 | 192.2 | -1 | 56.2 | 2.38 | 7.77 | 2 | 2.27 | 1.9 | 0.007 | 0.007 | 13.9
| 709 | 2008-04-30 | 120000 | 636.3 | -2.7 | 0.23 | 0.2 | -2.5 | 16.94 | 127.2 | 192.5 | -1 | 56 | 2.4 | 7.71 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.91
| 710 | 2008-04-30 | 130000 | 636.2 | -2.9 | 0.22 | 0.2 | -2.5 | 17.42 | 132.5 | 198.3 | -1 | 64.7 | 2.41 | 8 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.9
| 711 | 2008-04-30 | 140000 | 669.6 | -2.4 | 0.15 | 0.1 | -2 | 22.22 | 181.8 | 263.5 | -1 | 151.2 | 2.27 | 12.92 | 1.9 | 2.17 | 1.8 | 0.007 | 0.007 | 13.71
| 712 | 2008-04-30 | 150000 | 671.6 | -2.4 | 0.18 | 0.1 | -2 | 22.2 | 181.7 | 263.6 | -1 | 147 | 2.45 | 12.89 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.73
| 713 | 2008-04-30 | 160000 | 671.3 | -2.9 | 0.16 | 0.1 | -2.4 | 22.22 | 182.1 | 264 | -1 | 145.7 | 2.43 | 12.8 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.74
| 714 | 2008-04-30 | 170000 | 671 | -2.7 | 0.15 | 0.1 | -2.2 | 22.27 | 182.8 | 264.3 | -1 | 144.3 | 2.44 | 12.71 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.74
| 715 | 2008-04-30 | 180000 | 671.5 | -2.5 | 0.14 | 0.1 | -1.9 | 22.27 | 183.1 | 264.7 | -1 | 143 | 2.43 | 12.66 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.74
| 716 | 2008-04-30 | 190000 | 671.4 | -2.6 | 0.13 | 0.1 | -2.2 | 22.25 | 183.4 | 264.7 | -1 | 140.4 | 2.39 | 12.42 | 2 | 2.28 | 1.9 | 0.007 | 0.007 | 13.76
| 717 | 2008-04-30 | 200000 | 673.4 | -2.8 | 0.13 | 0.1 | -2.3 | 22.22 | 182.8 | 263.4 | -1 | 130.5 | 2.4 | 11.64 | 2 | 2.29 | 1.9 | 0.007 | 0.007 | 13.82
| 718 | 2008-04-30 | 210000 | 674.2 | -2.5 | 0.13 | 0.1 | -2.1 | 21.99 | 180.4 | 260.5 | -1 | 123 | 2.34 | 11.21 | 2 | 2.23 | 1.9 | 0.007 | 0.007 | 13.84
| 719 | 2008-04-30 | 220000 | 561.8 | 6.9 | 5.37 | 46.6 | -107.2 | 2.35 | 10.9 | 20.5 | -1 | 1.6 | 2.67 | 6.8 | 9.2 | 9.93 | 18 | 278.632 | 137.731 | 19.43
| 720 | 2008-04-30 | 230000 | 429.4 | -2.6 | 0.28 | 0.6 | -0.8 | 0.15 | 0.5 | 1.3 | -1 | 0.9 | 0 | 0 | 0 | 0 | 0.2 | 30.083 | 0 | 20.95
| 721 | 2008-05-01 | 0 | 405.2 | -2.5 | 0.26 | 0 | 0 | 0.35 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.05 | 0 | 0.01 | 0 | 19 | 0.001 | 20.95
| 722 | / | /
| 723 | / | / | -9999 | 635.223 | 4.069 | 0.947 | 2.429 | -12.153 | 18.452 | 148.677 | 216.351 | -9999 | 105.889 | 2.523 | 10.581 | 2.204 | 3.904 | 3.526 | 9.973 | 1.411 | 14.457

[10 empty] | July Total MW-hr | 156045.577
Excluding non-op hours
Used gas use column to confirm operation

## PEMS April
Rows highlighted in yellow indicate hours of start-up/shutdown/non-operating hours Bright yellow highlight indicates NH3 flow less than 1 lb/hour during these periods indicating not sufficient accuracy to provide reliable data
|  |  | Outlet | O2 | PNG | Inlet | NH3 |  |  |  |  | Gas | Gas Flow in scfm * HHV / 10^6 | HTIP * 8710 * (20.9 / 20.9 - O2dry) | NH3 Flow lb/hr * 379.43 / ( 60 * 17.03) | (nh3flow dscfm / flue gas flow dscfm ) * 10^6 | nh3flow fraction pppm * (20.9 / (20.9 -O2dry) | nh3flow fraction @ 15% O2 - (noxin - noxout @15% O2) | Correction Factor
|  |  | Nox | Dry | Flow | Nox | Flow |  |  |  |  | Flow |  |  | 17.03 lb / lb mole |  |  |  | 0.37763
|  |  | dry |  |  | dry | [5 empty] | scfm
DATE | TIME | GEN22 | NOX23 | OXY25 | GAS210 | NOX2I12 | NH3FLO216 | Constants | nox in | nox out corrected | noxin - noxout | fuel flow | heat input | flue gas flow | nh3 flow | nh3flow fraction | nh3flow fraction | nh3slip uncorrected | nh3slip | nh3slip | nh3slip | nh3slip W/OUT no flow and neg. data
|  | (MW) | ppm | % | lb/sec | ppm | lb/hour |  | ppm @15%O2 | ppm@15%O2 | ppm @15% O2 | scfm | mmbtu/min | dscfm | dscfm | ppm | ppm @15%O2 | ppm | ppm | lb/mmbtu | lb/hr | lb/hr
2008-04-01 | 0 | 272.4 | 2.52 | 13.84 | 23.05 | 12.37 | 25.422 |  | 10.3375 | 2.1059 | 8.2316 | 31499.7431 | 34.6497 | 893427.7485 | 9.4401 | 10.5661 | 8.8301 | 0.59847 | 0.226 | 0.00025707 | 0.53445 | 0.53445
[7 empty] | 0 | Fd dscf/mmBtu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2008-04-01 | 10000 | 273.9 | 2.53 | 13.84 | 23.23 | 12.17 | 25.156 | 8710 | 10.1704 | 2.1143 | 8.0561 | 31745.7281 | 34.9203 | 900404.6246 | 9.3413 | 10.3746 | 8.67 | 0.61387 | 0.23181 | 0.00026369 | 0.55248 | 0.55248
[7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2008-04-01 | 20000 | 274.3 | 2.52 | 13.84 | 23.26 | 12.11 | 24.985 | HHV btu/scf | 10.1203 | 2.1059 | 8.0143 | 31786.7256 | 34.9654 | 901567.4373 | 9.2778 | 10.2907 | 8.5999 | 0.58561 | 0.22114 | 0.00025155 | 0.52773 | 0.52773
[7 empty] | 0 | 1100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2008-04-01 | 30000 | 274.3 | 2.53 | 13.83 | 23.26 | 11.97 | 24.643 |  | 9.9891 | 2.1113 | 7.8778 | 31786.7256 | 34.9654 | 900292.2358 | 9.1508 | 10.1643 | 8.4822 | 0.60441 | 0.22824 | 0.00025925 | 0.5439 | 0.5439
[7 empty] | 0 | Gas Specifc Gravity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2008-04-01 | 40000 | 274.2 | 2.53 | 13.83 | 23.21 | 11.93 | 24.548 | 0.584 | 9.9557 | 2.1113 | 7.8444 | 31718.3964 | 34.8902 | 898356.9558 | 9.1155 | 10.1469 | 8.4677 | 0.62329 | 0.23537 | 0.00026735 | 0.55968 | 0.55968
[7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2008-04-01 | 50000 | 274.1 | 2.53 | 13.82 | 23.14 | 11.97 | 24.624 | Density of Air lb/cubic ft | 9.975 | 2.1083 | 7.8667 | 31622.7356 | 34.785 | 894382.525 | 9.1438 | 10.2235 | 8.5196 | 0.65295 | 0.24657 | 0.00027968 | 0.58372 | 0.58372
[7 empty] | 0 | 0.07518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2008-04-01 | 60000 | 274.1 | 2.54 | 13.81 | 23.09 | 11.89 | 24.928 |  | 9.8944 | 2.1137 | 7.7807 | 31554.4064 | 34.7098 | 891191.2338 | 9.2566 | 10.3868 | 8.6435 | 0.86279 | 0.32582 | 0.00036904 | 0.76857 | 0.76857
2008-04-01 | 70000 | 273.3 | 3.78 | 11.74 | 23.18 | 11.87 | 24.795 |  | 7.6455 | 2.4347 | 5.2108 | 31677.3989 | 34.8451 | 692486.2686 | 9.2072 | 13.2959 | 8.564 | 3.3532 | 1.2663 | 0.0011101 | 2.321 | 2.321
2008-04-01 | 80000 | 273.2 | 3.44 | 12.65 | 23.11 | 11.88 | 25.84 |  | 8.496 | 2.4601 | 6.0359 | 31581.7381 | 34.7399 | 766547.7357 | 9.5953 | 12.5175 | 8.9519 | 2.9161 | 1.1012 | 0.0010719 | 2.2343 | 2.2343
2008-04-01 | 90000 | 272 | 2.58 | 13.71 | 23.04 | 12.05 | 25.422 |  | 9.888 | 2.1171 | 7.7709 | 31486.0773 | 34.6347 | 876893.3822 | 9.4401 | 10.7654 | 8.8339 | 1.063 | 0.4014 | 0.00044834 | 0.93168 | 0.93168
2008-04-01 | 100000 | 269.3 | 2.58 | 13.72 | 22.85 | 12.32 | 26.239 |  | 10.1237 | 2.1201 | 8.0036 | 31226.4264 | 34.3491 | 870873.2851 | 9.7435 | 11.1881 | 9.1936 | 1.19 | 0.44937 | 0.00050261 | 1.0359 | 1.0359
2008-04-01 | 110000 | 267.4 | 2.57 | 13.72 | 22.59 | 12.48 | 26.638 |  | 10.2552 | 2.1118 | 8.1433 | 30871.1148 | 33.9582 | 860964.0048 | 9.8916 | 11.489 | 9.4408 | 1.2975 | 0.48998 | 0.00054803 | 1.1166 | 1.1166
2008-04-01 | 120000 | 265.8 | 2.57 | 13.73 | 22.52 | 12.46 | 26.581 |  | 10.253 | 2.1148 | 8.1382 | 30775.454 | 33.853 | 859493.1874 | 9.8705 | 11.484 | 9.4499 | 1.3117 | 0.49533 | 0.00055479 | 1.1269 | 1.1269
2008-04-01 | 130000 | 264.9 | 2.58 | 13.71 | 22.38 | 12.47 | 26.562 |  | 10.2327 | 2.1171 | 8.1156 | 30584.1323 | 33.6425 | 851774.0405 | 9.8634 | 11.5798 | 9.5022 | 1.3866 | 0.52364 | 0.00058486 | 1.1806 | 1.1806
2008-04-01 | 140000 | 264 | 2.58 | 13.7 | 22.27 | 12.53 | 26.771 |  | 10.2676 | 2.1142 | 8.1535 | 30433.8082 | 33.4772 | 846410.2788 | 9.941 | 11.7449 | 9.6243 | 1.4708 | 0.55543 | 0.00061951 | 1.2444 | 1.2444
2008-04-01 | 150000 | 263.2 | 2.58 | 13.7 | 22.27 | 12.58 | 26.923 |  | 10.3086 | 2.1142 | 8.1944 | 30433.8082 | 33.4772 | 846410.2788 | 9.9974 | 11.8116 | 9.6789 | 1.4845 | 0.56059 | 0.00062527 | 1.2559 | 1.2559
2008-04-01 | 160000 | 262.9 | 2.58 | 13.69 | 22.25 | 12.67 | 27.189 |  | 10.368 | 2.1112 | 8.2567 | 30406.4765 | 33.4471 | 844477.2587 | 10.0962 | 11.9556 | 9.7834 | 1.5266 | 0.5765 | 0.00064212 | 1.2886 | 1.2886
2008-04-01 | 170000 | 262.5 | 2.58 | 13.68 | 22.21 | 12.64 | 27.094 |  | 10.3291 | 2.1083 | 8.2208 | 30351.8132 | 33.387 | 841791.564 | 10.0609 | 11.9518 | 9.7667 | 1.546 | 0.5838 | 0.00064935 | 1.3008 | 1.3008
2008-04-01 | 180000 | 263 | 2.57 | 13.67 | 22.27 | 12.48 | 26.657 |  | 10.1842 | 2.0972 | 8.087 | 30433.8082 | 33.4772 | 842898.2029 | 9.8987 | 11.7436 | 9.5833 | 1.4963 | 0.56505 | 0.00062763 | 1.2607 | 1.2607
2008-04-01 | 190000 | 263.9 | 2.58 | 13.67 | 22.27 | 12.4 | 26.448 |  | 10.1189 | 2.1054 | 8.0136 | 30433.8082 | 33.4772 | 842898.2029 | 9.8211 | 11.6515 | 9.5082 | 1.4946 | 0.56441 | 0.00062692 | 1.2592 | 1.2592
2008-04-01 | 200000 | 265.1 | 2.58 | 13.67 | 22.39 | 12.34 | 26.22 |  | 10.07 | 2.1054 | 7.9646 | 30597.7982 | 33.6576 | 847440.0882 | 9.7364 | 11.4892 | 9.3757 | 1.4111 | 0.53287 | 0.00059188 | 1.1953 | 1.1953
2008-04-01 | 210000 | 266.1 | 2.58 | 13.68 | 22.53 | 12.34 | 26.049 |  | 10.0839 | 2.1083 | 7.9756 | 30789.1198 | 33.868 | 853920.0332 | 9.6729 | 11.3276 | 9.2567 | 1.281 | 0.48376 | 0.00053808 | 1.0934 | 1.0934
2008-04-01 | 220000 | 266.9 | 2.57 | 13.68 | 22.54 | 12.34 | 25.498 |  | 10.0839 | 2.1001 | 7.9838 | 30802.7856 | 33.8831 | 854299.0478 | 9.4683 | 11.0831 | 9.0568 | 1.073 | 0.40522 | 0.00045071 | 0.91629 | 0.91629
2008-04-01 | 230000 | 267.5 | 2.57 | 13.68 | 22.63 | 12.25 | 25.289 |  | 10.0104 | 2.1001 | 7.9102 | 30925.7781 | 34.0184 | 857710.1798 | 9.3907 | 10.9486 | 8.9469 | 1.0366 | 0.39146 | 0.00043542 | 0.88873 | 0.88873
2008-04-02 | 0 | 189.3 | 2.56 | 13.87 | 16.83 | 8.09 | 9.69 |  | 6.7896 | 2.1485 | 4.6411 | 22999.5955 | 25.2996 | 655121.7212 | 3.5982 | 5.4925 | 4.6096 | -0.031499 | -0.011895 | -1.3588e-05 | -0.020626
2008-04-02 | 10000 | 192.8 | 2.5 | 13.86 | 17.21 | 7.81 | 10.127 |  | 6.5453 | 2.0952 | 4.4501 | 23518.8971 | 25.8708 | 668961.9549 | 3.7605 | 5.6214 | 4.7111 | 0.26098 | 0.098555 | 0.00011242 | 0.17451 | 0.17451
2008-04-02 | 20000 | 192.9 | 2.52 | 13.86 | 17.16 | 7.79 | 10.07 |  | 6.5286 | 2.1119 | 4.4166 | 23450.568 | 25.7956 | 667018.428 | 3.7393 | 5.6061 | 4.6983 | 0.28164 | 0.10635 | 0.00012132 | 0.18777 | 0.18777
2008-04-02 | 30000 | 193.7 | 2.53 | 13.85 | 17.26 | 7.81 | 10.279 |  | 6.536 | 2.1173 | 4.4187 | 23587.2263 | 25.9459 | 669953.8428 | 3.817 | 5.6973 | 4.768 | 0.34926 | 0.13189 | 0.00015024 | 0.23388 | 0.23388
2008-04-02 | 40000 | 269.3 | 2.54 | 13.67 | 23.02 | 12.08 | 25.346 |  | 9.8578 | 2.0728 | 7.7851 | 31458.7456 | 34.6046 | 871284.9857 | 9.4119 | 10.8023 | 8.8151 | 1.0301 | 0.38898 | 0.00043206 | 0.89708 | 0.89708
2008-04-02 | 50000 | 266.1 | 2.48 | 13.79 | 22.64 | 10.48 | 21.071 |  | 8.6965 | 2.0579 | 6.6385 | 30939.444 | 34.0334 | 871364.836 | 7.8244 | 8.9795 | 7.4513 | 0.81278 | 0.30693 | 0.00034668 | 0.70791 | 0.70791
2008-04-02 | 60000 | 266.5 | 2 | 13.78 | 22.73 | 10.7 | 23.028 |  | 8.8666 | 1.6573 | 7.2093 | 31062.4365 | 34.1687 | 873600.0501 | 8.5511 | 9.7883 | 8.1111 | 0.90186 | 0.34057 | 0.00038413 | 0.78751 | 0.78751
2008-04-02 | 70000 | 267.2 | 4.54 | 10.6 | 22.82 | 10.88 | 24.776 |  | 6.2322 | 2.6006 | 3.6317 | 31185.4289 | 34.304 | 606277.7407 | 9.2002 | 15.1749 | 8.6924 | 5.0608 | 1.9111 | 0.00149 | 3.0668 | 3.0668
2008-04-02 | 80000 | 269.3 | 2.56 | 13.72 | 22.89 | 12.16 | 25.156 |  | 9.9922 | 2.1036 | 7.8886 | 31281.0898 | 34.4092 | 872397.7897 | 9.3413 | 10.7076 | 8.7987 | 0.91016 | 0.3437 | 0.00038442 | 0.79366 | 0.79366
2008-04-02 | 90000 | 268.1 | 2.59 | 13.69 | 22.62 | 12.39 | 25.707 |  | 10.1388 | 2.1194 | 8.0194 | 30912.1123 | 34.0033 | 858520.2513 | 9.5459 | 11.119 | 9.0988 | 1.0794 | 0.4076 | 0.000454 | 0.92624 | 0.92624
2008-04-02 | 100000 | 266.7 | 2.59 | 13.69 | 22.52 | 12.47 | 26.581 |  | 10.2043 | 2.1194 | 8.0849 | 30775.454 | 33.853 | 854724.8479 | 9.8705 | 11.5481 | 9.4499 | 1.365 | 0.51547 | 0.00057415 | 1.1662 | 1.1662
2008-04-02 | 110000 | 264.4 | 2.57 | 13.72 | 22.31 | 12.3 | 26.106 |  | 10.1072 | 2.1118 | 7.9954 | 30488.4715 | 33.5373 | 850292.4722 | 9.6941 | 11.4009 | 9.3684 | 1.373 | 0.51848 | 0.00057991 | 1.1669 | 1.1669
2008-04-02 | 120000 | 263.7 | 2.59 | 13.7 | 22.27 | 12.52 | 26.809 |  | 10.2594 | 2.1224 | 8.1371 | 30433.8082 | 33.4772 | 846410.2788 | 9.9551 | 11.7616 | 9.638 | 1.5009 | 0.56678 | 0.00063216 | 1.2698 | 1.2698
2008-04-02 | 130000 | 189.8 | 1.82 | 13.9 | 16.74 | 8.2 | 11.742 |  | 6.9114 | 1.534 | 5.3774 | 22876.603 | 25.1643 | 654411.0468 | 4.3602 | 6.6628 | 5.6158 | 0.23837 | 0.090014 | 0.00010327 | 0.15592 | 0.15592
2008-04-02 | 140000 | 192.9 | 2.48 | 13.9 | 17 | 7.74 | 9.956 |  | 6.5237 | 2.0903 | 4.4334 | 23231.9146 | 25.5551 | 664575.1371 | 3.697 | 5.563 | 4.6888 | 0.25536 | 0.096431 | 0.00011063 | 0.16963 | 0.16963
2008-04-02 | 150000 | 193.1 | 2.51 | 13.9 | 17 | 7.75 | 9.975 |  | 6.5321 | 2.1156 | 4.4166 | 23231.9146 | 25.5551 | 664575.1371 | 3.7041 | 5.5736 | 4.6977 | 0.28116 | 0.10618 | 0.00012181 | 0.18677 | 0.18677
2008-04-02 | 160000 | 193.7 | 2.5 | 13.89 | 17.09 | 7.75 | 10.032 |  | 6.5228 | 2.1041 | 4.4187 | 23354.9071 | 25.6904 | 667140.4183 | 3.7252 | 5.5839 | 4.6997 | 0.28101 | 0.10612 | 0.00012157 | 0.18739 | 0.18739
2008-04-02 | 170000 | 193.1 | 2.51 | 13.89 | 16.98 | 7.77 | 9.994 |  | 6.5397 | 2.1126 | 4.4271 | 23204.583 | 25.525 | 662846.3606 | 3.7111 | 5.5988 | 4.7122 | 0.28512 | 0.10767 | 0.00012335 | 0.18891 | 0.18891
2008-04-02 | 180000 | 193.1 | 2.51 | 13.89 | 17.04 | 7.77 | 9.994 |  | 6.5397 | 2.1126 | 4.4271 | 23286.578 | 25.6152 | 665188.5739 | 3.7111 | 5.5791 | 4.6956 | 0.26853 | 0.10141 | 0.00011617 | 0.17854 | 0.17854
2008-04-02 | 190000 | 192.3 | 2.5 | 13.87 | 16.99 | 7.69 | 9.728 |  | 6.4539 | 2.0982 | 4.3558 | 23218.2488 | 25.5401 | 661349.854 | 3.6123 | 5.4621 | 4.5841 | 0.22835 | 0.08623 | 9.8504e-05 | 0.15095 | 0.15095
2008-04-02 | 200000 | 192.5 | 2.51 | 13.88 | 17.04 | 7.68 | 9.614 |  | 6.4547 | 2.1095 | 4.3452 | 23286.578 | 25.6152 | 664241.0118 | 3.57 | 5.3746 | 4.5171 | 0.17194 | 0.064929 | 7.4276e-05 | 0.11416 | 0.11416
2008-04-02 | 210000 | 192.7 | 2.49 | 13.88 | 17.14 | 7.63 | 9.519 |  | 6.4127 | 2.0927 | 4.3199 | 23423.2363 | 25.7656 | 668139.1398 | 3.5347 | 5.2904 | 4.4464 | 0.12642 | 0.047741 | 5.4614e-05 | 0.084429 | 0.084429
2008-04-02 | 220000 | 193.2 | 2.52 | 13.87 | 17.15 | 7.57 | 9.253 |  | 6.3532 | 2.1149 | 4.2383 | 23436.9021 | 25.7806 | 667577.9868 | 3.436 | 5.1469 | 4.3196 | 0.08133 | 0.030713 | 3.5084e-05 | 0.05427 | 0.05427
2008-04-02 | 230000 | 193.6 | 2.51 | 13.87 | 17.19 | 7.57 | 9.367 |  | 6.3532 | 2.1065 | 4.2467 | 23491.5654 | 25.8407 | 669135.02 | 3.4783 | 5.1982 | 4.3626 | 0.11598 | 0.043798 | 5.0032e-05 | 0.077572 | 0.077572
2008-04-03 | 0 | 193.3 | 2.52 | 13.87 | 17.16 | 7.59 | 9.329 |  | 6.37 | 2.1149 | 4.255 | 23450.568 | 25.7956 | 667967.2451 | 3.4642 | 5.1862 | 4.3525 | 0.097486 | 0.036814 | 4.2054e-05 | 0.065088 | 0.065088
2008-04-03 | 10000 | 192.5 | 2.52 | 13.87 | 17.16 | 7.62 | 9.329 |  | 6.3952 | 2.1149 | 4.2802 | 23450.568 | 25.7956 | 667967.2451 | 3.4642 | 5.1862 | 4.3525 | 0.072308 | 0.027306 | 3.1193e-05 | 0.048278 | 0.048278
2008-04-03 | 20000 | 192.7 | 2.52 | 13.87 | 17.17 | 7.64 | 9.386 |  | 6.4119 | 2.1149 | 4.297 | 23464.2338 | 25.8107 | 668356.5034 | 3.4853 | 5.2148 | 4.3766 | 0.079567 | 0.030047 | 3.4324e-05 | 0.053155 | 0.053155
2008-04-03 | 30000 | 194.1 | 2.5 | 13.87 | 17.33 | 7.61 | 9.5 |  | 6.3868 | 2.0982 | 4.2886 | 23682.8871 | 26.0512 | 674584.6363 | 3.5277 | 5.2294 | 4.3888 | 0.10022 | 0.037846 | 4.3232e-05 | 0.067575 | 0.067575
2008-04-03 | 40000 | 193.8 | 2.52 | 13.87 | 17.29 | 7.61 | 9.462 |  | 6.3868 | 2.1149 | 4.2718 | 23628.2238 | 25.991 | 673027.6031 | 3.5136 | 5.2205 | 4.3814 | 0.10956 | 0.041374 | 4.7263e-05 | 0.073704 | 0.073704
2008-04-03 | 50000 | 197.7 | 2.5 | 13.87 | 17.6 | 7.73 | 10.469 |  | 6.4875 | 2.0982 | 4.3893 | 24051.8646 | 26.4571 | 685094.6104 | 3.8875 | 5.6744 | 4.7623 | 0.37297 | 0.14085 | 0.00016089 | 0.25541 | 0.25541
2008-04-03 | 60000 | 270.7 | 2.46 | 13.7 | 23.01 | 11.29 | 23.655 |  | 9.2515 | 2.0158 | 7.2357 | 31445.0798 | 34.5896 | 874535.2723 | 8.7839 | 10.0441 | 8.2306 | 0.99489 | 0.3757 | 0.00041905 | 0.86968 | 0.86968
2008-04-03 | 70000 | 271.5 | 4.9 | 10.55 | 23.04 | 11.48 | 25.479 |  | 6.5442 | 2.7932 | 3.7509 | 31486.0773 | 34.6347 | 609165.5477 | 9.4612 | 15.5315 | 8.8537 | 5.1028 | 1.927 | 0.0014951 | 3.107 | 3.107
2008-04-03 | 80000 | 270 | 2.37 | 13.76 | 22.94 | 11.53 | 27.17 |  | 9.5276 | 1.9584 | 7.5692 | 31349.4189 | 34.4844 | 879201.4789 | 10.0892 | 11.4754 | 9.4825 | 1.9133 | 0.72251 | 0.00081263 | 1.6814 | 1.6814
2008-04-03 | 90000 | 269.7 | 2.62 | 13.71 | 22.9 | 11.99 | 26.144 |  | 9.8388 | 2.1499 | 7.6889 | 31294.7556 | 34.4242 | 871565.037 | 9.7082 | 11.1388 | 9.1403 | 1.4514 | 0.54811 | 0.00061219 | 1.2645 | 1.2645
2008-04-03 | 100000 | 268.5 | 2.6 | 13.68 | 22.77 | 12.29 | 27.759 |  | 10.0431 | 2.1247 | 7.9184 | 31117.0998 | 34.2288 | 863016.385 | 10.3079 | 11.944 | 9.7603 | 1.8419 | 0.69557 | 0.00077367 | 1.5889 | 1.5889
2008-04-03 | 110000 | 266.5 | 2.59 | 13.68 | 22.5 | 12.49 | 28.272 |  | 10.2065 | 2.1165 | 8.09 | 30748.1223 | 33.8229 | 852782.9892 | 10.4984 | 12.3107 | 10.06 | 1.97 | 0.74393 | 0.00082745 | 1.6792 | 1.6792
2008-04-03 | 120000 | 264.4 | 2.59 | 13.69 | 22.28 | 12.54 | 28.253 |  | 10.2616 | 2.1194 | 8.1422 | 30447.474 | 33.4922 | 845615.8797 | 10.4913 | 12.4067 | 10.1525 | 2.0104 | 0.75917 | 0.00084558 | 1.6992 | 1.6992
2008-04-03 | 130000 | 262.9 | 2.59 | 13.69 | 22.18 | 12.65 | 28.481 |  | 10.3516 | 2.1194 | 8.2322 | 30310.8157 | 33.3419 | 841820.4763 | 10.576 | 12.5632 | 10.2806 | 2.0484 | 0.77354 | 0.00086159 | 1.7236 | 1.7236
2008-04-03 | 140000 | 260.1 | 2.49 | 13.73 | 21.93 | 12.17 | 27.113 |  | 10.0144 | 2.049 | 7.9654 | 29969.1699 | 32.9661 | 836975.3819 | 10.068 | 12.029 | 9.8984 | 1.933 | 0.72994 | 0.00081756 | 1.6171 | 1.6171
2008-04-03 | 150000 | 260.5 | 2.68 | 13.68 | 21.94 | 12.88 | 28.994 |  | 10.5252 | 2.19 | 8.3352 | 29982.8357 | 32.9811 | 831558.1681 | 10.7665 | 12.9474 | 10.5803 | 2.2451 | 0.84781 | 0.000943 | 1.8661 | 1.8661
2008-04-03 | 160000 | 259.9 | 2.58 | 13.67 | 21.83 | 12.91 | 29.089 |  | 10.5351 | 2.1054 | 8.4297 | 29832.5116 | 32.8158 | 826244.6237 | 10.8018 | 13.0733 | 10.6684 | 2.2387 | 0.84539 | 0.00093901 | 1.8489 | 1.8489
2008-04-03 | 170000 | 259.7 | 2.58 | 13.66 | 21.83 | 12.73 | 28.576 |  | 10.3739 | 2.1025 | 8.2714 | 29832.5116 | 32.8158 | 825103.4018 | 10.6113 | 12.8605 | 10.4803 | 2.2089 | 0.83413 | 0.00092522 | 1.8217 | 1.8217
2008-04-03 | 180000 | 261.1 | 2.58 | 13.64 | 22.02 | 12.5 | 28.006 |  | 10.1584 | 2.0967 | 8.0617 | 30092.1624 | 33.1014 | 829991.9918 | 10.3996 | 12.5298 | 10.1826 | 2.1209 | 0.80091 | 0.00088593 | 1.7595 | 1.7595
2008-04-03 | 190000 | 261.4 | 2.58 | 13.67 | 22.02 | 11.9 | 26.296 |  | 9.7109 | 2.1054 | 7.6055 | 30092.1624 | 33.1014 | 833435.942 | 9.7646 | 11.7161 | 9.5609 | 1.9553 | 0.73839 | 0.00082016 | 1.6289 | 1.6289
2008-04-03 | 200000 | 264.3 | 2.59 | 13.63 | 22.26 | 12.29 | 27.455 |  | 9.974 | 2.1019 | 7.8721 | 30420.1423 | 33.4622 | 837884.1157 | 10.195 | 12.1676 | 9.8746 | 2.0026 | 0.75623 | 0.00083535 | 1.6772 | 1.6772
2008-04-03 | 210000 | 265 | 2.6 | 13.62 | 22.27 | 12.22 | 27.17 |  | 9.9036 | 2.1071 | 7.7964 | 30433.8082 | 33.4772 | 837109.0669 | 10.0892 | 12.0524 | 9.7677 | 1.9713 | 0.74443 | 0.00082119 | 1.6495 | 1.6495
2008-04-03 | 220000 | 264.6 | 2.59 | 13.63 | 22.3 | 12.02 | 26.524 |  | 9.7549 | 2.1019 | 7.653 | 30474.8057 | 33.5223 | 839389.7475 | 9.8493 | 11.7339 | 9.5227 | 1.8697 | 0.70606 | 0.00077993 | 1.5687 | 1.5687
2008-04-03 | 230000 | 266.1 | 2.61 | 13.6 | 22.49 | 12.04 | 26.638 |  | 9.731 | 2.1095 | 7.6215 | 30734.4565 | 33.8079 | 843062.5611 | 9.8916 | 11.733 | 9.4828 | 1.8613 | 0.70288 | 0.00077323 | 1.5685 | 1.5685
2008-04-04 | 0 | 266.1 | 2.61 | 13.59 | 22.53 | 12.03 | 26.467 |  | 9.7096 | 2.1066 | 7.603 | 30789.1198 | 33.868 | 843406.6538 | 9.8281 | 11.6529 | 9.4052 | 1.8022 | 0.68056 | 0.00074766 | 1.5193 | 1.5193
2008-04-04 | 10000 | 266.2 | 2.62 | 13.59 | 22.54 | 12.01 | 26.429 |  | 9.6934 | 2.1146 | 7.5788 | 30802.7856 | 33.8831 | 843781.0021 | 9.814 | 11.631 | 9.3875 | 1.8087 | 0.68303 | 0.00075037 | 1.5255 | 1.5255
2008-04-04 | 20000 | 266.2 | 2.61 | 13.59 | 22.53 | 12.01 | 26.41 |  | 9.6934 | 2.1066 | 7.5869 | 30789.1198 | 33.868 | 843406.6538 | 9.807 | 11.6278 | 9.3849 | 1.7981 | 0.67901 | 0.00074595 | 1.5158 | 1.5158
2008-04-04 | 30000 | 266.3 | 2.61 | 13.59 | 22.53 | 11.99 | 26.41 |  | 9.6773 | 2.1066 | 7.5707 | 30789.1198 | 33.868 | 843406.6538 | 9.807 | 11.6278 | 9.3849 | 1.8142 | 0.68511 | 0.00075265 | 1.5294 | 1.5294
2008-04-04 | 40000 | 266.1 | 2.62 | 13.59 | 22.53 | 11.99 | 26.467 |  | 9.6773 | 2.1146 | 7.5627 | 30789.1198 | 33.868 | 843406.6538 | 9.8281 | 11.6529 | 9.4052 | 1.8425 | 0.6958 | 0.0007644 | 1.5533 | 1.5533
2008-04-04 | 50000 | 266 | 2.61 | 13.58 | 22.48 | 11.97 | 26.448 |  | 9.648 | 2.1037 | 7.5443 | 30720.7907 | 33.7929 | 840385.2746 | 9.8211 | 11.6864 | 9.4194 | 1.8751 | 0.70809 | 0.00077684 | 1.5751 | 1.5751
2008-04-04 | 60000 | 265.7 | 2.55 | 13.71 | 22.31 | 11.88 | 26.163 |  | 9.7485 | 2.0925 | 7.6561 | 30488.4715 | 33.5373 | 849109.8679 | 9.7152 | 11.4417 | 9.3889 | 1.7328 | 0.65436 | 0.00073087 | 1.4707 | 1.4707
2008-04-04 | 70000 | 265.2 | 4.99 | 10.37 | 22.28 | 12 | 25.954 |  | 6.7236 | 2.7959 | 3.9277 | 30447.474 | 33.4922 | 579001.9461 | 9.6376 | 16.6452 | 9.3264 | 5.3987 | 2.0387 | 0.0015548 | 3.1244 | 3.1244
2008-04-04 | 80000 | 263.2 | 2.51 | 13.64 | 22.17 | 11.29 | 24.073 |  | 9.1751 | 2.0398 | 7.1353 | 30297.1499 | 33.3269 | 835645.8882 | 8.9391 | 10.6973 | 8.6934 | 1.5581 | 0.5884 | 0.00065085 | 1.3015 | 1.3015
2008-04-04 | 90000 | 263.9 | 2.58 | 13.62 | 22.3 | 11.45 | 24.377 |  | 9.2795 | 2.0909 | 7.1886 | 30474.8057 | 33.5223 | 838236.7397 | 9.052 | 10.7989 | 8.7519 | 1.5633 | 0.59033 | 0.0006512 | 1.3098 | 1.3098
2008-04-04 | 100000 | 265.3 | 2.57 | 13.58 | 22.3 | 12.07 | 26.657 |  | 9.7286 | 2.0714 | 7.6571 | 30474.8057 | 33.5223 | 833656.211 | 9.8987 | 11.8738 | 9.5704 | 1.9133 | 0.72253 | 0.00079267 | 1.5943 | 1.5943
2008-04-04 | 110000 | 265.3 | 2.63 | 13.59 | 22.28 | 12.17 | 26.277 |  | 9.8226 | 2.1227 | 7.6999 | 30447.474 | 33.4922 | 834047.9471 | 9.7576 | 11.699 | 9.4425 | 1.7426 | 0.65806 | 0.00072293 | 1.4528 | 1.4528
2008-04-04 | 120000 | 264.6 | 2.62 | 13.59 | 22.28 | 12.16 | 26.182 |  | 9.8145 | 2.1146 | 7.6999 | 30447.474 | 33.4922 | 834047.9471 | 9.7223 | 11.6568 | 9.4083 | 1.7085 | 0.64517 | 0.00070877 | 1.4243 | 1.4243
2008-04-04 | 130000 | 265.2 | 2.61 | 13.58 | 22.38 | 12.09 | 25.935 |  | 9.7447 | 2.1037 | 7.641 | 30584.1323 | 33.6425 | 836646.9059 | 9.6306 | 11.5109 | 9.2779 | 1.6369 | 0.61816 | 0.00067817 | 1.3689 | 1.3689
2008-04-04 | 140000 | 264.1 | 2.64 | 13.59 | 22.27 | 12.25 | 26.448 |  | 9.8871 | 2.1308 | 7.7564 | 30433.8082 | 33.4772 | 833673.5988 | 9.8211 | 11.7805 | 9.5082 | 1.7518 | 0.66154 | 0.00072676 | 1.4598 | 1.4598
2008-04-04 | 150000 | 264.7 | 2.59 | 13.6 | 22.32 | 12.3 | 26.733 |  | 9.9411 | 2.0933 | 7.8478 | 30502.1373 | 33.5524 | 836689.9228 | 9.9269 | 11.8645 | 9.5891 | 1.7413 | 0.65757 | 0.00072338 | 1.4563 | 1.4563
2008-04-04 | 160000 | 264.5 | 2.63 | 13.59 | 22.29 | 12.28 | 26.41 |  | 9.9114 | 2.1227 | 7.7886 | 30461.1398 | 33.5073 | 834422.2953 | 9.807 | 11.753 | 9.486 | 1.6973 | 0.64097 | 0.00070416 | 1.4157 | 1.4157
2008-04-04 | 170000 | 264 | 2.61 | 13.59 | 22.26 | 12.36 | 26.638 |  | 9.9759 | 2.1066 | 7.8694 | 30420.1423 | 33.4622 | 833299.2505 | 9.8916 | 11.8704 | 9.5808 | 1.7114 | 0.64629 | 0.00071 | 1.4255 | 1.4255
2008-04-04 | 180000 | 264.5 | 2.6 | 13.59 | 22.27 | 12.27 | 26.353 |  | 9.9033 | 2.0985 | 7.8048 | 30433.8082 | 33.4772 | 833673.5988 | 9.7858 | 11.7382 | 9.474 | 1.6692 | 0.63035 | 0.0006925 | 1.391 | 1.391
2008-04-04 | 190000 | 265.2 | 2.61 | 13.59 | 22.27 | 12.29 | 26.334 |  | 9.9194 | 2.1066 | 7.8129 | 30433.8082 | 33.4772 | 833673.5988 | 9.7787 | 11.7297 | 9.4672 | 1.6543 | 0.62473 | 0.00068631 | 1.3786 | 1.3786
2008-04-04 | 200000 | 265.8 | 2.61 | 13.59 | 22.37 | 12.25 | 26.315 |  | 9.8871 | 2.1066 | 7.7806 | 30570.4665 | 33.6275 | 837417.0815 | 9.7717 | 11.6688 | 9.4181 | 1.6375 | 0.61837 | 0.00067933 | 1.3707 | 1.3707
2008-04-04 | 210000 | 266 | 2.62 | 13.6 | 22.48 | 12.27 | 26.353 |  | 9.9168 | 2.1175 | 7.7993 | 30720.7907 | 33.7929 | 842687.7 | 9.7858 | 11.6126 | 9.3855 | 1.5862 | 0.599 | 0.00065895 | 1.3361 | 1.3361
2008-04-04 | 220000 | 266.3 | 2.6 | 13.61 | 22.53 | 12.27 | 26.372 |  | 9.9305 | 2.1043 | 7.8262 | 30789.1198 | 33.868 | 845720.5267 | 9.7928 | 11.5793 | 9.3714 | 1.5452 | 0.58353 | 0.00064282 | 1.3063 | 1.3063
2008-04-04 | 230000 | 266.8 | 2.61 | 13.61 | 22.53 | 12.26 | 26.334 |  | 9.9224 | 2.1123 | 7.81 | 30789.1198 | 33.868 | 845720.5267 | 9.7787 | 11.5626 | 9.3579 | 1.5479 | 0.58454 | 0.00064393 | 1.3085 | 1.3085
2008-04-05 | 0 | 266.6 | 2.61 | 13.6 | 22.53 | 12.26 | 26.372 |  | 9.9088 | 2.1095 | 7.7993 | 30789.1198 | 33.868 | 844562.0054 | 9.7928 | 11.5952 | 9.3714 | 1.5721 | 0.59368 | 0.0006531 | 1.3272 | 1.3272
2008-04-05 | 10000 | 266.9 | 2.61 | 13.59 | 22.53 | 12.19 | 26.277 |  | 9.8387 | 2.1066 | 7.7321 | 30789.1198 | 33.868 | 843406.6538 | 9.7576 | 11.5692 | 9.3377 | 1.6055 | 0.6063 | 0.00066607 | 1.3535 | 1.3535
2008-04-05 | 20000 | 267 | 2.61 | 13.59 | 22.54 | 12.18 | 26.068 |  | 9.8306 | 2.1066 | 7.7241 | 30802.7856 | 33.8831 | 843781.0021 | 9.68 | 11.4721 | 9.2593 | 1.5352 | 0.57975 | 0.0006369 | 1.2948 | 1.2948
2008-04-05 | 30000 | 267 | 2.62 | 13.59 | 22.53 | 12.11 | 25.992 |  | 9.7741 | 2.1146 | 7.6595 | 30789.1198 | 33.868 | 843406.6538 | 9.6517 | 11.4438 | 9.2364 | 1.5769 | 0.59549 | 0.00065419 | 1.3294 | 1.3294
2008-04-05 | 40000 | 267.6 | 2.62 | 13.58 | 22.53 | 12.09 | 25.897 |  | 9.7447 | 2.1117 | 7.6329 | 30789.1198 | 33.868 | 842254.4589 | 9.6165 | 11.4175 | 9.2026 | 1.5697 | 0.59278 | 0.00065032 | 1.3215 | 1.3215
2008-04-05 | 50000 | 267.9 | 2.62 | 13.58 | 22.54 | 12.01 | 25.84 |  | 9.6802 | 2.1117 | 7.5684 | 30802.7856 | 33.8831 | 842628.2958 | 9.5953 | 11.3873 | 9.1783 | 1.6099 | 0.60794 | 0.00066696 | 1.3559 | 1.3559
2008-04-05 | 60000 | 268 | 2.4 | 14.14 | 22.55 | 12.03 | 25.935 |  | 10.4996 | 2.0947 | 8.4049 | 30816.4515 | 33.8981 | 912836.6289 | 9.6306 | 10.5502 | 9.208 | 0.8031 | 0.30327 | 0.00036028 | 0.73277 | 0.73277
2008-04-05 | 70000 | 267.6 | 5.03 | 9.96 | 22.54 | 12.08 | 27.037 |  | 6.5148 | 2.7127 | 3.8021 | 30802.7856 | 33.8831 | 563806.1358 | 10.0398 | 17.8072 | 9.6035 | 5.8014 | 2.1908 | 0.0016082 | 3.2694 | 3.2694
2008-04-05 | 80000 | 266.6 | 2.6 | 13.58 | 22.52 | 12.11 | 26.391 |  | 9.7608 | 2.0956 | 7.6652 | 30775.454 | 33.853 | 841880.6221 | 9.7999 | 11.6405 | 9.3824 | 1.7172 | 0.64846 | 0.00071142 | 1.445 | 1.445
2008-04-05 | 90000 | 265.6 | 2.62 | 13.57 | 22.37 | 12.17 | 26.068 |  | 9.7958 | 2.1089 | 7.6869 | 30570.4665 | 33.6275 | 835132.1781 | 9.68 | 11.5909 | 9.3297 | 1.6428 | 0.62036 | 0.00067966 | 1.3713 | 1.3713
2008-04-05 | 100000 | 264.4 | 2.63 | 13.58 | 22.27 | 12.23 | 26.41 |  | 9.8575 | 2.1198 | 7.7377 | 30433.8082 | 33.4772 | 832534.7004 | 9.807 | 11.7796 | 9.4945 | 1.7568 | 0.66342 | 0.00072783 | 1.4619 | 1.4619
2008-04-05 | 110000 | 263.4 | 2.62 | 13.57 | 22.26 | 12.28 | 26.448 |  | 9.8843 | 2.1089 | 7.7754 | 30420.1423 | 33.4622 | 831025.5827 | 9.8211 | 11.818 | 9.5124 | 1.737 | 0.65595 | 0.00071865 | 1.4428 | 1.4428
2008-04-05 | 120000 | 262.7 | 2.63 | 13.57 | 22.16 | 12.18 | 25.935 |  | 9.8038 | 2.1169 | 7.6869 | 30283.484 | 33.3118 | 827292.3141 | 9.6306 | 11.6411 | 9.37 | 1.6831 | 0.6356 | 0.00069636 | 1.3918 | 1.3918
2008-04-05 | 130000 | 262.5 | 2.63 | 13.56 | 22.13 | 12.2 | 25.973 |  | 9.8065 | 2.114 | 7.6925 | 30242.4865 | 33.2667 | 825046.7582 | 9.6447 | 11.6899 | 9.3965 | 1.704 | 0.64347 | 0.00070402 | 1.4052 | 1.4052
2008-04-05 | 140000 | 262.7 | 2.63 | 13.55 | 22.18 | 12.29 | 26.41 |  | 9.8654 | 2.1112 | 7.7543 | 30310.8157 | 33.3419 | 825785.8006 | 9.807 | 11.8759 | 9.533 | 1.7788 | 0.67171 | 0.00073392 | 1.4682 | 1.4682
2008-04-05 | 150000 | 264.3 | 2.7 | 13.44 | 22.97 | 12.33 | 25.878 |  | 9.7516 | 2.1354 | 7.6162 | 31390.4164 | 34.5295 | 842588.2061 | 9.6094 | 11.4046 | 9.0197 | 1.4035 | 0.53001 | 0.00057056 | 1.1821 | 1.1821
2008-04-05 | 160000 | 295.2 | 3.18 | 12.29 | 25.03 | 15.1 | 32.11 |  | 10.3473 | 2.1791 | 8.1682 | 34205.5778 | 37.6261 | 795519.6404 | 11.9236 | 14.9884 | 10.2708 | 2.1026 | 0.79401 | 0.00074058 | 1.6719 | 1.6719
2008-04-05 | 170000 | 295.4 | 3.07 | 12.32 | 24.94 | 14.92 | 32.205 |  | 10.2597 | 2.1111 | 8.1486 | 34082.5854 | 37.4908 | 795430.7379 | 11.9588 | 15.0344 | 10.3384 | 2.1898 | 0.82692 | 0.00077397 | 1.741 | 1.741
2008-04-05 | 180000 | 294.5 | 3.06 | 12.35 | 24.81 | 14.81 | 31.996 |  | 10.2198 | 2.1116 | 8.1082 | 33904.9295 | 37.2954 | 794060.9842 | 11.8812 | 14.9626 | 10.3251 | 2.2169 | 0.83717 | 0.00078632 | 1.7596 | 1.7596
2008-04-05 | 190000 | 296 | 2.95 | 12.29 | 24.94 | 14.94 | 32.984 |  | 10.2376 | 2.0215 | 8.2161 | 34082.5854 | 37.4908 | 792659.2022 | 12.2481 | 15.4519 | 10.5884 | 2.3723 | 0.89585 | 0.00083557 | 1.8796 | 1.8796
2008-04-05 | 200000 | 296.7 | 2.94 | 12.29 | 24.96 | 14.86 | 32.832 |  | 10.1828 | 2.0146 | 8.1682 | 34109.917 | 37.5209 | 793294.8552 | 12.1917 | 15.3684 | 10.5312 | 2.363 | 0.89234 | 0.0008323 | 1.8737 | 1.8737
2008-04-05 | 210000 | 296.4 | 2.96 | 12.28 | 24.94 | 14.87 | 32.813 |  | 10.1778 | 2.026 | 8.1519 | 34082.5854 | 37.4908 | 791739.644 | 12.1846 | 15.3897 | 10.5335 | 2.3817 | 0.89939 | 0.0008379 | 1.8848 | 1.8848
2008-04-05 | 220000 | 294.3 | 2.9 | 12.31 | 24.94 | 14.89 | 33.326 |  | 10.2271 | 1.9919 | 8.2353 | 34082.5854 | 37.4908 | 794504.7417 | 12.3751 | 15.5759 | 10.6982 | 2.4629 | 0.93008 | 0.00086952 | 1.9559 | 1.9559
2008-04-05 | 230000 | 265.4 | 2.47 | 13.44 | 22.06 | 12.09 | 26.429 |  | 9.5618 | 1.9535 | 7.6083 | 30146.8257 | 33.1615 | 809207.4804 | 9.814 | 12.1279 | 9.5918 | 1.9835 | 0.74902 | 0.00080632 | 1.6043 | 1.6043
2008-04-06 | 0 | 262.6 | 2.6 | 13.48 | 22.06 | 12.07 | 25.916 |  | 9.5974 | 2.0674 | 7.5301 | 30146.8257 | 33.1615 | 813569.7849 | 9.6235 | 11.8288 | 9.4056 | 1.8756 | 0.70827 | 0.00076656 | 1.5252 | 1.5252
2008-04-06 | 10000 | 262.6 | 2.59 | 13.48 | 22.08 | 12.06 | 26.011 |  | 9.5895 | 2.0594 | 7.5301 | 30174.1574 | 33.1916 | 814307.3822 | 9.6588 | 11.8614 | 9.4315 | 1.9015 | 0.71806 | 0.00077715 | 1.5477 | 1.5477
2008-04-06 | 20000 | 262.6 | 2.59 | 13.48 | 22.11 | 12.07 | 26.011 |  | 9.5974 | 2.0594 | 7.538 | 30215.1549 | 33.2367 | 815413.7781 | 9.6588 | 11.8453 | 9.4187 | 1.8807 | 0.71022 | 0.00076867 | 1.5329 | 1.5329
2008-04-06 | 30000 | 262.7 | 2.59 | 13.49 | 22.16 | 12.05 | 25.973 |  | 9.5945 | 2.0622 | 7.5323 | 30283.484 | 33.3118 | 818360.6832 | 9.6447 | 11.7854 | 9.3838 | 1.8515 | 0.69919 | 0.00075775 | 1.5145 | 1.5145
2008-04-06 | 40000 | 263.1 | 2.58 | 13.5 | 22.24 | 12.07 | 26.068 |  | 9.6234 | 2.057 | 7.5664 | 30392.8107 | 33.4321 | 822424.9391 | 9.68 | 11.77 | 9.3842 | 1.8179 | 0.68648 | 0.00074498 | 1.4944 | 1.4944
2008-04-06 | 50000 | 263.5 | 2.59 | 13.5 | 22.27 | 12.05 | 25.935 |  | 9.6074 | 2.065 | 7.5424 | 30433.8082 | 33.4772 | 823534.3253 | 9.6306 | 11.6942 | 9.3237 | 1.7813 | 0.67268 | 0.00073001 | 1.4663 | 1.4663
2008-04-06 | 60000 | 120.4 | 1.42 | 17.18 | 10.09 | 6.22 | 12.16 |  | 9.8651 | 2.2522 | 7.6129 | 13788.8246 | 15.1677 | 742235.0084 | 4.5154 | 6.0836 | 9.6487 | 2.0358 | 0.76876 | 0.0016596 | 1.5103 | 1.5103
2008-04-06 | 70000 | 1.3 | 0 | 20.62 | 0.04 | -0.01 | 0.171 |  | -0.21071 | 0 | -0.21071 | 54.6633 | 0.06013 | 39092.6551 | 0.063498 | 1.6243 | 34.2264 | 34.4371 | 13.0045 | 0.37298 | 1.3456
2008-04-06 | 80000 | 2.9 | 1.73 | 19.97 | 1.15 | 5.37 | 0.171 |  | 34.0677 | 10.9753 | 23.0925 | 1571.5707 | 1.7287 | 338382.6599 | 0.063498 | 0.18765 | 1.1905 | -21.902 | -8.2709 | -0.07142 | -7.4079
2008-04-06 | 90000 | 64.1 | 9.98 | 15.1 | 10.29 | 26.23 | 10.811 |  | 26.6822 | 10.1521 | 16.5302 | 14062.1413 | 15.4684 | 485490.3359 | 4.0145 | 8.269 | 8.4115 | -8.1186 | -3.0658 | -0.004245 | -3.9397
2008-04-06 | 100000 | 241.5 | 4.52 | 10.76 | 20.65 | 9.15 | 18.354 |  | 5.324 | 2.63 | 2.694 | 28219.9434 | 31.0419 | 557282.3765 | 6.8155 | 12.2299 | 7.116 | 4.422 | 1.6699 | 0.0013225 | 2.4632 | 2.4632
2008-04-06 | 110000 | 262.2 | 3.06 | 13.41 | 22.14 | 12.3 | 26.448 |  | 9.6889 | 2.4104 | 7.2785 | 30256.1524 | 33.2818 | 808889.1443 | 9.8211 | 12.1414 | 9.564 | 2.2855 | 0.86307 | 0.00092537 | 1.8479 | 1.8479
2008-04-06 | 120000 | 263.8 | 2.56 | 13.55 | 22.18 | 12.37 | 27.512 |  | 9.9297 | 2.055 | 7.8747 | 30310.8157 | 33.3419 | 825785.8006 | 10.2162 | 12.3714 | 9.9308 | 2.0561 | 0.77646 | 0.00084836 | 1.6972 | 1.6972
2008-04-06 | 130000 | 263.5 | 2.57 | 13.54 | 22.13 | 12.39 | 27.493 |  | 9.9322 | 2.0602 | 7.872 | 30242.4865 | 33.2667 | 822804.7833 | 10.2091 | 12.4077 | 9.9464 | 2.0744 | 0.78335 | 0.00085473 | 1.706 | 1.706
2008-04-06 | 140000 | 189.9 | 2.53 | 13.72 | 16.68 | 8.62 | 11.913 |  | 7.0833 | 2.079 | 5.0043 | 22794.608 | 25.0741 | 635718.4418 | 4.4237 | 6.9586 | 5.7181 | 0.71376 | 0.26954 | 0.00030147 | 0.45354 | 0.45354
2008-04-06 | 150000 | 193 | 2.46 | 13.75 | 16.98 | 7.51 | 10.488 |  | 6.1971 | 2.0299 | 4.1671 | 23204.583 | 25.525 | 649867.5508 | 3.8946 | 5.9929 | 4.9452 | 0.77802 | 0.2938 | 0.00032999 | 0.50538 | 0.50538
2008-04-06 | 160000 | 192.7 | 2.51 | 13.77 | 16.92 | 7.58 | 10.469 |  | 6.2724 | 2.077 | 4.1954 | 23122.588 | 25.4348 | 649387.668 | 3.8875 | 5.9864 | 4.9537 | 0.75833 | 0.28637 | 0.00032254 | 0.49223 | 0.49223
2008-04-06 | 170000 | 192.5 | 2.52 | 13.77 | 16.96 | 7.63 | 10.507 |  | 6.3137 | 2.0853 | 4.2285 | 23177.2513 | 25.495 | 650922.8634 | 3.9016 | 5.994 | 4.96 | 0.73148 | 0.27623 | 0.00031112 | 0.47592 | 0.47592
2008-04-06 | 180000 | 197.8 | 2.57 | 13.76 | 17.33 | 7.84 | 11.78 |  | 6.4784 | 2.1237 | 4.3548 | 23682.8871 | 26.0512 | 664191.8758 | 4.3743 | 6.5859 | 5.4422 | 1.0874 | 0.41063 | 0.00046186 | 0.72192 | 0.72192
2008-04-06 | 190000 | 264.9 | 2.59 | 13.57 | 22.28 | 12.24 | 27.246 |  | 9.8521 | 2.0847 | 7.7674 | 30447.474 | 33.4922 | 831772.2364 | 10.1174 | 12.1637 | 9.7907 | 2.0233 | 0.76405 | 0.00083708 | 1.6821 | 1.6821
2008-04-06 | 200000 | 264.5 | 2.6 | 13.61 | 22.3 | 11.8 | 25.745 |  | 9.5501 | 2.1043 | 7.4458 | 30474.8057 | 33.5223 | 837086.895 | 9.56 | 11.4206 | 9.243 | 1.7972 | 0.67867 | 0.00074762 | 1.5037 | 1.5037
2008-04-06 | 210000 | 266.6 | 2.62 | 13.59 | 22.5 | 12.2 | 26.885 |  | 9.8468 | 2.1146 | 7.7321 | 30748.1223 | 33.8229 | 842283.609 | 9.9833 | 11.8527 | 9.5665 | 1.8343 | 0.6927 | 0.00076099 | 1.5443 | 1.5443
2008-04-06 | 220000 | 265.7 | 2.58 | 13.6 | 22.43 | 12.13 | 26.771 |  | 9.8037 | 2.0852 | 7.7185 | 30652.4615 | 33.7177 | 840813.3946 | 9.941 | 11.8231 | 9.5556 | 1.8371 | 0.69376 | 0.0007632 | 1.544 | 1.544
2008-04-06 | 230000 | 24.8 | 1.86 | 19.18 | 2.56 | 5.71 | 1.729 |  | 19.5866 | 6.3802 | 13.2064 | 3498.453 | 3.8483 | 407290.9185 | 0.64204 | 1.5764 | 5.4073 | -7.7991 | -2.9452 | -0.013751 | -3.1751
2008-04-07 | 0 | 1.3 | 0.01 | 20.66 | 0.04 | 0.03 | 0.171 |  | 0.7375 | 0.24583 | 0.49167 | 54.6633 | 0.06013 | 45608.0976 | 0.063498 | 1.3923 | 34.2264 | 33.7347 | 12.7392 | 0.42627 | 1.5379
2008-04-07 | 10000 | 1.3 | 0.01 | 20.75 | 0.04 | -0.03 | 0.152 |  | -1.18 | 0.39333 | -1.5733 | 54.6633 | 0.06013 | 72972.9562 | 0.056443 | 0.77348 | 30.4234 | 31.9968 | 12.083 | 0.64689 | 2.3338
2008-04-07 | 20000 | 1.3 | 0.02 | 20.75 | 0.04 | -0.03 | 0.171 |  | -1.18 | 0.78667 | -1.9667 | 54.6633 | 0.06013 | 72972.9562 | 0.063498 | 0.87016 | 34.2264 | 36.193 | 13.6676 | 0.73173 | 2.6399
2008-04-07 | 30000 | 1.3 | 0.01 | 20.75 | 0.04 | -0.03 | 0.19 |  | -1.18 | 0.39333 | -1.5733 | 54.6633 | 0.06013 | 72972.9562 | 0.070554 | 0.96685 | 38.0293 | 39.6026 | 14.9552 | 0.80066 | 2.8886
2008-04-07 | 40000 | 1.3 | 0 | 20.74 | 0.16 | -0.05 | 0.19 |  | -1.8438 | 0 | -1.8438 | 218.6533 | 0.24052 | 273648.5859 | 0.070554 | 0.25783 | 9.5073 | 11.3511 | 4.2865 | 0.21515 | 3.1048
2008-04-07 | 50000 | 1.3 | 0.01 | 20.74 | 0.35 | -0.06 | 0.171 |  | -2.2125 | 0.36875 | -2.5812 | 478.3041 | 0.52613 | 598606.2816 | 0.063498 | 0.10608 | 3.9116 | 6.4928 | 2.4519 | 0.12306 | 3.8849
2008-04-07 | 60000 | 1.3 | 0 | 20.75 | 0.26 | -0.06 | 0.171 |  | -2.36 | 0 | -2.36 | 355.3116 | 0.39084 | 474324.2155 | 0.063498 | 0.13387 | 5.2656 | 7.6256 | 2.8797 | 0.15417 | 3.6154
2008-04-07 | 70000 | 1.3 | 0.02 | 20.76 | 0.26 | -0.06 | 0.171 |  | -2.5286 | 0.84286 | -3.3714 | 355.3116 | 0.39084 | 508204.5166 | 0.063498 | 0.12495 | 5.2656 | 8.637 | 3.2616 | 0.18709 | 4.3874
2008-04-07 | 80000 | 9.1 | 6.11 | 18.53 | 4.05 | 17.93 | 0.152 |  | 44.6359 | 15.2105 | 29.4253 | 5534.662 | 6.0881 | 467627.3303 | 0.056443 | 0.1207 | 0.30048 | -29.1248 | -10.9984 | -0.037268 | -13.6134
2008-04-07 | 90000 | 27.7 | 10.26 | 16.38 | 7.88 | 27.22 | 7.657 |  | 35.5305 | 13.3925 | 22.1381 | 10768.6757 | 11.8455 | 477068.7736 | 2.8433 | 5.96 | 7.7796 | -14.3585 | -5.4222 | -0.0096336 | -6.8469
2008-04-07 | 100000 | 141.2 | 6.59 | 14.61 | 14.63 | 21.45 | 19.646 |  | 20.12 | 6.1814 | 13.9386 | 19993.1124 | 21.9924 | 636483.1178 | 7.2952 | 11.4618 | 10.7511 | -3.1875 | -1.2037 | -0.0015368 | -2.0279
2008-04-07 | 110000 | 264.8 | 2.59 | 13.64 | 22.44 | 12.72 | 26.79 |  | 10.3372 | 2.1048 | 8.2324 | 30666.1273 | 33.7327 | 845822.9017 | 9.9481 | 11.7614 | 9.5582 | 1.3258 | 0.50066 | 0.00055381 | 1.1209 | 1.1209
2008-04-07 | 120000 | 265.5 | 3.14 | 12.11 | 22.28 | 12.57 | 34.295 |  | 8.4372 | 2.1076 | 6.3296 | 30447.474 | 33.4922 | 693616.6659 | 12.7349 | 18.3602 | 12.3237 | 5.9941 | 2.2636 | 0.002068 | 4.1557 | 4.1557
2008-04-07 | 130000 | 265.1 | 2.65 | 13.69 | 22.29 | 12.59 | 26.714 |  | 10.3025 | 2.1685 | 8.134 | 30461.1398 | 33.5073 | 845995.4201 | 9.9198 | 11.7256 | 9.5952 | 1.4612 | 0.5518 | 0.0006146 | 1.2356 | 1.2356
2008-04-07 | 140000 | 265.1 | 2.58 | 13.68 | 22.27 | 12.68 | 27.493 |  | 10.3618 | 2.1083 | 8.2535 | 30433.8082 | 33.4772 | 844065.652 | 10.2091 | 12.0952 | 9.8839 | 1.6304 | 0.61569 | 0.00068482 | 1.3755 | 1.3755
2008-04-07 | 150000 | 265.9 | 2.57 | 13.68 | 22.3 | 12.6 | 27.284 |  | 10.2964 | 2.1001 | 8.1963 | 30474.8057 | 33.5223 | 845202.6959 | 10.1315 | 11.9871 | 9.7955 | 1.5993 | 0.60393 | 0.00067174 | 1.3511 | 1.3511
2008-04-07 | 160000 | 265.4 | 2.59 | 13.68 | 22.27 | 12.63 | 27.322 |  | 10.3209 | 2.1165 | 8.2044 | 30433.8082 | 33.4772 | 844065.652 | 10.1456 | 12.0199 | 9.8224 | 1.618 | 0.61099 | 0.00067959 | 1.365 | 1.365
2008-04-07 | 170000 | 266.4 | 2.58 | 13.68 | 22.38 | 12.6 | 27.265 |  | 10.2964 | 2.1083 | 8.1881 | 30584.1323 | 33.6425 | 848234.8132 | 10.1244 | 11.9359 | 9.7537 | 1.5656 | 0.59123 | 0.00065761 | 1.3274 | 1.3274
2008-04-07 | 180000 | 266.3 | 2.58 | 13.68 | 22.37 | 12.63 | 27.303 |  | 10.3209 | 2.1083 | 8.2126 | 30570.4665 | 33.6275 | 847855.7986 | 10.1386 | 11.9579 | 9.7717 | 1.5591 | 0.58875 | 0.00065486 | 1.3213 | 1.3213
2008-04-07 | 190000 | 266.3 | 2.58 | 13.68 | 22.5 | 12.61 | 27.341 |  | 10.3046 | 2.1083 | 8.1963 | 30748.1223 | 33.8229 | 852782.9892 | 10.1527 | 11.9053 | 9.7287 | 1.5325 | 0.57871 | 0.00064369 | 1.3063 | 1.3063
2008-04-07 | 200000 | 266.9 | 2.58 | 13.68 | 22.54 | 12.52 | 27.094 |  | 10.231 | 2.1083 | 8.1227 | 30802.7856 | 33.8831 | 854299.0478 | 10.0609 | 11.7768 | 9.6237 | 1.501 | 0.56683 | 0.00063048 | 1.2817 | 1.2817
2008-04-07 | 210000 | 265.8 | 2.53 | 13.71 | 22.43 | 12.08 | 26.011 |  | 9.9127 | 2.0761 | 7.8366 | 30652.4615 | 33.7177 | 853677.021 | 9.6588 | 11.3143 | 9.2844 | 1.4478 | 0.54673 | 0.00061065 | 1.2354 | 1.2354
2008-04-07 | 220000 | 266 | 2.6 | 13.71 | 22.39 | 12.04 | 25.916 |  | 9.8798 | 2.1335 | 7.7463 | 30597.7982 | 33.6576 | 852154.6366 | 9.6235 | 11.2932 | 9.267 | 1.5207 | 0.57425 | 0.00064139 | 1.2953 | 1.2953
2008-04-07 | 230000 | 267.5 | 2.58 | 13.67 | 22.53 | 12.38 | 26.847 |  | 10.1026 | 2.1054 | 7.9972 | 30789.1198 | 33.868 | 852738.9543 | 9.9692 | 11.6908 | 9.5402 | 1.543 | 0.58268 | 0.00064721 | 1.3152 | 1.3152
2008-04-08 | 0 | 267.4 | 2.59 | 13.66 | 22.53 | 11.03 | 26.733 |  | 8.9885 | 2.1106 | 6.8779 | 30789.1198 | 33.868 | 851561.138 | 9.9269 | 11.6573 | 9.4997 | 2.6218 | 0.99008 | 0.0010982 | 2.2316 | 2.2316
2008-04-08 | 10000 | 267.2 | 2.6 | 13.65 | 22.53 | 9.78 | 26.676 |  | 7.9589 | 2.1159 | 5.843 | 30789.1198 | 33.868 | 850386.571 | 9.9057 | 11.6485 | 9.4795 | 3.6364 | 1.3732 | 0.0015211 | 3.091 | 3.091
2008-04-08 | 20000 | 267.3 | 2.59 | 13.64 | 22.53 | 9.75 | 26.562 |  | 7.9236 | 2.1048 | 5.8187 | 30789.1198 | 33.868 | 849215.2396 | 9.8634 | 11.6147 | 9.439 | 3.6202 | 1.3671 | 0.0015122 | 3.073 | 3.073
2008-04-08 | 30000 | 267.2 | 2.6 | 13.64 | 22.53 | 9.79 | 26.524 |  | 7.9561 | 2.1129 | 5.8431 | 30789.1198 | 33.868 | 849215.2396 | 9.8493 | 11.5981 | 9.4255 | 3.5823 | 1.3528 | 0.0014964 | 3.0408 | 3.0408
2008-04-08 | 40000 | 267.3 | 2.6 | 13.64 | 22.53 | 9.79 | 26.505 |  | 7.9561 | 2.1129 | 5.8431 | 30789.1198 | 33.868 | 849215.2396 | 9.8422 | 11.5898 | 9.4187 | 3.5756 | 1.3503 | 0.0014936 | 3.0351 | 3.0351
2008-04-08 | 50000 | 267.6 | 2.6 | 13.63 | 22.54 | 9.77 | 26.429 |  | 7.9289 | 2.11 | 5.8188 | 30802.7856 | 33.8831 | 848423.5386 | 9.814 | 11.5673 | 9.3875 | 3.5687 | 1.3476 | 0.0014886 | 3.0264 | 3.0264
2008-04-08 | 60000 | 268 | 2.6 | 13.63 | 22.56 | 9.8 | 26.315 |  | 7.9532 | 2.11 | 5.8432 | 30830.1173 | 33.9131 | 849176.3545 | 9.7717 | 11.5072 | 9.3388 | 3.4956 | 1.32 | 0.0014581 | 2.967 | 2.967
2008-04-08 | 70000 | 268 | 2.6 | 13.63 | 22.55 | 9.78 | 26.353 |  | 7.937 | 2.11 | 5.827 | 30816.4515 | 33.8981 | 848799.9465 | 9.7858 | 11.529 | 9.3564 | 3.5294 | 1.3328 | 0.0014723 | 2.9944 | 2.9944
2008-04-08 | 80000 | 267.1 | 2.59 | 13.63 | 22.49 | 9.74 | 26.334 |  | 7.9045 | 2.1019 | 5.8026 | 30734.4565 | 33.8079 | 846541.4988 | 9.7787 | 11.5514 | 9.3746 | 3.572 | 1.3489 | 0.00149 | 3.0225 | 3.0225
2008-04-08 | 90000 | 190.9 | 3.47 | 12.32 | 16.88 | 10.34 | 10.127 |  | 7.1103 | 2.3861 | 4.7241 | 23067.9247 | 25.3747 | 538366.9148 | 3.7605 | 6.985 | 4.8032 | 0.079099 | 0.02987 | 2.7958e-05 | 0.042565 | 0.042565
2008-04-08 | 100000 | 265.7 | 2.92 | 13.54 | 22.52 | 12.37 | 26.676 |  | 9.9162 | 2.3408 | 7.5754 | 30775.454 | 33.853 | 837305.1839 | 9.9057 | 11.8305 | 9.4837 | 1.9083 | 0.72062 | 0.00078629 | 1.5971 | 1.5971
2008-04-08 | 110000 | 266.1 | 2.6 | 13.62 | 22.52 | 12.45 | 27.227 |  | 10.09 | 2.1071 | 7.9828 | 30775.454 | 33.853 | 846506.3398 | 10.1103 | 11.9436 | 9.6796 | 1.6967 | 0.64074 | 0.00070681 | 1.4357 | 1.4357
2008-04-08 | 120000 | 265.5 | 2.61 | 13.61 | 22.38 | 12.46 | 27.113 |  | 10.0842 | 2.1123 | 7.9719 | 30584.1323 | 33.6425 | 840089.8973 | 10.068 | 11.9844 | 9.6993 | 1.7275 | 0.65234 | 0.00071862 | 1.4506 | 1.4506
2008-04-08 | 130000 | 264.5 | 2.62 | 13.61 | 22.28 | 12.53 | 27.246 |  | 10.1409 | 2.1204 | 8.0204 | 30447.474 | 33.4922 | 836336.1444 | 10.1174 | 12.0973 | 9.7907 | 1.7702 | 0.66849 | 0.00073641 | 1.4798 | 1.4798
2008-04-08 | 140000 | 264.8 | 2.59 | 13.6 | 22.35 | 12.46 | 27.018 |  | 10.0704 | 2.0933 | 7.9771 | 30543.1348 | 33.5974 | 837814.506 | 10.0327 | 11.9749 | 9.6783 | 1.7012 | 0.64243 | 0.00070673 | 1.4247 | 1.4247
2008-04-08 | 150000 | 264.8 | 2.63 | 13.6 | 22.31 | 12.34 | 26.524 |  | 9.9734 | 2.1256 | 7.8478 | 30488.4715 | 33.5373 | 836315.0617 | 9.8493 | 11.777 | 9.5184 | 1.6706 | 0.63087 | 0.00069401 | 1.3965 | 1.3965
2008-04-08 | 160000 | 263.5 | 2.59 | 13.6 | 22.21 | 12.44 | 26.828 |  | 10.0542 | 2.0933 | 7.961 | 30351.8132 | 33.387 | 832566.451 | 9.9622 | 11.9656 | 9.6708 | 1.7099 | 0.6457 | 0.00071033 | 1.423 | 1.423
2008-04-08 | 170000 | 191.1 | 2.59 | 13.79 | 16.88 | 7.66 | 9.88 |  | 6.3564 | 2.1492 | 4.2072 | 23067.9247 | 25.3747 | 649674.8424 | 3.6688 | 5.6471 | 4.6861 | 0.4789 | 0.18085 | 0.00020426 | 0.31099 | 0.31099
2008-04-08 | 180000 | 196.2 | 2.54 | 13.79 | 17.35 | 7.7 | 11.305 |  | 6.3896 | 2.1077 | 4.2819 | 23710.2188 | 26.0812 | 667764.1301 | 4.1979 | 6.2866 | 5.2167 | 0.93484 | 0.35302 | 0.00039874 | 0.62397 | 0.62397
2008-04-08 | 190000 | 264.2 | 2.58 | 13.59 | 22.28 | 12.42 | 26.961 |  | 10.0244 | 2.0824 | 7.942 | 30447.474 | 33.4922 | 834047.9471 | 10.0116 | 12.0036 | 9.6883 | 1.7463 | 0.65944 | 0.00072445 | 1.4558 | 1.4558
2008-04-08 | 200000 | 265.6 | 2.6 | 13.6 | 22.35 | 12.35 | 26.581 |  | 9.9815 | 2.1014 | 7.8801 | 30543.1348 | 33.5974 | 837814.506 | 9.8705 | 11.7812 | 9.5218 | 1.6416 | 0.61994 | 0.00068199 | 1.3748 | 1.3748
2008-04-08 | 210000 | 263.7 | 2.59 | 13.66 | 22.31 | 11.64 | 24.681 |  | 9.4856 | 2.1106 | 7.375 | 30488.4715 | 33.5373 | 843245.8495 | 9.1649 | 10.8686 | 8.857 | 1.482 | 0.55966 | 0.00062077 | 1.2491 | 1.2491
2008-04-08 | 220000 | 266.1 | 2.6 | 13.61 | 22.51 | 12.3 | 26.467 |  | 9.9547 | 2.1043 | 7.8505 | 30761.7881 | 33.838 | 844969.7761 | 9.8281 | 11.6313 | 9.4136 | 1.5631 | 0.59027 | 0.00065024 | 1.3202 | 1.3202
2008-04-08 | 230000 | 266.8 | 2.61 | 13.61 | 22.54 | 12.28 | 26.448 |  | 9.9385 | 2.1123 | 7.8262 | 30802.7856 | 33.8831 | 846095.902 | 9.8211 | 11.6075 | 9.3943 | 1.5681 | 0.59215 | 0.00065232 | 1.3261 | 1.3261
2008-04-09 | 0 | 266.9 | 2.61 | 13.61 | 22.54 | 12.22 | 26.315 |  | 9.89 | 2.1123 | 7.7776 | 30802.7856 | 33.8831 | 846095.902 | 9.7717 | 11.5491 | 9.347 | 1.5694 | 0.59265 | 0.00065286 | 1.3273 | 1.3273
2008-04-09 | 10000 | 267 | 2.61 | 13.6 | 22.54 | 12.23 | 26.315 |  | 9.8845 | 2.1095 | 7.7751 | 30802.7856 | 33.8831 | 844936.8665 | 9.7717 | 11.565 | 9.347 | 1.572 | 0.59362 | 0.00065304 | 1.3276 | 1.3276
2008-04-09 | 20000 | 267.4 | 2.61 | 13.6 | 22.54 | 12.21 | 26.258 |  | 9.8684 | 2.1095 | 7.7589 | 30802.7856 | 33.8831 | 844936.8665 | 9.7505 | 11.5399 | 9.3268 | 1.5679 | 0.59208 | 0.00065134 | 1.3242 | 1.3242
2008-04-09 | 30000 | 265.2 | 2.51 | 13.62 | 22.31 | 11.94 | 25.384 |  | 9.6766 | 2.0342 | 7.6424 | 30488.4715 | 33.5373 | 838612.6306 | 9.426 | 11.24 | 9.1093 | 1.4669 | 0.55393 | 0.00061105 | 1.2296 | 1.2296
2008-04-09 | 40000 | 196.1 | 2.66 | 13.81 | 17.33 | 7.73 | 10.773 |  | 6.4326 | 2.2135 | 4.219 | 23682.8871 | 26.0512 | 668875.8805 | 4.0004 | 5.9808 | 4.9769 | 0.7579 | 0.28621 | 0.00032418 | 0.50671 | 0.50671
2008-04-09 | 50000 | 266.8 | 2.55 | 13.61 | 22.5 | 12.16 | 26.372 |  | 9.8414 | 2.0638 | 7.7776 | 30748.1223 | 33.8229 | 844594.4008 | 9.7928 | 11.5947 | 9.3839 | 1.6063 | 0.60659 | 0.00066821 | 1.3561 | 1.3561
2008-04-09 | 60000 | 190.2 | 2.63 | 13.81 | 16.83 | 7.86 | 10.032 |  | 6.5408 | 2.1886 | 4.3522 | 22999.5955 | 25.2996 | 649577.6728 | 3.7252 | 5.7349 | 4.7723 | 0.42012 | 0.15865 | 0.0001797 | 0.27278 | 0.27278
2008-04-09 | 70000 | 255.9 | 2.56 | 13.65 | 21.77 | 11.59 | 24.833 |  | 9.4319 | 2.0833 | 7.3486 | 29750.5166 | 32.7256 | 821700.6502 | 9.2214 | 11.2223 | 9.1326 | 1.7841 | 0.67372 | 0.00074626 | 1.4653 | 1.4653
2008-04-09 | 80000 | 268 | 2.59 | 13.62 | 22.59 | 12.3 | 26.372 |  | 9.9684 | 2.099 | 7.8694 | 30871.1148 | 33.9582 | 849137.5762 | 9.7928 | 11.5327 | 9.3466 | 1.4772 | 0.55783 | 0.00061535 | 1.2538 | 1.2538
2008-04-09 | 90000 | 267.3 | 3.48 | 12.1 | 22.54 | 12.29 | 27.246 |  | 8.2399 | 2.3332 | 5.9067 | 30802.7856 | 33.8831 | 700913.537 | 10.1174 | 14.4346 | 9.6777 | 3.771 | 1.4241 | 0.0012996 | 2.642 | 2.642
2008-04-09 | 100000 | 266.6 | 2.61 | 13.63 | 22.53 | 12.35 | 26.6 |  | 10.0227 | 2.1182 | 7.9045 | 30789.1198 | 33.868 | 848047.1306 | 9.8775 | 11.6474 | 9.4525 | 1.5479 | 0.58454 | 0.0006457 | 1.3121 | 1.3121
2008-04-09 | 110000 | 265.7 | 2.59 | 13.63 | 22.45 | 12.39 | 26.543 |  | 10.0552 | 2.1019 | 7.9532 | 30679.7932 | 33.7478 | 845035.8669 | 9.8563 | 11.6638 | 9.4658 | 1.5126 | 0.5712 | 0.00063096 | 1.2776 | 1.2776
2008-04-09 | 120000 | 264.7 | 2.61 | 13.63 | 22.28 | 12.42 | 26.467 |  | 10.0795 | 2.1182 | 7.9613 | 30447.474 | 33.4922 | 838636.9316 | 9.8281 | 11.7192 | 9.5107 | 1.5494 | 0.5851 | 0.00064631 | 1.2988 | 1.2988
2008-04-09 | 130000 | 264.4 | 2.61 | 13.63 | 22.27 | 12.35 | 26.752 |  | 10.0227 | 2.1182 | 7.9045 | 30433.8082 | 33.4772 | 838260.5237 | 9.934 | 11.8507 | 9.6175 | 1.7129 | 0.64685 | 0.00071453 | 1.4352 | 1.4352
2008-04-09 | 140000 | 264.1 | 2.61 | 13.62 | 22.27 | 12.35 | 27.075 |  | 10.0089 | 2.1152 | 7.8937 | 30433.8082 | 33.4772 | 837109.0669 | 10.0539 | 12.0103 | 9.7336 | 1.8399 | 0.6948 | 0.00076645 | 1.5395 | 1.5395
2008-04-09 | 150000 | 263.2 | 2.6 | 13.62 | 22.26 | 12.37 | 27.227 |  | 10.0251 | 2.1071 | 7.918 | 30420.1423 | 33.4622 | 836733.176 | 10.1103 | 12.0831 | 9.7926 | 1.8746 | 0.70792 | 0.00078091 | 1.5679 | 1.5679
2008-04-09 | 160000 | 263 | 2.6 | 13.62 | 22.21 | 12.45 | 27.322 |  | 10.09 | 2.1071 | 7.9828 | 30351.8132 | 33.387 | 834853.7214 | 10.1456 | 12.1526 | 9.8489 | 1.8661 | 0.70469 | 0.00077735 | 1.5572 | 1.5572
2008-04-09 | 170000 | 263.1 | 2.6 | 13.63 | 22.25 | 12.46 | 27.322 |  | 10.112 | 2.11 | 8.0019 | 30406.4765 | 33.4471 | 837507.7078 | 10.1456 | 12.1141 | 9.8312 | 1.8293 | 0.69079 | 0.00076307 | 1.5314 | 1.5314
2008-04-09 | 180000 | 263.3 | 2.6 | 13.63 | 22.27 | 12.4 | 27.132 |  | 10.0633 | 2.11 | 7.9532 | 30433.8082 | 33.4772 | 838260.5237 | 10.0751 | 12.019 | 9.7541 | 1.8008 | 0.68005 | 0.00075121 | 1.5089 | 1.5089
2008-04-09 | 190000 | 264 | 2.59 | 13.65 | 22.27 | 12.36 | 27.189 |  | 10.0585 | 2.1077 | 7.9508 | 30433.8082 | 33.4772 | 840572.9665 | 10.0962 | 12.0111 | 9.7746 | 1.8238 | 0.68873 | 0.00076289 | 1.5324 | 1.5324
2008-04-09 | 200000 | 264.6 | 2.59 | 13.66 | 22.28 | 12.38 | 27.265 |  | 10.0887 | 2.1106 | 7.978 | 30447.474 | 33.4922 | 842111.9465 | 10.1244 | 12.0227 | 9.7975 | 1.8195 | 0.68708 | 0.00076211 | 1.5315 | 1.5315
2008-04-09 | 210000 | 265.4 | 2.58 | 13.66 | 22.32 | 12.35 | 27.246 |  | 10.0642 | 2.1025 | 7.9617 | 30502.1373 | 33.5524 | 843623.8172 | 10.1174 | 11.9928 | 9.7731 | 1.8114 | 0.68403 | 0.00075873 | 1.5274 | 1.5274
2008-04-09 | 220000 | 265.8 | 2.58 | 13.67 | 22.42 | 12.55 | 27.056 |  | 10.2414 | 2.1054 | 8.136 | 30638.7957 | 33.7027 | 848575.5595 | 10.0468 | 11.8396 | 9.6617 | 1.5257 | 0.57616 | 0.00063996 | 1.2941 | 1.2941
2008-04-09 | 230000 | 265.8 | 2.58 | 13.68 | 22.43 | 12.5 | 26.999 |  | 10.2147 | 2.1083 | 8.1064 | 30652.4615 | 33.7177 | 850129.8865 | 10.0257 | 11.7931 | 9.637 | 1.5307 | 0.57802 | 0.00064292 | 1.3007 | 1.3007
2008-04-10 | 0 | 265.9 | 2.58 | 13.69 | 22.46 | 12.56 | 27.018 |  | 10.2779 | 2.1112 | 8.1667 | 30693.459 | 33.7628 | 852447.6059 | 10.0327 | 11.7693 | 9.6309 | 1.4642 | 0.55293 | 0.00061587 | 1.2476 | 1.2476
2008-04-10 | 10000 | 266.1 | 2.58 | 13.69 | 22.53 | 12.52 | 26.942 |  | 10.2452 | 2.1112 | 8.134 | 30789.1198 | 33.868 | 855104.3883 | 10.0045 | 11.6997 | 9.574 | 1.44 | 0.54379 | 0.00060569 | 1.2308 | 1.2308
2008-04-10 | 20000 | 266.1 | 2.58 | 13.69 | 22.53 | 12.55 | 26.942 |  | 10.2698 | 2.1112 | 8.1585 | 30789.1198 | 33.868 | 855104.3883 | 10.0045 | 11.6997 | 9.574 | 1.4155 | 0.53452 | 0.00059536 | 1.2098 | 1.2098
2008-04-10 | 30000 | 266.1 | 2.57 | 13.7 | 22.52 | 12.55 | 27.056 |  | 10.284 | 2.106 | 8.1781 | 30775.454 | 33.853 | 855911.9658 | 10.0468 | 11.7382 | 9.6188 | 1.4407 | 0.54406 | 0.00060683 | 1.2326 | 1.2326
2008-04-10 | 40000 | 266.5 | 2.57 | 13.7 | 22.53 | 12.48 | 26.98 |  | 10.2267 | 2.106 | 8.1207 | 30789.1198 | 33.868 | 856292.0333 | 10.0186 | 11.7 | 9.5875 | 1.4668 | 0.55391 | 0.00061781 | 1.2554 | 1.2554
2008-04-10 | 50000 | 266.9 | 2.58 | 13.69 | 22.53 | 12.43 | 26.923 |  | 10.1716 | 2.1112 | 8.0603 | 30789.1198 | 33.868 | 855104.3883 | 9.9974 | 11.6915 | 9.5672 | 1.5069 | 0.56906 | 0.00063383 | 1.288 | 1.288
2008-04-10 | 60000 | 266.9 | 3.02 | 12.72 | 22.54 | 12.34 | 26.942 |  | 8.9005 | 2.1782 | 6.7222 | 30802.7856 | 33.8831 | 754039.0129 | 10.0045 | 13.2679 | 9.5697 | 2.8475 | 1.0753 | 0.0010557 | 2.1462 | 2.1462
2008-04-10 | 70000 | 266.7 | 2.59 | 13.65 | 22.53 | 12.41 | 26.771 |  | 10.0992 | 2.1077 | 7.9914 | 30789.1198 | 33.868 | 850386.571 | 9.941 | 11.69 | 9.5132 | 1.5218 | 0.57467 | 0.00063655 | 1.2935 | 1.2935
2008-04-10 | 80000 | 266.7 | 2.57 | 13.7 | 22.54 | 12.48 | 26.961 |  | 10.2267 | 2.106 | 8.1207 | 30802.7856 | 33.8831 | 856672.1007 | 10.0116 | 11.6866 | 9.5765 | 1.4558 | 0.54976 | 0.00061318 | 1.2466 | 1.2466
2008-04-10 | 90000 | 266.5 | 2.47 | 14.06 | 22.53 | 12.51 | 27.113 |  | 10.7908 | 2.1306 | 8.6602 | 30789.1198 | 33.868 | 901360.035 | 10.068 | 11.1698 | 9.6348 | 0.97453 | 0.36801 | 0.00043207 | 0.878 | 0.878
2008-04-10 | 100000 | 266.3 | 3.61 | 11.88 | 22.53 | 12.56 | 27.474 |  | 8.2155 | 2.3613 | 5.8542 | 30789.1198 | 33.868 | 683514.705 | 10.2021 | 14.9259 | 9.763 | 3.9088 | 1.4761 | 0.0013142 | 2.6705 | 2.6705
2008-04-10 | 110000 | 266.6 | 2.5 | 13.75 | 22.53 | 12.64 | 27.588 |  | 10.4302 | 2.0629 | 8.3673 | 30789.1198 | 33.868 | 862280.0894 | 10.2444 | 11.8806 | 9.8036 | 1.4363 | 0.54238 | 0.00060919 | 1.2379 | 1.2379
2008-04-10 | 120000 | 266.1 | 2.5 | 13.77 | 22.38 | 12.76 | 27.911 |  | 10.5588 | 2.0687 | 8.49 | 30584.1323 | 33.6425 | 858941.8445 | 10.3643 | 12.0664 | 9.9848 | 1.4948 | 0.56447 | 0.00063577 | 1.2833 | 1.2833
2008-04-10 | 130000 | 266.9 | 2.49 | 13.78 | 22.28 | 12.82 | 28.196 |  | 10.6233 | 2.0633 | 8.56 | 30447.474 | 33.4922 | 856304.8445 | 10.4702 | 12.2271 | 10.132 | 1.5721 | 0.59366 | 0.00066959 | 1.3456 | 1.3456
2008-04-10 | 140000 | 266.9 | 2.49 | 13.78 | 22.28 | 12.82 | 28.139 |  | 10.6233 | 2.0633 | 8.56 | 30447.474 | 33.4922 | 856304.8445 | 10.449 | 12.2024 | 10.1116 | 1.5516 | 0.58593 | 0.00066087 | 1.328 | 1.328
2008-04-10 | 150000 | 265.4 | 2.49 | 13.79 | 22.28 | 12.77 | 28.101 |  | 10.5968 | 2.0662 | 8.5305 | 30447.474 | 33.4922 | 857509.2114 | 10.4349 | 12.1688 | 10.0979 | 1.5674 | 0.59189 | 0.00066853 | 1.3434 | 1.3434
2008-04-10 | 160000 | 265.2 | 2.48 | 13.79 | 22.28 | 12.72 | 28.006 |  | 10.5553 | 2.0579 | 8.4973 | 30447.474 | 33.4922 | 857509.2114 | 10.3996 | 12.1277 | 10.0638 | 1.5664 | 0.59153 | 0.00066813 | 1.3426 | 1.3426
2008-04-10 | 170000 | 265.3 | 2.48 | 13.8 | 22.31 | 12.72 | 27.968 |  | 10.5701 | 2.0608 | 8.5093 | 30488.4715 | 33.5373 | 859873.2325 | 10.3855 | 12.0779 | 10.0366 | 1.5273 | 0.57675 | 0.00065235 | 1.3127 | 1.3127
2008-04-10 | 180000 | 266 | 2.48 | 13.79 | 22.37 | 12.62 | 28.177 |  | 10.4723 | 2.0579 | 8.4143 | 30570.4665 | 33.6275 | 860973.1175 | 10.4631 | 12.1526 | 10.0845 | 1.6701 | 0.63069 | 0.00071236 | 1.4373 | 1.4373
2008-04-10 | 190000 | 266.9 | 2.48 | 13.79 | 22.53 | 12.49 | 28.234 |  | 10.3644 | 2.0579 | 8.3065 | 30789.1198 | 33.868 | 867131.1729 | 10.4843 | 12.0908 | 10.0331 | 1.7266 | 0.65203 | 0.00073646 | 1.4966 | 1.4966
2008-04-10 | 200000 | 267.9 | 2.48 | 13.8 | 22.54 | 12.45 | 28.215 |  | 10.3458 | 2.0608 | 8.2849 | 30802.7856 | 33.8831 | 868737.905 | 10.4772 | 12.0603 | 10.0219 | 1.737 | 0.65594 | 0.00074192 | 1.5083 | 1.5083
2008-04-10 | 210000 | 268.3 | 2.48 | 13.8 | 22.62 | 12.4 | 28.025 |  | 10.3042 | 2.0608 | 8.2434 | 30912.1123 | 34.0033 | 871821.2693 | 10.4067 | 11.9367 | 9.9192 | 1.6758 | 0.63285 | 0.0007158 | 1.4604 | 1.4604
2008-04-10 | 220000 | 269.1 | 2.48 | 13.8 | 22.78 | 12.33 | 27.93 |  | 10.2461 | 2.0608 | 8.1852 | 31130.7656 | 34.2438 | 877987.998 | 10.3714 | 11.8127 | 9.8162 | 1.631 | 0.6159 | 0.00069663 | 1.4313 | 1.4313
2008-04-10 | 230000 | 270.3 | 2.48 | 13.8 | 22.82 | 12.23 | 27.702 |  | 10.163 | 2.0608 | 8.1021 | 31185.4289 | 34.304 | 879529.6802 | 10.2867 | 11.6957 | 9.719 | 1.6169 | 0.61057 | 0.00069061 | 1.4214 | 1.4214
2008-04-11 | 0 | 270.9 | 2.47 | 13.81 | 22.88 | 12.16 | 27.55 |  | 10.119 | 2.0554 | 8.0636 | 31267.4239 | 34.3942 | 883085.9865 | 10.2303 | 11.5847 | 9.6403 | 1.5767 | 0.5954 | 0.0006744 | 1.3917 | 1.3917
2008-04-11 | 10000 | 271.8 | 2.48 | 13.81 | 23.04 | 12.13 | 27.531 |  | 10.0941 | 2.0638 | 8.0303 | 31486.0773 | 34.6347 | 889261.413 | 10.2232 | 11.4963 | 9.5667 | 1.5364 | 0.5802 | 0.00065717 | 1.3657 | 1.3657
2008-04-11 | 20000 | 272.3 | 2.48 | 13.8 | 23.04 | 12.14 | 27.607 |  | 10.0882 | 2.0608 | 8.0273 | 31486.0773 | 34.6347 | 888008.9321 | 10.2514 | 11.5443 | 9.5932 | 1.5658 | 0.5913 | 0.00066881 | 1.3898 | 1.3898
2008-04-11 | 30000 | 272.7 | 2.48 | 13.81 | 23.05 | 12.08 | 27.474 |  | 10.0525 | 2.0638 | 7.9887 | 31499.7431 | 34.6497 | 889647.3772 | 10.2021 | 11.4675 | 9.5428 | 1.5541 | 0.58687 | 0.00066473 | 1.382 | 1.382
2008-04-11 | 40000 | 272.9 | 2.47 | 13.81 | 23.05 | 12.07 | 27.455 |  | 10.0441 | 2.0554 | 7.9887 | 31499.7431 | 34.6497 | 889647.3772 | 10.195 | 11.4596 | 9.5362 | 1.5475 | 0.58437 | 0.00066191 | 1.3761 | 1.3761
2008-04-11 | 50000 | 272.8 | 2.48 | 13.81 | 23.04 | 12.1 | 27.607 |  | 10.0691 | 2.0638 | 8.0054 | 31486.0773 | 34.6347 | 889261.413 | 10.2514 | 11.528 | 9.5932 | 1.5878 | 0.5996 | 0.00067915 | 1.4113 | 1.4113
2008-04-11 | 60000 | 273.4 | 2.47 | 13.82 | 23.06 | 12.05 | 27.493 |  | 10.0417 | 2.0583 | 7.9833 | 31513.4089 | 34.6647 | 891290.4506 | 10.2091 | 11.4543 | 9.5453 | 1.5619 | 0.58983 | 0.00066903 | 1.3915 | 1.3915
2008-04-11 | 70000 | 273.3 | 2.47 | 13.82 | 23.05 | 12.02 | 27.379 |  | 10.0167 | 2.0583 | 7.9583 | 31499.7431 | 34.6497 | 890903.9413 | 10.1668 | 11.4118 | 9.5098 | 1.5515 | 0.58588 | 0.00066455 | 1.3816 | 1.3816
2008-04-11 | 80000 | 272.7 | 3.45 | 12.26 | 23.05 | 12.08 | 27.588 |  | 8.2491 | 2.3559 | 5.8932 | 31499.7431 | 34.6497 | 730046.2852 | 10.2444 | 14.0325 | 9.5824 | 3.6892 | 1.3932 | 0.0012949 | 2.6921 | 2.6921
2008-04-11 | 90000 | 272.8 | 2.46 | 13.84 | 22.97 | 12.36 | 27.588 |  | 10.3292 | 2.0558 | 8.2734 | 31390.4164 | 34.5295 | 890326.9146 | 10.2444 | 11.5063 | 9.6158 | 1.3424 | 0.50693 | 0.00057662 | 1.1946 | 1.1946
2008-04-11 | 100000 | 270.6 | 2.49 | 13.8 | 22.72 | 12.73 | 28.101 |  | 10.5785 | 2.0692 | 8.5093 | 31048.7706 | 34.1536 | 875675.4748 | 10.4349 | 11.9164 | 9.9023 | 1.393 | 0.52606 | 0.00059501 | 1.2193 | 1.2193
2008-04-11 | 110000 | 267.7 | 2.49 | 13.79 | 22.44 | 13.05 | 28.69 |  | 10.8291 | 2.0662 | 8.7629 | 30666.1273 | 33.7327 | 863667.2668 | 10.6536 | 12.3353 | 10.236 | 1.4732 | 0.55632 | 0.00062835 | 1.2718 | 1.2718
2008-04-11 | 120000 | 265.1 | 2.49 | 13.8 | 22.2 | 13.05 | 28.5 |  | 10.8444 | 2.0692 | 8.7752 | 30338.1474 | 33.372 | 855633.6065 | 10.583 | 12.3687 | 10.2782 | 1.503 | 0.56757 | 0.00064196 | 1.2854 | 1.2854
2008-04-11 | 130000 | 263.2 | 2.49 | 13.8 | 22.04 | 13.23 | 28.861 |  | 10.9939 | 2.0692 | 8.9248 | 30119.494 | 33.1314 | 849466.8778 | 10.7171 | 12.6163 | 10.4839 | 1.5591 | 0.58878 | 0.00066596 | 1.3238 | 1.3238
2008-04-11 | 140000 | 261.5 | 2.49 | 13.8 | 21.92 | 13.15 | 29.412 |  | 10.9275 | 2.0692 | 8.8583 | 29955.5041 | 32.9511 | 844841.8313 | 10.9217 | 12.9275 | 10.7426 | 1.8843 | 0.71156 | 0.00080483 | 1.5912 | 1.5912
2008-04-11 | 150000 | 259.8 | 2.48 | 13.8 | 21.79 | 13.17 | 28.747 |  | 10.9441 | 2.0608 | 8.8832 | 29777.8482 | 32.7556 | 839831.3642 | 10.6748 | 12.7106 | 10.5623 | 1.6791 | 0.63408 | 0.00071719 | 1.4095 | 1.4095
2008-04-11 | 160000 | 258.3 | 2.48 | 13.8 | 21.62 | 13.15 | 28.082 |  | 10.9275 | 2.0608 | 8.8666 | 29545.5291 | 32.5001 | 833279.215 | 10.4278 | 12.5142 | 10.3991 | 1.5325 | 0.57872 | 0.00065458 | 1.2764 | 1.2764
2008-04-11 | 170000 | 256.3 | 2.47 | 13.8 | 21.52 | 12.96 | 27.189 |  | 10.7696 | 2.0525 | 8.717 | 29408.8708 | 32.3498 | 829425.0095 | 10.0962 | 12.1726 | 10.1152 | 1.3982 | 0.528 | 0.0005972 | 1.1592 | 1.1592
2008-04-11 | 180000 | 256 | 2.48 | 13.79 | 21.52 | 12.94 | 26.98 |  | 10.7378 | 2.0579 | 8.6799 | 29408.8708 | 32.3498 | 828258.4483 | 10.0186 | 12.096 | 10.0375 | 1.3576 | 0.51266 | 0.00057905 | 1.1239 | 1.1239
2008-04-11 | 190000 | 255.1 | 2.39 | 13.83 | 21.43 | 12.13 | 25.365 |  | 10.1226 | 1.9945 | 8.1281 | 29285.8783 | 32.2145 | 829460.9894 | 9.4189 | 11.3555 | 9.4763 | 1.3481 | 0.50909 | 0.00057826 | 1.1177 | 1.1177
2008-04-11 | 200000 | 256 | 2.45 | 13.82 | 21.54 | 12.03 | 25.08 |  | 10.025 | 2.0417 | 7.9833 | 29436.2024 | 32.3798 | 832541.0366 | 9.3131 | 11.1863 | 9.3219 | 1.3386 | 0.5055 | 0.00057337 | 1.1139 | 1.1139
2008-04-11 | 210000 | 261.2 | 2.56 | 13.73 | 21.87 | 13.13 | 28.348 |  | 10.8043 | 2.1066 | 8.6978 | 29887.1749 | 32.8759 | 834685.4355 | 10.5266 | 12.6115 | 10.3776 | 1.6799 | 0.63437 | 0.00071051 | 1.4015 | 1.4015
2008-04-11 | 220000 | 261.6 | 2.4 | 13.74 | 21.96 | 12.86 | 27.759 |  | 10.5969 | 1.9777 | 8.6193 | 30010.1674 | 33.0112 | 839290.9142 | 10.3079 | 12.2817 | 10.1204 | 1.5011 | 0.56686 | 0.00063579 | 1.2593 | 1.2593
2008-04-11 | 230000 | 264.1 | 2.59 | 13.72 | 22.13 | 13.08 | 28.006 |  | 10.7482 | 2.1283 | 8.6199 | 30242.4865 | 33.2667 | 843432.2013 | 10.3996 | 12.3301 | 10.132 | 1.5121 | 0.571 | 0.00063865 | 1.2747 | 1.2747
2008-04-12 | 0 | 265.4 | 2.5 | 13.72 | 22.27 | 13.01 | 28.101 |  | 10.6907 | 2.0543 | 8.6364 | 30433.8082 | 33.4772 | 848767.9676 | 10.4349 | 12.2942 | 10.1024 | 1.4661 | 0.55364 | 0.00061923 | 1.2438 | 1.2438
2008-04-12 | 10000 | 266.1 | 2.5 | 13.71 | 22.27 | 12.96 | 27.93 |  | 10.6348 | 2.0515 | 8.5833 | 30433.8082 | 33.4772 | 847587.4836 | 10.3714 | 12.2364 | 10.041 | 1.4577 | 0.55045 | 0.00061481 | 1.2349 | 1.2349
2008-04-12 | 20000 | 266.6 | 2.51 | 13.7 | 22.29 | 12.91 | 27.835 |  | 10.579 | 2.0568 | 8.5222 | 30461.1398 | 33.5073 | 847170.4137 | 10.3361 | 12.2007 | 9.9978 | 1.4756 | 0.55723 | 0.00062152 | 1.2495 | 1.2495
2008-04-12 | 30000 | 266.8 | 2.51 | 13.69 | 22.28 | 12.85 | 27.645 |  | 10.5153 | 2.054 | 8.4613 | 30447.474 | 33.4922 | 845615.8797 | 10.2656 | 12.1397 | 9.934 | 1.4727 | 0.55615 | 0.00061945 | 1.2448 | 1.2448
2008-04-12 | 40000 | 267.3 | 2.52 | 13.68 | 22.33 | 12.84 | 27.607 |  | 10.4925 | 2.0593 | 8.4332 | 30515.8032 | 33.5674 | 846339.7399 | 10.2514 | 12.1127 | 9.8982 | 1.4649 | 0.5532 | 0.00061532 | 1.2393 | 1.2393
2008-04-12 | 50000 | 267.9 | 2.52 | 13.68 | 22.43 | 12.74 | 27.474 |  | 10.4108 | 2.0593 | 8.3515 | 30652.4615 | 33.7177 | 850129.8865 | 10.2021 | 12.0006 | 9.8066 | 1.455 | 0.54947 | 0.00061116 | 1.2364 | 1.2364
2008-04-12 | 60000 | 268.3 | 2.52 | 13.67 | 22.55 | 12.58 | 27.189 |  | 10.2658 | 2.0564 | 8.2094 | 30816.4515 | 33.8981 | 853495.9352 | 10.0962 | 11.8293 | 9.6532 | 1.4438 | 0.54522 | 0.0006056 | 1.2317 | 1.2317
2008-04-12 | 70000 | 268 | 2.53 | 13.67 | 22.53 | 12.55 | 26.999 |  | 10.2414 | 2.0646 | 8.1768 | 30789.1198 | 33.868 | 852738.9543 | 10.0257 | 11.757 | 9.5943 | 1.4175 | 0.53529 | 0.00059456 | 1.2082 | 1.2082
2008-04-12 | 80000 | 266.1 | 3.49 | 12.11 | 22.32 | 12.69 | 27.512 |  | 8.5177 | 2.3425 | 6.1752 | 30502.1373 | 33.5524 | 694861.9382 | 10.2162 | 14.7024 | 9.8685 | 3.6933 | 1.3947 | 0.0012742 | 2.5652 | 2.5652
2008-04-12 | 90000 | 261.9 | 2.43 | 13.76 | 22.03 | 11.86 | 25.042 |  | 9.8003 | 2.008 | 7.7923 | 30105.8282 | 33.1164 | 844324.6984 | 9.299 | 11.0135 | 9.1008 | 1.3085 | 0.49413 | 0.00055576 | 1.1043 | 1.1043
2008-04-12 | 100000 | 258.8 | 2.48 | 13.72 | 21.79 | 11.74 | 24.624 |  | 9.6471 | 2.0379 | 7.6092 | 29777.8482 | 32.7556 | 830473.9117 | 9.1438 | 11.0103 | 9.0474 | 1.4383 | 0.54313 | 0.00060748 | 1.1939 | 1.1939
2008-04-12 | 110000 | 257.3 | 2.59 | 13.68 | 21.6 | 12.47 | 26.182 |  | 10.1902 | 2.1165 | 8.0737 | 29518.1974 | 32.47 | 818671.6696 | 9.7223 | 11.8757 | 9.7045 | 1.6308 | 0.61585 | 0.000685 | 1.3345 | 1.3345
2008-04-12 | 120000 | 253.9 | 2.53 | 13.66 | 21.38 | 12.53 | 26.068 |  | 10.2109 | 2.0617 | 8.1492 | 29217.5491 | 32.1393 | 808094.8571 | 9.68 | 11.9787 | 9.7617 | 1.6125 | 0.60893 | 0.00067543 | 1.3025 | 1.3025
2008-04-12 | 130000 | 248.7 | 2.53 | 13.68 | 20.94 | 12.25 | 25.118 |  | 10.0104 | 2.0675 | 7.9429 | 28616.2525 | 31.4779 | 793656.7019 | 9.3272 | 11.7522 | 9.6036 | 1.6606 | 0.62711 | 0.00069752 | 1.3174 | 1.3174
2008-04-12 | 140000 | 246.1 | 2.52 | 13.71 | 20.76 | 12.21 | 24.833 |  | 10.0193 | 2.0679 | 7.9515 | 28370.2675 | 31.2073 | 790117.4746 | 9.2214 | 11.6709 | 9.5769 | 1.6255 | 0.61383 | 0.0006856 | 1.2837 | 1.2837
2008-04-12 | 150000 | 245.7 | 2.51 | 13.7 | 20.64 | 12.23 | 24.966 |  | 10.0218 | 2.0568 | 7.965 | 28206.2775 | 31.0269 | 784459.2795 | 9.2707 | 11.818 | 9.6842 | 1.7192 | 0.64922 | 0.00072412 | 1.348 | 1.348
2008-04-12 | 160000 | 238.3 | 2.36 | 13.85 | 20.13 | 9.79 | 18.639 |  | 8.193 | 1.975 | 6.218 | 27509.3201 | 30.2603 | 781354.0473 | 6.9213 | 8.8581 | 7.4132 | 1.1951 | 0.45132 | 0.0005141 | 0.93341 | 0.93341
2008-04-12 | 170000 | 234.2 | 2.43 | 13.89 | 19.86 | 8.24 | 14.858 |  | 6.9352 | 2.0452 | 4.89 | 27140.3426 | 29.8544 | 775272.5985 | 5.5173 | 7.1166 | 5.9897 | 1.0997 | 0.41528 | 0.00047574 | 0.85218 | 0.85218
2008-04-12 | 180000 | 245.4 | 2.49 | 13.8 | 20.74 | 9.71 | 19 |  | 8.0689 | 2.0692 | 5.9997 | 28342.9359 | 31.1772 | 799362.2071 | 7.0554 | 8.8262 | 7.3345 | 1.3348 | 0.50405 | 0.00057012 | 1.0665 | 1.0665
2008-04-12 | 190000 | 254.9 | 2.57 | 13.66 | 21.43 | 11.98 | 25.061 |  | 9.7627 | 2.0943 | 7.6684 | 29285.8783 | 32.2145 | 809984.6954 | 9.306 | 11.4891 | 9.3627 | 1.6943 | 0.63983 | 0.0007097 | 1.3718 | 1.3718
2008-04-12 | 200000 | 258.9 | 2.51 | 13.66 | 21.74 | 11.95 | 25.574 |  | 9.7383 | 2.0454 | 7.6928 | 29709.5191 | 32.6805 | 821701.6929 | 9.4965 | 11.5571 | 9.4181 | 1.7253 | 0.65152 | 0.00072267 | 1.417 | 1.417
2008-04-12 | 210000 | 260.8 | 2.53 | 13.66 | 21.9 | 11.99 | 25.156 |  | 9.7709 | 2.0617 | 7.7091 | 29928.1724 | 32.921 | 827749.1755 | 9.3413 | 11.2852 | 9.1965 | 1.4874 | 0.56168 | 0.00062302 | 1.2306 | 1.2306
2008-04-12 | 220000 | 264.1 | 2.57 | 13.63 | 22.12 | 12.69 | 26.923 |  | 10.2986 | 2.0857 | 8.2129 | 30228.8207 | 33.2517 | 832614.4043 | 9.9974 | 12.0073 | 9.7446 | 1.5316 | 0.5784 | 0.00063891 | 1.2747 | 1.2747
2008-04-12 | 230000 | 265.1 | 2.54 | 13.63 | 22.28 | 12.68 | 26.942 |  | 10.2905 | 2.0613 | 8.2292 | 30447.474 | 33.4922 | 838636.9316 | 10.0045 | 11.9295 | 9.6814 | 1.4523 | 0.54842 | 0.0006058 | 1.2174 | 1.2174
2008-04-13 | 0 | 265.8 | 2.53 | 13.64 | 22.27 | 12.63 | 26.885 |  | 10.264 | 2.0561 | 8.208 | 30433.8082 | 33.4772 | 839415.1525 | 9.9833 | 11.8932 | 9.6653 | 1.4573 | 0.55032 | 0.00060873 | 1.2227 | 1.2227
2008-04-13 | 10000 | 266.3 | 2.53 | 13.64 | 22.28 | 12.65 | 26.885 |  | 10.2803 | 2.0561 | 8.2242 | 30447.474 | 33.4922 | 839792.0789 | 9.9833 | 11.8879 | 9.6609 | 1.4367 | 0.54254 | 0.00060013 | 1.206 | 1.206
2008-04-13 | 20000 | 267 | 2.54 | 13.64 | 22.31 | 12.6 | 26.79 |  | 10.2397 | 2.0642 | 8.1755 | 30488.4715 | 33.5373 | 840922.8582 | 9.9481 | 11.8299 | 9.6139 | 1.4384 | 0.54317 | 0.00060083 | 1.209 | 1.209
2008-04-13 | 30000 | 267.3 | 2.54 | 13.64 | 22.43 | 12.66 | 26.961 |  | 10.2884 | 2.0642 | 8.2242 | 30652.4615 | 33.7177 | 845445.9753 | 10.0116 | 11.8418 | 9.6235 | 1.3992 | 0.52839 | 0.00058448 | 1.1824 | 1.1824
2008-04-13 | 40000 | 267.5 | 2.53 | 13.63 | 22.49 | 12.66 | 26.999 |  | 10.2743 | 2.0532 | 8.221 | 30734.4565 | 33.8079 | 846541.4988 | 10.0257 | 11.8431 | 9.6113 | 1.3903 | 0.52501 | 0.00057994 | 1.1764 | 1.1764
2008-04-13 | 50000 | 267.8 | 2.53 | 13.63 | 22.48 | 12.54 | 26.866 |  | 10.1769 | 2.0532 | 8.1237 | 30720.7907 | 33.7929 | 846165.0908 | 9.9763 | 11.79 | 9.5682 | 1.4446 | 0.54551 | 0.00060259 | 1.2218 | 1.2218
2008-04-13 | 60000 | 191.7 | 2.34 | 13.84 | 16.84 | 7.75 | 10.222 |  | 6.4766 | 1.9555 | 4.5211 | 23013.2613 | 25.3146 | 652725.5221 | 3.7958 | 5.8153 | 4.8598 | 0.33869 | 0.1279 | 0.00014549 | 0.22098 | 0.22098
2008-04-13 | 70000 | 191.6 | 2.46 | 13.84 | 16.93 | 7.6 | 10.184 |  | 6.3513 | 2.0558 | 4.2955 | 23136.2538 | 25.4499 | 656213.9601 | 3.7817 | 5.7629 | 4.816 | 0.52053 | 0.19657 | 0.00022359 | 0.34142 | 0.34142
2008-04-13 | 80000 | 192.4 | 3.37 | 12.23 | 16.93 | 7.53 | 10.488 |  | 5.1242 | 2.2933 | 2.8309 | 23136.2538 | 25.4499 | 534356.4658 | 3.8946 | 7.2883 | 4.9598 | 2.1288 | 0.80392 | 0.00074463 | 1.137 | 1.137
2008-04-13 | 90000 | 197.4 | 2.41 | 13.86 | 17.38 | 8.75 | 12.407 |  | 7.3331 | 2.0197 | 5.3134 | 23751.2163 | 26.1263 | 675569.9463 | 4.6072 | 6.8197 | 5.7153 | 0.40198 | 0.1518 | 0.00017316 | 0.27144 | 0.27144
2008-04-13 | 100000 | 247.8 | 2.33 | 13.88 | 21.01 | 8.62 | 15.846 |  | 7.2447 | 1.9583 | 5.2865 | 28711.9133 | 31.5831 | 818996.6936 | 5.8842 | 7.1846 | 6.0383 | 0.75188 | 0.28393 | 0.00032481 | 0.61551 | 0.61551
2008-04-13 | 110000 | 252.3 | 2.34 | 13.86 | 21.34 | 9.14 | 18.259 |  | 7.6599 | 1.9611 | 5.6989 | 29162.8858 | 32.0792 | 829497.2759 | 6.7802 | 8.1739 | 6.8503 | 1.1514 | 0.4348 | 0.00049599 | 0.95465 | 0.95465
2008-04-13 | 120000 | 256.2 | 2.56 | 13.76 | 21.6 | 10.58 | 21.166 |  | 8.7426 | 2.1154 | 6.6272 | 29518.1974 | 32.47 | 827844.4614 | 7.8597 | 9.4941 | 7.8453 | 1.2181 | 0.46 | 0.00051738 | 1.008 | 1.008
2008-04-13 | 130000 | 258.4 | 2.48 | 13.68 | 21.78 | 11.67 | 23.864 |  | 9.5364 | 2.0266 | 7.5098 | 29764.1824 | 32.7406 | 825493.9335 | 8.8615 | 10.7348 | 8.7722 | 1.2624 | 0.47672 | 0.00053024 | 1.0416 | 1.0416
2008-04-13 | 140000 | 260.3 | 2.53 | 13.6 | 21.83 | 12.83 | 27.037 |  | 10.3695 | 2.0448 | 8.3247 | 29832.5116 | 32.8158 | 818321.73 | 10.0398 | 12.2687 | 9.9158 | 1.5912 | 0.60088 | 0.00066102 | 1.3015 | 1.3015
2008-04-13 | 150000 | 190.4 | 2.32 | 13.83 | 16.69 | 7.82 | 10.431 |  | 6.5259 | 1.9361 | 4.5898 | 22808.2738 | 25.0891 | 645996.4495 | 3.8734 | 5.996 | 5.0037 | 0.41392 | 0.15631 | 0.00017755 | 0.26727 | 0.26727
2008-04-13 | 160000 | 194.5 | 2.46 | 13.84 | 17.09 | 7.49 | 10.83 |  | 6.2593 | 2.0558 | 4.2035 | 23354.9071 | 25.6904 | 662415.6278 | 4.0216 | 6.071 | 5.0735 | 0.87 | 0.32854 | 0.00037371 | 0.57604 | 0.57604
2008-04-13 | 170000 | 260.5 | 2.48 | 13.67 | 21.94 | 11.94 | 25.118 |  | 9.7436 | 2.0238 | 7.7198 | 29982.8357 | 32.9811 | 830408.0185 | 9.3272 | 11.2321 | 9.1659 | 1.4461 | 0.54608 | 0.00060656 | 1.2003 | 1.2003
2008-04-13 | 180000 | 263.6 | 2.51 | 13.65 | 22.09 | 12.27 | 25.935 |  | 9.9852 | 2.0426 | 7.9426 | 30187.8232 | 33.2066 | 833778.9326 | 9.6306 | 11.5505 | 9.3997 | 1.4571 | 0.55025 | 0.00060949 | 1.2144 | 1.2144
2008-04-13 | 190000 | 265 | 2.45 | 13.65 | 22.17 | 12.07 | 25.688 |  | 9.8225 | 1.9938 | 7.8287 | 30297.1499 | 33.3269 | 836798.5032 | 9.5389 | 11.3992 | 9.2766 | 1.4479 | 0.54678 | 0.00060565 | 1.2111 | 1.2111
2008-04-13 | 200000 | 266.2 | 2.66 | 13.6 | 22.28 | 12.51 | 26.657 |  | 10.1108 | 2.1499 | 7.961 | 30447.474 | 33.4922 | 835190.4785 | 9.8987 | 11.852 | 9.579 | 1.6181 | 0.61103 | 0.00067218 | 1.3508 | 1.3508
2008-04-13 | 210000 | 266.6 | 2.55 | 13.6 | 22.3 | 12.54 | 26.695 |  | 10.1351 | 2.061 | 8.0741 | 30474.8057 | 33.5223 | 835940.2006 | 9.9128 | 11.8582 | 9.5841 | 1.51 | 0.5702 | 0.00062728 | 1.2617 | 1.2617
2008-04-13 | 220000 | 266.9 | 2.55 | 13.61 | 22.36 | 12.57 | 26.752 |  | 10.1733 | 2.0638 | 8.1095 | 30556.8007 | 33.6125 | 839339.1468 | 9.934 | 11.8354 | 9.5788 | 1.4693 | 0.55485 | 0.00061122 | 1.2327 | 1.2327
2008-04-13 | 230000 | 265.7 | 2.52 | 13.6 | 22.26 | 12.46 | 26.638 |  | 10.0704 | 2.0367 | 8.0337 | 30420.1423 | 33.4622 | 834440.7563 | 9.8916 | 11.8542 | 9.5808 | 1.5471 | 0.58423 | 0.0006427 | 1.2904 | 1.2904
2008-04-14 | 0 | 191.4 | 2.35 | 13.81 | 16.86 | 7.68 | 10.089 |  | 6.391 | 1.9556 | 4.4354 | 23040.593 | 25.3447 | 650735.5652 | 3.7464 | 5.7572 | 4.7909 | 0.35548 | 0.13424 | 0.00015205 | 0.23122 | 0.23122
2008-04-14 | 10000 | 192.8 | 2.45 | 13.81 | 17.03 | 7.64 | 10.298 |  | 6.3577 | 2.0388 | 4.3189 | 23272.9121 | 25.6002 | 657296.9559 | 3.824 | 5.8178 | 4.8413 | 0.52241 | 0.19728 | 0.00022345 | 0.34322 | 0.34322
2008-04-14 | 20000 | 193.3 | 2.49 | 13.8 | 17.01 | 7.6 | 10.279 |  | 6.3155 | 2.0692 | 4.2463 | 23245.5805 | 25.5701 | 655600.3444 | 3.817 | 5.8221 | 4.8381 | 0.59172 | 0.22345 | 0.00025274 | 0.38776 | 0.38776
2008-04-14 | 30000 | 193.1 | 2.5 | 13.79 | 17.03 | 7.62 | 10.298 |  | 6.3232 | 2.0745 | 4.2487 | 23272.9121 | 25.6002 | 655448.0193 | 3.824 | 5.8342 | 4.8413 | 0.59265 | 0.2238 | 0.00025278 | 0.38827 | 0.38827
2008-04-14 | 40000 | 193.7 | 2.47 | 13.79 | 17.11 | 7.71 | 10.697 |  | 6.3979 | 2.0496 | 4.3482 | 23382.2388 | 25.7205 | 658527.047 | 3.9722 | 6.0319 | 5.0054 | 0.65713 | 0.24815 | 0.00028029 | 0.43254 | 0.43254
2008-04-14 | 50000 | 193.7 | 2.49 | 13.79 | 17.1 | 7.7 | 10.45 |  | 6.3896 | 2.0662 | 4.3233 | 23368.573 | 25.7054 | 658142.1685 | 3.8804 | 5.8961 | 4.8927 | 0.56931 | 0.21499 | 0.00024283 | 0.37452 | 0.37452
2008-04-14 | 60000 | 198.2 | 2.5 | 13.77 | 17.48 | 7.98 | 12.046 |  | 6.6034 | 2.0687 | 4.5346 | 23887.8746 | 26.2767 | 670880.404 | 4.4731 | 6.6675 | 5.5173 | 0.98265 | 0.37108 | 0.00041795 | 0.65894 | 0.65894
2008-04-14 | 70000 | 264.3 | 2.49 | 13.63 | 22.33 | 11.67 | 24.719 |  | 9.4708 | 2.0208 | 7.4501 | 30515.8032 | 33.5674 | 840518.9714 | 9.179 | 10.9207 | 8.8627 | 1.4126 | 0.53346 | 0.00058927 | 1.1868 | 1.1868
2008-04-14 | 80000 | 265.4 | 2.52 | 13.62 | 22.35 | 11.83 | 25.194 |  | 9.5875 | 2.0423 | 7.5452 | 30543.1348 | 33.5974 | 840116.1942 | 9.3554 | 11.1359 | 9.0249 | 1.4797 | 0.5588 | 0.00061641 | 1.2426 | 1.2426
2008-04-14 | 90000 | 267.3 | 3.6 | 12.06 | 22.49 | 12.37 | 26.885 |  | 8.256 | 2.4027 | 5.8533 | 30734.4565 | 33.8079 | 696194.1964 | 9.9833 | 14.3399 | 9.5707 | 3.7175 | 1.4038 | 0.0012753 | 2.5869 | 2.5869
2008-04-14 | 100000 | 266.5 | 2.54 | 13.64 | 22.39 | 12.07 | 26.296 |  | 9.809 | 2.0642 | 7.7448 | 30597.7982 | 33.6576 | 843938.2696 | 9.7646 | 11.5703 | 9.4029 | 1.6581 | 0.62615 | 0.00069261 | 1.3987 | 1.3987
2008-04-14 | 110000 | 265.9 | 2.55 | 13.59 | 22.29 | 12.48 | 27.113 |  | 10.0728 | 2.0581 | 8.0146 | 30461.1398 | 33.5073 | 834422.2953 | 10.068 | 12.0658 | 9.7385 | 1.7239 | 0.65098 | 0.00071516 | 1.4378 | 1.4378
2008-04-14 | 120000 | 265.7 | 2.55 | 13.58 | 22.28 | 12.69 | 27.056 |  | 10.2283 | 2.0553 | 8.173 | 30447.474 | 33.4922 | 832908.5373 | 10.0468 | 12.0624 | 9.7224 | 1.5494 | 0.58511 | 0.00064192 | 1.29 | 1.29
2008-04-14 | 130000 | 266.5 | 2.55 | 13.58 | 22.38 | 12.56 | 26.695 |  | 10.1235 | 2.0553 | 8.0682 | 30584.1323 | 33.6425 | 836646.9059 | 9.9128 | 11.8482 | 9.5498 | 1.4816 | 0.55951 | 0.00061383 | 1.239 | 1.239
2008-04-14 | 140000 | 266.1 | 2.56 | 13.59 | 22.27 | 12.61 | 26.79 |  | 10.1777 | 2.0662 | 8.1115 | 30433.8082 | 33.4772 | 833673.5988 | 9.9481 | 11.9328 | 9.6311 | 1.5196 | 0.57386 | 0.00063043 | 1.2663 | 1.2663
2008-04-14 | 150000 | 265.9 | 2.55 | 13.59 | 22.28 | 12.71 | 27.037 |  | 10.2584 | 2.0581 | 8.2003 | 30447.474 | 33.4922 | 834047.9471 | 10.0398 | 12.0374 | 9.7156 | 1.5153 | 0.57222 | 0.00062863 | 1.2633 | 1.2633
2008-04-14 | 160000 | 265.8 | 2.55 | 13.6 | 22.27 | 12.65 | 26.999 |  | 10.224 | 2.061 | 8.163 | 30433.8082 | 33.4772 | 834815.6174 | 10.0257 | 12.0094 | 9.7063 | 1.5432 | 0.58278 | 0.00064111 | 1.2877 | 1.2877
2008-04-14 | 170000 | 265.1 | 2.56 | 13.6 | 22.27 | 12.7 | 27.284 |  | 10.2644 | 2.069 | 8.1953 | 30433.8082 | 33.4772 | 834815.6174 | 10.1315 | 12.1362 | 9.8087 | 1.6134 | 0.60926 | 0.00067024 | 1.3463 | 1.3463
2008-04-14 | 180000 | 266 | 2.54 | 13.61 | 22.28 | 12.49 | 27.322 |  | 10.1085 | 2.0557 | 8.0528 | 30447.474 | 33.4922 | 836336.1444 | 10.1456 | 12.131 | 9.818 | 1.7652 | 0.66658 | 0.0007343 | 1.4756 | 1.4756
2008-04-14 | 190000 | 266.9 | 2.54 | 13.6 | 22.32 | 12.46 | 27.322 |  | 10.0704 | 2.0529 | 8.0175 | 30502.1373 | 33.5524 | 836689.9228 | 10.1456 | 12.1259 | 9.8004 | 1.7828 | 0.67326 | 0.00074064 | 1.491 | 1.491
2008-04-14 | 200000 | 267.7 | 2.55 | 13.61 | 22.5 | 12.45 | 27.379 |  | 10.0761 | 2.0638 | 8.0123 | 30748.1223 | 33.8229 | 844594.4008 | 10.1668 | 12.0375 | 9.7423 | 1.7299 | 0.65327 | 0.00071964 | 1.4604 | 1.4604
2008-04-14 | 210000 | 268.8 | 2.53 | 13.62 | 22.54 | 12.32 | 27.17 |  | 9.9846 | 2.0504 | 7.9342 | 30802.7856 | 33.8831 | 847258.1216 | 10.0892 | 11.908 | 9.6507 | 1.7165 | 0.64821 | 0.00071505 | 1.4537 | 1.4537
2008-04-14 | 220000 | 194.3 | 2.53 | 13.79 | 17.04 | 9.12 | 12.996 |  | 7.5679 | 2.0994 | 5.4685 | 23286.578 | 25.6152 | 655832.8978 | 4.8259 | 7.3584 | 6.1061 | 0.63762 | 0.24078 | 0.00027196 | 0.41798 | 0.41798
2008-04-14 | 230000 | 193.5 | 2.44 | 13.82 | 17.06 | 7.77 | 10.431 |  | 6.475 | 2.0333 | 4.4417 | 23313.9096 | 25.6453 | 659384.8693 | 3.8734 | 5.8743 | 4.8952 | 0.45355 | 0.17127 | 0.00019427 | 0.29893 | 0.29893
2008-04-15 | 0 | 193 | 2.45 | 13.83 | 16.99 | 7.77 | 10.374 |  | 6.4842 | 2.0446 | 4.4396 | 23218.2488 | 25.5401 | 657608.1292 | 3.8522 | 5.8579 | 4.8885 | 0.44892 | 0.16952 | 0.00019256 | 0.29508 | 0.29508
2008-04-15 | 10000 | 193.2 | 2.48 | 13.83 | 17.01 | 7.75 | 10.298 |  | 6.4675 | 2.0696 | 4.3979 | 23245.5805 | 25.5701 | 658382.2412 | 3.824 | 5.8082 | 4.847 | 0.44912 | 0.1696 | 0.00019265 | 0.29556 | 0.29556
2008-04-15 | 20000 | 192.4 | 2.46 | 13.83 | 16.93 | 7.79 | 10.374 |  | 6.5008 | 2.0529 | 4.4479 | 23136.2538 | 25.4499 | 655285.7933 | 3.8522 | 5.8787 | 4.9058 | 0.4579 | 0.17292 | 0.00019641 | 0.29992 | 0.29992
2008-04-15 | 30000 | 193 | 2.46 | 13.84 | 17.03 | 7.73 | 10.298 |  | 6.4599 | 2.0558 | 4.4041 | 23272.9121 | 25.6002 | 660090.0024 | 3.824 | 5.7932 | 4.8413 | 0.4372 | 0.1651 | 0.0001878 | 0.28846 | 0.28846
2008-04-15 | 40000 | 193.5 | 2.47 | 13.84 | 17.14 | 7.7 | 10.412 |  | 6.4348 | 2.0642 | 4.3707 | 23423.2363 | 25.7656 | 664353.649 | 3.8663 | 5.8197 | 4.8635 | 0.49281 | 0.1861 | 0.00021169 | 0.32725 | 0.32725
2008-04-15 | 50000 | 268.9 | 2.5 | 13.65 | 22.74 | 11.88 | 26.695 |  | 9.6679 | 2.0345 | 7.6334 | 31076.1023 | 34.1837 | 858312.9438 | 9.9128 | 11.5492 | 9.3986 | 1.7652 | 0.66661 | 0.00073839 | 1.5144 | 1.5144
2008-04-15 | 60000 | 265.7 | 2.5 | 13.76 | 22.38 | 10.5 | 22.268 |  | 8.6765 | 2.0658 | 6.6106 | 30584.1323 | 33.6425 | 857738.8448 | 8.2689 | 9.6403 | 7.9661 | 1.3555 | 0.51186 | 0.00057571 | 1.1621 | 1.1621
2008-04-15 | 70000 | 270 | 2.53 | 13.67 | 22.79 | 12.46 | 27.094 |  | 10.1679 | 2.0646 | 8.1033 | 31144.4314 | 34.2589 | 862579.7056 | 10.0609 | 11.6638 | 9.5182 | 1.4148 | 0.53429 | 0.00059346 | 1.2199 | 1.2199
2008-04-15 | 80000 | 270.1 | 3.57 | 12.13 | 22.7 | 12.5 | 26.695 |  | 8.4094 | 2.4017 | 6.0076 | 31021.439 | 34.1236 | 708303.6373 | 9.9128 | 13.9951 | 9.4152 | 3.4075 | 1.2868 | 0.0011783 | 2.4125 | 2.4125
2008-04-15 | 90000 | 269.3 | 2.5 | 13.7 | 22.66 | 12.48 | 26.942 |  | 10.2267 | 2.0486 | 8.1781 | 30966.7756 | 34.0635 | 861232.9105 | 10.0045 | 11.6165 | 9.5191 | 1.341 | 0.50641 | 0.00056483 | 1.1544 | 1.1544
2008-04-15 | 100000 | 269.9 | 2.54 | 13.67 | 22.64 | 12.98 | 28.272 |  | 10.5923 | 2.0728 | 8.5195 | 30939.444 | 34.0334 | 856902.3491 | 10.4984 | 12.2515 | 9.9978 | 1.4783 | 0.55825 | 0.00062007 | 1.2662 | 1.2662
2008-04-15 | 110000 | 269 | 2.52 | 13.7 | 22.55 | 12.6 | 27.094 |  | 10.325 | 2.065 | 8.26 | 30816.4515 | 33.8981 | 857052.1682 | 10.0609 | 11.739 | 9.6195 | 1.3595 | 0.51338 | 0.0005726 | 1.1646 | 1.1646
2008-04-15 | 120000 | 269.3 | 2.5 | 13.69 | 22.58 | 12.79 | 27.74 |  | 10.4662 | 2.0458 | 8.4204 | 30857.449 | 33.9432 | 857002.09 | 10.3008 | 12.0196 | 9.8357 | 1.4154 | 0.53448 | 0.00059532 | 1.2124 | 1.2124
2008-04-15 | 130000 | 268.5 | 2.52 | 13.69 | 22.54 | 12.71 | 27.303 |  | 10.4007 | 2.0621 | 8.3386 | 30802.7856 | 33.8831 | 855483.9286 | 10.1386 | 11.8513 | 9.698 | 1.3594 | 0.51336 | 0.00057179 | 1.1624 | 1.1624
2008-04-15 | 140000 | 267.9 | 2.52 | 13.69 | 22.54 | 12.74 | 27.341 |  | 10.4252 | 2.0621 | 8.3631 | 30802.7856 | 33.8831 | 855483.9286 | 10.1527 | 11.8677 | 9.7115 | 1.3484 | 0.50918 | 0.00056714 | 1.153 | 1.153
2008-04-15 | 150000 | 268.1 | 2.52 | 13.69 | 22.52 | 12.59 | 27.512 |  | 10.3025 | 2.0621 | 8.2404 | 30775.454 | 33.853 | 854724.8479 | 10.2162 | 11.9526 | 9.7809 | 1.5405 | 0.58175 | 0.00064797 | 1.3161 | 1.3161
2008-04-15 | 160000 | 268 | 2.52 | 13.69 | 22.53 | 12.56 | 27.569 |  | 10.2779 | 2.0621 | 8.2158 | 30789.1198 | 33.868 | 855104.3883 | 10.2373 | 11.972 | 9.7968 | 1.581 | 0.59703 | 0.00066499 | 1.3513 | 1.3513
2008-04-15 | 170000 | 268.1 | 2.51 | 13.7 | 22.54 | 12.63 | 27.702 |  | 10.3496 | 2.0568 | 8.2928 | 30802.7856 | 33.8831 | 856672.1007 | 10.2867 | 12.0078 | 9.8397 | 1.5469 | 0.58416 | 0.00065156 | 1.3246 | 1.3246
2008-04-15 | 180000 | 268.7 | 2.51 | 13.7 | 22.54 | 12.56 | 27.664 |  | 10.2922 | 2.0568 | 8.2354 | 30802.7856 | 33.8831 | 856672.1007 | 10.2726 | 11.9913 | 9.8262 | 1.5908 | 0.60073 | 0.00067003 | 1.3622 | 1.3622
2008-04-15 | 190000 | 268.6 | 2.52 | 13.7 | 22.54 | 12.59 | 27.664 |  | 10.3168 | 2.065 | 8.2518 | 30802.7856 | 33.8831 | 856672.1007 | 10.2726 | 11.9913 | 9.8262 | 1.5744 | 0.59454 | 0.00066313 | 1.3481 | 1.3481
2008-04-15 | 200000 | 267.7 | 2.5 | 13.7 | 22.5 | 12.5 | 27.531 |  | 10.2431 | 2.0486 | 8.1944 | 30748.1223 | 33.8229 | 855151.8308 | 10.2232 | 11.9549 | 9.7963 | 1.6019 | 0.60493 | 0.00067472 | 1.3693 | 1.3693
2008-04-15 | 210000 | 188.7 | 2.47 | 13.91 | 16.68 | 8.09 | 9.937 |  | 6.8285 | 2.0848 | 4.7436 | 22794.608 | 25.0741 | 652998.3422 | 3.69 | 5.6508 | 4.7696 | 0.025987 | 0.0098133 | 1.1274e-05 | 0.016962 | 0.016962
2008-04-15 | 220000 | 192.7 | 2.43 | 13.93 | 17.03 | 7.76 | 10.374 |  | 6.5687 | 2.057 | 4.5118 | 23272.9121 | 25.6002 | 668613.4028 | 3.8522 | 5.7615 | 4.877 | 0.36527 | 0.13794 | 0.00015893 | 0.24412 | 0.24412
2008-04-15 | 230000 | 191.3 | 2.45 | 13.93 | 16.92 | 7.77 | 10.26 |  | 6.5772 | 2.0739 | 4.5033 | 23122.588 | 25.4348 | 664294.702 | 3.8099 | 5.7352 | 4.8548 | 0.3515 | 0.13274 | 0.00015294 | 0.2334 | 0.2334
2008-04-16 | 0 | 16.2 | 2.45 | 19.53 | 2.17 | 7.38 | 1.691 |  | 31.7825 | 10.5511 | 21.2314 | 2965.4856 | 3.262 | 433443.3805 | 0.62793 | 1.4487 | 6.2389 | -14.9925 | -5.6616 | -0.033187 | -6.4955
2008-04-16 | 10000 | 1.3 | 0 | 20.93 | 0.24 | 0 | 0.19 |  | 0 | 0 | 0 | 327.98 | 0.36078 | -2189188.6869 | 0.070554 | -0.032228 | 6.3382 | 6.3382 | 2.3935 | -0.64071 | -13.8693
2008-04-16 | 20000 | 1.3 | 0 | 20.95 | 0.18 | -0.05 | 0.171 |  | 5.9 | 0 | 5.9 | 245.985 | 0.27058 | -985134.9091 | 0.063498 | -0.064456 | 7.6059 | 1.7059 | 0.64418 | -0.10346 | -1.6797
2008-04-16 | 30000 | 1.3 | 0 | 20.95 | 0.08 | -0.06 | 0.19 |  | 7.08 | 0 | 7.08 | 109.3267 | 0.12026 | -437837.7374 | 0.070554 | -0.16114 | 19.0146 | 11.9346 | 4.5069 | -0.72386 | -5.2231
2008-04-16 | 40000 | 21.4 | 9.67 | 16.92 | 7.16 | 28.85 | 2.85 |  | 42.7676 | 14.3349 | 28.4327 | 9784.7358 | 10.7632 | 492292.4308 | 1.0583 | 2.1497 | 3.1868 | -25.2459 | -9.5336 | -0.019236 | -12.4227
2008-04-16 | 50000 | 106.4 | 8.34 | 15.04 | 12.78 | 26.08 | 17.461 |  | 26.258 | 8.3969 | 17.8611 | 17464.9335 | 19.2114 | 596796.7453 | 6.4839 | 10.8645 | 10.9386 | -6.9225 | -2.6141 | -0.0035825 | -4.1294
2008-04-16 | 60000 | 267.6 | 2.53 | 13.78 | 22.52 | 12.53 | 25.346 |  | 10.383 | 2.0965 | 8.2865 | 30775.454 | 33.853 | 865528.9542 | 9.4119 | 10.8741 | 9.0108 | 0.72433 | 0.27353 | 0.00030851 | 0.62665 | 0.62665
2008-04-16 | 70000 | 269.4 | 2.52 | 13.8 | 22.47 | 12.12 | 25.479 |  | 10.0715 | 2.0941 | 7.9775 | 30707.1248 | 33.7778 | 866039.9612 | 9.4612 | 10.9247 | 9.0783 | 1.1008 | 0.4157 | 0.00047019 | 0.95293 | 0.95293
2008-04-16 | 80000 | 268.1 | 3.55 | 12.23 | 22.44 | 11.72 | 24.833 |  | 7.9755 | 2.4158 | 5.5597 | 30666.1273 | 33.7327 | 708266.9281 | 9.2214 | 13.0196 | 8.8599 | 3.3002 | 1.2463 | 0.0011544 | 2.3364 | 2.3364
2008-04-16 | 90000 | 269.2 | 2.58 | 13.8 | 22.55 | 12.69 | 26.733 |  | 10.5452 | 2.1439 | 8.4013 | 30816.4515 | 33.8981 | 869123.3255 | 9.9269 | 11.4217 | 9.4913 | 1.09 | 0.41163 | 0.00046558 | 0.94695 | 0.94695
2008-04-16 | 100000 | 269.5 | 2.55 | 13.76 | 22.53 | 12.89 | 27.607 |  | 10.6514 | 2.1071 | 8.5443 | 30789.1198 | 33.868 | 863487.7646 | 10.2514 | 11.8721 | 9.8103 | 1.266 | 0.4781 | 0.00053774 | 1.0927 | 1.0927
2008-04-16 | 110000 | 267.9 | 2.55 | 13.77 | 22.54 | 12.91 | 27.531 |  | 10.6829 | 2.1101 | 8.5728 | 30802.7856 | 33.8831 | 865082.6263 | 10.2232 | 11.8176 | 9.779 | 1.2062 | 0.45549 | 0.00051302 | 1.043 | 1.043
2008-04-16 | 120000 | 267.7 | 2.55 | 13.78 | 22.53 | 13 | 27.778 |  | 10.7725 | 2.1131 | 8.6594 | 30789.1198 | 33.868 | 865913.2921 | 10.3149 | 11.9122 | 9.8711 | 1.2117 | 0.45756 | 0.00051608 | 1.0487 | 1.0487
2008-04-16 | 130000 | 266.6 | 2.56 | 13.77 | 22.53 | 12.96 | 27.588 |  | 10.7243 | 2.1184 | 8.6059 | 30789.1198 | 33.868 | 864698.8274 | 10.2444 | 11.8473 | 9.8036 | 1.1977 | 0.45227 | 0.00050941 | 1.0352 | 1.0352
2008-04-16 | 140000 | 265 | 2.55 | 13.77 | 22.5 | 13 | 27.702 |  | 10.7574 | 2.1101 | 8.6473 | 30748.1223 | 33.8229 | 863547.4308 | 10.2867 | 11.9122 | 9.8572 | 1.2099 | 0.4569 | 0.00051462 | 1.0444 | 1.0444
2008-04-16 | 150000 | 264.6 | 2.55 | 13.77 | 22.35 | 13.02 | 27.759 |  | 10.7739 | 2.1101 | 8.6638 | 30543.1348 | 33.5974 | 857790.448 | 10.3079 | 12.0168 | 9.9438 | 1.28 | 0.48335 | 0.0005444 | 1.0974 | 1.0974
2008-04-16 | 160000 | 264.6 | 2.55 | 13.76 | 22.28 | 13.02 | 27.778 |  | 10.7588 | 2.1071 | 8.6517 | 30447.474 | 33.4922 | 853906.2315 | 10.3149 | 12.0797 | 9.9818 | 1.3302 | 0.50231 | 0.00056496 | 1.1353 | 1.1353
2008-04-16 | 170000 | 264.5 | 2.55 | 13.75 | 22.31 | 12.97 | 27.626 |  | 10.7025 | 2.1042 | 8.5983 | 30488.4715 | 33.5373 | 853860.1329 | 10.2585 | 12.0143 | 9.9139 | 1.3155 | 0.49679 | 0.00055798 | 1.1228 | 1.1228
2008-04-16 | 180000 | 264.9 | 2.56 | 13.75 | 22.28 | 12.95 | 27.512 |  | 10.686 | 2.1124 | 8.5736 | 30447.474 | 33.4922 | 852711.9571 | 10.2162 | 11.9808 | 9.8862 | 1.3127 | 0.49571 | 0.00055676 | 1.1188 | 1.1188
2008-04-16 | 190000 | 265.8 | 2.56 | 13.74 | 22.33 | 12.93 | 27.436 |  | 10.6546 | 2.1095 | 8.5451 | 30515.8032 | 33.5674 | 853431.9724 | 10.1879 | 11.9376 | 9.8369 | 1.2918 | 0.4878 | 0.00054712 | 1.1019 | 1.1019
2008-04-16 | 200000 | 266.3 | 2.56 | 13.73 | 22.44 | 12.94 | 27.474 |  | 10.648 | 2.1066 | 8.5414 | 30666.1273 | 33.7327 | 856439.9256 | 10.2021 | 11.9122 | 9.8022 | 1.2608 | 0.47611 | 0.00053326 | 1.0793 | 1.0793
2008-04-16 | 210000 | 266.4 | 2.57 | 13.73 | 22.53 | 12.99 | 27.683 |  | 10.6891 | 2.1148 | 8.5743 | 30789.1198 | 33.868 | 859874.8451 | 10.2797 | 11.9548 | 9.8373 | 1.263 | 0.47694 | 0.00053419 | 1.0855 | 1.0855
2008-04-16 | 220000 | 267.5 | 2.56 | 13.73 | 22.54 | 13.01 | 27.873 |  | 10.7056 | 2.1066 | 8.599 | 30802.7856 | 33.8831 | 860256.5028 | 10.3502 | 12.0315 | 9.9004 | 1.3014 | 0.49145 | 0.00055044 | 1.119 | 1.119
2008-04-16 | 230000 | 206.8 | 2.55 | 13.87 | 18.03 | 9.7 | 15.105 |  | 8.1408 | 2.1401 | 6.0007 | 24639.4953 | 27.1034 | 701832.7174 | 5.609 | 7.992 | 6.7073 | 0.70662 | 0.26684 | 0.00030482 | 0.4957 | 0.4957
2008-04-17 | 0 | 193.1 | 2.44 | 13.93 | 17.08 | 7.87 | 10.602 |  | 6.6618 | 2.0654 | 4.5964 | 23341.2413 | 25.6754 | 670576.4486 | 3.9369 | 5.8709 | 4.9696 | 0.37322 | 0.14094 | 0.00016239 | 0.25016 | 0.25016
2008-04-17 | 10000 | 193.8 | 2.49 | 13.94 | 17.17 | 7.81 | 10.412 |  | 6.6205 | 2.1108 | 4.5098 | 23464.2338 | 25.8107 | 675078.4798 | 3.8663 | 5.7272 | 4.855 | 0.34522 | 0.13037 | 0.00015042 | 0.23295 | 0.23295
2008-04-17 | 20000 | 192.6 | 2.52 | 13.93 | 17.1 | 7.88 | 10.45 |  | 6.6703 | 2.1331 | 4.5372 | 23368.573 | 25.7054 | 671361.6669 | 3.8804 | 5.78 | 4.8927 | 0.3555 | 0.13425 | 0.00015468 | 0.23856 | 0.23856
2008-04-17 | 30000 | 192.1 | 2.46 | 13.92 | 17.15 | 7.93 | 10.811 |  | 6.703 | 2.0794 | 4.6236 | 23436.9021 | 25.7806 | 672360.0641 | 4.0145 | 5.9708 | 5.0469 | 0.42328 | 0.15984 | 0.0001839 | 0.28447 | 0.28447
2008-04-17 | 40000 | 192.9 | 2.5 | 13.93 | 17.19 | 7.92 | 10.773 |  | 6.7042 | 2.1162 | 4.5879 | 23491.5654 | 25.8407 | 674895.1493 | 4.0004 | 5.9274 | 5.0175 | 0.42953 | 0.1622 | 0.00018689 | 0.28976 | 0.28976
2008-04-17 | 50000 | 267.4 | 2.55 | 13.71 | 22.79 | 12.57 | 27.094 |  | 10.3147 | 2.0925 | 8.2223 | 31144.4314 | 34.2589 | 867378.4801 | 10.0609 | 11.5993 | 9.5182 | 1.2959 | 0.48938 | 0.00054659 | 1.1235 | 1.1235
2008-04-17 | 60000 | 268.7 | 2.57 | 13.7 | 22.82 | 12.68 | 27.018 |  | 10.3906 | 2.106 | 8.2846 | 31185.4289 | 34.304 | 867313.9902 | 10.0327 | 11.5676 | 9.479 | 1.1944 | 0.45104 | 0.00050308 | 1.0355 | 1.0355
2008-04-17 | 70000 | 268.7 | 2.77 | 13.42 | 22.82 | 12.69 | 26.98 |  | 10.0095 | 2.1849 | 7.8246 | 31185.4289 | 34.304 | 834847.6911 | 10.0186 | 12.0005 | 9.4657 | 1.6411 | 0.61971 | 0.00066534 | 1.3694 | 1.3694
2008-04-17 | 80000 | 269.3 | 3.33 | 12.48 | 22.8 | 12.7 | 27.075 |  | 8.899 | 2.3334 | 6.5657 | 31158.0973 | 34.2739 | 740996.1707 | 10.0539 | 13.5681 | 9.5073 | 2.9416 | 1.1109 | 0.0010595 | 2.1788 | 2.1788
2008-04-17 | 90000 | 268.2 | 2.57 | 13.72 | 22.62 | 12.76 | 27.075 |  | 10.4852 | 2.1118 | 8.3734 | 30912.1123 | 34.0033 | 862107.3833 | 10.0539 | 11.662 | 9.583 | 1.2096 | 0.45677 | 0.00051089 | 1.0423 | 1.0423
2008-04-17 | 100000 | 267.4 | 2.58 | 13.7 | 22.55 | 12.61 | 27.303 |  | 10.3332 | 2.1142 | 8.219 | 30816.4515 | 33.8981 | 857052.1682 | 10.1386 | 11.8296 | 9.6937 | 1.4746 | 0.55687 | 0.00062112 | 1.2633 | 1.2633
2008-04-17 | 110000 | 266.4 | 2.58 | 13.7 | 22.54 | 12.69 | 27.455 |  | 10.3987 | 2.1142 | 8.2846 | 30802.7856 | 33.8831 | 856672.1007 | 10.195 | 11.9007 | 9.752 | 1.4674 | 0.55413 | 0.00061806 | 1.2565 | 1.2565
2008-04-17 | 120000 | 265.7 | 2.57 | 13.7 | 22.47 | 12.78 | 27.702 |  | 10.4725 | 2.106 | 8.3665 | 30707.1248 | 33.7778 | 854011.6284 | 10.2867 | 12.0452 | 9.8704 | 1.5038 | 0.56789 | 0.00063341 | 1.2837 | 1.2837
2008-04-17 | 130000 | 265.3 | 2.57 | 13.7 | 22.44 | 12.73 | 27.493 |  | 10.4315 | 2.106 | 8.3256 | 30666.1273 | 33.7327 | 852871.4259 | 10.2091 | 11.9703 | 9.809 | 1.4834 | 0.56019 | 0.00062481 | 1.2646 | 1.2646
2008-04-17 | 140000 | 264.7 | 2.58 | 13.7 | 22.34 | 12.71 | 27.398 |  | 10.4151 | 2.1142 | 8.301 | 30529.469 | 33.5824 | 849070.7511 | 10.1738 | 11.9823 | 9.8188 | 1.5179 | 0.57319 | 0.00063932 | 1.2882 | 1.2882
2008-04-17 | 150000 | 264.3 | 2.57 | 13.7 | 22.28 | 12.68 | 27.36 |  | 10.3906 | 2.106 | 8.2846 | 30447.474 | 33.4922 | 846790.3462 | 10.1597 | 11.9979 | 9.8316 | 1.547 | 0.58421 | 0.00065161 | 1.3094 | 1.3094
2008-04-17 | 160000 | 264.4 | 2.58 | 13.7 | 22.28 | 12.72 | 27.474 |  | 10.4233 | 2.1142 | 8.3092 | 30447.474 | 33.4922 | 846790.3462 | 10.2021 | 12.0479 | 9.8726 | 1.5634 | 0.5904 | 0.00065851 | 1.3233 | 1.3233
2008-04-17 | 170000 | 265.3 | 2.56 | 13.7 | 22.28 | 12.71 | 27.417 |  | 10.4151 | 2.0978 | 8.3174 | 30447.474 | 33.4922 | 846790.3462 | 10.1809 | 12.0229 | 9.8521 | 1.5348 | 0.57957 | 0.00064643 | 1.299 | 1.299
2008-04-17 | 180000 | 266.4 | 2.56 | 13.7 | 22.45 | 12.63 | 27.227 |  | 10.3496 | 2.0978 | 8.2518 | 30679.7932 | 33.7478 | 853251.4934 | 10.1103 | 11.8492 | 9.7097 | 1.4579 | 0.55056 | 0.00061408 | 1.2434 | 1.2434
2008-04-17 | 190000 | 266.9 | 2.58 | 13.69 | 22.54 | 12.62 | 27.189 |  | 10.327 | 2.1112 | 8.2158 | 30802.7856 | 33.8831 | 855483.9286 | 10.0962 | 11.8018 | 9.6575 | 1.4417 | 0.54442 | 0.00060638 | 1.2328 | 1.2328
2008-04-17 | 200000 | 267.4 | 2.57 | 13.68 | 22.54 | 12.64 | 27.227 |  | 10.3291 | 2.1001 | 8.2289 | 30802.7856 | 33.8831 | 854299.0478 | 10.1103 | 11.8347 | 9.671 | 1.442 | 0.54456 | 0.0006057 | 1.2314 | 1.2314
2008-04-17 | 210000 | 268.2 | 2.58 | 13.68 | 22.54 | 12.61 | 27.113 |  | 10.3046 | 2.1083 | 8.1963 | 30802.7856 | 33.8831 | 854299.0478 | 10.068 | 11.7851 | 9.6305 | 1.4342 | 0.54161 | 0.00060242 | 1.2247 | 1.2247
2008-04-17 | 220000 | 267.8 | 2.57 | 13.68 | 22.49 | 12.52 | 27.075 |  | 10.231 | 2.1001 | 8.1309 | 30734.4565 | 33.8079 | 852403.9745 | 10.0539 | 11.7948 | 9.6384 | 1.5075 | 0.56927 | 0.00063319 | 1.2844 | 1.2844
2008-04-17 | 230000 | 189.1 | 2.55 | 13.88 | 16.64 | 8.13 | 9.747 |  | 6.8329 | 2.1432 | 4.6897 | 22739.9447 | 25.0139 | 648648.4998 | 3.6194 | 5.5799 | 4.6897 | -7.433e-05 | -2.8069e-05 | -3.211e-08 | -4.8192e-05
2008-04-18 | 0 | 192.3 | 2.5 | 13.89 | 16.99 | 7.93 | 10.412 |  | 6.6743 | 2.1041 | 4.5702 | 23218.2488 | 25.5401 | 663236.7295 | 3.8663 | 5.8295 | 4.9064 | 0.33624 | 0.12698 | 0.00014546 | 0.22291 | 0.22291
2008-04-18 | 10000 | 192.2 | 2.51 | 13.89 | 16.96 | 7.99 | 10.469 |  | 6.7248 | 2.1126 | 4.6123 | 23177.2513 | 25.495 | 662065.6229 | 3.8875 | 5.8718 | 4.942 | 0.32975 | 0.12452 | 0.00014265 | 0.21821 | 0.21821
2008-04-18 | 20000 | 192.4 | 2.5 | 13.89 | 16.99 | 8 | 10.507 |  | 6.7332 | 2.1041 | 4.6291 | 23218.2488 | 25.5401 | 663236.7295 | 3.9016 | 5.8827 | 4.9512 | 0.32209 | 0.12163 | 0.00013934 | 0.21353 | 0.21353
2008-04-18 | 30000 | 192.6 | 2.52 | 13.88 | 16.94 | 7.99 | 10.488 |  | 6.7152 | 2.1179 | 4.5973 | 23149.9196 | 25.4649 | 660342.8838 | 3.8946 | 5.8978 | 4.9568 | 0.35953 | 0.13577 | 0.00015532 | 0.23731 | 0.23731
2008-04-18 | 40000 | 192.3 | 2.51 | 13.88 | 16.96 | 8 | 10.526 |  | 6.7236 | 2.1095 | 4.6141 | 23177.2513 | 25.495 | 661122.5094 | 3.9087 | 5.9122 | 4.9689 | 0.35482 | 0.13399 | 0.00015328 | 0.23447 | 0.23447
2008-04-18 | 50000 | 265.9 | 2.56 | 13.68 | 22.4 | 12.29 | 26.98 |  | 10.0431 | 2.092 | 7.9511 | 30611.464 | 33.6726 | 848992.8426 | 10.0186 | 11.8006 | 9.6431 | 1.692 | 0.63896 | 0.0007107 | 1.4359 | 1.4359
2008-04-18 | 60000 | 266.3 | 2.5 | 13.75 | 22.33 | 11.3 | 24.054 |  | 9.3245 | 2.0629 | 7.2615 | 30515.8032 | 33.5674 | 854625.5835 | 8.9321 | 10.4515 | 8.6243 | 1.3627 | 0.51461 | 0.000578 | 1.1641 | 1.1641
2008-04-18 | 70000 | 266.9 | 3.65 | 12.16 | 22.43 | 11.66 | 23.788 |  | 7.8712 | 2.464 | 5.4072 | 30652.4615 | 33.7177 | 702281.2106 | 8.8333 | 12.578 | 8.4909 | 3.0837 | 1.1645 | 0.00107 | 2.1646 | 2.1646
2008-04-18 | 80000 | 267.1 | 2.44 | 13.77 | 22.42 | 11.86 | 25.441 |  | 9.814 | 2.0191 | 7.795 | 30638.7957 | 33.7027 | 860477.04 | 9.4471 | 10.9789 | 9.085 | 1.29 | 0.48715 | 0.00054868 | 1.1095 | 1.1095
2008-04-18 | 90000 | 266.4 | 2.54 | 13.74 | 22.36 | 11.78 | 24.225 |  | 9.707 | 2.093 | 7.614 | 30556.8007 | 33.6125 | 854578.5447 | 8.9956 | 10.5263 | 8.6739 | 1.06 | 0.40028 | 0.00044895 | 0.90543 | 0.90543
2008-04-18 | 100000 | 267.1 | 2.48 | 13.73 | 22.41 | 11.66 | 24.51 |  | 9.5947 | 2.0407 | 7.554 | 30625.1298 | 33.6876 | 855294.9525 | 9.1014 | 10.6413 | 8.7564 | 1.2024 | 0.45408 | 0.00050858 | 1.028 | 1.028
2008-04-18 | 110000 | 267.3 | 2.41 | 13.69 | 22.47 | 12.11 | 26.486 |  | 9.9097 | 1.9721 | 7.9376 | 30707.1248 | 33.7778 | 852827.1462 | 9.8352 | 11.5324 | 9.4371 | 1.4995 | 0.56626 | 0.00063071 | 1.2782 | 1.2782
2008-04-18 | 120000 | 268 | 2.58 | 13.67 | 22.47 | 12.54 | 26.258 |  | 10.2332 | 2.1054 | 8.1278 | 30707.1248 | 33.7778 | 850468.0117 | 9.7505 | 11.4649 | 9.3558 | 1.228 | 0.46375 | 0.0005151 | 1.0439 | 1.0439
2008-04-18 | 130000 | 267.3 | 2.61 | 13.67 | 22.48 | 12.64 | 26.353 |  | 10.3148 | 2.1299 | 8.1849 | 30720.7907 | 33.7929 | 850846.5021 | 9.7858 | 11.5012 | 9.3855 | 1.2006 | 0.45338 | 0.00050359 | 1.0211 | 1.0211
2008-04-18 | 140000 | 268.5 | 2.58 | 13.65 | 22.52 | 12.54 | 26.885 |  | 10.205 | 2.0996 | 8.1054 | 30775.454 | 33.853 | 850009.1246 | 9.9833 | 11.745 | 9.558 | 1.4526 | 0.54855 | 0.00060761 | 1.2342 | 1.2342
2008-04-18 | 150000 | 268.1 | 2.59 | 13.65 | 22.49 | 12.59 | 26.847 |  | 10.2457 | 2.1077 | 8.1379 | 30734.4565 | 33.8079 | 848876.7857 | 9.9692 | 11.744 | 9.5572 | 1.4193 | 0.53596 | 0.00059367 | 1.2042 | 1.2042
2008-04-18 | 160000 | 268.7 | 2.59 | 13.64 | 22.54 | 12.49 | 26.695 |  | 10.1503 | 2.1048 | 8.0455 | 30802.7856 | 33.8831 | 849592.166 | 9.9128 | 11.6677 | 9.482 | 1.4366 | 0.54249 | 0.00060007 | 1.2199 | 1.2199
2008-04-18 | 170000 | 268.6 | 2.6 | 13.63 | 22.53 | 12.49 | 26.6 |  | 10.1363 | 2.11 | 8.0263 | 30789.1198 | 33.868 | 848047.1306 | 9.8775 | 11.6474 | 9.4525 | 1.4262 | 0.53857 | 0.00059492 | 1.2089 | 1.2089
2008-04-18 | 180000 | 269.2 | 2.6 | 13.62 | 22.55 | 12.45 | 26.562 |  | 10.09 | 2.1071 | 7.9828 | 30816.4515 | 33.8981 | 847634.0125 | 9.8634 | 11.6364 | 9.4306 | 1.4478 | 0.54672 | 0.00060309 | 1.2266 | 1.2266
2008-04-18 | 190000 | 269.1 | 2.61 | 13.62 | 22.54 | 12.43 | 26.486 |  | 10.0738 | 2.1152 | 7.9585 | 30802.7856 | 33.8831 | 847258.1216 | 9.8352 | 11.6082 | 9.4078 | 1.4493 | 0.54729 | 0.00060372 | 1.2273 | 1.2273
2008-04-18 | 200000 | 269.7 | 2.6 | 13.62 | 22.63 | 12.39 | 26.505 |  | 10.0413 | 2.1071 | 7.9342 | 30925.7781 | 34.0184 | 850641.1398 | 9.8422 | 11.5704 | 9.3771 | 1.4429 | 0.54488 | 0.00060106 | 1.2268 | 1.2268
2008-04-18 | 210000 | 270.5 | 2.61 | 13.61 | 22.79 | 12.35 | 26.315 |  | 9.9952 | 2.1123 | 7.8829 | 31144.4314 | 34.2589 | 855480.2842 | 9.7717 | 11.4224 | 9.2445 | 1.3617 | 0.5142 | 0.00056644 | 1.1643 | 1.1643
2008-04-18 | 220000 | 270.1 | 2.61 | 13.61 | 22.75 | 12.55 | 26.353 |  | 10.1571 | 2.1123 | 8.0447 | 31089.7681 | 34.1987 | 853978.783 | 9.7858 | 11.4591 | 9.2741 | 1.2294 | 0.46426 | 0.00051143 | 1.0494 | 1.0494
2008-04-18 | 230000 | 269.8 | 2.61 | 13.6 | 22.63 | 12.53 | 26.258 |  | 10.127 | 2.1095 | 8.0175 | 30925.7781 | 34.0184 | 848310.6162 | 9.7505 | 11.494 | 9.2897 | 1.2722 | 0.48041 | 0.00052849 | 1.0787 | 1.0787
2008-04-19 | 0 | 270 | 2.61 | 13.6 | 22.66 | 12.48 | 26.239 |  | 10.0866 | 2.1095 | 7.9771 | 30966.7756 | 34.0635 | 849435.1994 | 9.7435 | 11.4705 | 9.2707 | 1.2936 | 0.48849 | 0.00053738 | 1.0983 | 1.0983
2008-04-19 | 10000 | 269.9 | 2.61 | 13.58 | 22.66 | 12.36 | 25.821 |  | 9.9623 | 2.1037 | 7.8586 | 30966.7756 | 34.0635 | 847114.3382 | 9.5882 | 11.3187 | 9.123 | 1.2644 | 0.47747 | 0.00052383 | 1.0706 | 1.0706
2008-04-19 | 20000 | 269.7 | 2.61 | 13.57 | 22.62 | 12.35 | 25.821 |  | 9.9407 | 2.1008 | 7.8398 | 30912.1123 | 34.0033 | 844465.3495 | 9.5882 | 11.3542 | 9.1391 | 1.2993 | 0.49065 | 0.00053755 | 1.0967 | 1.0967
2008-04-19 | 30000 | 269.8 | 2.62 | 13.57 | 22.64 | 12.29 | 25.612 |  | 9.8924 | 2.1089 | 7.7835 | 30939.444 | 34.0334 | 845212.0033 | 9.5106 | 11.2524 | 9.0572 | 1.2737 | 0.48097 | 0.00052695 | 1.076 | 1.076
2008-04-19 | 40000 | 269.3 | 2.63 | 13.56 | 22.55 | 12.45 | 25.878 |  | 10.0075 | 2.114 | 7.8935 | 30816.4515 | 33.8981 | 840705.1241 | 9.6094 | 11.4302 | 9.1877 | 1.2943 | 0.48876 | 0.00053475 | 1.0876 | 1.0876
2008-04-19 | 50000 | 269.6 | 2.62 | 13.55 | 22.56 | 12.39 | 25.878 |  | 9.9457 | 2.1031 | 7.8426 | 30830.1173 | 33.9131 | 839933.6186 | 9.6094 | 11.4407 | 9.1837 | 1.3411 | 0.50643 | 0.00055333 | 1.1259 | 1.1259
2008-04-19 | 60000 | 269.7 | 2.63 | 13.56 | 22.56 | 12.32 | 25.726 |  | 9.903 | 2.114 | 7.789 | 30830.1173 | 33.9131 | 841077.9424 | 9.553 | 11.358 | 9.1297 | 1.3408 | 0.50631 | 0.00055395 | 1.1272 | 1.1272
2008-04-19 | 70000 | 268.9 | 2.63 | 13.56 | 22.54 | 12.38 | 25.878 |  | 9.9512 | 2.114 | 7.8372 | 30802.7856 | 33.8831 | 840332.3059 | 9.6094 | 11.4352 | 9.1918 | 1.3546 | 0.51155 | 0.00055968 | 1.1378 | 1.1378
2008-04-19 | 80000 | 268.8 | 3.18 | 12.05 | 22.54 | 12.45 | 29.165 |  | 8.3 | 2.12 | 6.18 | 30802.7856 | 33.8831 | 696953.5735 | 10.83 | 15.539 | 10.3594 | 4.1794 | 1.5783 | 0.0014321 | 2.9115 | 2.9115
2008-04-19 | 90000 | 268 | 2.64 | 13.56 | 22.51 | 12.58 | 26.22 |  | 10.112 | 2.1221 | 7.9899 | 30761.7881 | 33.838 | 839213.8512 | 9.7364 | 11.6018 | 9.3257 | 1.3358 | 0.50443 | 0.0005519 | 1.1205 | 1.1205
2008-04-19 | 100000 | 267.2 | 2.63 | 13.55 | 22.38 | 12.79 | 26.847 |  | 10.2668 | 2.1112 | 8.1556 | 30584.1323 | 33.6425 | 833232.0206 | 9.9692 | 11.9645 | 9.6042 | 1.4485 | 0.54701 | 0.00059767 | 1.2064 | 1.2064
2008-04-19 | 110000 | 267 | 2.62 | 13.55 | 22.32 | 12.74 | 26.771 |  | 10.2267 | 2.1031 | 8.1235 | 30502.1373 | 33.5524 | 830998.1546 | 9.941 | 11.9627 | 9.6027 | 1.4792 | 0.55859 | 0.00061032 | 1.2287 | 1.2287
2008-04-19 | 120000 | 267.6 | 2.57 | 13.59 | 22.45 | 11.98 | 24.871 |  | 9.6692 | 2.0743 | 7.5949 | 30679.7932 | 33.7478 | 840411.8677 | 9.2355 | 10.9892 | 8.8695 | 1.2746 | 0.48133 | 0.00052878 | 1.0707 | 1.0707
2008-04-19 | 130000 | 267.2 | 2.61 | 13.58 | 22.45 | 12.16 | 25.346 |  | 9.8011 | 2.1037 | 7.6974 | 30679.7932 | 33.7478 | 839263.764 | 9.4119 | 11.2144 | 9.0389 | 1.3415 | 0.50661 | 0.00055579 | 1.1254 | 1.1254
2008-04-19 | 140000 | 267.5 | 2.68 | 13.55 | 22.47 | 12.59 | 26.163 |  | 10.1063 | 2.1513 | 7.955 | 30707.1248 | 33.7778 | 836582.8196 | 9.7152 | 11.613 | 9.322 | 1.367 | 0.51623 | 0.00056404 | 1.1431 | 1.1431
2008-04-19 | 150000 | 268.6 | 2.61 | 13.55 | 22.54 | 12.45 | 25.992 |  | 9.9939 | 2.0951 | 7.8988 | 30802.7856 | 33.8831 | 839188.9966 | 9.6517 | 11.5013 | 9.2323 | 1.3335 | 0.50358 | 0.00055022 | 1.1186 | 1.1186
2008-04-19 | 160000 | 268.2 | 2.63 | 13.55 | 22.53 | 12.53 | 25.992 |  | 10.0581 | 2.1112 | 7.9469 | 30789.1198 | 33.868 | 838816.6856 | 9.6517 | 11.5064 | 9.2364 | 1.2895 | 0.48694 | 0.00053204 | 1.0811 | 1.0811
2008-04-19 | 170000 | 267.7 | 2.63 | 13.55 | 22.5 | 12.5 | 25.745 |  | 10.034 | 2.1112 | 7.9229 | 30748.1223 | 33.8229 | 837699.7526 | 9.56 | 11.4122 | 9.1608 | 1.238 | 0.4675 | 0.00051079 | 1.0366 | 1.0366
2008-04-19 | 180000 | 267.4 | 2.62 | 13.55 | 22.46 | 12.49 | 25.84 |  | 10.026 | 2.1031 | 7.9229 | 30693.459 | 33.7628 | 836210.5086 | 9.5953 | 11.4747 | 9.211 | 1.2882 | 0.48645 | 0.00053149 | 1.0767 | 1.0767
2008-04-19 | 190000 | 267.3 | 2.63 | 13.55 | 22.44 | 12.51 | 25.802 |  | 10.042 | 2.1112 | 7.9309 | 30666.1273 | 33.7327 | 835465.8866 | 9.5812 | 11.4681 | 9.2057 | 1.2748 | 0.4814 | 0.00052598 | 1.0646 | 1.0646
2008-04-19 | 200000 | 266.3 | 2.56 | 13.56 | 22.36 | 11.89 | 25.593 |  | 9.5574 | 2.0578 | 7.4996 | 30556.8007 | 33.6125 | 833621.5776 | 9.5036 | 11.4003 | 9.1638 | 1.6642 | 0.62844 | 0.00068758 | 1.3867 | 1.3867
2008-04-19 | 210000 | 190.5 | 2.41 | 13.77 | 16.79 | 7.7 | 10.355 |  | 6.3717 | 1.9942 | 4.3774 | 22944.9322 | 25.2394 | 644398.2828 | 3.8452 | 5.9671 | 4.9377 | 0.56027 | 0.21158 | 0.0002383 | 0.36088 | 0.36088
2008-04-19 | 220000 | 192.2 | 2.47 | 13.76 | 17.01 | 7.64 | 10.697 |  | 6.3132 | 2.041 | 4.2721 | 23245.5805 | 25.5701 | 651927.5134 | 3.9722 | 6.093 | 5.0348 | 0.76267 | 0.28801 | 0.00032393 | 0.49698 | 0.49698
2008-04-19 | 230000 | 193.3 | 2.5 | 13.76 | 17.12 | 7.6 | 10.678 |  | 6.2801 | 2.0658 | 4.2143 | 23395.9046 | 25.7355 | 656143.3879 | 3.9651 | 6.0431 | 4.9936 | 0.77928 | 0.29428 | 0.00033099 | 0.51109 | 0.51109
2008-04-20 | 0 | 191.6 | 2.49 | 13.77 | 17 | 7.66 | 10.659 |  | 6.3386 | 2.0604 | 4.2781 | 23231.9146 | 25.5551 | 652458.0589 | 3.9581 | 6.0664 | 5.0199 | 0.74175 | 0.28011 | 0.00031549 | 0.48374 | 0.48374
2008-04-20 | 10000 | 13.9 | 2.1 | 19.49 | 1.85 | 5.25 | 0.494 |  | 21.9681 | 8.7872 | 13.1809 | 2528.1789 | 2.781 | 359042.4708 | 0.18344 | 0.51091 | 2.1379 | -11.043 | -4.1702 | -0.023751 | -3.9631
2008-04-20 | 20000 | 1.3 | 0 | 20.68 | 0.26 | -0.01 | 0.152 |  | -0.26818 | 0 | -0.26818 | 355.3116 | 0.39084 | 323402.8742 | 0.056443 | 0.17453 | 4.6805 | 4.9487 | 1.8688 | 0.068216 | 1.5997
2008-04-20 | 30000 | 1.3 | 0 | 20.69 | 0.26 | -0.06 | 0.171 |  | -1.6857 | 0 | -1.6857 | 355.3116 | 0.39084 | 338803.0111 | 0.063498 | 0.18742 | 5.2656 | 6.9513 | 2.625 | 0.10038 | 2.3541
2008-04-20 | 40000 | 1.3 | 0 | 20.63 | 0.23 | -0.06 | 0.152 |  | -1.3111 | 0 | -1.3111 | 314.3141 | 0.34575 | 233108.0546 | 0.056443 | 0.24213 | 5.291 | 6.6021 | 2.4932 | 0.074155 | 1.5383
2008-04-20 | 50000 | 1.3 | 0 | 20.71 | 0.15 | -0.07 | 0.171 |  | -2.1737 | 0 | -2.1737 | 204.9875 | 0.22549 | 216038.3573 | 0.063498 | 0.29392 | 9.127 | 11.3007 | 4.2675 | 0.18037 | 2.4403
2008-04-20 | 60000 | 2.2 | 1.11 | 20.32 | 0.8 | 3 | 0.171 |  | 30.5172 | 11.2914 | 19.2259 | 1093.2666 | 1.2026 | 377446.3253 | 0.063498 | 0.16823 | 1.7113 | -17.5145 | -6.614 | -0.091577 | -6.6078
2008-04-20 | 70000 | 12.3 | 10.26 | 17.25 | 6.21 | 30.01 | 0.171 |  | 48.5093 | 16.5847 | 31.9247 | 8486.4818 | 9.3351 | 465577.457 | 0.063498 | 0.13639 | 0.22046 | -31.7042 | -11.9725 | -0.026342 | -14.7541
2008-04-20 | 80000 | 1.8 | 1.18 | 20.4 | 0.5 | 3.26 | 0.152 |  | 38.468 | 13.924 | 24.544 | 683.2916 | 0.75162 | 273648.5859 | 0.056443 | 0.20626 | 2.4339 | -22.1101 | -8.3495 | -0.1341 | -6.0477
2008-04-20 | 90000 | 1.3 | 0.02 | 20.74 | 0.04 | 2.05 | 0.171 |  | 75.5937 | 0.7375 | 74.8562 | 54.6633 | 0.06013 | 68412.1465 | 0.063498 | 0.92817 | 34.2264 | -40.6299 | -15.3431 | -0.77009 | -2.7783
2008-04-20 | 100000 | 16.9 | 9.78 | 17.11 | 6.37 | 28.03 | 0.171 |  | 43.6351 | 15.2248 | 28.4103 | 8705.1351 | 9.5756 | 459931.7921 | 0.063498 | 0.13806 | 0.21492 | -28.1954 | -10.6474 | -0.022561 | -12.9621
2008-04-20 | 110000 | 65.6 | 8.37 | 15.39 | 10.97 | 25.1 | 6.897 |  | 26.8766 | 8.9624 | 17.9142 | 14991.4179 | 16.4906 | 544813.9722 | 2.5611 | 4.7009 | 5.0336 | -12.8806 | -4.8641 | -0.0070893 | -7.0144
2008-04-20 | 120000 | 209.5 | 4.73 | 12.21 | 18.82 | 14.93 | 29.469 |  | 10.1366 | 3.2114 | 6.9252 | 25719.0961 | 28.291 | 592642.8522 | 10.9429 | 18.4645 | 12.5363 | 5.6111 | 2.1189 | 0.0019582 | 3.3239 | 3.3239
2008-04-20 | 130000 | 263.3 | 2.21 | 13.86 | 22.12 | 11.84 | 25.707 |  | 9.9227 | 1.8521 | 8.0706 | 30228.8207 | 33.2517 | 859816.2953 | 9.5459 | 11.1023 | 9.3045 | 1.2339 | 0.46594 | 0.00053151 | 1.0604 | 1.0604
2008-04-20 | 140000 | 262.3 | 2.24 | 13.77 | 22.02 | 10.73 | 24.035 |  | 8.879 | 1.8536 | 7.0254 | 30092.1624 | 33.1014 | 845125.0856 | 8.925 | 10.5606 | 8.7388 | 1.7134 | 0.64703 | 0.00072877 | 1.4474 | 1.4474
2008-04-20 | 150000 | 265 | 2.41 | 13.7 | 22.12 | 11.59 | 25.422 |  | 9.4974 | 1.9749 | 7.5225 | 30228.8207 | 33.2517 | 840709.2666 | 9.4401 | 11.2287 | 9.2013 | 1.6788 | 0.63397 | 0.00070711 | 1.4107 | 1.4107
2008-04-20 | 160000 | 266.2 | 2.58 | 13.66 | 22.27 | 11.96 | 25.612 |  | 9.7464 | 2.1025 | 7.6439 | 30433.8082 | 33.4772 | 841733.9789 | 9.5106 | 11.2989 | 9.2076 | 1.5637 | 0.5905 | 0.00065499 | 1.3156 | 1.3156
2008-04-20 | 170000 | 195.9 | 2.5 | 13.81 | 17.19 | 8.28 | 12.084 |  | 6.8903 | 2.0804 | 4.8099 | 23491.5654 | 25.8407 | 663472.3824 | 4.4872 | 6.7632 | 5.6281 | 0.8182 | 0.30898 | 0.00034997 | 0.54261 | 0.54261
2008-04-20 | 180000 | 267.5 | 2.44 | 13.64 | 22.53 | 12.19 | 26.999 |  | 9.9065 | 1.9829 | 7.9236 | 30789.1198 | 33.868 | 849215.2396 | 10.0257 | 11.8058 | 9.5943 | 1.6707 | 0.63091 | 0.00069788 | 1.4181 | 1.4181
2008-04-20 | 190000 | 268 | 2.5 | 13.67 | 22.45 | 11.67 | 25.061 |  | 9.5232 | 2.0401 | 7.4831 | 30679.7932 | 33.7478 | 849711.0308 | 9.306 | 10.952 | 8.9373 | 1.4542 | 0.54914 | 0.00060995 | 1.2351 | 1.2351
2008-04-20 | 200000 | 266.6 | 2.51 | 13.71 | 22.43 | 10.85 | 23.294 |  | 8.9033 | 2.0597 | 6.8437 | 30652.4615 | 33.7177 | 853677.021 | 8.6499 | 10.1325 | 8.3146 | 1.4709 | 0.55545 | 0.0006204 | 1.2551 | 1.2551
2008-04-20 | 210000 | 270 | 2.52 | 13.64 | 22.72 | 11.92 | 26.41 |  | 9.6871 | 2.0479 | 7.6391 | 31048.7706 | 34.1536 | 856376.8417 | 9.807 | 11.4517 | 9.3065 | 1.6673 | 0.62964 | 0.00069648 | 1.4272 | 1.4272
2008-04-20 | 220000 | 270.2 | 2.55 | 13.63 | 22.72 | 11.96 | 26.353 |  | 9.7062 | 2.0695 | 7.6367 | 31048.7706 | 34.1536 | 855198.8818 | 9.7858 | 11.4427 | 9.2864 | 1.6497 | 0.62296 | 0.00068814 | 1.4101 | 1.4101
2008-04-20 | 230000 | 270 | 2.52 | 13.63 | 22.71 | 11.89 | 26.296 |  | 9.6494 | 2.0451 | 7.6043 | 31035.1048 | 34.1386 | 854822.4738 | 9.7646 | 11.423 | 9.2704 | 1.6661 | 0.62917 | 0.000695 | 1.4236 | 1.4236
2008-04-21 | 0 | 189.3 | 2.38 | 13.82 | 16.72 | 7.77 | 9.994 |  | 6.475 | 1.9833 | 4.4917 | 22849.2713 | 25.1342 | 646243.553 | 3.7111 | 5.7426 | 4.7855 | 0.29384 | 0.11096 | 0.00012586 | 0.1898 | 0.1898
2008-04-21 | 10000 | 191.7 | 2.46 | 13.82 | 16.93 | 7.54 | 10.146 |  | 6.2833 | 2.05 | 4.2333 | 23136.2538 | 25.4499 | 654360.2484 | 3.7676 | 5.7576 | 4.798 | 0.56469 | 0.21324 | 0.00024188 | 0.36935 | 0.36935
2008-04-21 | 20000 | 192.5 | 2.48 | 13.82 | 16.95 | 7.47 | 10.146 |  | 6.225 | 2.0667 | 4.1583 | 23163.5855 | 25.4799 | 655133.267 | 3.7676 | 5.7508 | 4.7924 | 0.63403 | 0.23943 | 0.00027158 | 0.41519 | 0.41519
2008-04-21 | 30000 | 192.5 | 2.47 | 13.82 | 17.01 | 7.52 | 10.241 |  | 6.2667 | 2.0583 | 4.2083 | 23245.5805 | 25.5701 | 657452.3228 | 3.8028 | 5.7842 | 4.8202 | 0.61184 | 0.23105 | 0.00026207 | 0.40207 | 0.40207
2008-04-21 | 40000 | 192.9 | 2.48 | 13.81 | 17.08 | 7.52 | 10.279 |  | 6.2578 | 2.0638 | 4.1941 | 23341.2413 | 25.6754 | 659226.7767 | 3.817 | 5.79 | 4.8182 | 0.62415 | 0.2357 | 0.00026697 | 0.41127 | 0.41127
2008-04-21 | 50000 | 267.2 | 2.43 | 13.62 | 22.63 | 11.7 | 26.6 |  | 9.4821 | 1.9694 | 7.5128 | 30925.7781 | 34.0184 | 850641.1398 | 9.8775 | 11.6118 | 9.4107 | 1.8979 | 0.71671 | 0.00079061 | 1.6137 | 1.6137
2008-04-21 | 60000 | 269.9 | 2.54 | 13.61 | 22.72 | 11.95 | 26.353 |  | 9.6715 | 2.0557 | 7.6158 | 31048.7706 | 34.1536 | 852852.6572 | 9.7858 | 11.4742 | 9.2864 | 1.6706 | 0.63087 | 0.00069497 | 1.4241 | 1.4241
2008-04-21 | 70000 | 269 | 2.55 | 13.64 | 22.6 | 11.74 | 25.688 |  | 9.5408 | 2.0723 | 7.4685 | 30884.7806 | 33.9733 | 851853.7246 | 9.5389 | 11.1978 | 9.1001 | 1.6316 | 0.61616 | 0.00068157 | 1.3893 | 1.3893
2008-04-21 | 80000 | 269.1 | 2.5 | 13.64 | 22.56 | 11.85 | 26.068 |  | 9.6302 | 2.0317 | 7.5985 | 30830.1173 | 33.9131 | 850346.0189 | 9.68 | 11.3836 | 9.2511 | 1.6526 | 0.62408 | 0.00069032 | 1.4047 | 1.4047
2008-04-21 | 90000 | 268.2 | 3.53 | 12.14 | 22.53 | 11.96 | 26.182 |  | 8.0553 | 2.3775 | 5.6777 | 30789.1198 | 33.868 | 703801.6712 | 9.7223 | 13.814 | 9.3039 | 3.6262 | 1.3694 | 0.0012553 | 2.551 | 2.551
2008-04-21 | 100000 | 268.4 | 2.52 | 13.66 | 22.52 | 12.08 | 26.733 |  | 9.8442 | 2.0536 | 7.7906 | 30775.454 | 33.853 | 851183.1704 | 9.9269 | 11.6625 | 9.5039 | 1.7133 | 0.64701 | 0.00071767 | 1.4577 | 1.4577
2008-04-21 | 110000 | 268.3 | 2.53 | 13.64 | 22.54 | 12.09 | 26.695 |  | 9.8252 | 2.0561 | 7.7691 | 30802.7856 | 33.8831 | 849592.166 | 9.9128 | 11.6677 | 9.482 | 1.7129 | 0.64683 | 0.00071549 | 1.4546 | 1.4546
2008-04-21 | 120000 | 267.7 | 2.54 | 13.63 | 22.49 | 12.07 | 26.562 |  | 9.7955 | 2.0613 | 7.7341 | 30734.4565 | 33.8079 | 846541.4988 | 9.8634 | 11.6514 | 9.4557 | 1.7216 | 0.65014 | 0.00071817 | 1.4568 | 1.4568
2008-04-21 | 130000 | 267.3 | 2.54 | 13.62 | 22.45 | 12.04 | 26.391 |  | 9.7577 | 2.0585 | 7.6992 | 30679.7932 | 33.7478 | 843875.1034 | 9.7999 | 11.613 | 9.4116 | 1.7124 | 0.64667 | 0.00071335 | 1.4444 | 1.4444
2008-04-21 | 140000 | 267.3 | 2.54 | 13.63 | 22.43 | 12.09 | 26.543 |  | 9.8117 | 2.0613 | 7.7503 | 30652.4615 | 33.7177 | 844283.051 | 9.8563 | 11.6742 | 9.4743 | 1.7239 | 0.651 | 0.00071912 | 1.4548 | 1.4548
2008-04-21 | 150000 | 267.7 | 2.54 | 13.62 | 22.52 | 12.02 | 26.372 |  | 9.7415 | 2.0585 | 7.683 | 30775.454 | 33.853 | 846506.3398 | 9.7928 | 11.5685 | 9.3756 | 1.6926 | 0.63919 | 0.0007051 | 1.4322 | 1.4322
2008-04-21 | 160000 | 268.7 | 2.54 | 13.61 | 22.54 | 12.15 | 26.125 |  | 9.8333 | 2.0557 | 7.7776 | 30802.7856 | 33.8831 | 846095.902 | 9.7011 | 11.4658 | 9.2796 | 1.5019 | 0.56717 | 0.00062479 | 1.2702 | 1.2702
2008-04-21 | 170000 | 268.1 | 2.54 | 13.61 | 22.53 | 12.23 | 26.258 |  | 9.8981 | 2.0557 | 7.8424 | 30789.1198 | 33.868 | 845720.5267 | 9.7505 | 11.5292 | 9.3309 | 1.4885 | 0.56212 | 0.00061923 | 1.2583 | 1.2583
2008-04-21 | 180000 | 268.8 | 2.55 | 13.61 | 22.54 | 12.16 | 26.106 |  | 9.8414 | 2.0638 | 7.7776 | 30802.7856 | 33.8831 | 846095.902 | 9.6941 | 11.4574 | 9.2728 | 1.4952 | 0.56462 | 0.00062198 | 1.2645 | 1.2645
2008-04-21 | 190000 | 268.5 | 2.55 | 13.6 | 22.54 | 12.2 | 26.163 |  | 9.8603 | 2.061 | 7.7993 | 30802.7856 | 33.8831 | 844936.8665 | 9.7152 | 11.4982 | 9.293 | 1.4937 | 0.56408 | 0.00062054 | 1.2615 | 1.2615
2008-04-21 | 200000 | 268.6 | 2.55 | 13.6 | 22.54 | 12.24 | 26.125 |  | 9.8926 | 2.061 | 7.8316 | 30802.7856 | 33.8831 | 844936.8665 | 9.7011 | 11.4815 | 9.2796 | 1.4479 | 0.54677 | 0.0006015 | 1.2228 | 1.2228
2008-04-21 | 210000 | 268.7 | 2.54 | 13.61 | 22.54 | 12.16 | 26.106 |  | 9.8414 | 2.0557 | 7.7857 | 30802.7856 | 33.8831 | 846095.902 | 9.6941 | 11.4574 | 9.2728 | 1.4871 | 0.56156 | 0.00061862 | 1.2576 | 1.2576
2008-04-21 | 220000 | 268.5 | 2.54 | 13.61 | 22.54 | 12.21 | 26.068 |  | 9.8819 | 2.0557 | 7.8262 | 30802.7856 | 33.8831 | 846095.902 | 9.68 | 11.4407 | 9.2593 | 1.4331 | 0.54118 | 0.00059617 | 1.212 | 1.212
2008-04-21 | 230000 | 268.7 | 2.55 | 13.6 | 22.54 | 12.17 | 26.049 |  | 9.836 | 2.061 | 7.7751 | 30802.7856 | 33.8831 | 844936.8665 | 9.6729 | 11.4481 | 9.2526 | 1.4775 | 0.55794 | 0.00061379 | 1.2478 | 1.2478
2008-04-22 | 0 | 268.7 | 2.55 | 13.6 | 22.54 | 12.17 | 26.068 |  | 9.836 | 2.061 | 7.7751 | 30802.7856 | 33.8831 | 844936.8665 | 9.68 | 11.4564 | 9.2593 | 1.4842 | 0.56049 | 0.00061659 | 1.2535 | 1.2535
2008-04-22 | 10000 | 268.7 | 2.55 | 13.59 | 22.54 | 12.08 | 26.182 |  | 9.7499 | 2.0581 | 7.6918 | 30802.7856 | 33.8831 | 843781.0021 | 9.7223 | 11.5223 | 9.2998 | 1.608 | 0.60723 | 0.0006671 | 1.3562 | 1.3562
2008-04-22 | 20000 | 268.5 | 2.55 | 13.59 | 22.54 | 12.21 | 26.106 |  | 9.8549 | 2.0581 | 7.7967 | 30802.7856 | 33.8831 | 843781.0021 | 9.6941 | 11.4888 | 9.2728 | 1.4761 | 0.55741 | 0.00061237 | 1.2449 | 1.2449
2008-04-22 | 30000 | 268.2 | 2.56 | 13.58 | 22.53 | 12.21 | 25.973 |  | 9.8414 | 2.0634 | 7.778 | 30789.1198 | 33.868 | 842254.4589 | 9.6447 | 11.451 | 9.2297 | 1.4517 | 0.54819 | 0.00060141 | 1.2221 | 1.2221
2008-04-22 | 40000 | 268.2 | 2.56 | 13.56 | 22.52 | 12.15 | 25.935 |  | 9.7663 | 2.0578 | 7.7086 | 30775.454 | 33.853 | 839586.6694 | 9.6306 | 11.4706 | 9.2202 | 1.5117 | 0.57085 | 0.00062456 | 1.2686 | 1.2686
2008-04-22 | 50000 | 268.3 | 2.56 | 13.55 | 22.53 | 12.16 | 25.897 |  | 9.7611 | 2.055 | 7.7061 | 30789.1198 | 33.868 | 838816.6856 | 9.6165 | 11.4643 | 9.2026 | 1.4965 | 0.56513 | 0.00061747 | 1.2547 | 1.2547
2008-04-22 | 60000 | 267.8 | 2.58 | 13.55 | 22.49 | 12.18 | 25.916 |  | 9.7771 | 2.071 | 7.7061 | 30734.4565 | 33.8079 | 837327.4416 | 9.6235 | 11.4931 | 9.2258 | 1.5197 | 0.57387 | 0.00062701 | 1.2719 | 1.2719
2008-04-22 | 70000 | 267.4 | 2.57 | 13.55 | 22.41 | 12.27 | 26.201 |  | 9.8494 | 2.063 | 7.7864 | 30625.1298 | 33.6876 | 834348.9536 | 9.7293 | 11.661 | 9.3605 | 1.5741 | 0.59444 | 0.00064949 | 1.3128 | 1.3128
2008-04-22 | 80000 | 267.1 | 2.57 | 13.54 | 22.35 | 12.28 | 26.22 |  | 9.844 | 2.0602 | 7.7838 | 30543.1348 | 33.5974 | 830984.4965 | 9.7364 | 11.7167 | 9.3925 | 1.6086 | 0.60747 | 0.00066282 | 1.3362 | 1.3362
2008-04-22 | 90000 | 266.4 | 2.57 | 13.54 | 22.28 | 12.35 | 26.391 |  | 9.9001 | 2.0602 | 7.8399 | 30447.474 | 33.4922 | 828381.8605 | 9.7999 | 11.8302 | 9.4834 | 1.6435 | 0.62063 | 0.00067718 | 1.3608 | 1.3608
2008-04-22 | 100000 | 265.4 | 3.49 | 12.03 | 22.26 | 12.4 | 26.638 |  | 8.248 | 2.3214 | 5.9266 | 30420.1423 | 33.4622 | 686743.8017 | 9.8916 | 14.4037 | 9.5808 | 3.6542 | 1.3799 | 0.0012493 | 2.5084 | 2.5084
2008-04-22 | 110000 | 263.9 | 2.58 | 13.53 | 22.1 | 12.52 | 26.562 |  | 10.0228 | 2.0654 | 7.9574 | 30201.489 | 33.2216 | 820574.4569 | 9.8634 | 12.0201 | 9.6226 | 1.6652 | 0.62884 | 0.00068521 | 1.3658 | 1.3658
2008-04-22 | 120000 | 262.3 | 2.58 | 13.52 | 22.05 | 12.5 | 26.391 |  | 9.9932 | 2.0626 | 7.9306 | 30133.1599 | 33.1465 | 817608.5797 | 9.7999 | 11.9861 | 9.5823 | 1.6517 | 0.62374 | 0.00067873 | 1.3499 | 1.3499
2008-04-22 | 130000 | 261.3 | 2.58 | 13.52 | 21.91 | 12.5 | 26.334 |  | 9.9932 | 2.0626 | 7.9306 | 29941.8382 | 32.936 | 812417.4141 | 9.7787 | 12.0366 | 9.6227 | 1.6921 | 0.639 | 0.00069533 | 1.3741 | 1.3741
2008-04-22 | 140000 | 260.4 | 2.58 | 13.51 | 21.81 | 12.53 | 26.391 |  | 10.0037 | 2.0598 | 7.9438 | 29805.1799 | 32.7857 | 807615.1093 | 9.7999 | 12.1344 | 9.6878 | 1.7439 | 0.65857 | 0.00071566 | 1.4078 | 1.4078
2008-04-22 | 150000 | 260.2 | 3.54 | 12.11 | 21.8 | 12.49 | 26.619 |  | 8.3835 | 2.3761 | 6.0074 | 29791.5141 | 32.7707 | 678673.3984 | 9.8846 | 14.5645 | 9.776 | 3.7686 | 1.4231 | 0.0013002 | 2.5565 | 2.5565
2008-04-22 | 160000 | 261 | 2.52 | 13.68 | 21.84 | 12.41 | 26.6 |  | 10.1411 | 2.0593 | 8.0819 | 29846.1774 | 32.8308 | 827768.0215 | 9.8775 | 11.9327 | 9.7511 | 1.6692 | 0.63036 | 0.00070113 | 1.3811 | 1.3811
2008-04-22 | 170000 | 260.5 | 2.53 | 13.66 | 21.82 | 12.43 | 26.733 |  | 10.1294 | 2.0617 | 8.0677 | 29818.8457 | 32.8007 | 824725.4342 | 9.9269 | 12.0366 | 9.8088 | 1.7412 | 0.65751 | 0.00072932 | 1.4353 | 1.4353
2008-04-22 | 180000 | 261 | 2.52 | 13.65 | 21.88 | 12.31 | 26.372 |  | 10.0178 | 2.0508 | 7.967 | 29900.8407 | 32.8909 | 825852.5598 | 9.7928 | 11.8579 | 9.6498 | 1.6828 | 0.63548 | 0.00070391 | 1.3891 | 1.3891
2008-04-22 | 190000 | 261.6 | 2.53 | 13.65 | 22.01 | 12.31 | 26.182 |  | 10.0178 | 2.0589 | 7.9589 | 30078.4965 | 33.0863 | 830759.362 | 9.7223 | 11.7029 | 9.5237 | 1.5648 | 0.59093 | 0.00065456 | 1.2994 | 1.2994
2008-04-22 | 200000 | 261.7 | 2.54 | 13.64 | 22.03 | 12.33 | 26.239 |  | 10.0202 | 2.0642 | 7.9561 | 30105.8282 | 33.1164 | 830368.9182 | 9.7435 | 11.7339 | 9.5358 | 1.5797 | 0.59656 | 0.00065988 | 1.3112 | 1.3112
2008-04-22 | 210000 | 262.2 | 2.53 | 13.63 | 22.05 | 12.29 | 26.391 |  | 9.974 | 2.0532 | 7.9208 | 30133.1599 | 33.1465 | 829979.5486 | 9.7999 | 11.8074 | 9.5823 | 1.6616 | 0.62746 | 0.00069311 | 1.3785 | 1.3785
2008-04-22 | 220000 | 262.4 | 2.54 | 13.63 | 22.05 | 12.28 | 26.334 |  | 9.9659 | 2.0613 | 7.9045 | 30133.1599 | 33.1465 | 829979.5486 | 9.7787 | 11.7819 | 9.5616 | 1.6571 | 0.62578 | 0.00069125 | 1.3747 | 1.3747
2008-04-22 | 230000 | 261.6 | 2.49 | 13.65 | 21.92 | 12.12 | 25.973 |  | 9.8632 | 2.0263 | 7.8368 | 29955.5041 | 32.9511 | 827362.3451 | 9.6447 | 11.6571 | 9.4865 | 1.6497 | 0.62297 | 0.00069005 | 1.3643 | 1.3643
2008-04-23 | 0 | 191.8 | 2.52 | 13.86 | 16.8 | 7.54 | 9.823 |  | 6.319 | 2.1119 | 4.2071 | 22958.598 | 25.2545 | 653025.0344 | 3.6476 | 5.5857 | 4.6812 | 0.47412 | 0.17904 | 0.00020424 | 0.30947 | 0.30947
2008-04-23 | 10000 | 193.9 | 2.44 | 13.86 | 17.03 | 7.43 | 10.564 |  | 6.2268 | 2.0449 | 4.182 | 23272.9121 | 25.6002 | 661965.2581 | 3.9228 | 5.926 | 4.9664 | 0.7844 | 0.29621 | 0.0003379 | 0.51901 | 0.51901
2008-04-23 | 20000 | 193.7 | 2.46 | 13.86 | 17 | 7.37 | 10.146 |  | 6.1766 | 2.0616 | 4.1149 | 23231.9146 | 25.5551 | 660799.142 | 3.7676 | 5.7015 | 4.7783 | 0.66335 | 0.2505 | 0.00028575 | 0.43815 | 0.43815
2008-04-23 | 30000 | 194.1 | 2.46 | 13.85 | 17.06 | 7.4 | 10.412 |  | 6.1929 | 2.0587 | 4.1342 | 23313.9096 | 25.6453 | 662190.7624 | 3.8663 | 5.8387 | 4.8863 | 0.75211 | 0.28402 | 0.00032353 | 0.49782 | 0.49782
2008-04-23 | 40000 | 194 | 2.48 | 13.86 | 17.07 | 7.5 | 10.773 |  | 6.2855 | 2.0784 | 4.2071 | 23327.5755 | 25.6603 | 663520.0796 | 4.0004 | 6.029 | 5.0527 | 0.84565 | 0.31934 | 0.00036428 | 0.56085 | 0.56085
2008-04-23 | 50000 | 262.8 | 2.5 | 13.66 | 22.13 | 12.25 | 26.98 |  | 9.9827 | 2.0373 | 7.9454 | 30242.4865 | 33.2667 | 836442.4316 | 10.0186 | 11.9777 | 9.7608 | 1.8154 | 0.68553 | 0.0007604 | 1.5178 | 1.5178
2008-04-23 | 60000 | 264.1 | 2.53 | 13.67 | 22.12 | 12.4 | 26.79 |  | 10.1189 | 2.0646 | 8.0544 | 30228.8207 | 33.2517 | 837220.8464 | 9.9481 | 11.8822 | 9.6964 | 1.6421 | 0.6201 | 0.00068877 | 1.3742 | 1.3742
2008-04-23 | 70000 | 264.4 | 2.52 | 13.67 | 22.23 | 12.38 | 26.714 |  | 10.1026 | 2.0564 | 8.0462 | 30379.1448 | 33.4171 | 841384.2412 | 9.9198 | 11.7899 | 9.6211 | 1.5749 | 0.59473 | 0.00066059 | 1.3245 | 1.3245
2008-04-23 | 80000 | 264.5 | 2.53 | 13.67 | 22.25 | 12.32 | 26.581 |  | 10.0537 | 2.0646 | 7.9891 | 30406.4765 | 33.4471 | 842141.222 | 9.8705 | 11.7207 | 9.5646 | 1.5755 | 0.59496 | 0.00066084 | 1.3262 | 1.3262
2008-04-23 | 90000 | 194.4 | 3.42 | 12.29 | 17 | 8.47 | 11.419 |  | 5.8041 | 2.3436 | 3.4605 | 23231.9146 | 25.5551 | 540304.9895 | 4.2403 | 7.8479 | 5.3778 | 1.9173 | 0.72402 | 0.0006753 | 1.0354 | 1.0354
2008-04-23 | 100000 | 193.3 | 2.42 | 13.9 | 17.01 | 7.48 | 10.735 |  | 6.3046 | 2.0397 | 4.2649 | 23245.5805 | 25.5701 | 664966.0636 | 3.9863 | 5.9947 | 5.0527 | 0.78783 | 0.29751 | 0.00034131 | 0.52364 | 0.52364
2008-04-23 | 110000 | 193.9 | 2.45 | 13.88 | 17.05 | 7.47 | 10.697 |  | 6.2782 | 2.0591 | 4.2191 | 23300.2438 | 25.6303 | 664630.8246 | 3.9722 | 5.9765 | 5.023 | 0.8039 | 0.30358 | 0.00034728 | 0.53406 | 0.53406
2008-04-23 | 120000 | 191.7 | 2.44 | 13.89 | 16.89 | 7.52 | 10.735 |  | 6.3292 | 2.0536 | 4.2756 | 23081.5905 | 25.3897 | 659333.0407 | 3.9863 | 6.0459 | 5.0886 | 0.81298 | 0.30701 | 0.0003517 | 0.53578 | 0.53578
2008-04-23 | 130000 | 193.7 | 2.45 | 13.89 | 16.94 | 7.46 | 10.64 |  | 6.2787 | 2.0621 | 4.2167 | 23149.9196 | 25.4649 | 661284.8851 | 3.951 | 5.9747 | 5.0287 | 0.81198 | 0.30663 | 0.00035127 | 0.53671 | 0.53671
2008-04-23 | 140000 | 193.5 | 2.46 | 13.89 | 16.95 | 7.44 | 10.564 |  | 6.2619 | 2.0705 | 4.1914 | 23163.5855 | 25.4799 | 661675.254 | 3.9228 | 5.9286 | 4.9898 | 0.79836 | 0.30149 | 0.00034538 | 0.52802 | 0.52802
2008-04-23 | 150000 | 191.7 | 2.43 | 13.89 | 16.84 | 7.48 | 10.621 |  | 6.2956 | 2.0452 | 4.2504 | 23013.2613 | 25.3146 | 657381.1963 | 3.9439 | 5.9995 | 5.0495 | 0.79914 | 0.30178 | 0.00034572 | 0.5251 | 0.5251
2008-04-23 | 160000 | 193.5 | 2.47 | 13.9 | 16.94 | 7.38 | 10.431 |  | 6.2203 | 2.0819 | 4.1384 | 23149.9196 | 25.4649 | 662229.5778 | 3.8734 | 5.849 | 4.9299 | 0.79146 | 0.29888 | 0.00034289 | 0.52389 | 0.52389
2008-04-23 | 170000 | 192.1 | 2.44 | 13.91 | 16.93 | 7.47 | 10.602 |  | 6.3052 | 2.0595 | 4.2456 | 23136.2538 | 25.4499 | 662785.4876 | 3.9369 | 5.9399 | 5.0137 | 0.76803 | 0.29003 | 0.00033321 | 0.50881 | 0.50881
2008-04-23 | 180000 | 192.9 | 2.44 | 13.91 | 16.93 | 7.49 | 10.621 |  | 6.322 | 2.0595 | 4.2625 | 23136.2538 | 25.4499 | 662785.4876 | 3.9439 | 5.9506 | 5.0227 | 0.76013 | 0.28705 | 0.00032978 | 0.50358 | 0.50358
2008-04-23 | 190000 | 192.2 | 2.44 | 13.93 | 16.93 | 7.52 | 10.678 |  | 6.3656 | 2.0654 | 4.3001 | 23136.2538 | 25.4499 | 664687.3111 | 3.9651 | 5.9654 | 5.0496 | 0.74946 | 0.28302 | 0.00032609 | 0.49793 | 0.49793
2008-04-23 | 200000 | 193.3 | 2.42 | 13.94 | 16.97 | 7.47 | 10.621 |  | 6.3323 | 2.0514 | 4.2809 | 23190.9171 | 25.51 | 667215.0147 | 3.9439 | 5.9111 | 5.0108 | 0.72992 | 0.27564 | 0.00031804 | 0.4868 | 0.4868
2008-04-23 | 210000 | 192 | 2.45 | 13.96 | 16.92 | 7.53 | 10.317 |  | 6.4016 | 2.0829 | 4.3187 | 23122.588 | 25.4348 | 667166.2929 | 3.8311 | 5.7423 | 4.8818 | 0.56304 | 0.21262 | 0.00024604 | 0.37547 | 0.37547
2008-04-23 | 220000 | 9.4 | 1.69 | 19.99 | 1.23 | 5.04 | 2.584 |  | 32.6769 | 10.9571 | 21.7198 | 1680.8974 | 1.849 | 369876.66 | 0.95953 | 2.5942 | 16.8195 | -4.9003 | -1.8505 | -0.016331 | -1.8117
2008-04-23 | 230000 | 1.3 | 0 | 21.01 | 0.04 | 0.01 | 0.209 |  | -0.53636 | 0 | -0.53636 | 54.6633 | 0.06013 | -99508.5767 | 0.077609 | -0.77992 | 41.8322 | 42.3686 | 15.9997 | -1.1681 | -4.2141
2008-04-24 | 0 | 1.3 | 0 | 21.04 | 0.04 | -0.05 | 0.19 |  | 2.1071 | 0 | 2.1071 | 54.6633 | 0.06013 | -78185.3102 | 0.070554 | -0.90239 | 38.0293 | 35.9221 | 13.5653 | -0.77813 | -2.8073
2008-04-24 | 10000 | 1.3 | 0 | 21.06 | 0.04 | -0.06 | 0.19 |  | 2.2125 | 0 | 2.2125 | 54.6633 | 0.06013 | -68412.1465 | 0.070554 | -1.0313 | 38.0293 | 35.8168 | 13.5255 | -0.67887 | -2.4492
2008-04-24 | 20000 | 1.3 | 0 | 21.08 | 0.04 | -0.06 | 0.19 |  | 1.9667 | 0 | 1.9667 | 54.6633 | 0.06013 | -60810.7969 | 0.070554 | -1.1602 | 38.0293 | 36.0626 | 13.6183 | -0.60758 | -2.192
2008-04-24 | 30000 | 1.3 | 0 | 21.1 | 0.17 | -0.06 | 0.171 |  | 1.77 | 0 | 1.77 | 232.3191 | 0.25555 | -232601.298 | 0.063498 | -0.27299 | 8.0533 | 6.2833 | 2.3728 | -0.095274 | -1.4608
2008-04-24 | 40000 | 1.3 | 0.06 | 20.91 | 0.25 | 0.83 | 0.19 |  | -489.7 | -35.4 | -454.3 | 341.6458 | 0.37581 | -6841214.6465 | 0.070554 | -0.010313 | 6.0847 | 460.3847 | 173.8553 | -139.6171 | -3148.1731
2008-04-24 | 50000 | 28.1 | 10.23 | 16.61 | 7.91 | 29.86 | 0.532 |  | 41.0662 | 14.0692 | 26.997 | 10809.6732 | 11.8906 | 504559.5138 | 0.19755 | 0.39153 | 0.53847 | -26.4585 | -9.9915 | -0.018704 | -13.3439
2008-04-24 | 60000 | 149.7 | 5.54 | 14.59 | 14.75 | 18.39 | 12.692 |  | 17.1951 | 5.18 | 12.0151 | 20157.1024 | 22.1728 | 639669.8322 | 4.713 | 7.3678 | 6.8891 | -5.126 | -1.9357 | -0.0024636 | -3.2774
2008-04-24 | 70000 | 193.4 | 2.28 | 14.1 | 17.04 | 7.95 | 11.134 |  | 6.8978 | 1.9782 | 4.9196 | 23286.578 | 25.6152 | 685731.1622 | 4.1344 | 6.0292 | 5.2313 | 0.3117 | 0.11771 | 0.00013901 | 0.21365 | 0.21365
2008-04-24 | 80000 | 193 | 2.37 | 14.11 | 16.93 | 7.8 | 10.868 |  | 6.7776 | 2.0594 | 4.7183 | 23136.2538 | 25.4499 | 682307.8879 | 4.0357 | 5.9147 | 5.1395 | 0.42119 | 0.15906 | 0.00018812 | 0.28726 | 0.28726
2008-04-24 | 90000 | 193.6 | 3.38 | 12.5 | 16.93 | 8.64 | 11.286 |  | 6.0686 | 2.374 | 3.6945 | 23136.2538 | 25.4499 | 551532.2094 | 4.1909 | 7.5986 | 5.3371 | 1.6426 | 0.6203 | 0.00059302 | 0.90554 | 0.90554
2008-04-24 | 100000 | 193.4 | 3.09 | 13.03 | 16.93 | 7.91 | 11.286 |  | 5.93 | 2.3165 | 3.6135 | 23136.2538 | 25.4499 | 588674.7851 | 4.1909 | 7.1192 | 5.3371 | 1.7237 | 0.65091 | 0.00066419 | 1.0142 | 1.0142
2008-04-24 | 110000 | 193 | 1.9 | 12.21 | 16.93 | 7.39 | 11.077 |  | 5.0174 | 1.29 | 3.7274 | 23136.2538 | 25.4499 | 533126.6466 | 4.1133 | 7.7154 | 5.2383 | 1.5109 | 0.57056 | 0.00052727 | 0.80514 | 0.80514
2008-04-24 | 120000 | 192.7 | 1.75 | 13.89 | 16.93 | 7.94 | 11.229 |  | 6.6827 | 1.4729 | 5.2098 | 23136.2538 | 25.4499 | 660894.5162 | 4.1697 | 6.3092 | 5.3102 | 0.10033 | 0.037888 | 4.3404e-05 | 0.066278 | 0.066278
2008-04-24 | 130000 | 192.1 | 8.44 | 3.51 | 16.93 | 7.9 | 10.868 |  | 2.6803 | 2.8635 | -0.18321 | 23136.2538 | 25.4499 | 266410.0379 | 4.0357 | 15.1483 | 5.1395 | 5.3227 | 2.01 | 0.00092821 | 1.4174 | 1.4174
2008-04-24 | 140000 | 191.9 | 8.48 | 3.83 | 16.93 | 7.8 | 10.792 |  | 2.696 | 2.931 | -0.23503 | 23136.2538 | 25.4499 | 271404.2507 | 4.0074 | 14.7656 | 5.1035 | 5.3385 | 2.016 | 0.00094843 | 1.4483 | 1.4483
2008-04-24 | 150000 | 195.1 | 6.52 | 6.3 | 17.2 | 7.82 | 11.324 |  | 3.1601 | 2.6348 | 0.52534 | 23505.2313 | 25.8558 | 322380.5258 | 4.205 | 13.0436 | 5.271 | 4.7457 | 1.7921 | 0.00098574 | 1.5292 | 1.5292
2008-04-24 | 160000 | 266.1 | 3.2 | 12.7 | 22.27 | 12.85 | 27.835 |  | 9.2457 | 2.3024 | 6.9433 | 30433.8082 | 33.4772 | 743189.5131 | 10.3361 | 13.9078 | 10.0068 | 3.0635 | 1.1569 | 0.001133 | 2.2757 | 2.2757
2008-04-24 | 170000 | 266.9 | 2.52 | 12.94 | 22.28 | 12.84 | 29.944 |  | 9.5171 | 1.8678 | 7.6492 | 30447.474 | 33.4922 | 765941.0167 | 11.1193 | 14.5171 | 10.7602 | 3.1109 | 1.1748 | 0.0011852 | 2.3817 | 2.3817
2008-04-24 | 180000 | 267 | 2.52 | 13.74 | 22.3 | 12.9 | 28.101 |  | 10.6299 | 2.0765 | 8.5534 | 30474.8057 | 33.5223 | 852285.4001 | 10.4349 | 12.2434 | 10.0888 | 1.5355 | 0.57985 | 0.00065036 | 1.3081 | 1.3081
2008-04-24 | 190000 | 268.1 | 2.5 | 13.73 | 22.51 | 12.81 | 27.911 |  | 10.541 | 2.0572 | 8.4838 | 30761.7881 | 33.838 | 859111.5297 | 10.3643 | 12.064 | 9.9271 | 1.4433 | 0.54504 | 0.00061047 | 1.2394 | 1.2394
2008-04-24 | 200000 | 269.1 | 2.5 | 13.74 | 22.53 | 12.82 | 28.044 |  | 10.564 | 2.0601 | 8.5039 | 30789.1198 | 33.868 | 861075.7876 | 10.4137 | 12.0938 | 9.9656 | 1.4617 | 0.55198 | 0.0006191 | 1.2581 | 1.2581
2008-04-24 | 210000 | 268 | 2.42 | 13.76 | 22.42 | 12.44 | 27.132 |  | 10.2796 | 1.9997 | 8.2798 | 30638.7957 | 33.7027 | 859271.8901 | 10.0751 | 11.7251 | 9.6888 | 1.409 | 0.53208 | 0.00059845 | 1.2102 | 1.2102
2008-04-24 | 220000 | 27.5 | 2.25 | 19.17 | 2.9 | 6.9 | 1.501 |  | 23.5318 | 7.6734 | 15.8584 | 3963.0913 | 4.3594 | 458717.2827 | 0.55737 | 1.2151 | 4.1439 | -11.7145 | -4.4238 | -0.020535 | -5.3712
2008-04-24 | 230000 | 1.3 | 0 | 20.84 | 0.45 | 0 | 0.19 |  | 0 | 0 | 0 | 614.9624 | 0.67646 | 2052364.3939 | 0.070554 | 0.034377 | 3.3804 | 3.3804 | 1.2765 | 0.17086 | 6.9347
2008-04-25 | 0 | 1.3 | 0 | 20.92 | 0.28 | -0.06 | 0.171 |  | 17.7 | 0 | 17.7 | 382.6433 | 0.42091 | -3831080.202 | 0.063498 | -0.016575 | 4.8895 | -12.8105 | -4.8376 | 1.9425 | 49.056
2008-04-25 | 10000 | 1.3 | 0.01 | 20.93 | 0.26 | -0.07 | 0.171 |  | 13.7667 | -1.9667 | 15.7333 | 355.3116 | 0.39084 | -2371621.0775 | 0.063498 | -0.026774 | 5.2656 | -10.4677 | -3.9529 | 1.0582 | 24.8143
2008-04-25 | 20000 | 1.3 | 0.01 | 20.92 | 0.26 | -0.06 | 0.19 |  | 17.7 | -2.95 | 20.65 | 355.3116 | 0.39084 | -3557431.6162 | 0.070554 | -0.019833 | 5.8507 | -14.7993 | -5.5887 | 2.244 | 52.6239
2008-04-25 | 30000 | 1.3 | 0.2 | 20.8 | 0.38 | 0.87 | 0.152 |  | 51.33 | 11.8 | 39.53 | 519.3016 | 0.57123 | 1039864.6263 | 0.056443 | 0.054279 | 3.2025 | -36.3275 | -13.7184 | -1.1017 | -37.7587
2008-04-25 | 40000 | 30.9 | 10.29 | 16.45 | 8.08 | 29.86 | 0.532 |  | 39.5897 | 13.6429 | 25.9467 | 11041.9924 | 12.1462 | 496872.039 | 0.19755 | 0.39759 | 0.52714 | -25.4196 | -9.5992 | -0.017323 | -12.6246
2008-04-25 | 50000 | 163.8 | 5.57 | 14.4 | 15.45 | 17.98 | 11.495 |  | 16.3203 | 5.0558 | 11.2645 | 21113.7107 | 23.2251 | 650441.6387 | 4.2685 | 6.5625 | 5.9567 | -5.3078 | -2.0044 | -0.0024764 | -3.4508
2008-04-25 | 60000 | 271.6 | 2.46 | 13.74 | 22.8 | 12.66 | 27.436 |  | 10.4321 | 2.0271 | 8.405 | 31158.0973 | 34.2739 | 871394.9382 | 10.1879 | 11.6915 | 9.6341 | 1.2291 | 0.46413 | 0.00052057 | 1.0705 | 1.0705
2008-04-25 | 70000 | 272.8 | 2.5 | 13.74 | 22.81 | 12.58 | 27.265 |  | 10.3662 | 2.0601 | 8.3061 | 31171.7631 | 34.2889 | 871777.129 | 10.1244 | 11.6136 | 9.5698 | 1.2637 | 0.47721 | 0.00053524 | 1.1012 | 1.1012
2008-04-25 | 80000 | 272.2 | 2.5 | 13.74 | 22.81 | 12.58 | 27.303 |  | 10.3662 | 2.0601 | 8.3061 | 31171.7631 | 34.2889 | 871777.129 | 10.1386 | 11.6298 | 9.5832 | 1.277 | 0.48225 | 0.00054089 | 1.1128 | 1.1128
2008-04-25 | 90000 | 270.7 | 3.45 | 12.17 | 22.75 | 12.62 | 28.272 |  | 8.529 | 2.3316 | 6.1974 | 31089.7681 | 34.1987 | 713116.3034 | 10.4984 | 14.7218 | 9.9495 | 3.7521 | 1.4169 | 0.0013034 | 2.6745 | 2.6745
2008-04-25 | 100000 | 269.4 | 2.43 | 13.79 | 22.58 | 12.72 | 28.177 |  | 10.5553 | 2.0165 | 8.5388 | 30857.449 | 33.9432 | 869055.5652 | 10.4631 | 12.0396 | 9.9907 | 1.4519 | 0.54827 | 0.00061926 | 1.2612 | 1.2612
2008-04-25 | 110000 | 268 | 2.49 | 13.76 | 22.5 | 12.63 | 28.234 |  | 10.4366 | 2.0576 | 8.379 | 30748.1223 | 33.8229 | 862337.9807 | 10.4843 | 12.158 | 10.0465 | 1.6675 | 0.6297 | 0.00070825 | 1.4373 | 1.4373
2008-04-25 | 120000 | 243.6 | 2.42 | 13.93 | 20.62 | 9.23 | 18.297 |  | 7.8131 | 2.0485 | 5.7646 | 28178.9459 | 30.9968 | 809560.0919 | 6.7943 | 8.3926 | 7.1042 | 1.3396 | 0.50589 | 0.00058288 | 1.084 | 1.084
2008-04-25 | 130000 | 266.8 | 2.41 | 13.77 | 22.29 | 12.95 | 29.013 |  | 10.716 | 1.9942 | 8.7217 | 30461.1398 | 33.5073 | 855487.6548 | 10.7735 | 12.5934 | 10.4209 | 1.6992 | 0.64167 | 0.00072273 | 1.453 | 1.453
2008-04-25 | 140000 | 266 | 2.49 | 13.77 | 22.28 | 13.01 | 29.032 |  | 10.7656 | 2.0604 | 8.7052 | 30447.474 | 33.4922 | 855103.856 | 10.7806 | 12.6074 | 10.4325 | 1.7273 | 0.65227 | 0.00073466 | 1.4763 | 1.4763
2008-04-25 | 150000 | 265.7 | 2.49 | 13.77 | 22.28 | 12.99 | 28.918 |  | 10.7491 | 2.0604 | 8.6886 | 30447.474 | 33.4922 | 855103.856 | 10.7383 | 12.5578 | 10.3915 | 1.7028 | 0.64305 | 0.00072428 | 1.4555 | 1.4555
2008-04-25 | 160000 | 258 | 2.33 | 13.88 | 21.71 | 11.13 | 23.636 |  | 9.3543 | 1.9583 | 7.396 | 29668.5216 | 32.6354 | 846283.5896 | 8.7769 | 10.3711 | 8.7164 | 1.3204 | 0.49863 | 0.00057042 | 1.1169 | 1.1169
2008-04-25 | 170000 | 191.8 | 2.42 | 13.97 | 16.76 | 8.01 | 11.21 |  | 6.8195 | 2.0603 | 4.7592 | 22903.9347 | 25.1943 | 661811.01 | 4.1627 | 6.2898 | 5.355 | 0.5958 | 0.22499 | 0.00026072 | 0.39413 | 0.39413
2008-04-25 | 180000 | 192 | 2.43 | 13.96 | 16.83 | 7.92 | 11.02 |  | 6.7331 | 2.0659 | 4.6673 | 22999.5955 | 25.2996 | 663617.536 | 4.0921 | 6.1664 | 5.2423 | 0.57501 | 0.21714 | 0.00025127 | 0.38142 | 0.38142
2008-04-25 | 190000 | 197.6 | 2.47 | 13.94 | 17.36 | 8.18 | 12.369 |  | 6.9342 | 2.0938 | 4.8404 | 23723.8846 | 26.0963 | 682548.7716 | 4.593 | 6.7293 | 5.7044 | 0.86402 | 0.32628 | 0.00037647 | 0.58947 | 0.58947
2008-04-25 | 200000 | 264 | 2.38 | 13.75 | 22.11 | 12.81 | 28.006 |  | 10.5705 | 1.9639 | 8.6066 | 30215.1549 | 33.2367 | 846205.627 | 10.3996 | 12.2897 | 10.1411 | 1.5346 | 0.5795 | 0.00065088 | 1.298 | 1.298
2008-04-25 | 210000 | 191.5 | 2.37 | 13.95 | 16.84 | 7.88 | 10.279 |  | 6.6895 | 2.0119 | 4.6776 | 23013.2613 | 25.3146 | 663056.4296 | 3.817 | 5.7566 | 4.8869 | 0.20934 | 0.079055 | 9.1347e-05 | 0.13875 | 0.13875
2008-04-25 | 220000 | 12.2 | 1.82 | 19.81 | 1.6 | 5.55 | 1.577 |  | 30.0413 | 9.8514 | 20.1899 | 2186.5331 | 2.4052 | 401685.9976 | 0.5856 | 1.4578 | 7.8911 | -12.2988 | -4.6444 | -0.034218 | -4.938
2008-04-25 | 230000 | 1.3 | 0 | 20.92 | 0.04 | 0.01 | 0.19 |  | -2.95 | 0 | -2.95 | 54.6633 | 0.06013 | -547297.1717 | 0.070554 | -0.12891 | 38.0293 | 40.9793 | 15.475 | -6.2137 | -22.4178
2008-04-26 | 0 | 1.3 | 0 | 20.92 | 0.17 | -0.03 | 0.171 |  | 8.85 | 0 | 8.85 | 232.3191 | 0.25555 | -2326012.9798 | 0.063498 | -0.027299 | 8.0533 | -0.79674 | -0.30087 | 0.12081 | 1.8524
2008-04-26 | 10000 | 1.3 | 0 | 20.92 | 0.35 | -0.06 | 0.171 |  | 17.7 | 0 | 17.7 | 478.3041 | 0.52613 | -4788850.2525 | 0.063498 | -0.01326 | 3.9116 | -13.7884 | -5.2069 | 2.0907 | 66.0009
2008-04-26 | 20000 | 1.3 | 0 | 20.93 | 0.26 | -0.06 | 0.19 |  | 11.8 | 0 | 11.8 | 355.3116 | 0.39084 | -2371621.0775 | 0.070554 | -0.029749 | 5.8507 | -5.9493 | -2.2467 | 0.6014 | 14.1032
2008-04-26 | 30000 | 1.3 | 0.12 | 20.78 | 0.29 | 1.06 | 0.19 |  | 52.1167 | 5.9 | 46.2167 | 396.3091 | 0.43594 | 661317.4158 | 0.070554 | 0.10669 | 5.2454 | -40.9712 | -15.472 | -1.0354 | -27.0828
2008-04-26 | 40000 | 33.4 | 10.29 | 16.32 | 8.29 | 29.91 | 0.247 |  | 38.5303 | 13.2557 | 25.2747 | 11328.9748 | 12.4619 | 495315.8901 | 0.09172 | 0.18517 | 0.23854 | -25.0361 | -9.4544 | -0.016578 | -12.3952
2008-04-26 | 50000 | 165.5 | 4.92 | 14.27 | 15.44 | 15.42 | 8.949 |  | 13.7222 | 4.3783 | 9.3439 | 21100.0448 | 23.21 | 637275.1381 | 3.3231 | 5.2145 | 4.6404 | -4.7035 | -1.7762 | -0.0021514 | -2.9961
2008-04-26 | 60000 | 193.6 | 3.41 | 12.34 | 17.11 | 8.2 | 11.685 |  | 5.6519 | 2.3504 | 3.3015 | 23382.2388 | 25.7205 | 546977.4888 | 4.339 | 7.9328 | 5.4677 | 2.1662 | 0.81801 | 0.00076742 | 1.1843 | 1.1843
2008-04-26 | 70000 | 269.4 | 2.32 | 13.88 | 22.64 | 10.94 | 23.484 |  | 9.1946 | 1.9499 | 7.2447 | 30939.444 | 34.0334 | 882536.18 | 8.7204 | 9.8811 | 8.3046 | 1.0599 | 0.40025 | 0.00045787 | 0.93498 | 0.93498
2008-04-26 | 80000 | 268.8 | 2.48 | 13.85 | 22.54 | 11.09 | 23.161 |  | 9.281 | 2.0755 | 7.2055 | 30802.7856 | 33.8831 | 874899.1667 | 8.6005 | 9.8303 | 8.2267 | 1.0212 | 0.38564 | 0.00043928 | 0.89306 | 0.89306
2008-04-26 | 90000 | 268.9 | 2.53 | 13.78 | 22.58 | 12.4 | 26.239 |  | 10.2753 | 2.0965 | 8.1788 | 30857.449 | 33.9432 | 867834.9816 | 9.7435 | 11.2273 | 9.3035 | 1.1247 | 0.42474 | 0.00047906 | 0.97565 | 0.97565
2008-04-26 | 100000 | 268.5 | 2.52 | 13.74 | 22.51 | 13.24 | 28.918 |  | 10.9101 | 2.0765 | 8.8335 | 30761.7881 | 33.838 | 860311.4061 | 10.7383 | 12.4818 | 10.2853 | 1.4518 | 0.54824 | 0.00061491 | 1.2484 | 1.2484
2008-04-26 | 110000 | 265.1 | 2.52 | 13.74 | 22.21 | 13.2 | 28.272 |  | 10.8771 | 2.0765 | 8.8006 | 30351.8132 | 33.387 | 848845.6832 | 10.4984 | 12.3678 | 10.1914 | 1.3908 | 0.52521 | 0.00058908 | 1.1801 | 1.1801
2008-04-26 | 120000 | 262.2 | 2.51 | 13.73 | 21.97 | 13.19 | 28.12 |  | 10.8537 | 2.0654 | 8.7883 | 30023.8332 | 33.0262 | 838502.0127 | 10.4419 | 12.4531 | 10.2473 | 1.459 | 0.55097 | 0.00061711 | 1.2228 | 1.2228
2008-04-26 | 130000 | 259 | 2.51 | 13.74 | 21.68 | 13.08 | 27.607 |  | 10.7782 | 2.0683 | 8.7099 | 29627.5241 | 32.5903 | 828589.5728 | 10.2514 | 12.3722 | 10.1949 | 1.485 | 0.56079 | 0.00062898 | 1.2299 | 1.2299
2008-04-26 | 140000 | 256.3 | 2.51 | 13.76 | 21.47 | 13.04 | 27.36 |  | 10.7754 | 2.0741 | 8.7013 | 29340.5416 | 32.2746 | 822862.0642 | 10.1597 | 12.3468 | 10.2025 | 1.5013 | 0.56693 | 0.00063765 | 1.2348 | 1.2348
2008-04-26 | 150000 | 255.2 | 2.48 | 13.77 | 21.32 | 13.04 | 27.417 |  | 10.7905 | 2.0522 | 8.7383 | 29135.5541 | 32.0491 | 818259.1656 | 10.1809 | 12.4421 | 10.2957 | 1.5574 | 0.58814 | 0.00066243 | 1.2738 | 1.2738
2008-04-26 | 160000 | 254.1 | 2.49 | 13.77 | 21.33 | 12.94 | 26.961 |  | 10.7077 | 2.0604 | 8.6473 | 29149.22 | 32.0641 | 818642.9644 | 10.0116 | 12.2295 | 10.1197 | 1.4725 | 0.55605 | 0.00062629 | 1.2049 | 1.2049
2008-04-26 | 170000 | 190.9 | 2.3 | 13.95 | 16.58 | 8.31 | 11.533 |  | 7.0545 | 1.9525 | 5.102 | 22657.9497 | 24.9237 | 652819.2163 | 4.2826 | 6.5602 | 5.5691 | 0.46705 | 0.17637 | 0.0002038 | 0.30476 | 0.30476
2008-04-26 | 180000 | 192.8 | 2.41 | 13.93 | 16.87 | 7.58 | 10.45 |  | 6.4164 | 2.04 | 4.3763 | 23054.2588 | 25.3597 | 662331.6562 | 3.8804 | 5.8588 | 4.9594 | 0.58303 | 0.22017 | 0.00025368 | 0.38599 | 0.38599
2008-04-26 | 190000 | 192 | 2.44 | 13.93 | 16.74 | 7.64 | 10.507 |  | 6.4671 | 2.0654 | 4.4017 | 22876.603 | 25.1643 | 657227.7371 | 3.9016 | 5.9365 | 5.0251 | 0.62341 | 0.23542 | 0.00027125 | 0.40954 | 0.40954
2008-04-26 | 200000 | 193.6 | 2.42 | 13.92 | 16.84 | 7.61 | 10.621 |  | 6.4325 | 2.0456 | 4.387 | 23013.2613 | 25.3146 | 660206.6169 | 3.9439 | 5.9738 | 5.0495 | 0.66253 | 0.25019 | 0.00028785 | 0.43721 | 0.43721
2008-04-26 | 210000 | 193.5 | 2.45 | 13.89 | 16.9 | 7.57 | 10.355 |  | 6.3713 | 2.0621 | 4.3093 | 23095.2563 | 25.4048 | 659723.4096 | 3.8452 | 5.8285 | 4.9056 | 0.59628 | 0.22517 | 0.00025796 | 0.3932 | 0.3932
2008-04-26 | 220000 | 13.2 | 2.08 | 19.59 | 1.59 | 5.08 | 0.513 |  | 22.8794 | 9.3679 | 13.5115 | 2172.8673 | 2.3902 | 332138.3599 | 0.19049 | 0.57354 | 2.5831 | -10.9283 | -4.1269 | -0.025299 | -3.6281
2008-04-26 | 230000 | 1.3 | 0 | 20.82 | 0.04 | -0.01 | 0.171 |  | -0.7375 | 0 | -0.7375 | 54.6633 | 0.06013 | 136824.2929 | 0.063498 | 0.46409 | 34.2264 | 34.9639 | 13.2034 | 1.3254 | 4.7818
2008-04-27 | 0 | 1.3 | 0 | 20.82 | 0.04 | -0.06 | 0.19 |  | -4.425 | 0 | -4.425 | 54.6633 | 0.06013 | 136824.2929 | 0.070554 | 0.51565 | 38.0293 | 42.4543 | 16.032 | 1.6093 | 5.8062
2008-04-27 | 10000 | 1.3 | 0 | 20.75 | 0.04 | -0.07 | 0.171 |  | -2.7533 | 0 | -2.7533 | 54.6633 | 0.06013 | 72972.9562 | 0.063498 | 0.87016 | 34.2264 | 36.9797 | 13.9647 | 0.74764 | 2.6973
2008-04-27 | 20000 | 1.3 | 0 | 20.82 | 0.04 | -0.06 | 0.171 |  | -4.425 | 0 | -4.425 | 54.6633 | 0.06013 | 136824.2929 | 0.063498 | 0.46409 | 34.2264 | 38.6514 | 14.5959 | 1.4652 | 5.2861
2008-04-27 | 30000 | 1.3 | 0 | 20.81 | 0.04 | -0.06 | 0.19 |  | -3.9333 | 0 | -3.9333 | 54.6633 | 0.06013 | 121621.5937 | 0.070554 | 0.58011 | 38.0293 | 41.9626 | 15.8464 | 1.414 | 5.1013
2008-04-27 | 40000 | 1.3 | 0 | 20.74 | 0.04 | -0.07 | 0.19 |  | -2.5812 | 0 | -2.5812 | 54.6633 | 0.06013 | 68412.1465 | 0.070554 | 1.0313 | 38.0293 | 40.6105 | 15.3358 | 0.76973 | 2.777
2008-04-27 | 50000 | 1.3 | 0 | 20.81 | 0.04 | -0.06 | 0.19 |  | -3.9333 | 0 | -3.9333 | 54.6633 | 0.06013 | 121621.5937 | 0.070554 | 0.58011 | 38.0293 | 41.9626 | 15.8464 | 1.414 | 5.1013
2008-04-27 | 60000 | 1.3 | 0 | 20.81 | 0.04 | -0.07 | 0.19 |  | -4.5889 | 0 | -4.5889 | 54.6633 | 0.06013 | 121621.5937 | 0.070554 | 0.58011 | 38.0293 | 42.6182 | 16.0939 | 1.4361 | 5.181
2008-04-27 | 70000 | 1.3 | 0 | 20.81 | 0.04 | -0.06 | 0.171 |  | -3.9333 | 0 | -3.9333 | 54.6633 | 0.06013 | 121621.5937 | 0.063498 | 0.5221 | 34.2264 | 38.1597 | 14.4103 | 1.2858 | 4.639
2008-04-27 | 80000 | 1.3 | 0 | 20.82 | 0.04 | -0.06 | 0.171 |  | -4.425 | 0 | -4.425 | 54.6633 | 0.06013 | 136824.2929 | 0.063498 | 0.46409 | 34.2264 | 38.6514 | 14.5959 | 1.4652 | 5.2861
2008-04-27 | 90000 | 1.3 | 0.02 | 20.82 | 0.04 | 2.08 | 0.171 |  | 153.4 | 1.475 | 151.925 | 54.6633 | 0.06013 | 136824.2929 | 0.063498 | 0.46409 | 34.2264 | -117.6986 | -44.4466 | -4.4617 | -16.0968
2008-04-27 | 100000 | 1.3 | 0.02 | 20.81 | 0.05 | -0.06 | 0.171 |  | -3.9333 | 1.3111 | -5.2444 | 68.3292 | 0.075162 | 152026.9921 | 0.063498 | 0.41768 | 27.3811 | 32.6255 | 12.3204 | 1.0993 | 4.9577
2008-04-27 | 110000 | 1.3 | 0 | 20.81 | 0.04 | -0.06 | 0.152 |  | -3.9333 | 0 | -3.9333 | 54.6633 | 0.06013 | 121621.5937 | 0.056443 | 0.46409 | 30.4234 | 34.3568 | 12.9742 | 1.1577 | 4.1766
2008-04-27 | 120000 | 1.3 | 0.01 | 20.72 | 0.04 | -0.06 | 0.171 |  | -1.9667 | 0.32778 | -2.2944 | 54.6633 | 0.06013 | 60810.7969 | 0.063498 | 1.0442 | 34.2264 | 36.5208 | 13.7914 | 0.6153 | 2.2199
2008-04-27 | 130000 | 1.3 | 0 | 20.79 | 0.04 | -0.07 | 0.152 |  | -3.7545 | 0 | -3.7545 | 54.6633 | 0.06013 | 99508.5767 | 0.056443 | 0.56722 | 30.4234 | 34.178 | 12.9066 | 0.94226 | 3.3995
2008-04-27 | 140000 | 1.3 | 0.01 | 20.78 | 0.04 | -0.07 | 0.171 |  | -3.4417 | 0.49167 | -3.9333 | 54.6633 | 0.06013 | 91216.1953 | 0.063498 | 0.69613 | 34.2264 | 38.1597 | 14.4103 | 0.96436 | 3.4792
2008-04-27 | 150000 | 1.3 | 0 | 20.78 | 0.04 | -0.06 | 0.152 |  | -2.95 | 0 | -2.95 | 54.6633 | 0.06013 | 91216.1953 | 0.056443 | 0.61878 | 30.4234 | 33.3734 | 12.6028 | 0.84341 | 3.0428
2008-04-27 | 160000 | 1.3 | 0 | 20.69 | 0.04 | -0.06 | 0.171 |  | -1.6857 | 0 | -1.6857 | 54.6633 | 0.06013 | 52123.5402 | 0.063498 | 1.2182 | 34.2264 | 35.9121 | 13.5615 | 0.51861 | 1.871
2008-04-27 | 170000 | 1.3 | 0 | 20.77 | 0.04 | -0.06 | 0.152 |  | -2.7231 | 0 | -2.7231 | 54.6633 | 0.06013 | 84199.5649 | 0.056443 | 0.67035 | 30.4234 | 33.1465 | 12.5171 | 0.77324 | 2.7897
2008-04-27 | 180000 | 1.3 | 0 | 20.76 | 0.04 | -0.07 | 0.171 |  | -2.95 | 0 | -2.95 | 54.6633 | 0.06013 | 78185.3102 | 0.063498 | 0.81215 | 34.2264 | 37.1764 | 14.0389 | 0.8053 | 2.9053
2008-04-27 | 190000 | 1.3 | 0 | 20.76 | 0.04 | -0.07 | 0.209 |  | -2.95 | 0 | -2.95 | 54.6633 | 0.06013 | 78185.3102 | 0.077609 | 0.99263 | 41.8322 | 44.7822 | 16.9111 | 0.97005 | 3.4997
2008-04-27 | 200000 | 1.3 | 0 | 20.76 | 0.04 | -0.06 | 0.171 |  | -2.5286 | 0 | -2.5286 | 54.6633 | 0.06013 | 78185.3102 | 0.063498 | 0.81215 | 34.2264 | 36.7549 | 13.8798 | 0.79617 | 2.8724
2008-04-27 | 210000 | 1.3 | 0 | 20.75 | 0.04 | -0.06 | 0.171 |  | -2.36 | 0 | -2.36 | 54.6633 | 0.06013 | 72972.9562 | 0.063498 | 0.87016 | 34.2264 | 36.5864 | 13.8161 | 0.73968 | 2.6686
2008-04-27 | 220000 | 1.3 | 0 | 20.75 | 0.04 | -0.06 | 0.171 |  | -2.36 | 0 | -2.36 | 54.6633 | 0.06013 | 72972.9562 | 0.063498 | 0.87016 | 34.2264 | 36.5864 | 13.8161 | 0.73968 | 2.6686
2008-04-27 | 230000 | 1.3 | 0 | 20.74 | 0.04 | -0.06 | 0.171 |  | -2.2125 | 0 | -2.2125 | 54.6633 | 0.06013 | 68412.1465 | 0.063498 | 0.92817 | 34.2264 | 36.4389 | 13.7604 | 0.69066 | 2.4917
2008-04-28 | 0 | 1.2 | 0 | 20.73 | 0.04 | -0.06 | 0.171 |  | -2.0824 | 0 | -2.0824 | 54.6633 | 0.06013 | 64387.9026 | 0.063498 | 0.98618 | 34.2264 | 36.3087 | 13.7113 | 0.64771 | 2.3368
2008-04-28 | 10000 | 1.3 | 0 | 20.72 | 0.04 | -0.06 | 0.171 |  | -1.9667 | 0 | -1.9667 | 54.6633 | 0.06013 | 60810.7969 | 0.063498 | 1.0442 | 34.2264 | 36.193 | 13.6676 | 0.60978 | 2.1999
2008-04-28 | 20000 | 1.3 | 0.39 | 20.58 | 0.19 | 0.71 | 0.19 |  | 13.0906 | 7.1906 | 5.9 | 259.6508 | 0.28562 | 162478.8479 | 0.070554 | 0.43423 | 8.0062 | 2.1062 | 0.79535 | 0.01996 | 0.34205
2008-04-28 | 30000 | 21.9 | 10.29 | 16.6 | 7.27 | 29.76 | 0.19 |  | 40.8335 | 14.1188 | 26.7147 | 9935.06 | 10.9286 | 462657.0277 | 0.070554 | 0.1525 | 0.20924 | -26.5054 | -10.0093 | -0.018693 | -12.2574
2008-04-28 | 40000 | 54.6 | 10.29 | 15.15 | 9.67 | 30.01 | 1.14 |  | 30.7929 | 10.5584 | 20.2344 | 13214.8597 | 14.5363 | 460205.5348 | 0.42332 | 0.91985 | 0.94385 | -19.2906 | -7.2847 | -0.010174 | -8.8736
2008-04-28 | 50000 | 204.8 | 3.61 | 13.8 | 18.06 | 12.2 | 14.383 |  | 10.138 | 2.9999 | 7.1382 | 24680.4928 | 27.1485 | 696069.5015 | 5.3409 | 7.673 | 6.3761 | -0.76205 | -0.28777 | -0.00032549 | -0.5302
2008-04-28 | 60000 | 262.8 | 3.46 | 12.02 | 22.04 | 12.63 | 26.277 |  | 8.3916 | 2.2989 | 6.0927 | 30119.494 | 33.1314 | 679190.8595 | 9.7576 | 14.3665 | 9.5453 | 3.4526 | 1.3038 | 0.0011791 | 2.3439 | 2.3439
2008-04-28 | 70000 | 262.7 | 2.49 | 13.66 | 21.92 | 12.02 | 24.529 |  | 9.7953 | 2.0291 | 7.7662 | 29955.5041 | 32.9511 | 828505.1108 | 9.1085 | 10.9939 | 8.9591 | 1.1929 | 0.45049 | 0.00049968 | 0.9879 | 0.9879
2008-04-28 | 80000 | 262.1 | 2.56 | 13.62 | 21.94 | 12.46 | 25.878 |  | 10.0981 | 2.0747 | 8.0234 | 29982.8357 | 32.9811 | 824704.6667 | 9.6094 | 11.6519 | 9.4432 | 1.4198 | 0.53617 | 0.00059146 | 1.1704 | 1.1704
2008-04-28 | 90000 | 261.6 | 2.54 | 13.6 | 22 | 12.65 | 26.296 |  | 10.224 | 2.0529 | 8.1711 | 30064.8307 | 33.0713 | 824694.3683 | 9.7646 | 11.8403 | 9.5696 | 1.3985 | 0.5281 | 0.00058096 | 1.1528 | 1.1528
2008-04-28 | 100000 | 260.6 | 2.56 | 13.61 | 21.83 | 12.78 | 26.486 |  | 10.3432 | 2.0719 | 8.2713 | 29832.5116 | 32.8158 | 819444.2564 | 9.8352 | 12.0023 | 9.7138 | 1.4424 | 0.5447 | 0.00060004 | 1.1815 | 1.1815
2008-04-28 | 110000 | 259.1 | 2.54 | 13.62 | 21.79 | 12.77 | 26.524 |  | 10.3493 | 2.0585 | 8.2908 | 29777.8482 | 32.7556 | 819066.303 | 9.8493 | 12.025 | 9.7456 | 1.4548 | 0.54936 | 0.000606 | 1.191 | 1.191
2008-04-28 | 120000 | 258.8 | 2.54 | 13.61 | 21.56 | 12.69 | 26.258 |  | 10.2704 | 2.0557 | 8.2147 | 29463.5341 | 32.4099 | 809309.1236 | 9.7505 | 12.0479 | 9.7507 | 1.5361 | 0.58006 | 0.000639 | 1.2426 | 1.2426
2008-04-28 | 130000 | 257.5 | 2.52 | 13.61 | 21.55 | 12.62 | 26.144 |  | 10.2137 | 2.0395 | 8.1742 | 29449.8683 | 32.3949 | 808933.7483 | 9.7082 | 12.0012 | 9.7129 | 1.5387 | 0.58106 | 0.00064009 | 1.2441 | 1.2441
2008-04-28 | 140000 | 257.4 | 2.55 | 13.61 | 21.55 | 12.65 | 26.049 |  | 10.238 | 2.0638 | 8.1742 | 29449.8683 | 32.3949 | 808933.7483 | 9.6729 | 11.9576 | 9.6776 | 1.5034 | 0.56773 | 0.00062541 | 1.2156 | 1.2156
2008-04-28 | 150000 | 255.8 | 2.43 | 13.63 | 21.42 | 12.78 | 26.866 |  | 10.3717 | 1.9721 | 8.3996 | 29272.2124 | 32.1994 | 806265.8472 | 9.9763 | 12.3734 | 10.0417 | 1.6421 | 0.62012 | 0.000685 | 1.3234 | 1.3234
2008-04-28 | 160000 | 256.1 | 2.53 | 13.62 | 21.43 | 12.79 | 26.372 |  | 10.3655 | 2.0504 | 8.3151 | 29285.8783 | 32.2145 | 805534.2301 | 9.7928 | 12.157 | 9.8525 | 1.5374 | 0.58056 | 0.00064042 | 1.2378 | 1.2378
2008-04-28 | 170000 | 255.6 | 2.35 | 13.66 | 21.44 | 11.9 | 25.175 |  | 9.6975 | 1.9151 | 7.7825 | 29299.5441 | 32.2295 | 810362.6631 | 9.3484 | 11.536 | 9.4009 | 1.6184 | 0.61117 | 0.00067791 | 1.3109 | 1.3109
2008-04-28 | 180000 | 259.5 | 2.55 | 13.6 | 21.76 | 12.68 | 26.125 |  | 10.2482 | 2.061 | 8.1873 | 29736.8507 | 32.7105 | 815697.7025 | 9.7011 | 11.893 | 9.6122 | 1.4249 | 0.53809 | 0.00059195 | 1.1618 | 1.1618
2008-04-28 | 190000 | 258.9 | 2.4 | 13.65 | 21.74 | 11.43 | 23.408 |  | 9.3017 | 1.9531 | 7.3486 | 29709.5191 | 32.6805 | 820568.3113 | 8.6922 | 10.5929 | 8.6204 | 1.2719 | 0.4803 | 0.00053202 | 1.0432 | 1.0432
2008-04-28 | 200000 | 258.5 | 2.47 | 13.72 | 21.73 | 10.61 | 21.223 |  | 8.7185 | 2.0297 | 6.6889 | 29695.8532 | 32.6654 | 828187.1547 | 7.8808 | 9.5158 | 7.8194 | 1.1305 | 0.42691 | 0.00047749 | 0.93585 | 0.93585
2008-04-28 | 210000 | 206 | 2.47 | 13.79 | 17.84 | 7.51 | 10.564 |  | 6.2319 | 2.0496 | 4.1823 | 24379.8445 | 26.8178 | 686623.1746 | 3.9228 | 5.7132 | 4.7409 | 0.55859 | 0.21094 | 0.00023826 | 0.38337 | 0.38337
2008-04-28 | 220000 | 192.1 | 2.5 | 13.81 | 16.91 | 7.6 | 10.07 |  | 6.3244 | 2.0804 | 4.244 | 23108.9221 | 25.4198 | 652665.386 | 3.7393 | 5.7293 | 4.7677 | 0.52371 | 0.19777 | 0.00022401 | 0.34165 | 0.34165
2008-04-28 | 230000 | 17.5 | 2.43 | 19.22 | 2.38 | 7.34 | 2.47 |  | 25.7774 | 8.5339 | 17.2435 | 3252.468 | 3.5777 | 387668.83 | 0.9172 | 2.3659 | 8.3089 | -8.9345 | -3.374 | -0.016128 | -3.4621
2008-04-29 | 0 | 1.3 | 0 | 20.73 | 0.27 | 0.03 | 0.171 |  | 1.0412 | 0 | 1.0412 | 368.9775 | 0.40588 | 434618.3422 | 0.063498 | 0.1461 | 5.0706 | 4.0294 | 1.5216 | 0.07188 | 1.7505
2008-04-29 | 10000 | 1.3 | 0 | 20.72 | 0.25 | -0.05 | 0.209 |  | -1.6389 | 0 | -1.6389 | 341.6458 | 0.37581 | 380067.4804 | 0.077609 | 0.2042 | 6.6932 | 8.332 | 3.1464 | 0.14038 | 3.1653
2008-04-29 | 20000 | 1.3 | 0 | 20.72 | 0.26 | -0.06 | 0.19 |  | -1.9667 | 0 | -1.9667 | 355.3116 | 0.39084 | 395270.1796 | 0.070554 | 0.17849 | 5.8507 | 7.8173 | 2.9521 | 0.13171 | 3.0886
2008-04-29 | 30000 | 1.3 | 0 | 20.71 | 0.07 | 0.04 | 0.19 |  | 1.2421 | 0 | 1.2421 | 95.6608 | 0.10523 | 100817.9001 | 0.070554 | 0.69981 | 21.731 | 20.4889 | 7.7372 | 0.32703 | 2.0647
2008-04-29 | 40000 | 18.3 | 9.79 | 16.88 | 6.71 | 29.22 | 0.342 |  | 42.8851 | 14.3684 | 28.5167 | 9169.7734 | 10.0868 | 456761.6943 | 0.127 | 0.27804 | 0.40806 | -28.1086 | -10.6147 | -0.021205 | -12.8332
2008-04-29 | 50000 | 94.5 | 8.41 | 14.76 | 11.74 | 25.82 | 6.707 |  | 24.8107 | 8.0813 | 16.7295 | 16043.6869 | 17.6481 | 523230.358 | 2.4905 | 4.7599 | 4.5739 | -12.1556 | -4.5903 | -0.0060038 | -6.3573
2008-04-29 | 60000 | 197.9 | 2.35 | 13.77 | 17.38 | 8.43 | 11.723 |  | 6.9757 | 1.9446 | 5.0311 | 23751.2163 | 26.1263 | 667042.4155 | 4.3532 | 6.5261 | 5.4002 | 0.36911 | 0.13939 | 0.00015699 | 0.2461 | 0.2461
2008-04-29 | 70000 | 265.1 | 3.19 | 12.09 | 22.18 | 12.07 | 27.645 |  | 8.0832 | 2.1363 | 5.9469 | 30310.8157 | 33.3419 | 688935.9403 | 10.2656 | 14.9006 | 9.9788 | 4.032 | 1.5226 | 0.0013879 | 2.7765 | 2.7765
2008-04-29 | 80000 | 267.5 | 2.48 | 13.58 | 22.27 | 12.42 | 26.106 |  | 10.0107 | 1.9989 | 8.0117 | 30433.8082 | 33.4772 | 832534.7004 | 9.6941 | 11.644 | 9.3852 | 1.3735 | 0.51867 | 0.00056902 | 1.143 | 1.143
2008-04-29 | 90000 | 266.7 | 2.5 | 13.57 | 22.27 | 12.43 | 26.581 |  | 10.005 | 2.0123 | 7.9928 | 30433.8082 | 33.4772 | 831398.9096 | 9.8705 | 11.8721 | 9.556 | 1.5632 | 0.59032 | 0.00064675 | 1.2991 | 1.2991
2008-04-29 | 100000 | 265.4 | 2.5 | 13.58 | 22.25 | 12.35 | 26.733 |  | 9.9542 | 2.015 | 7.9392 | 30406.4765 | 33.4471 | 831787.0267 | 9.9269 | 11.9344 | 9.6193 | 1.6801 | 0.63444 | 0.00069604 | 1.3968 | 1.3968
2008-04-29 | 110000 | 264.4 | 2.5 | 13.59 | 22.19 | 12.47 | 26.942 |  | 10.0647 | 2.0178 | 8.0469 | 30324.4815 | 33.3569 | 830678.8126 | 10.0045 | 12.0438 | 9.7207 | 1.6738 | 0.63207 | 0.00069438 | 1.3897 | 1.3897
2008-04-29 | 120000 | 263.4 | 2.49 | 13.6 | 22.05 | 12.6 | 27.341 |  | 10.1836 | 2.0125 | 8.1711 | 30133.1599 | 33.1465 | 826568.6737 | 10.1527 | 12.2829 | 9.9273 | 1.7562 | 0.66319 | 0.00072957 | 1.451 | 1.451
2008-04-29 | 130000 | 263.8 | 2.49 | 13.61 | 22.07 | 12.51 | 27.094 |  | 10.1247 | 2.0152 | 8.1095 | 30160.4915 | 33.1765 | 828453.2634 | 10.0609 | 12.1443 | 9.8287 | 1.7192 | 0.64923 | 0.00071519 | 1.4237 | 1.4237
2008-04-29 | 140000 | 263.4 | 2.48 | 13.62 | 22.05 | 12.54 | 27.132 |  | 10.1629 | 2.0099 | 8.153 | 30133.1599 | 33.1465 | 828839.4668 | 10.0751 | 12.1556 | 9.8514 | 1.6984 | 0.64136 | 0.00070749 | 1.407 | 1.407
2008-04-29 | 150000 | 262.8 | 2.48 | 13.63 | 22.05 | 12.6 | 27.36 |  | 10.2256 | 2.0127 | 8.2129 | 30133.1599 | 33.1465 | 829979.5486 | 10.1597 | 12.2409 | 9.9342 | 1.7213 | 0.65 | 0.00071801 | 1.428 | 1.428
2008-04-29 | 160000 | 262.6 | 2.47 | 13.63 | 22.05 | 12.59 | 27.474 |  | 10.2175 | 2.0045 | 8.2129 | 30133.1599 | 33.1465 | 829979.5486 | 10.2021 | 12.2919 | 9.9756 | 1.7626 | 0.66563 | 0.00073527 | 1.4623 | 1.4623
2008-04-29 | 170000 | 263.3 | 2.47 | 13.64 | 22.05 | 12.52 | 27.17 |  | 10.1747 | 2.0073 | 8.1674 | 30133.1599 | 33.1465 | 831122.7711 | 10.0892 | 12.1392 | 9.8652 | 1.6978 | 0.64116 | 0.00070921 | 1.4105 | 1.4105
2008-04-29 | 180000 | 264 | 2.46 | 13.65 | 22.1 | 12.54 | 27.189 |  | 10.205 | 2.0019 | 8.203 | 30201.489 | 33.2216 | 834156.379 | 10.0962 | 12.1035 | 9.8498 | 1.6467 | 0.62185 | 0.00068881 | 1.373 | 1.373
2008-04-29 | 190000 | 264.7 | 2.47 | 13.65 | 22.26 | 12.63 | 26.885 |  | 10.2782 | 2.0101 | 8.2681 | 30420.1423 | 33.4622 | 840195.5202 | 9.9833 | 11.8822 | 9.6696 | 1.4015 | 0.52924 | 0.00058623 | 1.177 | 1.177
2008-04-29 | 200000 | 265.2 | 2.45 | 13.66 | 22.21 | 12.63 | 27.265 |  | 10.2924 | 1.9965 | 8.2959 | 30351.8132 | 33.387 | 839466.1729 | 10.1244 | 12.0606 | 9.8284 | 1.5325 | 0.57872 | 0.00064192 | 1.2859 | 1.2859
2008-04-29 | 210000 | 186.7 | 2.49 | 13.85 | 16.49 | 8.48 | 10.241 |  | 7.0967 | 2.0838 | 5.0129 | 22534.9572 | 24.7885 | 640065.9831 | 3.8028 | 5.9413 | 4.9722 | -0.040734 | -0.015382 | -1.7522e-05 | -0.026061
2008-04-29 | 220000 | 9.3 | 1.82 | 19.89 | 1.34 | 5.16 | 0.608 |  | 30.1426 | 10.6317 | 19.5109 | 1831.2215 | 2.0143 | 363058.5199 | 0.22577 | 0.62186 | 3.6326 | -15.8782 | -5.9961 | -0.047676 | -5.7621
2008-04-29 | 230000 | 1.3 | 0 | 20.72 | 0.51 | -0.01 | 0.171 |  | -0.32778 | 0 | -0.32778 | 696.9574 | 0.76665 | 775337.6599 | 0.063498 | 0.081898 | 2.6844 | 3.0122 | 1.1375 | 0.050749 | 2.3344
2008-04-30 | 0 | 1.3 | 0 | 20.8 | 0.3 | -0.06 | 0.19 |  | -3.54 | 0 | -3.54 | 409.975 | 0.45097 | 820945.7576 | 0.070554 | 0.085942 | 5.0706 | 8.6106 | 3.2516 | 0.26113 | 7.0656
2008-04-30 | 10000 | 1.3 | 0 | 20.81 | 0.27 | -0.06 | 0.171 |  | -3.9333 | 0 | -3.9333 | 368.9775 | 0.40588 | 820945.7576 | 0.063498 | 0.077348 | 5.0706 | 9.0039 | 3.4001 | 0.30339 | 7.3884
2008-04-30 | 20000 | 1.3 | 0 | 20.81 | 0.26 | -0.07 | 0.19 |  | -4.5889 | 0 | -4.5889 | 355.3116 | 0.39084 | 790540.3592 | 0.070554 | 0.089247 | 5.8507 | 10.4395 | 3.9423 | 0.35177 | 8.2492
2008-04-30 | 30000 | 1.3 | 0 | 20.82 | 0.29 | 0.14 | 0.19 |  | 10.325 | 0 | 10.325 | 396.3091 | 0.43594 | 991976.1237 | 0.070554 | 0.071124 | 5.2454 | -5.0796 | -1.9182 | -0.19256 | -5.0366
2008-04-30 | 40000 | 20.3 | 10.13 | 16.83 | 7.08 | 29.31 | 0.152 |  | 42.4887 | 14.6848 | 27.8039 | 9675.4092 | 10.643 | 476027.5155 | 0.056443 | 0.11857 | 0.17188 | -27.632 | -10.4347 | -0.020589 | -13.1477
2008-04-30 | 50000 | 111.4 | 7.32 | 14.63 | 12.86 | 22.5 | 5.472 |  | 21.1722 | 6.888 | 14.2842 | 17574.2601 | 19.3317 | 561263.2877 | 2.0319 | 3.6203 | 3.4067 | -10.8775 | -4.1077 | -0.0052612 | -6.1024
2008-04-30 | 60000 | 197.9 | 2.37 | 13.87 | 17.65 | 8.28 | 12.464 |  | 6.9491 | 1.989 | 4.96 | 24120.1937 | 26.5322 | 687040.9019 | 4.6283 | 6.7366 | 5.6538 | 0.69373 | 0.26197 | 0.00029926 | 0.47641 | 0.47641
2008-04-30 | 70000 | 265.4 | 2.31 | 13.98 | 22.31 | 11.48 | 24.168 |  | 9.7879 | 1.9695 | 7.8184 | 30488.4715 | 33.5373 | 882239.8772 | 8.9744 | 10.1723 | 8.6729 | 0.85457 | 0.32271 | 0.00037451 | 0.7536 | 0.7536
2008-04-30 | 80000 | 266 | 3.45 | 12.02 | 22.24 | 11.22 | 22.838 |  | 7.4547 | 2.2922 | 5.1625 | 30392.8107 | 33.4321 | 685354.1159 | 8.4805 | 12.374 | 8.2214 | 3.0589 | 1.1551 | 0.0010447 | 2.0955 | 2.0955
2008-04-30 | 90000 | 262.6 | 2.43 | 13.77 | 21.99 | 11.79 | 24.111 |  | 9.7561 | 2.0108 | 7.7453 | 30051.1649 | 33.0563 | 843973.6891 | 8.9533 | 10.6085 | 8.7784 | 1.0331 | 0.39012 | 0.0004394 | 0.8715 | 0.8715
2008-04-30 | 100000 | 192.7 | 2.32 | 13.91 | 16.93 | 7.82 | 10.659 |  | 6.6006 | 1.9582 | 4.6423 | 23136.2538 | 25.4499 | 662785.4876 | 3.9581 | 5.9719 | 5.0406 | 0.39828 | 0.1504 | 0.00017279 | 0.26385 | 0.26385
2008-04-30 | 110000 | 192.2 | 2.38 | 13.9 | 16.93 | 7.77 | 10.678 |  | 6.549 | 2.006 | 4.543 | 23136.2538 | 25.4499 | 661838.6512 | 3.9651 | 5.9911 | 5.0496 | 0.50661 | 0.19131 | 0.00021948 | 0.33514 | 0.33514
2008-04-30 | 120000 | 192.5 | 2.4 | 13.91 | 16.94 | 7.71 | 10.64 |  | 6.5077 | 2.0258 | 4.482 | 23149.9196 | 25.4649 | 663176.9735 | 3.951 | 5.9577 | 5.0287 | 0.54669 | 0.20645 | 0.00023718 | 0.36239 | 0.36239
2008-04-30 | 130000 | 198.3 | 2.41 | 13.9 | 17.42 | 8 | 12.293 |  | 6.7429 | 2.0313 | 4.7116 | 23805.8796 | 26.1865 | 680994.0522 | 4.5648 | 6.7032 | 5.6498 | 0.93824 | 0.35431 | 0.00040648 | 0.63865 | 0.63865
2008-04-30 | 140000 | 263.5 | 2.27 | 13.71 | 22.22 | 12.92 | 28.728 |  | 10.6019 | 1.8627 | 8.7392 | 30365.479 | 33.402 | 845684.5032 | 10.6677 | 12.6143 | 10.3511 | 1.6119 | 0.60869 | 0.00067986 | 1.3625 | 1.3625
2008-04-30 | 150000 | 263.6 | 2.45 | 13.73 | 22.2 | 12.89 | 27.93 |  | 10.6068 | 2.016 | 8.5908 | 30338.1474 | 33.372 | 847280.1403 | 10.3714 | 12.2408 | 10.0726 | 1.4818 | 0.55958 | 0.00062675 | 1.255 | 1.255
2008-04-30 | 160000 | 264 | 2.43 | 13.74 | 22.22 | 12.8 | 27.683 |  | 10.5475 | 2.0024 | 8.5451 | 30365.479 | 33.402 | 849227.874 | 10.2797 | 12.1047 | 9.9746 | 1.4294 | 0.5398 | 0.00060544 | 1.2134 | 1.2134
2008-04-30 | 170000 | 264.3 | 2.44 | 13.74 | 22.27 | 12.71 | 27.417 |  | 10.4733 | 2.0106 | 8.4627 | 30433.8082 | 33.4772 | 851138.8278 | 10.1809 | 11.9615 | 9.8565 | 1.3938 | 0.52635 | 0.00059035 | 1.1858 | 1.1858
2008-04-30 | 180000 | 264.7 | 2.43 | 13.74 | 22.27 | 12.66 | 27.17 |  | 10.4321 | 2.0024 | 8.4297 | 30433.8082 | 33.4772 | 851138.8278 | 10.0892 | 11.8537 | 9.7677 | 1.338 | 0.50527 | 0.00056671 | 1.1383 | 1.1383
2008-04-30 | 190000 | 264.7 | 2.39 | 13.76 | 22.25 | 12.42 | 26.676 |  | 10.263 | 1.9749 | 8.2881 | 30406.4765 | 33.4471 | 852756.4475 | 9.9057 | 11.6161 | 9.5988 | 1.3107 | 0.49495 | 0.00055669 | 1.1172 | 1.1172
2008-04-30 | 200000 | 263.4 | 2.4 | 13.82 | 22.22 | 11.64 | 24.795 |  | 9.7 | 2 | 7.7 | 30365.479 | 33.402 | 858823.6692 | 9.2072 | 10.7208 | 8.934 | 1.234 | 0.46599 | 0.00052855 | 1.0593 | 1.0593
2008-04-30 | 210000 | 260.5 | 2.34 | 13.84 | 21.99 | 11.21 | 23.37 |  | 9.3681 | 1.9555 | 7.4126 | 30051.1649 | 33.0563 | 852341.7001 | 8.6781 | 10.1815 | 8.5086 | 1.096 | 0.41388 | 0.00047078 | 0.93374 | 0.93374
2008-04-30 | 220000 | 20.5 | 2.67 | 19.43 | 2.35 | 6.8 | 0.304 |  | 27.2925 | 10.7163 | 16.5762 | 3211.4706 | 3.5326 | 437465.4264 | 0.11289 | 0.25805 | 1.0357 | -15.5405 | -5.8686 | -0.03206 | -6.7954
2008-04-30 | 230000 | 1.3 | 0 | 20.95 | 0.15 | 0 | 0.171 |  | 0 | 0 | 0 | 204.9875 | 0.22549 | -820945.7576 | 0.063498 | -0.077348 | 9.127 | 9.127 | 3.4466 | -0.55358 | -7.4894
2008-05-01 | 0 | 1.3 | 0 | 20.95 | 0.35 | -0.05 | 0.171 |  | 5.9 | 0 | 5.9 | 478.3041 | 0.52613 | -1915540.101 | 0.063498 | -0.033149 | 3.9116 | -1.9884 | -0.75089 | 0.1206 | 3.8072
[7 empty] | total aqueous NH3 flow | [13 empty] | Total NH3 (lbs): | 733.0266
133.8
132.4
131.5
129.7
129.2
129.6
131.2
130.5
136
133.8
138.1
140.2
139.9
139.8
140.9
141.7
143.1
142.6
140.3
139.2
138
137.1
134.2
133.1
51
53.3
53
54.1
133.4
110.9
121.2
130.4
132.4
135.3
139.9
137.4
141.1
61.8
52.4
52.5
52.8
52.6
52.6
51.2
50.6
50.1
48.7
49.3
49.1
49.1
49.4
50
49.8
55.1
124.5
134.1
143
137.6
146.1
148.8
148.7
149.9
142.7
152.6
153.1
150.4
147.4
138.4
144.5
143
139.6
140.2
139.3
139.1
139
139
139.3
139.2
137.7
136.6
126.7
128.3
140.3
138.3
137.8
136.5
139.2
140.7
139
140.2
138.7
138.6
138.5
138.7
138.8
138.6
138.8
138.3
137.2
136.8
136.3
136
136.5
142.3
138.9
137.2
139
139.2
136.5
136.7
139
136.2
169
169.5
168.4
173.6
172.8
172.7
175.4
139.1
136.4
136.9
136.9
136.7
137.2
136.5
64
0.9
0.9
56.9
96.6
139.2
144.8
144.7
62.7
55.2
55.1
55.3
62
143.4
135.5
141.5
140.9
9.1
0.9
0.8
0.9
1
1
0.9
0.9
0.9
0.8
40.3
103.4
141
180.5
140.6
144.7
143.6
143.8
143.5
143.7
143.9
142.6
136.9
136.4
141.3
140.7
140.4
139.8
139.6
139.5
139.1
138.5
138.7
138.6
53.3
140.4
143.3
142.7
143.4
142.2
139.6
141.2
52
59.5
141.9
139.9
129.9
139.3
139.2
138.5
138.5
138.2
133.6
56.7
138.8
52.8
130.7
138.8
143.4
140
139.7
139.3
140.8
142.5
143.3
143.8
143.8
142.8
143.1
143.5
143.4
142.4
142.1
142.2
141.8
141.8
142.4
142
141.7
141.8
140.9
141.9
142.7
144.6
145.2
146.9
148.4
148.1
147.9
147.4
147.2
148.3
148.6
148.5
147.5
147
145.8
145
144.9
145.3
144.6
144.5
145.3
144.7
144.1
145.2
145.2
147.9
151
150
151.9
154.8
151.3
147.8
143.1
142
133.5
132
149.2
146.1
147.4
147.9
147
146.5
145.5
145.3
144.6
143.1
142.1
144.8
131.8
129.6
137.8
137.2
132.2
130.7
131.4
98.1
78.2
100
131.9
134.6
132.4
141.7
141.8
141.5
141.5
141
141.9
142.1
141.4
53.8
53.6
55.2
65.3
83.4
96.1
111.4
125.6
142.3
54.9
57
132.2
136.5
135.2
140.3
140.5
140.8
140.2
53.1
54.2
54.1
54.2
56.3
55
63.4
130.1
132.6
141.5
138.4
142.7
142.4
140.5
141
142.3
142.1
143.6
143.8
143.8
144.1
143
68.4
54.9
54.6
54.2
54.6
54.2
54.8
140.5
117.2
142.6
140.5
141.8
148.8
142.6
146
143.7
143.9
144.8
145.1
145.8
145.6
145.6
144.9
52.3
54.6
54
8.9
1
0.9
1
15
91.9
133.4
134.1
130.7
140.7
145.3
144.9
146.2
145.2
145.8
146.1
146.2
145.4
144.8
144.4
144.6
145.7
146.7
79.5
55.8
54.8
55
56.9
56.7
142.6
142.2
142
142.5
142.5
143.7
144.5
145.8
144.7
144.2
144
144.6
144.3
143.3
143.1
143.3
142.7
142.5
51.3
54.8
55.1
55.3
55.2
55.4
142
126.6
125.2
133.9
127.5
129
139.4
138.2
138.7
141.5
141.3
140.5
140
139.8
139.4
139.5
138.5
138.7
138.2
138.1
135.9
135.9
134.8
136.2
136.2
135.4
136.2
153.5
138
141.3
140.9
130.9
133.4
137.7
136.8
136.8
135.5
136
135.8
134.7
54.5
56.3
56.2
56.1
2.6
0.8
0.9
0.8
0.9
0.9
0.9
0.8
0.9
0.9
36.3
155.1
135.3
126.5
133.8
134.8
63.6
142.1
131.9
122.6
139
138.7
138.4
52.6
53.4
53.4
53.9
54.1
140
138.7
135.2
137.2
137.8
140.7
140.5
139.8
138.9
139.7
138.8
137.5
138.2
137.4
137.7
137.5
137.4
137.2
137.1
137.2
137.8
137.4
136.7
136.5
136.3
136.4
137.9
138
138.9
140.2
139.8
138.9
138.6
138.9
140.1
140
140.7
138.8
137.8
138.1
138.9
138.6
136.7
51.7
55.6
53.4
54.8
56.7
142
141
140.6
139.9
60.1
56.5
56.3
56.5
56
55.6
55.9
54.9
55.8
55.9
56.2
55.9
54.3
13.6
1.1
1
1
1
0.9
1
2.8
66.8
58.6
57.2
59.4
59.4
58.3
59.1
57.2
56.8
59.6
146.5
157.6
147.9
146.9
147.6
142.8
7.9
1
0.9
0.9
1
0.8
2.8
60.5
144.4
143.5
143.7
148.8
148.3
148.6
96.3
152.7
152.8
152.2
124.4
59
58
65.1
147.4
54.1
8.3
1
0.9
0.9
1
1
1.3
47.1
61.5
123.6
121.9
138.1
152.2
148.8
148
145.3
144
144.3
141.9
60.7
55
55.3
55.9
54.5
2.7
0.9
1
0.9
0.9
1
1
1
1
0.9
0.9
0.9
0.9
0.8
0.9
0.8
0.9
0.8
0.9
0.8
0.9
1.1
0.9
0.9
0.9
0.9
0.9
0.9
1
1
6
75.7
138.3
129.1
136.2
138.4
139.4
139.6
138.2
137.6
137.1
141.4
138.8
132.5
137.5
123.2
111.7
55.6
53
13
0.9
1.1
1
1
1.8
35.3
61.7
145.5
137.4
139.9
140.7
141.8
143.9
142.6
142.8
144
144.6
143
143.1
141.5
143.5
53.9
3.2
0.9
1
0.9
1
1
0.8
28.8
65.6
127.2
120.2
126.9
56.1
56.2
56
64.7
151.2
147
145.7
144.3
143
140.4
130.5
123
1.6
0.9
0.9
Note on F125: LINERRO: Total gas flow while duct burners were operating is derived from CEMS CT gas flow data and PI data for duct burner flow

## May CEMS data
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-01
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | 7.1 | 4 | 2.4 | 0 | 0 | 0 | 0.0C | 0 | 433.3 | 0.5 | HS | 3:00
| 3 | 63.3 | 4.2 | 132.8 | 0 | 0 | 0 | 0.0C | 0 | 580.1 | 17.8 | HS
| 4 | 43.4 | 6.4 | 182.3 | 19.3 | 49.3 | 0 | 0.0C | 0 | 630.3 | 89.2 |  |  | 4:47 |  |  | Dur. 107 min
| 5 | 2 | 6.2 | 12.7 | 0.2 | 0.6 | 0 | 0.16153 | 0.3722 | 667.4 | 180.2
| 6 | 2 | 6 | 13.1 | 0 | 0 | 0 | 1.3005 | 2.458 | 675.3 | 185.2
| 7 | 2.1 | 5.8 | 14.9 | 0.2 | 0.6 | 0 | 0.39828 | 0.91939 | 676.5 | 184.8
| 8 | 2 | 4 | 13.1 | 0.2 | 0.6 | 0 | 0.4675 | 1.07 | 676.5 | 185.2
| 9 | 2 | 4 | 13 | 0.2 | 0.6 | 0 | 0.48425 | 1.1039 | 675.7 | 184.5
| 10 | 2 | 4 | 12.9 | 0.2 | 0.6 | 0 | 0.50936 | 1.1535 | 674.9 | 183.4
| 11 | 2 | 4 | 12.9 | 0.1 | 0.3 | 0 | 0.45491 | 1.0331 | 675.3 | 182
| 12 | 2 | 4 | 12.9 | 0.2 | 0.6 | 0 | 0.51418 | 1.1634 | 674.5 | 182.1
| 13 | 2 | 4 | 12.9 | 0.1 | 0.3 | 0 | 0.51825 | 1.1709 | 674.5 | 181.9
| 14 | 2 | 4 | 12.8 | 0.2 | 0.6 | 0 | 0.53016 | 1.1929 | 674.1 | 181.4
| 15 | 2 | 4 | 12.8 | 0.2 | 0.6 | 0 | 0.56216 | 1.2586 | 672.5 | 180.9
| 16 | 2 | 4 | 12.8 | 0.2 | 0.6 | 0 | 0.5797 | 1.2949 | 672.5 | 180.5
| 17 | 2 | 4 | 12.8 | 0.2 | 0.6 | 0 | 0.5865 | 1.3101 | 672.5 | 179.9
| 18 | 2 | 4 | 12.8 | 0.1 | 0.3 | 0 | 0.56389 | 1.2561 | 672.5 | 180.4
| 19 | 2 | 4 | 12.8 | 0.2 | 0.6 | 0 | 0.55519 | 1.2349 | 673.7 | 181.2
| 20 | 1.9 | 4 | 12.7 | 0.2 | 0.6 | 0 | 0.47211 | 1.0479 | 675.3 | 178.9
| 21 | 38.2 | 4.1 | 91.9 | 0 | 0 | 0 | 0.0C | 0 | 647.2 | 37.6 | SD |  |  | 21:00 | 21:22
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-02
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-03
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-04
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-05
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | 30.8X | 4.2 | 33.3 | 0.0X | 0 | 0 | 0 | 0 | 152.3 | 3.3 | CS | 0:53
| 1 | 68.3X | 4.3 | 144.3 | 0.0X | 0 | 0 | 0 | 0 | 474.4 | 18.4 | CS
| 2 | 65.5X | 4.4 | 141 | 0.0X | 0 | 0 | 0 | 0 | 602.6 | 20.5 | CS
| 3 | 39.8X | 4.4 | 105.9 | 0.0X | 0 | 0 | 0 | 0 | 602.3 | 35.1 | CS
| 4 | 46.8X | 4.4 | 136.7 | 0.0X | 0 | 0 | 0 | 0 | 601.9 | 43.9 | CS
| 5 | 4.1X | 4.4 | 26.3 | 0.0X | 0 | 0 | 0.64623 | 1.1423 | 650.4 | 172.1 |  |  | 5:04 |  |  | Dur. 4 hr 11 min vs. 6 hr permit limit
| 6 | 2 | 2.1 | 14.7 | 0.2 | 1 | 0 | 0.47638 | 1.0585 | 663.8 | 181.7
| 7 | 2 | 2.1 | 14.6 | 0.2 | 0.6 | 0 | 0.46232 | 1.0199 | 666.6 | 180.6
| 8 | 2 | 2.1 | 12.8 | 0.2 | 0.6 | 0 | 0.42468 | 0.93426 | 666.2 | 180.4
| 9 | 2.2 | 2.1 | 14.6 | 0.2 | 0.6 | 0 | 0.39543 | 0.86477 | 670.1 | 179.3
| 10 | 2.3 | 2.1 | 14.5 | 0.2 | 0.6 | 0 | 0.38948 | 0.84788 | 669 | 177.8
| 11 | 2.3 | 2.2 | 14.3 | 0.2 | 0.6 | 0 | 0.40196 | 0.86662 | 667.4 | 176.4
| 12 | 2.3 | 2.2 | 16.1 | 0.2 | 0.6 | 0 | 0.41049 | 0.88337 | 667.4 | 175.3
| 13 | 2.3 | 2.2 | 14.2 | 0.2 | 0.6 | 0 | 0.40281 | 0.86642 | 667 | 174.3
| 14 | 2.3 | 2.2 | 14.1 | 0.2 | 0.6 | 0 | 0.43526 | 0.92838 | 665.8 | 173.2
| 15 | 2.3 | 2.2 | 14.1 | 0.2 | 0.6 | 0 | 0.43043 | 0.91683 | 665.8 | 173.4
| 16 | 2.3 | 2.2 | 14.3 | 0.2 | 0.6 | 0 | 0.41492 | 0.89371 | 666.6 | 174.7
| 17 | 2.3 | 2.3 | 14.3 | 0.2 | 0.6 | 0 | 0.45931 | 0.99301 | 667.4 | 176.2
| 18 | 2.1 | 2.3 | 14.4 | 0.2 | 0.6 | 0 | 0.43279 | 0.94522 | 668.6 | 177.1
| 19 | 2.1 | 2.3 | 14.3 | 0.2 | 0.6 | 0 | 0.47269 | 1.0358 | 671.3 | 177.1
| 20 | 2.1 | 2.3 | 14.6 | 0.2 | 0.6 | 0 | 0.54312 | 1.1992 | 671.3 | 180.7
| 21 | 27.8 | 2.3 | 81.7 | 0 | 0 | 0 | 0 | 0 | 651.6 | 56.2 | SD |  |  | 20:59 | 21:19
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-06
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | 38.2 | 2.3 | 46 | 0 | 0 | 0 | 0 | 0 | 481.1 | 6.2 | HS | 3:53
| 4 | 49.4 | 2.3 | 137.7 | 0 | 0 | 0 | 0 | 0 | 595.5 | 40.3 | HS |  | 5:03 |  |  | Dur. 66 min
| 5 | 1.7 | 2.3 | 9.2 | 0.2 | 0.8 | 0 | 0.2017 | 0.38153 | 633 | 144.7
| 6 | 2.2 | 2.3 | 14.7 | 0 | 0 | 0 | 1.3426 | 2.4627 | 659.9 | 182
| 7 | 2.1 | 2.3 | 14.7 | 0.2 | 1 | 0 | 0.48264 | 1.076 | 670.9 | 181.7
| 8 | 2.1 | 2.3 | 14.6 | 0.2 | 0.6 | 0 | 0.4662 | 1.0294 | 672.1 | 181.5
| 9 | 2 | 2.2 | 14.5 | 0.2 | 0.6 | 0 | 0.41942 | 0.92747 | 671.7 | 179.5
| 10 | 2.2 | 2.2 | 14.4 | 0.2 | 0.6 | 0 | 0.43081 | 0.94924 | 673.3 | 177.9
| 11 | 2.1 | 2.2 | 14.6 | 0.2 | 0.6 | 0 | 0.51993 | 1.147 | 672.9 | 180.5
| 12 | 2 | 2.2 | 14.5 | 0.2 | 0.6 | 0 | 0.50674 | 1.1108 | 672.1 | 178.6
| 13 | 2.1 | 2.2 | 10.9 | 0.3 | 0.7 | 0 | 0.073632 | 0.12477 | 639 | 121.3
| 14 | 2.1 | 2.2 | 10.9 | 0.3 | 0.7 | 0 | 0.16304 | 0.27588 | 633.4 | 121.4
| 15 | 2.1 | 2.1 | 10.9 | 0.3 | 0.7 | 0 | 0.14722 | 0.24972 | 634.2 | 122.8
| 16 | 2.1 | 2.1 | 10.8 | 0.3 | 0.7 | 0 | 0.14204 | 0.23977 | 633.4 | 121.5
| 17 | 45.4 | 2.1 | 88.6 | 0 | 0 | 0 | 0.0C | 0 | 627.5 | 26.7 | SD |  |  | 17:00 | 17:16
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-07
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-08
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-09
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-10
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-11
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-12
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-13
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-14
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-15
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-16
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-17
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-18
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-19
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-20
|  |  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-21
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-22
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-23
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-24
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-25
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-26
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-27
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-28
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-29
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-30
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-05-31
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load |  | Start-up begin | Start-up complete | Shutdown begin | Shutdown complete
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup

## May CEMS Raw data
This data is raw hourly CEMs database data which may include invalid data such as values obtained during calibration checks.
May
| Record# | DATE | TIME | CATTMP12 | COH13 | CO_14 | CO_COR15 | CO_HCOR16 | GAS17 | GEN18 | GEN29 | HGAS110 | NH3FLO112 | NOX113 | NOX1I14 | NOXCOR115 | NOXH116 | NOXHCOR117 | NOXHRT118 | NOXRT119 | OXY120
| 1 | 2008-05-01 | 0 | 405.2 | -2.5 | 0.26 | 0 | 0 | 0.35 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.05 | 0 | 0.01 | 0 | 19 | 0.001 | 20.95
| 2 | 2008-05-01 | 10000 | 395.8 | -2.6 | 0.28 | 0 | 0 | 0.26 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.006 | 0 | 20.95
| 3 | 2008-05-01 | 20000 | 387.9 | -2.6 | 0.27 | 0 | 0 | 0.26 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.006 | 0 | 20.96
| 4 | 2008-05-01 | 30000 | 389.8 | -2.6 | 0.24 | 0.2 | -0.4 | 0.32 | 0.5 | 1.3 | -1 | 1 | 0.16 | 0.44 | 0.7 | 0.16 | 0.6 | 0.008 | 0.003 | 20.84
| 5 | 2008-05-01 | 40000 | 579.9 | 22.1 | 16.52 | 25.5 | 32.3 | 6.87 | 17.7 | 18.2 | -1 | 1 | 10.26 | 29.58 | 16 | 40.75 | 63 | 0.232 | 0.059 | 17.08
| 6 | 2008-05-01 | 50000 | 630.1 | 20.3 | 13.63 | 14.5 | 22 | 13.71 | 88.8 | 120.8 | -1 | 59.3 | 7.94 | 25.26 | 8.2 | 45.01 | 46.8 | 0.172 | 0.03 | 14.84
| 7 | 2008-05-01 | 60000 | 667.5 | -2.8 | 0.16 | 0.1 | -2.5 | 21.95 | 180.2 | 260 | -1 | 97.6 | 2.27 | 9.68 | 1.9 | 2.16 | 1.8 | 0.007 | 0.007 | 14
| 8 | 2008-05-01 | 70000 | 675.5 | 93.7 | 3.35 | 2 | 23.6 | 22.52 | 185.2 | 268.3 | -1 | 136 | 3.39 | 11.79 | 2.7 | 9.56 | 4.4 | 56.995 | 49.074 | 12.27
| 9 | 2008-05-01 | 80000 | 676.5 | -2.8 | 0.2 | 0.2 | -2.1 | 22.5 | 184.8 | 267.8 | -1 | 133.4 | 2.46 | 11.99 | 2.1 | 2.35 | 2 | 0.007 | 0.008 | 13.84
| 10 | 2008-05-01 | 90000 | 676.6 | -2.9 | 0.16 | 0.1 | -2.3 | 22.53 | 185.2 | 268.4 | -1 | 146.9 | 2.45 | 12.94 | 2 | 2.34 | 2 | 0.007 | 0.007 | 13.77
| 11 | 2008-05-01 | 100000 | 675.7 | -2.8 | 0.15 | 0.1 | -2.3 | 22.44 | 184.5 | 267.7 | -1 | 147.7 | 2.41 | 12.96 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.77
| 12 | 2008-05-01 | 110000 | 675 | -2.4 | 0.16 | 0.1 | -2 | 22.26 | 183.4 | 266.2 | -1 | 145 | 2.43 | 12.76 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.78
| 13 | 2008-05-01 | 120000 | 675.3 | -2.7 | 0.15 | 0.1 | -2.3 | 22.23 | 182 | 264.4 | -1 | 139.7 | 2.43 | 12.47 | 2 | 2.31 | 1.9 | 0.007 | 0.007 | 13.81
| 14 | 2008-05-01 | 130000 | 674.6 | -2.4 | 0.15 | 0.1 | -2.1 | 22.21 | 182.1 | 264.6 | -1 | 145.4 | 2.43 | 12.79 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.79
| 15 | 2008-05-01 | 140000 | 674.7 | -2.9 | 0.15 | 0.1 | -2.4 | 22.24 | 181.9 | 264.8 | -1 | 147.7 | 2.43 | 12.98 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.77
| 16 | 2008-05-01 | 150000 | 674.3 | -2.6 | 0.15 | 0.1 | -2.3 | 22.15 | 181.5 | 264.3 | -1 | 147.2 | 2.44 | 12.96 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.77
| 17 | 2008-05-01 | 160000 | 672.7 | -3 | 0.16 | 0.1 | -2.4 | 22.07 | 180.9 | 263.6 | -1 | 148.8 | 2.45 | 13.06 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.76
| 18 | 2008-05-01 | 170000 | 672.8 | -2.6 | 0.16 | 0.1 | -2.1 | 22.05 | 180.5 | 263.1 | -1 | 149.4 | 2.43 | 13.06 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.75
| 19 | 2008-05-01 | 180000 | 672.9 | -2.7 | 0.15 | 0.1 | -2.2 | 22.05 | 180 | 262.6 | -1 | 149.9 | 2.44 | 13.09 | 2 | 2.33 | 1.9 | 0.007 | 0.007 | 13.75
| 20 | 2008-05-01 | 190000 | 672.9 | -2.6 | 0.15 | 0.1 | -2 | 22.05 | 180.4 | 263 | -1 | 148.2 | 2.44 | 13.05 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.73
| 21 | 2008-05-01 | 200000 | 673.9 | -2.4 | 0.16 | 0.1 | -1.9 | 22.08 | 181.2 | 264 | -1 | 147 | 2.44 | 12.99 | 2 | 2.32 | 1.9 | 0.007 | 0.007 | 13.71
| 22 | 2008-05-01 | 210000 | 675.5 | -2.6 | 0.16 | 0.1 | -2.1 | 21.91 | 179.1 | 261 | -1 | 132.7 | 2.35 | 12 | 1.9 | 2.24 | 1.9 | 0.007 | 0.007 | 13.75
| 23 | 2008-05-01 | 220000 | 562.3 | 6.4 | 5.05 | 51.2 | -193.4 | 2.3 | 11 | 20.6 | -0.9 | 2.2 | 2.43 | 6.43 | 7.2 | 8.88 | 14 | 0.056 | 4.775 | 19.4
| 24 | 2008-05-01 | 230000 | 426.8 | -2.8 | 0.31 | 69.3 | -620.4 | 0.1 | 0.5 | 1.3 | -1 | 1 | 0 | 0 | 0.9 | 0.01 | 1.1 | 25.343 | 17.414 | 20.87
| 25 | 2008-05-02 | 0 | 408.1 | -2.6 | 0.29 | 70.1 | -615.1 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.05 | 0.4 | 0.01 | 1.4 | 61.748 | 12.664 | 20.88
| 26 | 2008-05-02 | 10000 | 402.4 | -2.9 | 0.27 | 57.3 | -667.1 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0.8 | 0.01 | -0.9 | 6.347 | 6.334 | 20.87
| 27 | 2008-05-02 | 20000 | 396.9 | -2.7 | 0.27 | 44.9 | -414.2 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0.5 | 0.01 | 0.5 | 0.013 | 0.002 | 20.86
| 28 | 2008-05-02 | 30000 | 393.3 | -2.7 | 0.26 | 38.9 | -383.1 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | 0 | -0.06 | 0.3 | 0.01 | 0.3 | 0.013 | 0.001 | 20.86
| 29 | 2008-05-02 | 40000 | 389.1 | -2.8 | 0.27 | 35.8 | -350.3 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | 0 | -0.06 | 0.3 | 0.01 | -0.4 | 0.011 | 0.001 | 20.78
| 30 | 2008-05-02 | 50000 | 384.5 | -2.5 | 0.28 | 34.8 | -299.5 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0.5 | 0.01 | 0.6 | 0.012 | 0.002 | 20.77
| 31 | 2008-05-02 | 60000 | 379.9 | -2.5 | 0.3 | 44.5 | -385.1 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0.7 | 0.01 | 0.4 | 0.013 | 0.003 | 20.78
| 32 | 2008-05-02 | 70000 | 375.5 | -2.5 | 0.31 | 48.7 | -399.2 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0.7 | 0.01 | -0.1 | 0.016 | 0.003 | 20.86
| 33 | 2008-05-02 | 80000 | 371.5 | -2.5 | 0.33 | 58.1 | -422.5 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0.01 | -0.06 | 2.1 | 0.03 | 3.6 | 0.021 | 0.008 | 20.86
| 34 | 2008-05-02 | 90000 | 362.3 | -2.5 | 0.28 | 48.5 | -461.4 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | 2.17 | 0.1 | 0.01 | 0.9 | 6.346 | 3.166 | 20.86
| 35 | 2008-05-02 | 100000 | 344.8 | -2.4 | 0.29 | 40.2 | -353.6 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0.6 | 0 | -0.1 | 0.01 | 0.002 | 20.78
| 36 | 2008-05-02 | 110000 | 334.2 | -2.6 | 0.28 | 34.6 | -305.1 | 0.07 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0.2 | 0.01 | 1.2 | 0.012 | 0.001 | 20.85
| 37 | 2008-05-02 | 120000 | 328.1 | -2.7 | 0.26 | 25.2 | -269.5 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.2 | 0.01 | 0.6 | 0.009 | 0 | 20.83
| 38 | 2008-05-02 | 130000 | 323.7 | -2.7 | 0.26 | 20.9 | -213.2 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.006 | 0 | 20.75
| 39 | 2008-05-02 | 140000 | 320.4 | -2.3 | 0.25 | 17.4 | -156.5 | 0.1 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | 0 | 0.005 | 0 | 20.81
| 40 | 2008-05-02 | 150000 | 317.7 | -2.4 | 0.25 | 15.6 | -158.7 | 0.12 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.01 | 0.5 | 0.006 | 0 | 20.8
| 41 | 2008-05-02 | 160000 | 315.1 | -2.5 | 0.25 | 14.4 | -140.9 | 0.05 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.4 | 0.005 | 0 | 20.79
| 42 | 2008-05-02 | 170000 | 312.2 | -2.2 | 0.27 | 16 | -130.6 | 0.04 | 0.5 | 1.3 | 0.5 | 1 | 0 | -0.06 | 0 | 0.01 | 0.5 | 0.006 | 0 | 20.8
| 43 | 2008-05-02 | 180000 | 308.5 | -2.5 | 0.27 | 19 | -172.8 | 0.05 | 0.5 | 1.3 | -0.9 | 1 | 0 | -0.06 | 0 | 0.01 | 0.7 | 0.007 | 0 | 20.81
| 44 | 2008-05-02 | 190000 | 305 | -2.6 | 0.27 | 25 | -225.2 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0.1 | 0.01 | 0.1 | 0.008 | 0.001 | 20.83
| 45 | 2008-05-02 | 200000 | 301.7 | -2.6 | 0.28 | 34.9 | -344.6 | 0.04 | 0.5 | 1.3 | -1 | 1.1 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.011 | 0.001 | 20.85
| 46 | 2008-05-02 | 210000 | 298.6 | -2.7 | 0.27 | 49.3 | -472 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.2 | 0.01 | 0.6 | 6.346 | 1.583 | 20.86
| 47 | 2008-05-02 | 220000 | 295.4 | -2.5 | 0.27 | 64.6 | -593.2 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.7 | 0 | -0.9 | 11.097 | 1.583 | 20.87
| 48 | 2008-05-02 | 230000 | 292 | -2.5 | 0.26 | 65.6 | -619.4 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -1.1 | 0.01 | 0.9 | 14.267 | 6.331 | 20.8
| 49 | 2008-05-03 | 0 | 288.3 | -2.5 | 0.26 | 65.1 | -663.9 | 0.04 | 0.5 | 1.3 | -0.9 | 1 | 0 | -0.06 | -0.5 | 0.01 | 0.9 | 99.735 | 14.245 | 20.8
| 50 | 2008-05-03 | 10000 | 285 | -2.6 | 0.26 | 62.4 | -647.8 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.6 | 0.02 | 2 | 42.758 | 4.749 | 20.87
| 51 | 2008-05-03 | 20000 | 281.6 | -2.5 | 0.25 | 64.5 | -633.6 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.9 | 0.01 | 1.7 | 63.333 | 1.583 | 20.87
| 52 | 2008-05-03 | 30000 | 278.5 | -2.6 | 0.26 | 67.3 | -695.3 | 0.03 | 0.5 | 1.3 | -1 | 1.1 | 0 | -0.06 | -0.8 | 0.01 | 1.5 | 55.421 | 1.583 | 20.88
| 53 | 2008-05-03 | 40000 | 275.1 | -2.5 | 0.26 | 69.8 | -678.7 | 0.04 | 0.5 | 1.3 | -1 | 1.2 | 0 | -0.06 | -1 | 0 | 2.3 | 123.48 | 3.166 | 20.88
| 54 | 2008-05-03 | 50000 | 271.7 | -2.8 | 0.26 | 70 | -788.5 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.7 | 0.01 | 2.5 | 98.155 | 6.331 | 20.88
| 55 | 2008-05-03 | 60000 | 268.2 | -2.7 | 0.28 | 65.9 | -683.8 | 0.04 | 0.5 | 1.3 | -1 | 1.1 | 0 | -0.06 | -0.9 | 0.01 | 2.9 | 212.112 | 1.583 | 20.89
| 56 | 2008-05-03 | 70000 | 260.2 | -2.4 | 0.27 | 58.6 | -512.9 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.8 | 0.01 | 5.6 | 376.723 | 11.08 | 20.89
| 57 | 2008-05-03 | 80000 | 247.9 | -2.6 | 0.27 | 47.5 | -522 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.7 | 0.01 | 5 | 519.163 | 11.08 | 20.9
| 58 | 2008-05-03 | 90000 | 239.3 | -2.6 | 0.27 | 40.6 | -416 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | 2.15 | -0.7 | 0.01 | 4.3 | 531.823 | 3.166 | 20.9
| 59 | 2008-05-03 | 100000 | 233.6 | -2.3 | 0.27 | 27.9 | -240.2 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.4 | 0.02 | 4.4 | 781.894 | 11.08 | 20.9
| 60 | 2008-05-03 | 110000 | 229.6 | -2.7 | 0.28 | 14.8 | -141.2 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.2 | 0.01 | 2.6 | 557.142 | 9.498 | 20.91
| 61 | 2008-05-03 | 120000 | 226.4 | -2.7 | 0.28 | 12.7 | -115 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.2 | 0.01 | 3.1 | 739.16 | 3.167 | 20.84
| 62 | 2008-05-03 | 130000 | 223.3 | -2.6 | 0.29 | 19.6 | -195.7 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.4 | 0 | 2.5 | 599.881 | 3.167 | 20.91
| 63 | 2008-05-03 | 140000 | 220.9 | -2.5 | 0.28 | 31.3 | -252.1 | 0.04 | 0.5 | 1.3 | -1 | 1.1 | 0 | -0.06 | -0.4 | 0 | 4.6 | 549.238 | 4.75 | 20.9
| 64 | 2008-05-03 | 150000 | 218 | -2.7 | 0.28 | 49.5 | -538 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.8 | 0.01 | 4.4 | 721.753 | 4.749 | 20.9
| 65 | 2008-05-03 | 160000 | 215.8 | -2.8 | 0.28 | 55.2 | -537.3 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.7 | 0.01 | 5 | 383.052 | 14.245 | 20.9
| 66 | 2008-05-03 | 170000 | 213.7 | -2.7 | 0.28 | 67.2 | -650.7 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.9 | 0 | 3.8 | 218.445 | 14.245 | 20.89
| 67 | 2008-05-03 | 180000 | 211.4 | -2.5 | 0.28 | 67.1 | -615.8 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.8 | 0.01 | 3.5 | 121.896 | 6.331 | 20.81
| 68 | 2008-05-03 | 190000 | 208.8 | -2.6 | 0.28 | 63.9 | -651.9 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.8 | 0.01 | 2.6 | 253.263 | 9.497 | 20.81
| 69 | 2008-05-03 | 200000 | 206.5 | -2.7 | 0.28 | 50.2 | -488.3 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.5 | 0.01 | 3 | 455.853 | 17.411 | 20.9
| 70 | 2008-05-03 | 210000 | 204.1 | -2.6 | 0.27 | 21.8 | -208.7 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.3 | 0 | 2.6 | 565.06 | 15.829 | 20.91
| 71 | 2008-05-03 | 220000 | 201.6 | -2.5 | 0.27 | 15.5 | -105.2 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.3 | 0.01 | 3.1 | 712.25 | 1.585 | 20.91
| 72 | 2008-05-03 | 230000 | 199.4 | -2.4 | 0.26 | 15.7 | -138.3 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.3 | 0 | 3 | 447.938 | 6.333 | 20.91
| 73 | 2008-05-04 | 0 | 197 | -2.6 | 0.26 | 22.8 | -229.2 | 0.04 | 0.5 | 1.3 | -0.9 | 1 | 0 | -0.06 | -0.4 | 0.01 | 3.9 | 565.058 | 4.749 | 20.83
| 74 | 2008-05-04 | 10000 | 194.7 | -2.6 | 0.26 | 48.7 | -403.9 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.8 | 0 | 3.6 | 525.493 | 12.662 | 20.9
| 75 | 2008-05-04 | 20000 | 192.7 | -2.6 | 0.27 | 60.2 | -588.9 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -1 | 0.01 | 4.6 | 261.182 | 1.583 | 20.89
| 76 | 2008-05-04 | 30000 | 190.8 | -2.6 | 0.27 | 56.4 | -525 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.6 | 0.01 | 1.9 | 307.074 | 9.497 | 20.89
| 77 | 2008-05-04 | 40000 | 188.7 | -2.4 | 0.27 | 54.2 | -481.4 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -1 | 0.01 | 4 | 397.291 | 3.166 | 20.89
| 78 | 2008-05-04 | 50000 | 186.2 | -2.7 | 0.27 | 37.4 | -386.1 | 0.03 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.5 | 0.01 | 3.7 | 552.397 | 7.915 | 20.9
| 79 | 2008-05-04 | 60000 | 184.4 | -2.6 | 0.28 | 46.8 | -468 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.4 | 0 | 3.4 | 305.492 | 9.497 | 20.9
| 80 | 2008-05-04 | 70000 | 182.3 | -2.6 | 0.27 | 49 | -434.1 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0 | 3.6 | 313.413 | 25.325 | 20.9
| 81 | 2008-05-04 | 80000 | 180.6 | -2.8 | 0.29 | 52.6 | -422.5 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.4 | 0.01 | 5.4 | 414.707 | 9.497 | 20.9
| 82 | 2008-05-04 | 90000 | 178.8 | -2.7 | 0.29 | 69.4 | -647.8 | 0.05 | 0.5 | 1.3 | -1 | 0.8 | 0 | 2.14 | -0.8 | 0 | 2.6 | 295.996 | 14.245 | 20.89
| 83 | 2008-05-04 | 100000 | 177.1 | -2.5 | 0.3 | 83.6 | -685.6 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -1.1 | 0 | 1.5 | 170.958 | 1.583 | 20.88
| 84 | 2008-05-04 | 110000 | 175.2 | -2.6 | 0.29 | 78.9 | -701.1 | 0.03 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.9 | 0.01 | -0.3 | 20.595 | 0 | 20.87
| 85 | 2008-05-04 | 120000 | 173.3 | -2.9 | 0.29 | 56 | -570.7 | 0.03 | 0.5 | 1.3 | 168.7 | 0.6 | 0 | -0.06 | -0.6 | 0 | -1.1 | 0.013 | 0 | 20.87
| 86 | 2008-05-04 | 130000 | 171.5 | -2.6 | 0.29 | 34.7 | -332.1 | 0.12 | 0.5 | 1.3 | 134.7 | 0.6 | 0 | -0.07 | -0.4 | 0.01 | 0.7 | 0.01 | 0 | 20.85
| 87 | 2008-05-04 | 140000 | 170 | -2.8 | 0.29 | 25.8 | -234.3 | 0.26 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.3 | 0 | -0.3 | 0.007 | 0 | 20.83
| 88 | 2008-05-04 | 150000 | 168.4 | -2.5 | 0.29 | 20.2 | -181.5 | 0.15 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.2 | 0.01 | 0.3 | 0.006 | 0 | 20.81
| 89 | 2008-05-04 | 160000 | 166.7 | -2.7 | 0.28 | 16.7 | -149.4 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0 | 0.1 | 0.005 | 0 | 20.8
| 90 | 2008-05-04 | 170000 | 165.2 | -2.7 | 0.29 | 15.8 | -148 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.1 | 0 | 0 | 0.004 | 0 | 20.72
| 91 | 2008-05-04 | 180000 | 163.9 | -2.6 | 0.3 | 16 | -146 | 0.04 | 0.5 | 1.3 | -1 | 1.1 | 0 | -0.06 | 0 | 0 | 0.1 | 0.005 | 0 | 20.79
| 92 | 2008-05-04 | 190000 | 162.3 | -2.6 | 0.31 | 16 | -138.4 | 0.04 | 0.5 | 1.3 | -1 | 1.1 | 0 | -0.06 | -0.1 | 0 | 0.1 | 0.005 | 0 | 20.71
| 93 | 2008-05-04 | 200000 | 160.4 | -2.6 | 0.3 | 17.4 | -138.6 | 0.04 | 0.5 | 1.3 | -1 | 1.1 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0.005 | 0 | 20.79
| 94 | 2008-05-04 | 210000 | 158.9 | -2.6 | 0.3 | 18.8 | -154.6 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.005 | 0 | 20.73
| 95 | 2008-05-04 | 220000 | 157 | -2.8 | 0.29 | 18.7 | -174.8 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | -0.1 | 0 | 0.2 | 0.006 | 0 | 20.81
| 96 | 2008-05-04 | 230000 | 156.9 | -2.8 | 0.28 | 18.3 | -185.1 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.2 | 0.01 | 0.4 | 0.006 | 0 | 20.81
| 97 | 2008-05-05 | 0 | 153.9 | -2.4 | 0.28 | 20.7 | -187.8 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.2 | 0.01 | 0.4 | 0.007 | 0 | 20.82
| 98 | 2008-05-05 | 10000 | 148 | 36.1 | 2.76 | 23.9 | -72.2 | 0.65 | 1 | 1.8 | -1 | 0.9 | 1.06 | 2.69 | 1.8 | 1.96 | 4.1 | 0.019 | 0.007 | 20.43
| 99 | 2008-05-05 | 20000 | 473.4 | 22.8 | 15.52 | 22.8 | 33.2 | 6.92 | 18.4 | 18.9 | -1 | 1.1 | 10.29 | 30.01 | 15.1 | 46.25 | 68.1 | 0.251 | 0.056 | 16.89
| 100 | 2008-05-05 | 30000 | 602.9 | 12.2 | 13.86 | 19.9 | 17.3 | 7.06 | 20.5 | 20.8 | -1 | 45.3 | 10.29 | 30.01 | 14.8 | 45.54 | 65.7 | 0.242 | 0.055 | 16.8
| 101 | 2008-05-05 | 40000 | 602.6 | 47.2 | 20.04 | 23.6 | 55.4 | 8.76 | 35.1 | 52.6 | -1 | 103 | 10.26 | 30.01 | 12.1 | 33.66 | 39.5 | 0.146 | 0.044 | 15.88
| 102 | 2008-05-05 | 50000 | 602.2 | 41.4 | 19.61 | 21.4 | 45.3 | 9.58 | 43.7 | 71.2 | -1 | 91.9 | 10.29 | 30.01 | 11.2 | 42.68 | 45.9 | 0.169 | 0.041 | 15.46
| 103 | 2008-05-05 | 60000 | 650.7 | 94.5 | 3.55 | 8.1 | -15.8 | 21.11 | 171.9 | 243.5 | -1 | 91.9 | 3.56 | 10.76 | 5.7 | 11.44 | 8.9 | 0.033 | 0.021 | 12.25
| 104 | 2008-05-05 | 70000 | 664.1 | -2.6 | 0.28 | 0.2 | -2.2 | 22.21 | 181.7 | 259.3 | -1 | 139.9 | 2.5 | 12.71 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.66
| 105 | 2008-05-05 | 80000 | 666.7 | -2.6 | 0.23 | 0.2 | -2.1 | 22.05 | 180.7 | 260.3 | -1 | 134.1 | 2.45 | 12.3 | 2 | 2.35 | 1.9 | 0.007 | 0.007 | 13.66
| 106 | 2008-05-05 | 90000 | 666.3 | -2.4 | 0.23 | 0.2 | -2.1 | 22.05 | 180.4 | 263.8 | -1 | 137.4 | 2.5 | 12.78 | 2 | 2.38 | 1.9 | 0.007 | 0.007 | 13.64
| 107 | 2008-05-05 | 100000 | 670.5 | -2.6 | 0.22 | 0.2 | -2.1 | 21.95 | 179.3 | 262.8 | -1 | 132.8 | 2.72 | 12.77 | 2.2 | 2.6 | 2.1 | 0.008 | 0.008 | 13.63
| 108 | 2008-05-05 | 110000 | 669.2 | -2.6 | 0.22 | 0.2 | -2.1 | 21.82 | 177.8 | 260.2 | -1 | 130.2 | 2.85 | 12.75 | 2.3 | 2.73 | 2.2 | 0.008 | 0.009 | 13.64
| 109 | 2008-05-05 | 120000 | 667.7 | -2.7 | 0.22 | 0.2 | -2.4 | 21.61 | 176.4 | 258 | -1 | 127.8 | 2.84 | 12.6 | 2.3 | 2.72 | 2.2 | 0.008 | 0.009 | 13.64
| 110 | 2008-05-05 | 130000 | 667.5 | -2.4 | 0.22 | 0.2 | -2 | 21.54 | 175.3 | 256.5 | -1 | 127.4 | 2.85 | 12.57 | 2.3 | 2.73 | 2.2 | 0.008 | 0.009 | 13.65
| 111 | 2008-05-05 | 140000 | 667 | -2.6 | 0.21 | 0.2 | -2 | 21.5 | 174.4 | 255.3 | -1 | 126.8 | 2.84 | 12.54 | 2.3 | 2.72 | 2.2 | 0.008 | 0.009 | 13.66
| 112 | 2008-05-05 | 150000 | 666.1 | -2.4 | 0.2 | 0.2 | -1.8 | 21.32 | 173.2 | 253.9 | -1 | 126.6 | 2.84 | 12.51 | 2.3 | 2.72 | 2.2 | 0.008 | 0.009 | 13.66
| 113 | 2008-05-05 | 160000 | 665.9 | -2.7 | 0.21 | 0.2 | -2.1 | 21.32 | 173.4 | 254 | -1 | 124.9 | 2.84 | 12.39 | 2.3 | 2.72 | 2.2 | 0.008 | 0.008 | 13.65
| 114 | 2008-05-05 | 170000 | 666.6 | -2.3 | 0.21 | 0.2 | -1.9 | 21.53 | 174.7 | 255.6 | -1 | 127.2 | 2.84 | 12.52 | 2.3 | 2.72 | 2.2 | 0.008 | 0.009 | 13.66
| 115 | 2008-05-05 | 180000 | 667.7 | -2.8 | 0.21 | 0.2 | -2.2 | 21.61 | 176.2 | 257.6 | -1 | 132.7 | 2.77 | 12.74 | 2.3 | 2.65 | 2.2 | 0.008 | 0.008 | 13.66
| 116 | 2008-05-05 | 190000 | 668.7 | -2.6 | 0.2 | 0.2 | -2.1 | 21.71 | 177.1 | 258.2 | -1 | 130.5 | 2.58 | 12.34 | 2.1 | 2.46 | 2 | 0.007 | 0.008 | 13.7
| 117 | 2008-05-05 | 200000 | 671.4 | -2.4 | 0.19 | 0.2 | -1.9 | 21.6 | 177.1 | 257.4 | -1 | 118.8 | 2.55 | 11.16 | 2.1 | 2.43 | 2 | 0.007 | 0.008 | 13.76
| 118 | 2008-05-05 | 210000 | 671.6 | -2.7 | 0.2 | 0.2 | -2.2 | 22.04 | 180.8 | 263.3 | -1 | 137.3 | 2.58 | 12.43 | 2.1 | 2.46 | 2 | 0.007 | 0.008 | 13.67
| 119 | 2008-05-05 | 220000 | 578 | 3.7 | 4.31 | 28.1 | -75.3 | 3 | 17.2 | 28.5 | -1 | 7.3 | 1.99 | 5.64 | 4.8 | 7.37 | 10.5 | 0.04 | 0.018 | 19.16
| 120 | 2008-05-05 | 230000 | 456.5 | -2.4 | 0.31 | 26.9 | -208.4 | 0.05 | 0.5 | 1.3 | -1 | 1.8 | 0 | 0.03 | 0.3 | 0.01 | 0.7 | 0.008 | 0.001 | 20.83
| 121 | 2008-05-06 | 0 | 434.4 | -2.6 | 0.29 | 25.8 | -227.2 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.03 | 0 | 0.01 | 0.5 | 0.008 | 0 | 20.83
| 122 | 2008-05-06 | 10000 | 426 | -2.7 | 0.28 | 23.9 | -234.7 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.05 | 0 | 0.01 | 0.3 | 0.007 | 0 | 20.83
| 123 | 2008-05-06 | 20000 | 421 | -2.7 | 0.28 | 22.7 | -221.7 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.03 | -0.2 | 0.01 | 0.5 | 0.008 | 0 | 20.82
| 124 | 2008-05-06 | 30000 | 416.7 | -2.7 | 0.29 | 23.3 | -225.2 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.03 | -0.2 | 0 | 0.2 | 0.006 | 0 | 20.83
| 125 | 2008-05-06 | 40000 | 427.7 | -0.7 | 1.97 | 19.7 | -183.8 | 0.76 | 1.5 | 2.3 | -1 | 0.9 | 1.13 | 3.43 | 1.8 | 2.94 | 5 | 0.024 | 0.007 | 20.37
| 126 | 2008-05-06 | 50000 | 595.5 | 40.7 | 18.26 | 22.5 | 49.5 | 9.11 | 40 | 51.4 | -1 | 35.4 | 10.06 | 29.31 | 12.3 | 42.08 | 50.3 | 0.185 | 0.045 | 15.91
| 127 | 2008-05-06 | 60000 | 633.2 | -2.6 | 0.27 | 0.2 | -2 | 18.49 | 144.6 | 213.2 | -1 | 69.8 | 2.11 | 8.36 | 1.8 | 2.01 | 1.7 | 0.006 | 0.007 | 13.82
| 128 | 2008-05-06 | 70000 | 660 | 94.4 | 3.4 | 4.5 | 5.3 | 22.26 | 182 | 264.9 | -1 | 141.9 | 3.62 | 12.77 | 2.4 | 9.79 | 4.3 | 23.758 | 4.757 | 12.11
| 129 | 2008-05-06 | 80000 | 671.1 | -2.5 | 0.28 | 0.2 | -2.1 | 22.16 | 181.7 | 265.5 | -1 | 140.5 | 2.58 | 12.79 | 2.1 | 2.45 | 2 | 0.007 | 0.008 | 13.7
| 130 | 2008-05-06 | 90000 | 672.1 | -3.1 | 0.22 | 0.2 | -2.5 | 22.07 | 181.5 | 265.3 | -1 | 139.1 | 2.59 | 12.84 | 2.1 | 2.47 | 2 | 0.007 | 0.008 | 13.66
| 131 | 2008-05-06 | 100000 | 671.7 | -2.7 | 0.21 | 0.2 | -2.2 | 21.92 | 179.5 | 265.5 | -1 | 126.6 | 2.53 | 11.87 | 2.1 | 2.41 | 2 | 0.007 | 0.008 | 13.72
| 132 | 2008-05-06 | 110000 | 673.3 | -2.7 | 0.2 | 0.2 | -2.2 | 21.72 | 177.9 | 264.4 | -1 | 120 | 2.58 | 11.37 | 2.1 | 2.46 | 2 | 0.008 | 0.008 | 13.76
| 133 | 2008-05-06 | 120000 | 673.1 | -2.4 | 0.21 | 0.2 | -1.9 | 22.05 | 180.6 | 268.2 | -1 | 140.8 | 2.59 | 12.82 | 2.1 | 2.47 | 2 | 0.007 | 0.008 | 13.66
| 134 | 2008-05-06 | 130000 | 672.5 | -3 | 0.2 | 0.2 | -2.5 | 21.88 | 178.8 | 266.4 | -1 | 137.5 | 2.53 | 12.6 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.67
| 135 | 2008-05-06 | 140000 | 639.4 | -2.8 | 0.26 | 0.2 | -2.3 | 16.4 | 121.3 | 191.6 | -1 | 52.1 | 2.46 | 7.97 | 2.1 | 2.34 | 2 | 0.007 | 0.008 | 13.89
| 136 | 2008-05-06 | 150000 | 633.8 | -2.8 | 0.26 | 0.2 | -2.3 | 16.4 | 121.5 | 190.8 | -1 | 54.4 | 2.48 | 7.97 | 2.1 | 2.37 | 2 | 0.007 | 0.008 | 13.88
| 137 | 2008-05-06 | 160000 | 634.2 | -3 | 0.3 | 0.3 | -2.3 | 16.44 | 122.8 | 192.7 | -1 | 51.9 | 2.54 | 7.79 | 2.1 | 2.42 | 2 | 0.007 | 0.008 | 13.88
| 138 | 2008-05-06 | 170000 | 633.5 | -2.7 | 0.31 | 0.3 | -2.2 | 16.36 | 121.6 | 191.3 | -1 | 51.5 | 2.52 | 7.77 | 2.1 | 2.4 | 2 | 0.007 | 0.008 | 13.88
| 139 | 2008-05-06 | 180000 | 553.8 | 4 | 4.47 | 34.9 | -135.5 | 1.43 | 6.1 | 11.6 | -1 | 2.8 | 1.8 | 4.98 | 4.4 | 7.18 | 10.2 | 0.04 | 0.016 | 19.77
| 140 | 2008-05-06 | 190000 | 447.9 | -2.7 | 0.3 | 34.9 | -310.6 | 0.09 | 0.5 | 1.3 | -1 | 0.9 | 0 | 0.01 | 0.3 | 0.01 | 0.1 | 0.009 | 0.001 | 20.84
| 141 | 2008-05-06 | 200000 | 430.7 | -2.8 | 0.29 | 41.2 | -402.2 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0 | -1.5 | 0.009 | 1.583 | 20.85
| 142 | 2008-05-06 | 210000 | 424.5 | -2.9 | 0.29 | 48.1 | -490.4 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.2 | 0 | -1 | 11.093 | 6.332 | 20.86
| 143 | 2008-05-06 | 220000 | 419 | -2.8 | 0.29 | 54.6 | -547.4 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 30.088 | 3.166 | 20.87
| 144 | 2008-05-06 | 230000 | 414.4 | -2.7 | 0.29 | 59.1 | -578.3 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.5 | 0.01 | -0.6 | 44.334 | 1.583 | 20.87
| 145 | 2008-05-07 | 0 | 408.3 | -2.6 | 0.29 | 64.9 | -615.3 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.9 | 0.01 | 1.5 | 82.323 | 6.331 | 20.87
| 146 | 2008-05-07 | 10000 | 401.7 | -2.7 | 0.29 | 68.3 | -647.9 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.9 | 0.01 | 2.7 | 163.049 | 3.166 | 20.88
| 147 | 2008-05-07 | 20000 | 395.8 | -2.9 | 0.29 | 64.4 | -642.6 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | -1 | 0.01 | 4.3 | 189.958 | 1.583 | 20.88
| 148 | 2008-05-07 | 30000 | 379.8 | -2.7 | 0.29 | 66.3 | -659.7 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -1 | 0.01 | 4.5 | 345.066 | 6.332 | 20.89
| 149 | 2008-05-07 | 40000 | 356.3 | -2.8 | 0.28 | 48.3 | -490.1 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.8 | 0.02 | 5.9 | 335.569 | 3.166 | 20.9
| 150 | 2008-05-07 | 50000 | 346.1 | -2.8 | 0.3 | 45.6 | -432.9 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.6 | 0.02 | 4.9 | 547.658 | 11.08 | 20.9
| 151 | 2008-05-07 | 60000 | 341.1 | -2.9 | 0.3 | 25.3 | -277.7 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.4 | 0.01 | 5.1 | 536.577 | 11.081 | 20.91
| 152 | 2008-05-07 | 70000 | 338.1 | -2.6 | 0.3 | 9.8 | -103.6 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0.01 | 2.6 | 470.094 | 7.915 | 20.92
| 153 | 2008-05-07 | 80000 | 334.9 | -2.8 | 0.3 | 3.6 | -59.5 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | 1 | 215.268 | 6.333 | 20.85
| 154 | 2008-05-07 | 90000 | 331.4 | -2.8 | 0.29 | 2 | -16.1 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | 2.11 | 0 | 0.01 | 0.6 | 286.489 | 0.003 | 20.86
| 155 | 2008-05-07 | 100000 | 327.8 | -2.6 | 0.3 | 0.5 | -13.6 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.3 | 113.965 | 3.168 | 20.94
| 156 | 2008-05-07 | 110000 | 324.7 | -2.5 | 0.3 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0.01 | 0 | 23.75 | 0.002 | 20.87
| 157 | 2008-05-07 | 120000 | 321.7 | -3.1 | 0.31 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 75.98 | 0.002 | 20.95
| 158 | 2008-05-07 | 130000 | 318.7 | -2.8 | 0.31 | 0 | 0 | 0.08 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0.01 | 0 | 34.827 | 0.002 | 20.95
| 159 | 2008-05-07 | 140000 | 315.4 | -2.8 | 0.31 | 1 | -8 | 0.09 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.5 | 0.009 | 0.002 | 20.96
| 160 | 2008-05-07 | 150000 | 311.9 | -2.6 | 0.31 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0 | 37.992 | 0.002 | 20.96
| 161 | 2008-05-07 | 160000 | 308.3 | -2.6 | 0.31 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | 0 | 34.829 | 3.167 | 20.95
| 162 | 2008-05-07 | 170000 | 304.8 | -2.5 | 0.31 | 0.4 | -8.8 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | 0 | 0.02 | 0.1 | 22.166 | 0.002 | 20.95
| 163 | 2008-05-07 | 180000 | 301.1 | -2.6 | 0.3 | 1.6 | -16.9 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0.01 | 0.5 | 90.228 | 0.002 | 20.94
| 164 | 2008-05-07 | 190000 | 297.4 | -3.2 | 0.31 | 0.6 | -9.7 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 75.979 | 0.002 | 20.94
| 165 | 2008-05-07 | 200000 | 293.7 | -2.8 | 0.3 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0.01 | 0 | 123.462 | 0.002 | 20.94
| 166 | 2008-05-07 | 210000 | 289.7 | -2.8 | 0.31 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0 | 7.922 | 0.002 | 20.95
| 167 | 2008-05-07 | 220000 | 286.2 | -2.7 | 0.3 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0 | 49.073 | 0.002 | 20.95
| 168 | 2008-05-07 | 230000 | 282.5 | -2.7 | 0.29 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0 | 6.339 | 0.002 | 20.95
| 169 | 2008-05-08 | 0 | 278.5 | -2.9 | 0.3 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0.01 | 0 | 19 | 0.002 | 20.95
| 170 | 2008-05-08 | 10000 | 273.4 | -2.9 | 0.29 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 11.086 | 0.002 | 20.96
| 171 | 2008-05-08 | 20000 | 257 | -2.9 | 0.29 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 3.173 | 0.001 | 20.96
| 172 | 2008-05-08 | 30000 | 241.1 | -2.9 | 0.28 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0 | 0.005 | 0.001 | 20.97
| 173 | 2008-05-08 | 40000 | 232.7 | -2.7 | 0.29 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.005 | 0.001 | 20.98
| 174 | 2008-05-08 | 50000 | 228.2 | -2.5 | 0.3 | 0 | 0 | 0.02 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | 0 | 0.01 | 0 | 0.006 | 0.001 | 20.97
| 175 | 2008-05-08 | 60000 | 224.9 | -2.6 | 0.34 | 0 | 0 | 0.02 | 0.5 | 1.3 | -1 | 0.7 | 0.01 | -0.06 | 0 | 0.01 | 0 | 3.173 | 0 | 20.96
| 176 | 2008-05-08 | 70000 | 222.4 | -3.1 | 0.35 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0.01 | -0.06 | 0 | 0.01 | 0 | 0.006 | 0 | 20.95
| 177 | 2008-05-08 | 80000 | 220.3 | -2.7 | 0.31 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0 | 18.999 | 1.583 | 20.95
| 178 | 2008-05-08 | 90000 | 218 | -2.6 | 0.29 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | 2.15 | 0 | 0.01 | 0 | 0.006 | 0.002 | 20.95
| 179 | 2008-05-08 | 100000 | 216.2 | -2.7 | 0.3 | 1.5 | -15.9 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | -0.1 | 196.266 | 1.585 | 20.86
| 180 | 2008-05-08 | 110000 | 214 | -2.8 | 0.3 | 0 | 0 | 0.02 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 156.7 | 0.003 | 20.93
| 181 | 2008-05-08 | 120000 | 211.8 | -2.6 | 0.3 | 3.1 | -18.8 | 0.06 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.2 | 438.43 | 1.585 | 20.92
| 182 | 2008-05-08 | 130000 | 209.1 | -2.6 | 0.31 | 16.3 | -147.1 | 0.26 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.3 | 0.01 | 2.6 | 685.346 | 7.915 | 20.91
| 183 | 2008-05-08 | 140000 | 206.7 | -2.7 | 0.3 | 20.3 | -206.4 | 0.27 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.2 | 0.01 | 2.4 | 644.191 | 11.081 | 20.83
| 184 | 2008-05-08 | 150000 | 204.5 | -2.7 | 0.31 | 20.7 | -208.1 | 0.21 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.3 | 0.01 | 2.5 | 574.553 | 6.333 | 20.91
| 185 | 2008-05-08 | 160000 | 201.9 | -2.6 | 0.3 | 53.5 | -516.3 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.9 | 0.01 | 4.5 | 427.369 | 1.583 | 20.9
| 186 | 2008-05-08 | 170000 | 199.7 | -2.7 | 0.3 | 53.8 | -502.9 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.7 | 0.01 | 5.1 | 478.014 | 14.245 | 20.9
| 187 | 2008-05-08 | 180000 | 197.7 | -2.6 | 0.3 | 57.3 | -504.7 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.7 | 0.01 | 5.1 | 438.445 | 7.915 | 20.89
| 188 | 2008-05-08 | 190000 | 195.4 | -2.5 | 0.3 | 62 | -525.2 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.9 | 0.01 | 4.1 | 356.141 | 4.749 | 20.89
| 189 | 2008-05-08 | 200000 | 193.1 | -2.5 | 0.3 | 44 | -363.7 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.6 | 0.01 | 4.4 | 571.395 | 14.245 | 20.82
| 190 | 2008-05-08 | 210000 | 190.9 | -2.3 | 0.29 | 32.6 | -302.5 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.7 | 0.01 | 4.8 | 761.321 | 1.584 | 20.9
| 191 | 2008-05-08 | 220000 | 188.9 | -2.7 | 0.29 | 19.4 | -192.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.3 | 0.01 | 2.5 | 826.205 | 7.915 | 20.91
| 192 | 2008-05-08 | 230000 | 186.1 | -2.6 | 0.29 | 17.7 | -142.4 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.3 | 0.01 | 3 | 780.307 | 1.585 | 20.91
| 193 | 2008-05-09 | 0 | 184.1 | -2.7 | 0.28 | 20.9 | -196.8 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.5 | 0.01 | 4.7 | 745.494 | 4.75 | 20.83
| 194 | 2008-05-09 | 10000 | 181.7 | -2.4 | 0.28 | 20.6 | -167.2 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.4 | 0.02 | 3.6 | 826.206 | 11.081 | 20.91
| 195 | 2008-05-09 | 20000 | 179.1 | -2.5 | 0.29 | 38.1 | -332.9 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.6 | 0.01 | 4.5 | 474.845 | 9.497 | 20.9
| 196 | 2008-05-09 | 30000 | 177 | -2.5 | 0.29 | 10.5 | -114.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.2 | 0.02 | 2 | 902.175 | 1.585 | 20.91
| 197 | 2008-05-09 | 40000 | 175.1 | -2.6 | 0.29 | 6.3 | -65.3 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.1 | 0.01 | 0.9 | 591.956 | 1.585 | 20.92
| 198 | 2008-05-09 | 50000 | 173 | -2.5 | 0.3 | 4.1 | -42.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | 0 | 0.01 | 0.7 | 436.847 | 6.333 | 20.92
| 199 | 2008-05-09 | 60000 | 171.4 | -2.4 | 0.31 | 0.8 | -4.8 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | 0 | 0.01 | 0.2 | 257.998 | 6.332 | 20.93
| 200 | 2008-05-09 | 70000 | 169.5 | -2.3 | 0.37 | 0.3 | 1.2 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | 0 | 0.01 | 0 | 248.497 | 4.748 | 20.93
| 201 | 2008-05-09 | 80000 | 167.5 | -2.5 | 0.43 | 0.8 | -5.6 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0.02 | -0.06 | 0 | 0.03 | 0.1 | 447.92 | 101.295 | 20.93
| 202 | 2008-05-09 | 90000 | 165.9 | -2.6 | 0.36 | 2.8 | -15.1 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0.01 | 2.15 | 0 | 0 | 0.9 | 354.549 | 41.151 | 20.85
| 203 | 2008-05-09 | 100000 | 164.4 | -2.5 | 0.33 | 1 | -12 | 0.05 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.2 | 49.074 | 3.166 | 20.94
| 204 | 2008-05-09 | 110000 | 162.6 | -2.7 | 0.35 | 1.2 | -2.5 | 0.05 | 0.5 | 1.3 | -1 | 0.8 | 0.01 | -0.06 | 0.1 | 0.02 | 0.5 | 348.209 | 33.238 | 20.85
| 205 | 2008-05-09 | 120000 | 161.1 | -2.9 | 0.34 | 1 | -14.4 | 0.05 | 0.5 | 1.3 | -1 | 0.8 | 0.01 | -0.04 | 0 | 0.01 | 0.1 | 357.709 | 71.223 | 20.93
| 206 | 2008-05-09 | 130000 | 159.7 | -2.6 | 0.32 | 8.4 | -85.6 | 0.26 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0 | 0.02 | 2.3 | 731.24 | 20.576 | 20.92
| 207 | 2008-05-09 | 140000 | 157.9 | -2.6 | 0.32 | 24.7 | -224.2 | 0.26 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 2.7 | 729.66 | 12.662 | 20.91
| 208 | 2008-05-09 | 150000 | 156.6 | -2.7 | 0.34 | 72 | -573.9 | 0.16 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0 | 0.01 | 3.8 | 310.244 | 33.238 | 20.89
| 209 | 2008-05-09 | 160000 | 155.2 | -2.8 | 0.32 | 75.7 | -673.4 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.4 | 0.01 | -0.3 | 19.013 | 4.749 | 20.87
| 210 | 2008-05-09 | 170000 | 154 | -2.5 | 0.32 | 60.7 | -472.4 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.2 | 0.01 | 0.3 | 19.008 | 0.001 | 20.87
| 211 | 2008-05-09 | 180000 | 152.6 | -2.8 | 0.32 | 52 | -441.6 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.2 | 0 | -0.9 | 0.011 | 0 | 20.86
| 212 | 2008-05-09 | 190000 | 150.9 | -2.7 | 0.32 | 39.6 | -346.1 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | -0.8 | 0.009 | 0.001 | 20.85
| 213 | 2008-05-09 | 200000 | 149.5 | -2.3 | 0.35 | 31.3 | -188.8 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0.1 | 0 | -0.3 | 0.007 | 0.001 | 20.83
| 214 | 2008-05-09 | 210000 | 147.8 | -2.6 | 0.34 | 33.4 | -254.8 | 0.03 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0.008 | 0.001 | 20.76
| 215 | 2008-05-09 | 220000 | 146.4 | -2.5 | 0.33 | 34.7 | -260.4 | 0.02 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.9 | 0.011 | 0 | 20.84
| 216 | 2008-05-09 | 230000 | 145 | -2.7 | 0.35 | 32.7 | -268.9 | 0.02 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0.1 | 0.01 | 0.5 | 0.009 | 0.001 | 20.83
| 217 | 2008-05-10 | 0 | 143.6 | -2.5 | 0.36 | 29.2 | -208 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.6 | 0.008 | 0 | 20.75
| 218 | 2008-05-10 | 10000 | 142.3 | -2.7 | 0.37 | 26.8 | -199.2 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.006 | 0 | 20.82
| 219 | 2008-05-10 | 20000 | 140.8 | -2.6 | 0.37 | 25 | -166.2 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.05 | 0 | 0.01 | 0.6 | 0.007 | 0 | 20.81
| 220 | 2008-05-10 | 30000 | 139.6 | -2.8 | 0.37 | 22.6 | -169.1 | 0.02 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.3 | 0.01 | 0.5 | 0.006 | 0.001 | 20.8
| 221 | 2008-05-10 | 40000 | 138.2 | -2.9 | 0.37 | 21.2 | -159.2 | 0.03 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0.2 | 0.01 | 0.6 | 0.006 | 0.001 | 20.8
| 222 | 2008-05-10 | 50000 | 137 | -2.5 | 0.39 | 22 | -138.8 | 0.02 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.3 | 0.01 | 0.4 | 0.005 | 0.001 | 20.79
| 223 | 2008-05-10 | 60000 | 135.1 | -2.8 | 0.4 | 22.2 | -159.2 | 0.02 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0.3 | 0.01 | 0.2 | 0.005 | 0.001 | 20.79
| 224 | 2008-05-10 | 70000 | 134.3 | -2.6 | 0.38 | 22 | -149.5 | 0.02 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.1 | 0.02 | 0.8 | 0.006 | 0 | 20.79
| 225 | 2008-05-10 | 80000 | 133.1 | -2.6 | 0.39 | 21.8 | -144.1 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.1 | 0.01 | 0.4 | 0.006 | 0 | 20.79
| 226 | 2008-05-10 | 90000 | 129.7 | -2.8 | 0.39 | 19.4 | -138.6 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | 2.21 | 0.1 | 0.01 | 0.1 | 0.004 | 0 | 20.71
| 227 | 2008-05-10 | 100000 | 124.7 | -2.6 | 0.38 | 17.9 | -123.5 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0 | 0.1 | 0.004 | 0 | 20.7
| 228 | 2008-05-10 | 110000 | 122.2 | -2.7 | 0.39 | 17.2 | -121.7 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | 0.1 | 0.004 | 0 | 20.77
| 229 | 2008-05-10 | 120000 | 120.9 | -2.4 | 0.39 | 15.9 | -100.9 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.1 | 0.01 | 0.1 | 0.004 | 0 | 20.75
| 230 | 2008-05-10 | 130000 | 119.7 | -2.7 | 0.37 | 14.4 | -104 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.004 | 0 | 20.75
| 231 | 2008-05-10 | 140000 | 119 | -2.5 | 0.36 | 13.2 | -86.6 | 0.02 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.74
| 232 | 2008-05-10 | 150000 | 117.6 | -2.9 | 0.38 | 13.2 | -104.1 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.01 | 0.3 | 0.004 | 0 | 20.73
| 233 | 2008-05-10 | 160000 | 117.4 | -2.5 | 0.38 | 12.9 | -81.9 | 0.02 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.003 | 0 | 20.73
| 234 | 2008-05-10 | 170000 | 115.3 | -2.8 | 0.36 | 12.4 | -93.5 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.73
| 235 | 2008-05-10 | 180000 | 115.2 | -2.7 | 0.35 | 11.8 | -88.4 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0 | 0 | 0.002 | 0 | 20.72
| 236 | 2008-05-10 | 190000 | 114.3 | -2.7 | 0.33 | 11.8 | -92.3 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.73
| 237 | 2008-05-10 | 200000 | 113.8 | -2.8 | 0.34 | 14.4 | -117.4 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.76
| 238 | 2008-05-10 | 210000 | 112.2 | -2.7 | 0.35 | 18 | -138.8 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.2 | 0.01 | 0.5 | 0.005 | 0 | 20.78
| 239 | 2008-05-10 | 220000 | 111.7 | -2.3 | 0.36 | 23 | -153.7 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.06 | -0.3 | 0.01 | 0.4 | 0.006 | 0 | 20.81
| 240 | 2008-05-10 | 230000 | 110.5 | -2.9 | 0.37 | 26.4 | -209.2 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.06 | -0.4 | 0.01 | 0.2 | 0.007 | 0 | 20.82
| 241 | 2008-05-11 | 0 | 110.5 | -2.6 | 0.35 | 27.9 | -202.7 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.4 | 0 | 0.1 | 0.007 | 0 | 20.82
| 242 | 2008-05-11 | 10000 | 109.4 | -2.7 | 0.34 | 30.9 | -244.4 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.06 | -0.4 | 0.01 | 0.1 | 0.007 | 0 | 20.83
| 243 | 2008-05-11 | 20000 | 108.5 | -2.7 | 0.35 | 29.3 | -239.6 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | -0.01 | -0.06 | -0.5 | 0.01 | 0.9 | 0.008 | 0 | 20.83
| 244 | 2008-05-11 | 30000 | 108.1 | -3.1 | 0.36 | 34.7 | -295.9 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.06 | -0.6 | 0 | 0.2 | 0.008 | 0 | 20.84
| 245 | 2008-05-11 | 40000 | 107 | -2.6 | 0.36 | 41.2 | -293.3 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.06 | -0.6 | 0 | -0.2 | 0.009 | 0 | 20.84
| 246 | 2008-05-11 | 50000 | 106.9 | -2.6 | 0.36 | 45.6 | -310.4 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | -0.01 | -0.07 | -0.8 | 0.01 | 0 | 0.011 | 0 | 20.77
| 247 | 2008-05-11 | 60000 | 104.9 | -2.5 | 0.37 | 56.8 | -389.6 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | -0.01 | -0.06 | -1.1 | 0.01 | 0.5 | 0.013 | 0 | 20.86
| 248 | 2008-05-11 | 70000 | 104.8 | -2.7 | 0.37 | 75.5 | -539.1 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.06 | -1.5 | 0.01 | 0.3 | 0.018 | 0 | 20.87
| 249 | 2008-05-11 | 80000 | 104.2 | -2.6 | 0.37 | 95 | -623.3 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.06 | -1.6 | 0.01 | 0.9 | 52.25 | 0 | 20.87
| 250 | 2008-05-11 | 90000 | 102.9 | -2.5 | 0.37 | 91.9 | -644.7 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | 2.2 | -1.6 | 0.01 | 2.2 | 61.75 | 1.583 | 20.88
| 251 | 2008-05-11 | 100000 | 102.7 | -2.6 | 0.38 | 94 | -640 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.07 | -1.6 | 0 | 2.1 | 87.074 | 0 | 20.88
| 252 | 2008-05-11 | 110000 | 102.8 | -2.9 | 0.39 | 85.4 | -611.8 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.06 | -1.6 | 0.01 | 3.9 | 291.252 | 3.166 | 20.89
| 253 | 2008-05-11 | 120000 | 101.5 | -2.6 | 0.38 | 51 | -279.4 | 0.07 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.06 | -0.9 | 0.02 | 5.8 | 675.855 | 3.167 | 20.9
| 254 | 2008-05-11 | 130000 | 101 | -2.4 | 0.39 | 47.9 | -306.4 | 0.18 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.06 | -0.8 | 0.01 | 3.3 | 644.194 | 1.584 | 20.9
| 255 | 2008-05-11 | 140000 | 101.1 | -2.7 | 0.39 | 43.3 | -283 | 0.26 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.06 | -0.9 | 0.01 | 3.7 | 785.06 | 0.002 | 20.9
| 256 | 2008-05-11 | 150000 | 100 | -2.8 | 0.39 | 44.4 | -314.3 | 0.09 | 0.5 | 1.3 | -1 | 0.9 | -0.01 | -0.06 | -0.8 | 0.01 | 3.5 | 702.758 | 6.333 | 20.91
| 257 | 2008-05-11 | 160000 | 99.1 | -2.7 | 0.39 | 29 | -183.7 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | -0.01 | -0.06 | -0.7 | 0.01 | 3.4 | 750.237 | 3.169 | 20.91
| 258 | 2008-05-11 | 170000 | 99 | -2.8 | 0.39 | 31 | -219.3 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | -0.01 | -0.06 | -0.5 | 0.01 | 4.3 | 631.534 | 6.333 | 20.91
| 259 | 2008-05-11 | 180000 | 99 | -2.5 | 0.39 | 29.9 | -187.5 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | -0.4 | 0.01 | 2.8 | 715.419 | 3.167 | 20.83
| 260 | 2008-05-11 | 190000 | 97.6 | -2.7 | 0.38 | 29.2 | -248.2 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | -0.3 | 0.01 | 2.6 | 723.331 | 7.916 | 20.91
| 261 | 2008-05-11 | 200000 | 97.6 | -2.8 | 0.38 | 13.9 | -95.7 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.2 | 0.01 | 2.2 | 886.348 | 0.002 | 20.91
| 262 | 2008-05-11 | 210000 | 97.3 | -2.6 | 0.37 | 6.6 | -38.1 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0.01 | 2.1 | 579.299 | 1.586 | 20.85
| 263 | 2008-05-11 | 220000 | 95.7 | -2.6 | 0.37 | 1.8 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | -0.01 | -0.06 | 0 | 0.01 | 0.5 | 378.285 | 0.003 | 20.85
| 264 | 2008-05-11 | 230000 | 95.7 | -2.8 | 0.36 | 0.6 | -11.1 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.06 | 0 | 0.01 | 0 | 134.544 | 0.004 | 20.93
| 265 | 2008-05-12 | 0 | 95.5 | -2.6 | 0.36 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.06 | 0 | 0 | 0 | 189.94 | 0.004 | 20.93
| 266 | 2008-05-12 | 10000 | 94.3 | -2.5 | 0.36 | 1.7 | -4.8 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | -0.1 | 0 | 0.1 | 132.961 | 1.585 | 20.94
| 267 | 2008-05-12 | 20000 | 94.3 | -2.7 | 0.37 | 1.5 | -7.7 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | -0.01 | -0.06 | 0 | 0.01 | 0.1 | 156.702 | 0.004 | 20.86
| 268 | 2008-05-12 | 30000 | 94.2 | -2.4 | 0.36 | 3 | -41.6 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0 | 240.588 | 0.003 | 20.93
| 269 | 2008-05-12 | 40000 | 92.8 | -3 | 0.36 | 0.7 | -7.1 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0 | 0.3 | 242.173 | 0.003 | 20.93
| 270 | 2008-05-12 | 50000 | 92.3 | -2.7 | 0.36 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0 | 170.947 | 0.002 | 20.93
| 271 | 2008-05-12 | 60000 | 92.3 | -2.5 | 0.4 | 0.4 | -5.6 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.1 | 87.06 | 0.002 | 20.94
| 272 | 2008-05-12 | 70000 | 92.2 | -2.8 | 0.4 | 0.6 | -2.5 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.2 | 110.801 | 1.584 | 20.94
| 273 | 2008-05-12 | 80000 | 91.4 | -2.6 | 0.39 | 1.4 | -15 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0 | 0.6 | 140.877 | 1.585 | 20.93
| 274 | 2008-05-12 | 90000 | 90.8 | -2.8 | 0.39 | 0.6 | -13.6 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | 2.19 | 0 | 0.01 | 0.3 | 134.542 | 0.003 | 20.93
| 275 | 2008-05-12 | 100000 | 90.8 | -2.8 | 0.39 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 183.607 | 0.002 | 20.94
| 276 | 2008-05-12 | 110000 | 90.9 | -2.5 | 0.38 | 0.6 | -3.9 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.01 | 0.2 | 113.966 | 0.003 | 20.94
| 277 | 2008-05-12 | 120000 | 90.9 | -2.9 | 0.37 | 0.6 | -0.8 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.3 | 42.743 | 0.002 | 20.87
| 278 | 2008-05-12 | 130000 | 90.9 | -2.6 | 0.37 | 4.5 | -32.6 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | 0 | -0.06 | -0.1 | 0.01 | 0.9 | 276.992 | 1.585 | 20.93
| 279 | 2008-05-12 | 140000 | 90.9 | -2.7 | 0.37 | 2.4 | -31.5 | 0.06 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0 | 0.2 | 218.431 | 0.003 | 20.93
| 280 | 2008-05-12 | 150000 | 90.8 | -2.7 | 0.36 | 4.1 | -33.7 | 0.1 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0 | 0.8 | 205.767 | 0.003 | 20.93
| 281 | 2008-05-12 | 160000 | 90.9 | -2.8 | 0.37 | 9.6 | -62.4 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.1 | 0.01 | 1.9 | 572.968 | 4.751 | 20.92
| 282 | 2008-05-12 | 170000 | 90.9 | -2.8 | 0.37 | 29.7 | -243.1 | 0.02 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | -0.3 | 0.01 | 2.9 | 781.892 | 3.168 | 20.84
| 283 | 2008-05-12 | 180000 | 90.9 | -3 | 0.39 | 73.2 | -593.6 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.6 | 0 | 1.8 | 213.692 | 7.914 | 20.89
| 284 | 2008-05-12 | 190000 | 90.1 | -2.9 | 0.39 | 75.9 | -551.2 | 0.01 | 0.5 | 1.3 | -1.1 | 0.9 | 0 | -0.07 | -0.2 | 0.01 | 1.6 | 17.43 | 9.498 | 20.87
| 285 | 2008-05-12 | 200000 | 88.8 | -2.9 | 0.4 | 74.2 | -551.3 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.8 | 0.01 | 0.3 | 30.089 | 0 | 20.86
| 286 | 2008-05-12 | 210000 | 88.8 | -2.8 | 0.39 | 71.8 | -523.4 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | -0.9 | 0.01 | -0.2 | 58.578 | 3.166 | 20.87
| 287 | 2008-05-12 | 220000 | 88.8 | -2.7 | 0.39 | 78 | -529.2 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.9 | 0 | -1.1 | 6.346 | 0 | 20.87
| 288 | 2008-05-12 | 230000 | 88.8 | -2.9 | 0.39 | 78.3 | -619.6 | 0 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | -0.8 | 0.01 | 0.4 | 45.916 | 0 | 20.87
| 289 | 2008-05-13 | 0 | 87.9 | -2.9 | 0.39 | 77.1 | -559.5 | 0.01 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.7 | 0 | -0.8 | 7.929 | 0 | 20.86
| 290 | 2008-05-13 | 10000 | 87.4 | -2.7 | 0.39 | 66.8 | -481.4 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.6 | 0.02 | 0.8 | 0.017 | 0 | 20.86
| 291 | 2008-05-13 | 20000 | 87.5 | -2.6 | 0.39 | 65.5 | -446.9 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.7 | 0 | -1.5 | 0.011 | 0 | 20.86
| 292 | 2008-05-13 | 30000 | 87.5 | -2.7 | 0.39 | 56.4 | -388.6 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.6 | 0.01 | 0.5 | 0.013 | 0 | 20.85
| 293 | 2008-05-13 | 40000 | 87.5 | -2.7 | 0.4 | 57.6 | -408.2 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.6 | 0 | -0.3 | 0.013 | 0 | 20.85
| 294 | 2008-05-13 | 50000 | 87.4 | -3.1 | 0.4 | 61.4 | -446.5 | 0.01 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.1 | 0 | -0.7 | 0.011 | 0.001 | 20.86
| 295 | 2008-05-13 | 60000 | 85.4 | -2.7 | 0.42 | 61.4 | -418.6 | 0.01 | 0.5 | 1.3 | -0.9 | 0.9 | 0 | -0.07 | 0.2 | 0.02 | 0.5 | 3.179 | 1.584 | 20.85
| 296 | 2008-05-13 | 70000 | 85.4 | -3.2 | 0.46 | 69.9 | -484.9 | 0.01 | 0.5 | 1.3 | -1 | 0.8 | 0.01 | -0.07 | 1.5 | 0.01 | -0.6 | 0.013 | 3.171 | 20.85
| 297 | 2008-05-13 | 80000 | 85.4 | -2.8 | 0.43 | 70.3 | -446 | 0.01 | 0.5 | 1.3 | -1 | 1 | 0.01 | -0.06 | 1.3 | 0.01 | -0.9 | 0.012 | 3.17 | 20.86
| 298 | 2008-05-13 | 90000 | 85.4 | -2.7 | 0.42 | 69.7 | -442 | 0.01 | 0.5 | 1.3 | -1 | 0.8 | 0 | 2.19 | 0.8 | 0.01 | 1 | 0.015 | 6.334 | 20.86
| 299 | 2008-05-13 | 100000 | 85.3 | -2.8 | 0.42 | 67.5 | -425.1 | 0.01 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.6 | 0.01 | 0.8 | 7.928 | 4.751 | 20.86
| 300 | 2008-05-13 | 110000 | 85.4 | -2.6 | 0.42 | 71.1 | -404.8 | 0.01 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | 0.3 | 0 | -0.7 | 0.013 | 7.915 | 20.86
| 301 | 2008-05-13 | 120000 | 85.3 | -2.7 | 0.43 | 77.5 | -467.4 | 0.01 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | 0.1 | 0.01 | 0.6 | 15.844 | 6.332 | 20.86
| 302 | 2008-05-13 | 130000 | 85.4 | -2.9 | 0.45 | 81.1 | -482.3 | 0.01 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | 0.2 | 0.01 | -0.7 | 3.181 | 1.584 | 20.86
| 303 | 2008-05-13 | 140000 | 83.5 | -2.7 | 0.46 | 96.8 | -569.9 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0.3 | 0 | -1.1 | 56.996 | 6.333 | 20.87
| 304 | 2008-05-13 | 150000 | 83.3 | -3 | 0.48 | 107.8 | -648.4 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 1 | 0.01 | 3.1 | 44.343 | 34.824 | 20.87
| 305 | 2008-05-13 | 160000 | 83.2 | -2.7 | 0.49 | 97.6 | -508.1 | 0.04 | 0.5 | 1.3 | -1 | 1.1 | 0.01 | -0.07 | 2.1 | 0.02 | 4.6 | 178.877 | 142.453 | 20.88
| 306 | 2008-05-13 | 170000 | 83.2 | -2.9 | 0.49 | 102.6 | -626.1 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0.7 | 0.01 | 3.8 | 359.311 | 45.902 | 20.89
| 307 | 2008-05-13 | 180000 | 83.2 | -2.7 | 0.45 | 77.4 | -437.8 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.01 | 4.6 | 305.5 | 22.16 | 20.89
| 308 | 2008-05-13 | 190000 | 83.1 | -2.8 | 0.39 | 52.9 | -291.9 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | -0.6 | 0.01 | 2 | 428.942 | 4.749 | 20.9
| 309 | 2008-05-13 | 200000 | 83.2 | -3 | 0.38 | 34.4 | -237.2 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | -0.6 | 0.01 | 3.7 | 482.758 | 3.167 | 20.83
| 310 | 2008-05-13 | 210000 | 83.2 | -2.9 | 0.4 | 6.4 | -41.8 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | -0.1 | 0.01 | 1.1 | 481.165 | 0.002 | 20.93
| 311 | 2008-05-13 | 220000 | 83.2 | -2.9 | 0.39 | 1.1 | -9.3 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | 0 | 0.01 | 0.6 | 155.12 | 9.498 | 20.94
| 312 | 2008-05-13 | 230000 | 83.3 | -2.8 | 0.41 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0.01 | -0.06 | 0 | 0.02 | 0 | 189.935 | 18.993 | 20.94
| 313 | 2008-05-14 | 0 | 82.2 | -2.6 | 0.42 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0 | 11.085 | 3.166 | 20.95
| 314 | 2008-05-14 | 10000 | 81.7 | -2.6 | 0.44 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | 0 | 0.01 | 0 | 3.173 | 0 | 20.96
| 315 | 2008-05-14 | 20000 | 81.6 | -2.3 | 0.44 | 0.8 | -3.9 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.02 | 0.4 | 7.921 | 1.583 | 20.96
| 316 | 2008-05-14 | 30000 | 81.6 | -3 | 0.44 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.005 | 0 | 20.82
| 317 | 2008-05-14 | 40000 | 81.6 | -2.7 | 0.41 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.005 | 0 | 20.9
| 318 | 2008-05-14 | 50000 | 81.7 | -2.7 | 0.36 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | 0 | 0 | 0 | 0.005 | 0.001 | 20.99
| 319 | 2008-05-14 | 60000 | 81.7 | -2.7 | 0.4 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | 1 | 0 | -0.06 | 0 | 0.01 | 0 | 0.004 | 0.001 | 21
| 320 | 2008-05-14 | 70000 | 81.7 | -2.7 | 0.46 | 0 | 0 | 0.04 | 0.5 | 1.3 | -0.9 | 1 | 0.01 | -0.06 | 0 | 0.01 | 0 | 0.003 | 0 | 20.94
| 321 | 2008-05-14 | 80000 | 81.7 | -2.7 | 0.46 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0.01 | -0.06 | 0 | 0.01 | 0 | 0.003 | 0 | 21.03
| 322 | 2008-05-14 | 90000 | 81.6 | -2.9 | 0.43 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | 2.2 | 0 | 0.01 | 0 | 0.003 | 0 | 21.04
| 323 | 2008-05-14 | 100000 | 81.7 | -2.6 | 0.43 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0.01 | -0.06 | 0 | 0.01 | 0 | 0.002 | 0 | 21.06
| 324 | 2008-05-14 | 110000 | 81.6 | -3 | 0.46 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0.01 | -0.07 | 0 | 0.02 | 0 | 0.002 | 0 | 21
| 325 | 2008-05-14 | 120000 | 81.6 | -2.7 | 0.44 | 0 | 0 | 0.02 | 0.5 | 1.3 | -1 | 1 | 0.01 | -0.06 | 0 | 0.01 | 0 | 0.002 | 0 | 21.08
| 326 | 2008-05-14 | 130000 | 81.6 | -2.6 | 0.44 | 0 | 0 | 0.01 | 0.5 | 1.2 | -1 | 1 | 0.02 | -0.06 | 0 | 0.03 | 0 | 0.002 | 0 | 21.09
| 327 | 2008-05-14 | 140000 | 81.6 | -2.7 | 0.42 | 0 | 0 | 0.17 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.01 | 0 | 0.002 | 0 | 21.02
| 328 | 2008-05-14 | 150000 | 81.7 | -2.6 | 0.4 | 0 | 0 | 0.08 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.01 | 0 | 0.002 | 0 | 21.09
| 329 | 2008-05-14 | 160000 | 81.7 | -2.9 | 0.39 | 0 | 0 | 0.22 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0.02 | 0 | 0.002 | 0 | 21.08
| 330 | 2008-05-14 | 170000 | 82.5 | -2.8 | 0.39 | 0 | 0 | 0.03 | 0.5 | 1.2 | -0.9 | 0.9 | 0 | -0.07 | 0 | 0.01 | 0 | 0.002 | 0 | 21.07
| 331 | 2008-05-14 | 180000 | 83.3 | -2.8 | 0.39 | 0 | 0 | 0.04 | 0.5 | 1.2 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | 0 | 0.003 | 0.001 | 21.06
| 332 | 2008-05-14 | 190000 | 83.4 | -3 | 0.39 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.07 | 0 | 0.01 | 0 | 0.002 | 0.001 | 20.98
| 333 | 2008-05-14 | 200000 | 83.6 | -2.6 | 0.39 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0 | 0 | 0.003 | 0.001 | 20.99
| 334 | 2008-05-14 | 210000 | 83.5 | -3 | 0.38 | 0 | 0 | 0.02 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0 | 0.01 | 0 | 0.002 | 0.001 | 21.07
| 335 | 2008-05-14 | 220000 | 82.1 | -2.9 | 0.37 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0 | 0 | 0.003 | 0.001 | 21.06
| 336 | 2008-05-14 | 230000 | 81.7 | -2.3 | 0.38 | 0 | 0 | 0.02 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.05 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.06
| 337 | 2008-05-15 | 0 | 81.6 | -2.6 | 0.38 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | 0 | 0 | 0 | 0.003 | 0.001 | 21.06
| 338 | 2008-05-15 | 10000 | 81.6 | -2.9 | 0.38 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.003 | 0 | 21.05
| 339 | 2008-05-15 | 20000 | 81.7 | -2.5 | 0.38 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | 0 | 0.003 | 0 | 21.05
| 340 | 2008-05-15 | 30000 | 81.6 | -2.9 | 0.38 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | 0 | 0.004 | 0.001 | 21.04
| 341 | 2008-05-15 | 40000 | 81.7 | -2.4 | 0.39 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.003 | 0.001 | 21.04
| 342 | 2008-05-15 | 50000 | 81.4 | -2.5 | 0.39 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.003 | 0.001 | 20.96
| 343 | 2008-05-15 | 60000 | 79.7 | -2.6 | 0.41 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.003 | 0 | 21.03
| 344 | 2008-05-15 | 70000 | 79.7 | -2.7 | 0.42 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.003 | 0 | 21.03
| 345 | 2008-05-15 | 80000 | 79.7 | -2.5 | 0.43 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0 | 0 | 0.004 | 0 | 21.03
| 346 | 2008-05-15 | 90000 | 79.7 | -3.1 | 0.42 | 0 | 0 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | 2.19 | 0 | 0.01 | 0 | 0.003 | 0 | 21.02
| 347 | 2008-05-15 | 100000 | 80.8 | -2.6 | 0.41 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0 | 0 | 0.004 | 0 | 21.01
| 348 | 2008-05-15 | 110000 | 81.8 | -2.5 | 0.41 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0 | 0.004 | 0 | 21
| 349 | 2008-05-15 | 120000 | 81.7 | -2.5 | 0.42 | 0 | 0 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0 | 0.005 | 0.001 | 20.98
| 350 | 2008-05-15 | 130000 | 81.7 | -2.6 | 0.42 | 0 | 0 | 0.15 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0 | 0.007 | 0.001 | 20.96
| 351 | 2008-05-15 | 140000 | 81.7 | -2.7 | 0.41 | 0 | 0 | 0.08 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0 | 0 | 0 | 7.923 | 1.585 | 20.95
| 352 | 2008-05-15 | 150000 | 81.9 | -2.7 | 0.41 | 7.8 | -55.2 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.1 | 0.01 | 1.2 | 256.417 | 14.245 | 20.85
| 353 | 2008-05-15 | 160000 | 83.5 | -2.5 | 0.42 | 38.7 | -191.6 | 0.04 | 0.5 | 1.3 | -0.9 | 0.7 | 0 | -0.06 | 0.1 | 0 | 2.6 | 550.814 | 28.49 | 20.91
| 354 | 2008-05-15 | 170000 | 83.5 | -2.6 | 0.43 | 92.8 | -572 | 0.04 | 0.5 | 1.3 | -0.9 | 0.6 | 0 | -0.06 | 0.1 | 0 | 5.4 | 101.326 | 26.908 | 20.89
| 355 | 2008-05-15 | 180000 | 85.2 | -2.7 | 0.43 | 94.1 | -570.8 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.2 | 0.01 | 1.9 | 58.582 | 7.915 | 20.8
| 356 | 2008-05-15 | 190000 | 85.1 | -2.4 | 0.44 | 104.7 | -495.6 | 0.04 | 0.5 | 1.3 | 142.5 | 0.6 | 0 | -0.07 | 0.3 | 0.01 | 0.7 | 101.318 | 20.577 | 20.88
| 357 | 2008-05-15 | 200000 | 84.7 | -2.9 | 0.44 | 93.9 | -605.4 | 0.04 | 0.5 | 1.3 | 157.9 | 0.6 | 0 | -0.06 | 0.3 | 0.01 | 2.5 | 178.871 | 17.412 | 20.8
| 358 | 2008-05-15 | 210000 | 83.2 | -2.9 | 0.44 | 84.9 | -569.2 | 0.04 | 0.5 | 1.3 | 221.8 | 0.6 | 0 | -0.06 | 0.2 | 0.01 | 2.8 | 261.178 | 34.822 | 20.89
| 359 | 2008-05-15 | 220000 | 83.2 | -2.7 | 0.45 | 103.6 | -625.1 | 0.04 | 0.5 | 1.3 | 405.9 | 0.4 | 0 | -0.07 | 0.2 | 0.01 | 1.7 | 220.022 | 30.074 | 20.88
| 360 | 2008-05-15 | 230000 | 83.2 | -2.6 | 0.47 | 103.6 | -590 | 0.04 | 0.5 | 1.3 | 462.9 | 0.4 | 0 | -0.06 | 0.9 | 0.02 | 3.7 | 145.636 | 37.989 | 20.87
| 361 | 2008-05-16 | 0 | 82.8 | -2.8 | 0.5 | 93.4 | -575.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.4 | 0.01 | -0.06 | 1.1 | 0.01 | -0.3 | 9.512 | 22.162 | 20.79
| 362 | 2008-05-16 | 10000 | 81.5 | -2.9 | 0.47 | 76.3 | -446.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.4 | 0 | -0.06 | 0.5 | 0.01 | 0 | 6.345 | 6.333 | 20.86
| 363 | 2008-05-16 | 20000 | 81.7 | -2.7 | 0.48 | 70.8 | -402.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | 0 | -0.07 | 0.6 | 0.01 | -0.4 | 0.012 | 4.75 | 20.85
| 364 | 2008-05-16 | 30000 | 81.5 | -2.6 | 0.5 | 60.7 | -304.9 | 0.04 | 0.5 | 1.3 | 460.6 | 0.3 | 0 | -0.07 | 0.4 | 0.01 | 0.2 | 0.011 | 0.002 | 20.77
| 365 | 2008-05-16 | 40000 | 79.8 | -2.7 | 0.51 | 57.4 | -301.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.5 | 0 | -0.07 | 0.3 | 0.01 | 0.5 | 0.012 | 0.001 | 20.84
| 366 | 2008-05-16 | 50000 | 79.6 | -2.5 | 0.54 | 55.8 | -262.4 | 0.04 | 0.5 | 1.3 | 461.5 | 0.5 | 0 | -0.06 | 0.4 | 0 | -0.1 | 0.009 | 0.002 | 20.84
| 367 | 2008-05-16 | 60000 | 79.1 | -2.9 | 0.61 | 55.2 | -256.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.5 | 0.01 | -0.06 | 0.8 | 0.01 | 0.2 | 0.009 | 0.003 | 20.83
| 368 | 2008-05-16 | 70000 | 78.2 | -2.5 | 0.59 | 55.1 | -236.5 | 0.03 | 0.5 | 1.3 | 461.9 | 0.3 | 0.01 | -0.06 | 0.9 | 0.01 | 0 | 0.008 | 0.003 | 20.83
| 369 | 2008-05-16 | 80000 | 78.3 | -2.5 | 0.57 | 53.7 | -234 | 0.04 | 0.5 | 1.3 | 313.2 | 0.4 | 0.01 | -0.05 | 1.1 | 0.01 | -0.1 | 0.009 | 0.004 | 20.83
| 370 | 2008-05-16 | 90000 | 79.5 | -2.9 | 0.56 | 48.2 | -239.7 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0.01 | 2.21 | 1.2 | 0.02 | 1 | 0.01 | 0.004 | 20.83
| 371 | 2008-05-16 | 100000 | 79.7 | -2.7 | 0.55 | 42.2 | -204.7 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0.02 | -0.04 | 1.2 | 0.01 | 0.7 | 0.008 | 0.004 | 20.74
| 372 | 2008-05-16 | 110000 | 79.8 | -3 | 0.56 | 40.9 | -201.9 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0.02 | -0.04 | 1.4 | 0.02 | 0.6 | 0.007 | 0.005 | 20.82
| 373 | 2008-05-16 | 120000 | 80.8 | -3 | 0.56 | 35.5 | -192.4 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0.02 | -0.03 | 1.2 | 0.02 | 1.2 | 0.008 | 0.004 | 20.8
| 374 | 2008-05-16 | 130000 | 81.6 | -3 | 0.52 | 28.9 | -165.1 | 0.04 | 0.5 | 1.3 | -0.8 | 0.7 | 0 | -0.06 | 0.1 | 0.01 | 0.5 | 0.006 | 0 | 20.79
| 375 | 2008-05-16 | 140000 | 82 | -2.6 | 0.5 | 24.4 | -130.2 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.4 | 0.005 | 0 | 20.78
| 376 | 2008-05-16 | 150000 | 83.2 | -2.4 | 0.49 | 21.8 | -104.4 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0.004 | 0 | 20.76
| 377 | 2008-05-16 | 160000 | 83.7 | -2.6 | 0.5 | 19.3 | -97.9 | 0.03 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.07 | 0 | 0.01 | 0.1 | 0.003 | 0 | 20.75
| 378 | 2008-05-16 | 170000 | 85.3 | -2.6 | 0.49 | 17.6 | -92.6 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.06 | 0.1 | 0.01 | 0.3 | 0.004 | 0.001 | 20.73
| 379 | 2008-05-16 | 180000 | 85.9 | -2.7 | 0.5 | 17.5 | -98.7 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0.2 | 0.01 | 0.3 | 0.004 | 0.001 | 20.73
| 380 | 2008-05-16 | 190000 | 87.4 | -2.6 | 0.53 | 18.1 | -93.3 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0.1 | 0.02 | 0.5 | 0.004 | 0 | 20.73
| 381 | 2008-05-16 | 200000 | 87.5 | -2.6 | 0.55 | 19.1 | -93.8 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0.01 | -0.07 | 0.4 | 0.01 | 0.3 | 0.004 | 0.001 | 20.73
| 382 | 2008-05-16 | 210000 | 87.6 | -2.6 | 0.55 | 19.7 | -92 | 0.04 | 0.5 | 1.2 | -1 | 0.7 | 0.01 | -0.05 | 0.3 | 0.01 | 0.2 | 0.004 | 0.001 | 20.73
| 383 | 2008-05-16 | 220000 | 87.6 | -2.7 | 0.61 | 22.5 | -94.2 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0.02 | -0.04 | 0.8 | 0.03 | 1.3 | 0.006 | 0.003 | 20.74
| 384 | 2008-05-16 | 230000 | 87.4 | -2.8 | 0.61 | 23.1 | -112 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0.05 | -0.01 | 2.1 | 0.05 | 1.8 | 0.008 | 0.008 | 20.74
| 385 | 2008-05-17 | 0 | 85.4 | -2.7 | 0.57 | 22.5 | -108.4 | 0.03 | 0.5 | 1.2 | -1 | 0.7 | 0.04 | -0.02 | 1.5 | 0.03 | 0.9 | 0.005 | 0.006 | 20.75
| 386 | 2008-05-17 | 10000 | 85.5 | -2.6 | 0.6 | 23 | -93.2 | 0.02 | 0.5 | 1.2 | -0.9 | 0.8 | 0.02 | -0.03 | 0.8 | 0.03 | 1.2 | 0.006 | 0.003 | 20.74
| 387 | 2008-05-17 | 20000 | 84.9 | -2.9 | 0.58 | 22.2 | -112 | 0.02 | 0.5 | 1.2 | -1 | 0.7 | 0.01 | -0.06 | 0.5 | 0 | 0.1 | 0.003 | 0.002 | 20.74
| 388 | 2008-05-17 | 30000 | 83.4 | -2.8 | 0.58 | 21.7 | -104.4 | 0.02 | 0.5 | 1.3 | -1 | 0.7 | 0.01 | -0.07 | 0.3 | 0.01 | 0.1 | 0.003 | 0.001 | 20.74
| 389 | 2008-05-17 | 40000 | 83.5 | -2.8 | 0.53 | 20.7 | -102.1 | 0.02 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.1 | 0 | -0.1 | 0.003 | 0 | 20.67
| 390 | 2008-05-17 | 50000 | 82.2 | -3 | 0.56 | 23.3 | -126.7 | 0.02 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.76
| 391 | 2008-05-17 | 60000 | 81.5 | -3 | 0.58 | 25.4 | -141 | 0.02 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | 0.2 | 0 | 0.1 | 0.004 | 0.001 | 20.76
| 392 | 2008-05-17 | 70000 | 81.6 | -2.8 | 0.55 | 26.2 | -136.1 | 0.01 | 0.5 | 1.3 | 41.2 | 0.7 | 0.01 | -0.05 | 0.4 | 0.01 | 0.3 | 0.005 | 0.002 | 20.77
| 393 | 2008-05-17 | 80000 | 81.6 | -3.1 | 0.54 | 27 | -151.9 | 0.02 | 0.5 | 1.3 | 27.7 | 0.7 | 0.02 | -0.03 | 0.9 | 0.04 | 1.8 | 0.008 | 0.004 | 20.78
| 394 | 2008-05-17 | 90000 | 82.1 | -2.6 | 0.52 | 24.3 | -119.6 | 0.03 | 0.5 | 1.2 | -1 | 0.7 | 0.02 | 2.21 | 0.9 | 0.03 | 1.5 | 0.007 | 0.003 | 20.77
| 395 | 2008-05-17 | 100000 | 84.1 | -2.6 | 0.49 | 22.6 | -115.2 | 0.03 | 0.5 | 1.2 | -1 | 0.7 | 0.01 | -0.06 | 0.3 | 0.01 | -0.1 | 0.003 | 0.001 | 20.77
| 396 | 2008-05-17 | 110000 | 86.3 | -2.5 | 0.45 | 19.4 | -109 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0 | 0.003 | 0 | 20.76
| 397 | 2008-05-17 | 120000 | 87.7 | -2.6 | 0.45 | 18.5 | -104.4 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.75
| 398 | 2008-05-17 | 130000 | 88.8 | -2.6 | 0.46 | 17.8 | -95.8 | 0.03 | 0.5 | 1.3 | -0.9 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.3 | 0.004 | 0 | 20.75
| 399 | 2008-05-17 | 140000 | 88.9 | -2.5 | 0.47 | 17.6 | -97.5 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0 | 0 | 0.003 | 0 | 20.74
| 400 | 2008-05-17 | 150000 | 88.8 | -2.5 | 0.43 | 16.2 | -93.7 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | 0 | 0 | 0 | 0.003 | 0 | 20.74
| 401 | 2008-05-17 | 160000 | 88.8 | -2.6 | 0.43 | 15.6 | -90.3 | 0.02 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | -0.1 | 0 | -0.1 | 0.003 | 0 | 20.74
| 402 | 2008-05-17 | 170000 | 88.8 | -2.6 | 0.42 | 14.3 | -85.4 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.08 | 0 | 0 | -0.1 | 0.003 | 0 | 20.65
| 403 | 2008-05-17 | 180000 | 88.9 | -2.8 | 0.43 | 14.4 | -92.5 | 0.03 | 0.5 | 1.3 | -1 | 1 | 0 | -0.08 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.72
| 404 | 2008-05-17 | 190000 | 88.9 | -2.6 | 0.43 | 15.2 | -95.3 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.3 | 0.004 | 0 | 20.66
| 405 | 2008-05-17 | 200000 | 88.8 | -2.5 | 0.42 | 17.2 | -104.2 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.08 | -0.1 | 0 | -0.2 | 0.003 | 0 | 20.68
| 406 | 2008-05-17 | 210000 | 88.3 | -2.7 | 0.41 | 19.2 | -124.8 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.09 | -0.2 | 0.01 | 0.2 | 0.004 | 0 | 20.77
| 407 | 2008-05-17 | 220000 | 87.4 | -2.7 | 0.42 | 20.4 | -128.4 | 0.04 | 0.5 | 1.3 | -0.9 | 0.8 | 0 | -0.08 | -0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.78
| 408 | 2008-05-17 | 230000 | 85.1 | -2.6 | 0.42 | 24.5 | -152.5 | 0.03 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.09 | -0.2 | 0.01 | 0.4 | 0.006 | 0 | 20.8
| 409 | 2008-05-18 | 0 | 83.4 | -2.5 | 0.42 | 25.1 | -145.8 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.09 | -0.2 | 0.01 | 0.2 | 0.005 | 0 | 20.8
| 410 | 2008-05-18 | 10000 | 82.1 | -2.6 | 0.43 | 26 | -161.3 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.09 | -0.2 | 0.01 | 0.4 | 0.006 | 0 | 20.8
| 411 | 2008-05-18 | 20000 | 81 | -2.6 | 0.42 | 26.1 | -166.2 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.09 | -0.4 | 0.01 | 0.6 | 0.006 | 0 | 20.73
| 412 | 2008-05-18 | 30000 | 79.5 | -3 | 0.42 | 27.5 | -188.2 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.09 | -0.4 | 0.01 | 0.2 | 0.006 | 0 | 20.73
| 413 | 2008-05-18 | 40000 | 78.5 | -2.5 | 0.42 | 27.7 | -162 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.09 | -0.4 | 0.01 | 0.5 | 0.006 | 0 | 20.81
| 414 | 2008-05-18 | 50000 | 78.3 | -2.5 | 0.43 | 29.7 | -176.8 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.08 | -0.4 | 0.01 | 0.6 | 0.007 | 0 | 20.81
| 415 | 2008-05-18 | 60000 | 76.4 | -2.6 | 0.42 | 31.1 | -187.9 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | -0.01 | -0.07 | -0.4 | 0.01 | 0.1 | 0.005 | 0 | 20.82
| 416 | 2008-05-18 | 70000 | 76.2 | -2.4 | 0.42 | 32.1 | -182 | 0.04 | 0.5 | 1.3 | -0.9 | 0.8 | -0.01 | -0.09 | -0.5 | 0.01 | 0.3 | 0.006 | 0 | 20.82
| 417 | 2008-05-18 | 80000 | 76.2 | -2.8 | 0.43 | 33.6 | -223.2 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.09 | -0.5 | 0.01 | 0.3 | 0.007 | 0 | 20.82
| 418 | 2008-05-18 | 90000 | 76.2 | -2.5 | 0.43 | 32.3 | -191.1 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | -0.01 | 2.19 | -0.4 | 0.02 | 1.1 | 0.008 | 0 | 20.82
| 419 | 2008-05-18 | 100000 | 76.2 | -2.6 | 0.44 | 30.8 | -185.2 | 0.04 | 0.5 | 1.3 | -0.9 | 0.7 | 0 | -0.05 | -0.3 | 0.02 | 0.9 | 0.007 | 0 | 20.81
| 420 | 2008-05-18 | 110000 | 76.1 | -2.4 | 0.44 | 28.7 | -147.8 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.2 | 0.01 | 0.7 | 0.006 | 0 | 20.81
| 421 | 2008-05-18 | 120000 | 76.8 | -2.5 | 0.45 | 26.4 | -147 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.2 | 0.01 | 0.7 | 0.006 | 0 | 20.8
| 422 | 2008-05-18 | 130000 | 78.2 | -2.8 | 0.44 | 23.5 | -153 | 0.04 | 0.5 | 1.3 | -0.9 | 0.9 | -0.01 | -0.07 | -0.4 | 0.01 | 0.8 | 0.006 | 0 | 20.79
| 423 | 2008-05-18 | 140000 | 78.4 | -2.8 | 0.42 | 19.2 | -131.1 | 0.04 | 0.5 | 1.3 | -0.7 | 0.9 | -0.01 | -0.08 | -0.3 | 0.01 | 0.4 | 0.005 | 0 | 20.77
| 424 | 2008-05-18 | 150000 | 78.3 | -2.8 | 0.41 | 17 | -110.4 | 0.03 | 0.5 | 1.3 | 17.5 | 0.9 | 0 | -0.09 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.76
| 425 | 2008-05-18 | 160000 | 78.3 | -2.6 | 0.42 | 16.4 | -104.9 | 0.03 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | -0.1 | 0.01 | 0.6 | 0.004 | 0 | 20.75
| 426 | 2008-05-18 | 170000 | 79.4 | -2.7 | 0.42 | 15.3 | -99.3 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.09 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.74
| 427 | 2008-05-18 | 180000 | 79.8 | -2.8 | 0.42 | 14.8 | -96.4 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.09 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.66
| 428 | 2008-05-18 | 190000 | 79.7 | -2.4 | 0.42 | 15 | -85.5 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.09 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.73
| 429 | 2008-05-18 | 200000 | 79.6 | -2.7 | 0.43 | 15.1 | -93.9 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.09 | -0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.73
| 430 | 2008-05-18 | 210000 | 79.7 | -2.8 | 0.43 | 15.9 | -104.1 | 0.04 | 0.5 | 1.3 | -0.9 | 0.8 | 0 | -0.08 | -0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.74
| 431 | 2008-05-18 | 220000 | 79.7 | -2.8 | 0.43 | 16.4 | -109.8 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.07 | -0.1 | 0.01 | 0 | 0.003 | 0 | 20.75
| 432 | 2008-05-18 | 230000 | 78.9 | -2.8 | 0.43 | 16.8 | -106.3 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.4 | 0.004 | 0 | 20.75
| 433 | 2008-05-19 | 0 | 78.3 | -2.6 | 0.43 | 17.1 | -107.5 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | -0.2 | 0.01 | 0.2 | 0.004 | 0 | 20.75
| 434 | 2008-05-19 | 10000 | 78.2 | -2.7 | 0.43 | 16.2 | -101 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0 | 0 | 0.003 | 0 | 20.74
| 435 | 2008-05-19 | 20000 | 78.2 | -2.8 | 0.43 | 15.8 | -104.1 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.07 | -0.1 | 0 | -0.1 | 0.003 | 0 | 20.74
| 436 | 2008-05-19 | 30000 | 77.5 | -2.6 | 0.44 | 14.7 | -88.1 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.07 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.65
| 437 | 2008-05-19 | 40000 | 76.2 | -2.5 | 0.44 | 14.7 | -84.4 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.65
| 438 | 2008-05-19 | 50000 | 76.2 | -2.7 | 0.45 | 15.1 | -90.2 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | -0.1 | 0 | 0.1 | 0.003 | 0 | 20.72
| 439 | 2008-05-19 | 60000 | 75.4 | -2.7 | 0.5 | 16.6 | -89.9 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0 | 0 | 0.003 | 0 | 20.72
| 440 | 2008-05-19 | 70000 | 74.8 | -2.3 | 0.5 | 17 | -77.6 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0.1 | 0 | 0 | 0.003 | 0 | 20.72
| 441 | 2008-05-19 | 80000 | 75.8 | -2.5 | 0.59 | 19.9 | -87.1 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0.02 | -0.03 | 0.6 | 0.02 | 0.8 | 0.004 | 0.002 | 20.72
| 442 | 2008-05-19 | 90000 | 76.1 | -2.4 | 0.57 | 18.9 | -82.5 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0.02 | 2.22 | 0.7 | 0.03 | 1.1 | 0.005 | 0.003 | 20.72
| 443 | 2008-05-19 | 100000 | 76.2 | -2.6 | 0.54 | 17.4 | -92.5 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0.02 | -0.03 | 0.6 | 0.03 | 0.8 | 0.004 | 0.002 | 20.72
| 444 | 2008-05-19 | 110000 | 76.4 | -2.5 | 0.49 | 15.4 | -76.8 | 0.04 | 0.5 | 1.2 | -1 | 0.8 | 0.01 | -0.04 | 0.3 | 0.01 | 0.3 | 0.003 | 0.001 | 20.71
| 445 | 2008-05-19 | 120000 | 78.2 | -2.5 | 0.44 | 13 | -73.1 | 0.04 | 0.5 | 1.3 | -1 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.003 | 0 | 20.7
| 446 | 2008-05-19 | 130000 | 78.3 | -2.5 | 0.44 | 12.3 | -67.9 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.69
| 447 | 2008-05-19 | 140000 | 79.4 | -2.7 | 0.45 | 11.9 | -72.1 | 0.04 | 0.5 | 1.3 | -1 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.002 | 0 | 20.68
| 448 | 2008-05-19 | 150000 | 79.6 | -2.7 | 0.44 | 11.3 | -69.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | 0 | 0 | 0 | 0.002 | 0 | 20.67
| 449 | 2008-05-19 | 160000 | 79.1 | -2.5 | 0.4 | 10.4 | -61.4 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.07 | -0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.67
| 450 | 2008-05-19 | 170000 | 76.9 | -2.6 | 0.39 | 10.1 | -72.4 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.08 | -0.1 | 0 | 0.2 | 0.002 | 0 | 20.67
| 451 | 2008-05-19 | 180000 | 76.1 | -2.5 | 0.39 | 9.8 | -64 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0.003 | 0 | 20.67
| 452 | 2008-05-19 | 190000 | 78.2 | -2.8 | 0.39 | 9.8 | -68.3 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.002 | 0 | 20.66
| 453 | 2008-05-19 | 200000 | 78.2 | -2.6 | 0.4 | 10 | -66.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.07 | 0 | 0 | 0 | 0.002 | 0 | 20.66
| 454 | 2008-05-19 | 210000 | 78.3 | -2.7 | 0.4 | 10.3 | -70.2 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.07 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.67
| 455 | 2008-05-19 | 220000 | 78.3 | -2.6 | 0.39 | 10.3 | -68.3 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.08 | -0.1 | 0 | 0.1 | 0.002 | 0 | 20.67
| 456 | 2008-05-19 | 230000 | 78.1 | -2.5 | 0.39 | 11.3 | -71.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.09 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.69
| 457 | 2008-05-20 | 0 | 78.2 | -2.4 | 0.4 | 10.9 | -64.4 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.09 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.68
| 458 | 2008-05-20 | 10000 | 78.3 | -2.8 | 0.4 | 10.7 | -72.8 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.09 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.68
| 459 | 2008-05-20 | 20000 | 78.1 | -2.4 | 0.41 | 10.4 | -61 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.67
| 460 | 2008-05-20 | 30000 | 78.2 | -2.8 | 0.43 | 11.6 | -77.7 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.08 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.61
| 461 | 2008-05-20 | 40000 | 76.6 | -2.5 | 0.45 | 13.1 | -75.8 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.69
| 462 | 2008-05-20 | 50000 | 76.1 | -2.4 | 0.47 | 14.3 | -74.3 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.71
| 463 | 2008-05-20 | 60000 | 75.4 | -2.6 | 0.48 | 15.2 | -83.4 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.07 | -0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.71
| 464 | 2008-05-20 | 70000 | 74.7 | -2.6 | 0.51 | 16 | -85.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.63
| 465 | 2008-05-20 | 80000 | 73.9 | -2.5 | 0.51 | 17 | -84.9 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.5 | 0.003 | 0 | 20.57
| 466 | 2008-05-20 | 90000 | 72.8 | -2.7 | 0.52 | 17.5 | -96.1 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | 2.18 | -0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.72
| 467 | 2008-05-20 | 100000 | 72.8 | -2.6 | 0.49 | 17.2 | -86.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.07 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.73
| 468 | 2008-05-20 | 110000 | 72.8 | -2.1 | 0.49 | 17.7 | -73.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.06 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.73
| 469 | 2008-05-20 | 120000 | 71.5 | -2.7 | 0.5 | 17.5 | -89.8 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.07 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.66
| 470 | 2008-05-20 | 130000 | 71.4 | -2.5 | 0.5 | 19 | -99.4 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.07 | -0.3 | 0 | 0.1 | 0.003 | 0 | 20.74
| 471 | 2008-05-20 | 140000 | 71.4 | -2.4 | 0.49 | 21.5 | -102.4 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.08 | -0.3 | 0.01 | 0.6 | 0.004 | 0 | 20.76
| 472 | 2008-05-20 | 150000 | 70.2 | -2.5 | 0.49 | 23.3 | -118.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.77
| 473 | 2008-05-20 | 160000 | 69.5 | -2.7 | 0.5 | 24 | -129.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.78
| 474 | 2008-05-20 | 170000 | 69.4 | -2.6 | 0.49 | 24.7 | -134.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -0.3 | 0.01 | 0.1 | 0.004 | 0 | 20.78
| 475 | 2008-05-20 | 180000 | 68.5 | -2.9 | 0.49 | 25.7 | -149.7 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.3 | 0.01 | 0.3 | 0.005 | 0 | 20.79
| 476 | 2008-05-20 | 190000 | 67.8 | -2.6 | 0.5 | 28.4 | -148.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.4 | 0.01 | 0.3 | 0.005 | 0 | 20.79
| 477 | 2008-05-20 | 200000 | 67.7 | -2.7 | 0.5 | 30.6 | -168.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -0.4 | 0.01 | 0.3 | 0.006 | 0 | 20.8
| 478 | 2008-05-20 | 210000 | 67.7 | -2.5 | 0.49 | 33.1 | -162.1 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.5 | 0.01 | 0.3 | 0.006 | 0 | 20.81
| 479 | 2008-05-20 | 220000 | 67.9 | -2.5 | 0.49 | 38.7 | -213.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.4 | 0.01 | 0.6 | 0.007 | 0 | 20.82
| 480 | 2008-05-20 | 230000 | 67.8 | -2.5 | 0.49 | 43.8 | -225.7 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.6 | 0.01 | 0.4 | 0.008 | 0 | 20.83
| 481 | 2008-05-21 | 0 | 67.7 | -2.6 | 0.49 | 48.1 | -251.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.7 | 0.01 | 0.4 | 0.008 | 0 | 20.76
| 482 | 2008-05-21 | 10000 | 67.8 | -2.8 | 0.49 | 48.1 | -282.7 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.7 | 0.02 | 1.4 | 0.01 | 0 | 20.84
| 483 | 2008-05-21 | 20000 | 67.8 | -2.5 | 0.48 | 49.2 | -253 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.8 | 0.01 | 0.7 | 0.01 | 0 | 20.84
| 484 | 2008-05-21 | 30000 | 67.3 | -2.3 | 0.48 | 47.8 | -234.2 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.7 | 0.01 | 0.7 | 0.009 | 0 | 20.84
| 485 | 2008-05-21 | 40000 | 65.7 | -2.5 | 0.48 | 47.7 | -253.5 | 0.04 | 0.5 | 1.3 | -0.9 | 0.5 | -0.01 | -0.06 | -0.8 | 0.01 | 0.1 | 0.008 | 0 | 20.84
| 486 | 2008-05-21 | 50000 | 65.8 | -2.7 | 0.49 | 49.1 | -277.7 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.7 | 0.01 | 0.8 | 0.009 | 0 | 20.76
| 487 | 2008-05-21 | 60000 | 66 | -2.7 | 0.48 | 49.3 | -278.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -0.8 | 0 | -0.1 | 0.007 | 0 | 20.76
| 488 | 2008-05-21 | 70000 | 65.9 | -2.6 | 0.49 | 50 | -276.2 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.7 | 0.01 | 0.1 | 0.008 | 0 | 20.84
| 489 | 2008-05-21 | 80000 | 66 | -2.8 | 0.48 | 63.7 | -354.7 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.07 | -0.8 | 0.01 | 0.2 | 0.01 | 0 | 20.85
| 490 | 2008-05-21 | 90000 | 66.1 | -2.7 | 0.49 | 76.5 | -412.1 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | 2.19 | -1.1 | 0.01 | 0.8 | 0.015 | 0 | 20.86
| 491 | 2008-05-21 | 100000 | 65.9 | -2.5 | 0.49 | 73.8 | -402.1 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.06 | -1.1 | 0.01 | 1.5 | 0.014 | 0 | 20.78
| 492 | 2008-05-21 | 110000 | 65.8 | -2.5 | 0.49 | 80.3 | -415 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -1.1 | 0.02 | 2.3 | 0.018 | 0 | 20.86
| 493 | 2008-05-21 | 120000 | 65.9 | -2.6 | 0.49 | 89.9 | -472.1 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -1.3 | 0.01 | 1.1 | 0.015 | 0 | 20.86
| 494 | 2008-05-21 | 130000 | 65.7 | -2.6 | 0.49 | 86.4 | -464.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -1.1 | 0.01 | 0.3 | 0.013 | 0 | 20.86
| 495 | 2008-05-21 | 140000 | 65.7 | -2.5 | 0.49 | 74.7 | -363.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.07 | -1.1 | 0.01 | -0.6 | 0.011 | 0 | 20.86
| 496 | 2008-05-21 | 150000 | 65.8 | -2.6 | 0.49 | 69.2 | -346.2 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -1 | 0.01 | 0.5 | 0.011 | 0 | 20.85
| 497 | 2008-05-21 | 160000 | 65.9 | -2.6 | 0.51 | 67.5 | -358.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.8 | 0.01 | 0 | 0.01 | 0 | 20.85
| 498 | 2008-05-21 | 170000 | 65.7 | -2.6 | 0.5 | 68.3 | -344.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.9 | 0 | -0.4 | 0.01 | 0 | 20.85
| 499 | 2008-05-21 | 180000 | 65.8 | -2.6 | 0.48 | 60.1 | -329.9 | 0.03 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.9 | 0 | 0 | 0.011 | 0 | 20.85
| 500 | 2008-05-21 | 190000 | 65.4 | -2.4 | 0.49 | 58.1 | -288.6 | 0.04 | 0.5 | 1.3 | 171.1 | 0.4 | -0.01 | -0.08 | -0.9 | 0.01 | 0.5 | 0.01 | 0 | 20.85
| 501 | 2008-05-21 | 200000 | 63.9 | -2.6 | 0.49 | 57.7 | -310.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.09 | -0.8 | 0 | 0 | 0.009 | 0 | 20.85
| 502 | 2008-05-21 | 210000 | 63.7 | -2.2 | 0.48 | 60.8 | -271 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.09 | -1 | 0 | -0.9 | 0.008 | 0 | 20.85
| 503 | 2008-05-21 | 220000 | 63.7 | -2.8 | 0.48 | 51.7 | -292.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.09 | -0.7 | 0.01 | 0.4 | 0.009 | 0 | 20.84
| 504 | 2008-05-21 | 230000 | 63.8 | -2.3 | 0.48 | 49.4 | -237.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.09 | -0.6 | 0.01 | 0.5 | 0.009 | 0 | 20.84
| 505 | 2008-05-22 | 0 | 63.8 | -2.4 | 0.48 | 47.3 | -233.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.09 | -0.6 | 0.01 | 1.1 | 0.011 | 0 | 20.84
| 506 | 2008-05-22 | 10000 | 63.9 | -2.7 | 0.48 | 42.7 | -239.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -0.6 | 0 | -0.3 | 0.007 | 0 | 20.83
| 507 | 2008-05-22 | 20000 | 62.6 | -2.4 | 0.48 | 40.1 | -197.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.09 | -0.6 | 0.01 | 0.8 | 0.007 | 0 | 20.75
| 508 | 2008-05-22 | 30000 | 62.1 | -2.7 | 0.48 | 35.9 | -205.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.09 | -0.5 | 0.01 | 0.4 | 0.007 | 0 | 20.74
| 509 | 2008-05-22 | 40000 | 62.1 | -2.6 | 0.49 | 32.5 | -185.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.08 | -0.5 | 0 | -0.1 | 0.005 | 0 | 20.73
| 510 | 2008-05-22 | 50000 | 62.2 | -2.8 | 0.49 | 30 | -167 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.09 | -0.5 | 0.01 | 0.5 | 0.005 | 0 | 20.8
| 511 | 2008-05-22 | 60000 | 62.1 | -2.6 | 0.5 | 32.9 | -174.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.08 | -0.5 | 0.01 | 0.6 | 0.006 | 0 | 20.81
| 512 | 2008-05-22 | 70000 | 62.1 | -2.6 | 0.51 | 35.4 | -190.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.08 | -0.5 | 0.01 | 0.7 | 0.007 | 0 | 20.81
| 513 | 2008-05-22 | 80000 | 62.2 | -2.3 | 0.51 | 34.3 | -155.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.07 | -0.5 | 0.01 | 0.3 | 0.006 | 0 | 20.81
| 514 | 2008-05-22 | 90000 | 62.1 | -2.5 | 0.51 | 29.9 | -149.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | 2.17 | -0.4 | 0.01 | 0.3 | 0.005 | 0 | 20.8
| 515 | 2008-05-22 | 100000 | 62.2 | -2.6 | 0.52 | 26.4 | -130.4 | 0.04 | 0.5 | 1.3 | 8.4 | 0.5 | -0.01 | -0.06 | -0.3 | 0.01 | 0.2 | 0.004 | 0 | 20.71
| 516 | 2008-05-22 | 110000 | 62.2 | -2.7 | 0.52 | 24.5 | -124.6 | 0.04 | 0.5 | 1.3 | -0.9 | 0.5 | -0.01 | -0.06 | -0.3 | 0.01 | 0.2 | 0.004 | 0 | 20.77
| 517 | 2008-05-22 | 120000 | 62.3 | -2.7 | 0.51 | 22.1 | -114.1 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.07 | -0.3 | 0.01 | 0.4 | 0.004 | 0 | 20.76
| 518 | 2008-05-22 | 130000 | 62.4 | -2.6 | 0.54 | 21.5 | -101.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.06 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.75
| 519 | 2008-05-22 | 140000 | 64.2 | -2.7 | 0.55 | 19.9 | -97.8 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.06 | -0.2 | 0 | 0 | 0.003 | 0 | 20.74
| 520 | 2008-05-22 | 150000 | 64.2 | -2.5 | 0.51 | 16.8 | -83.1 | 0.03 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.72
| 521 | 2008-05-22 | 160000 | 64.2 | -2.7 | 0.51 | 15.5 | -79.9 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.71
| 522 | 2008-05-22 | 170000 | 64.1 | -2.5 | 0.51 | 14.5 | -66.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -0.2 | 0.01 | 0.2 | 0.002 | 0 | 20.69
| 523 | 2008-05-22 | 180000 | 64.2 | -2.8 | 0.51 | 14.2 | -76.3 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.69
| 524 | 2008-05-22 | 190000 | 64 | -2.8 | 0.51 | 13.6 | -74.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0 | 0.1 | 0.002 | 0 | 20.68
| 525 | 2008-05-22 | 200000 | 64 | -2.6 | 0.51 | 13.1 | -65.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.002 | 0 | 20.67
| 526 | 2008-05-22 | 210000 | 64.1 | -2.4 | 0.52 | 12.9 | -60 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0 | 0.002 | 0 | 20.66
| 527 | 2008-05-22 | 220000 | 64.1 | -2.6 | 0.51 | 12.4 | -60.7 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.1 | 0 | 0.1 | 0.002 | 0 | 20.65
| 528 | 2008-05-22 | 230000 | 64.2 | -2.5 | 0.51 | 12.1 | -59.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.1 | 0.002 | 0 | 20.65
| 529 | 2008-05-23 | 0 | 64.2 | -2.7 | 0.51 | 11.9 | -58.4 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.64
| 530 | 2008-05-23 | 10000 | 64.1 | -2.5 | 0.51 | 11.3 | -58 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.63
| 531 | 2008-05-23 | 20000 | 64.1 | -2.7 | 0.51 | 10.9 | -58.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.62
| 532 | 2008-05-23 | 30000 | 64 | -2.7 | 0.51 | 10.7 | -58.5 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | -0.01 | -0.1 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.61
| 533 | 2008-05-23 | 40000 | 64.1 | -2.6 | 0.52 | 10.4 | -53 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.002 | 0 | 20.61
| 534 | 2008-05-23 | 50000 | 64.1 | -2.5 | 0.51 | 10.2 | -49 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.1 | 0 | 0.1 | 0.002 | 0 | 20.6
| 535 | 2008-05-23 | 60000 | 64.1 | -2.6 | 0.52 | 10.1 | -48.7 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.1 | 0 | 0 | 0.002 | 0 | 20.59
| 536 | 2008-05-23 | 70000 | 64.1 | -2.5 | 0.52 | 9.9 | -46.3 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.06 | -0.1 | 0.01 | 0 | 0.002 | 0 | 20.59
| 537 | 2008-05-23 | 80000 | 64 | -2.9 | 0.52 | 9.4 | -51.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.1 | 0.01 | 0.1 | 0.001 | 0 | 20.57
| 538 | 2008-05-23 | 90000 | 64 | -2.6 | 0.53 | 9.3 | -46.2 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | 2.18 | -0.1 | 0 | 0.1 | 0.001 | 0 | 20.56
| 539 | 2008-05-23 | 100000 | 64 | -2.7 | 0.53 | 9 | -44.9 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.1 | 0 | 0.1 | 0.001 | 0 | 20.56
| 540 | 2008-05-23 | 110000 | 65.2 | -2.7 | 0.53 | 9 | -44.1 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.1 | 0 | 0 | 0.001 | 0 | 20.55
| 541 | 2008-05-23 | 120000 | 66.1 | -2.5 | 0.54 | 8.8 | -40.2 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.001 | 0 | 20.54
| 542 | 2008-05-23 | 130000 | 66 | -2.6 | 0.55 | 8.7 | -43.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.05 | -0.1 | 0.02 | 0.2 | 0.002 | 0 | 20.53
| 543 | 2008-05-23 | 140000 | 65.9 | -2.6 | 0.55 | 8.7 | -42.5 | 0.03 | 0.5 | 1.3 | -1 | 0.4 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.001 | 0 | 20.52
| 544 | 2008-05-23 | 150000 | 65.8 | -2.5 | 0.56 | 8.9 | -39.1 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.1 | 0 | 0 | 0.001 | 0 | 20.53
| 545 | 2008-05-23 | 160000 | 66 | -2.6 | 0.57 | 8.9 | -40.3 | 0.03 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | 0 | 0 | 0.1 | 0.001 | 0 | 20.52
| 546 | 2008-05-23 | 170000 | 65.8 | -2.7 | 0.56 | 8.9 | -42.4 | 0.03 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.1 | 0 | 0.1 | 0.001 | 0 | 20.53
| 547 | 2008-05-23 | 180000 | 65.8 | -3.1 | 0.55 | 8.9 | -48.4 | 0.03 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.001 | 0 | 20.53
| 548 | 2008-05-23 | 190000 | 65.6 | -2.9 | 0.55 | 8.8 | -44.8 | 0.03 | 0.5 | 1.3 | -1.1 | 0.6 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.001 | 0 | 20.53
| 549 | 2008-05-23 | 200000 | 65.8 | -2 | 0.53 | 8.8 | -33.8 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.001 | 0 | 20.54
| 550 | 2008-05-23 | 210000 | 65.8 | -2.7 | 0.61 | 9.9 | -47.2 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | 0 | -0.06 | 0.1 | 0.01 | 0.1 | 0.001 | 0 | 20.54
| 551 | 2008-05-23 | 220000 | 65.8 | -2.5 | 0.66 | 10.8 | -41 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0.01 | -0.06 | 0.1 | 0.01 | 0.2 | 0.002 | 0.001 | 20.54
| 552 | 2008-05-23 | 230000 | 66 | -2.6 | 0.67 | 11.2 | -44 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | 0.01 | -0.06 | 0.1 | 0.01 | 0.1 | 0.001 | 0.001 | 20.54
| 553 | 2008-05-24 | 0 | 67.6 | -2.5 | 0.63 | 10.6 | -43.9 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | 0 | -0.07 | 0 | 0 | 0.1 | 0.001 | 0 | 20.55
| 554 | 2008-05-24 | 10000 | 67.9 | -2.5 | 0.66 | 11 | -43.2 | 0.04 | 0.5 | 1.2 | -1 | 0.5 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.002 | 0 | 20.55
| 555 | 2008-05-24 | 20000 | 68 | -2.8 | 0.62 | 10.4 | -45.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0.002 | 0 | 20.55
| 556 | 2008-05-24 | 30000 | 67.9 | -2.4 | 0.6 | 10.1 | -39.8 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.001 | 0 | 20.55
| 557 | 2008-05-24 | 40000 | 67.9 | -2.4 | 0.62 | 10.2 | -39.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | 0 | 0 | 0 | 0.001 | 0 | 20.54
| 558 | 2008-05-24 | 50000 | 67.9 | -3 | 0.66 | 11 | -49.3 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | 0 | 0.01 | 0 | 0.001 | 0 | 20.55
| 559 | 2008-05-24 | 60000 | 67.9 | -2.9 | 0.66 | 11.5 | -48.1 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.002 | 0 | 20.56
| 560 | 2008-05-24 | 70000 | 67.9 | -2.7 | 0.62 | 11.1 | -48.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0.001 | 0 | 20.57
| 561 | 2008-05-24 | 80000 | 67.9 | -2.7 | 0.62 | 11.4 | -48.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0.002 | 0 | 20.58
| 562 | 2008-05-24 | 90000 | 67.9 | -2.7 | 0.63 | 11.7 | -49.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | 2.2 | 0 | 0.01 | 0.2 | 0.002 | 0 | 20.58
| 563 | 2008-05-24 | 100000 | 67.8 | -2.9 | 0.64 | 12.1 | -55.2 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | 0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.59
| 564 | 2008-05-24 | 110000 | 67.9 | -2.7 | 0.65 | 12.4 | -51.7 | 0.04 | 0.5 | 1.3 | 56.7 | 0.5 | 0.01 | -0.06 | 0.2 | 0.02 | 0.4 | 0.002 | 0.001 | 20.59
| 565 | 2008-05-24 | 120000 | 68.8 | -2.8 | 0.63 | 12 | -50.7 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0.01 | -0.06 | 0.2 | 0.02 | 0.3 | 0.002 | 0.001 | 20.59
| 566 | 2008-05-24 | 130000 | 69.4 | -2.3 | 0.56 | 10.6 | -43.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.59
| 567 | 2008-05-24 | 140000 | 69.4 | -3 | 0.56 | 10.6 | -57.1 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.59
| 568 | 2008-05-24 | 150000 | 69.5 | -2.7 | 0.58 | 11.1 | -50.4 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0.002 | 0 | 20.59
| 569 | 2008-05-24 | 160000 | 70.7 | -2.5 | 0.58 | 11 | -46 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0.002 | 0 | 20.59
| 570 | 2008-05-24 | 170000 | 71.4 | -2.6 | 0.56 | 10.8 | -51.3 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | 0 | -0.06 | 0 | 0.02 | 0.3 | 0.002 | 0 | 20.59
| 571 | 2008-05-24 | 180000 | 71.3 | -2.5 | 0.56 | 11.6 | -50.8 | 0.04 | 0.5 | 1.3 | -1 | 0.3 | 0 | -0.08 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.61
| 572 | 2008-05-24 | 190000 | 71.4 | -2.8 | 0.55 | 12.2 | -58.1 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.09 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.64
| 573 | 2008-05-24 | 200000 | 71.4 | -2.8 | 0.55 | 13.6 | -65.8 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.08 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.66
| 574 | 2008-05-24 | 210000 | 71.5 | -2.6 | 0.54 | 15.5 | -74 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.08 | -0.1 | 0.01 | 0.1 | 0.003 | 0 | 20.69
| 575 | 2008-05-24 | 220000 | 71.5 | -2.4 | 0.54 | 17.5 | -76.6 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.1 | 0.02 | 0.5 | 0.004 | 0 | 20.72
| 576 | 2008-05-24 | 230000 | 71.4 | -2.3 | 0.54 | 18.2 | -84.3 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.08 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.72
| 577 | 2008-05-25 | 0 | 71.4 | -2.6 | 0.54 | 19.7 | -90.8 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.09 | -0.2 | 0 | 0 | 0.003 | 0 | 20.74
| 578 | 2008-05-25 | 10000 | 71.4 | -2.9 | 0.54 | 20.8 | -104.2 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.08 | -0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.75
| 579 | 2008-05-25 | 20000 | 71.4 | -2.6 | 0.53 | 20.9 | -104.7 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.09 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.75
| 580 | 2008-05-25 | 30000 | 71.3 | -2.6 | 0.53 | 21.6 | -107.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.1 | 0.004 | 0 | 20.75
| 581 | 2008-05-25 | 40000 | 71.5 | -2.6 | 0.53 | 21.6 | -108.9 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | -0.01 | -0.09 | -0.3 | 0.01 | 0.6 | 0.004 | 0 | 20.68
| 582 | 2008-05-25 | 50000 | 71.5 | -2.5 | 0.53 | 23.1 | -107.3 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.5 | 0.005 | 0 | 20.69
| 583 | 2008-05-25 | 60000 | 71.3 | -2.5 | 0.53 | 24.5 | -120 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.08 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.77
| 584 | 2008-05-25 | 70000 | 71.4 | -2.7 | 0.53 | 25.3 | -134.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.004 | 0 | 20.77
| 585 | 2008-05-25 | 80000 | 71.4 | -2.7 | 0.53 | 26.7 | -129.3 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.3 | 0.01 | 0.2 | 0.004 | 0 | 20.78
| 586 | 2008-05-25 | 90000 | 71.4 | -2.6 | 0.53 | 26.9 | -131 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | 2.2 | -0.2 | 0.01 | 0.5 | 0.005 | 0 | 20.78
| 587 | 2008-05-25 | 100000 | 71.4 | -2.9 | 0.54 | 26.1 | -136.1 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.2 | 0.01 | 0.5 | 0.005 | 0 | 20.78
| 588 | 2008-05-25 | 110000 | 71.4 | -2.3 | 0.54 | 25.1 | -116.6 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.09 | -0.2 | 0.01 | 0 | 0.004 | 0 | 20.7
| 589 | 2008-05-25 | 120000 | 71.3 | -2.7 | 0.54 | 23.1 | -113 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0 | 0 | 0.003 | 0 | 20.76
| 590 | 2008-05-25 | 130000 | 71.4 | -2.5 | 0.53 | 21.4 | -101.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.004 | 0 | 20.75
| 591 | 2008-05-25 | 140000 | 71.4 | -2.5 | 0.53 | 20.2 | -94.8 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | 0 | -0.09 | -0.2 | 0 | 0.1 | 0.003 | 0 | 20.74
| 592 | 2008-05-25 | 150000 | 71.3 | -2.5 | 0.53 | 19 | -90.9 | 0.04 | 0.5 | 1.3 | -1.1 | 0.5 | 0 | -0.09 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.73
| 593 | 2008-05-25 | 160000 | 71.3 | -2.5 | 0.53 | 18.1 | -86 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.09 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.73
| 594 | 2008-05-25 | 170000 | 71.4 | -2.3 | 0.53 | 16.8 | -73.1 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | 0 | -0.09 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.71
| 595 | 2008-05-25 | 180000 | 71.4 | -2.5 | 0.54 | 16.1 | -73.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.08 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.7
| 596 | 2008-05-25 | 190000 | 71.5 | -2.6 | 0.53 | 16 | -80.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.07 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.7
| 597 | 2008-05-25 | 200000 | 71.4 | -2.6 | 0.54 | 15.8 | -75.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.7
| 598 | 2008-05-25 | 210000 | 71.3 | -2.6 | 0.54 | 15.9 | -81.2 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.07 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.7
| 599 | 2008-05-25 | 220000 | 71.4 | -3 | 0.53 | 15.5 | -88.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.7
| 600 | 2008-05-25 | 230000 | 71.5 | -2.8 | 0.52 | 15.3 | -79.7 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.07 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.7
| 601 | 2008-05-26 | 0 | 71.4 | -2.9 | 0.52 | 15 | -78.4 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.7
| 602 | 2008-05-26 | 10000 | 71.4 | -2.9 | 0.52 | 14.5 | -79.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.1 | -0.2 | 0.01 | 0.4 | 0.003 | 0 | 20.69
| 603 | 2008-05-26 | 20000 | 71.4 | -2.7 | 0.52 | 14.2 | -73.3 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.61
| 604 | 2008-05-26 | 30000 | 71.3 | -2.5 | 0.52 | 14.1 | -67.8 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.1 | 0.002 | 0 | 20.68
| 605 | 2008-05-26 | 40000 | 71.4 | -2.6 | 0.52 | 13.6 | -68.8 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.002 | 0 | 20.67
| 606 | 2008-05-26 | 50000 | 70.7 | -3 | 0.52 | 13.4 | -75.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.08 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.67
| 607 | 2008-05-26 | 60000 | 69.4 | -2.8 | 0.52 | 13.5 | -70.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.002 | 0 | 20.67
| 608 | 2008-05-26 | 70000 | 69.5 | -2.7 | 0.52 | 13.6 | -69.4 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.67
| 609 | 2008-05-26 | 80000 | 69.5 | -2.8 | 0.53 | 14 | -75.3 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.68
| 610 | 2008-05-26 | 90000 | 69.4 | -2.4 | 0.52 | 14.1 | -67.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | 2.21 | -0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.68
| 611 | 2008-05-26 | 100000 | 69.4 | -2.5 | 0.53 | 14.5 | -69.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0.002 | 0 | 20.68
| 612 | 2008-05-26 | 110000 | 69.5 | -2.3 | 0.52 | 14.8 | -64.9 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.07 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.69
| 613 | 2008-05-26 | 120000 | 69.5 | -2.8 | 0.53 | 14.7 | -79.2 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.1 | 0 | -0.1 | 0.002 | 0 | 20.61
| 614 | 2008-05-26 | 130000 | 70.8 | -2.6 | 0.53 | 14.6 | -70.8 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.09 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.68
| 615 | 2008-05-26 | 140000 | 71.4 | -2.6 | 0.54 | 15.5 | -73.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.08 | -0.1 | 0.02 | 0.4 | 0.003 | 0 | 20.69
| 616 | 2008-05-26 | 150000 | 71.4 | -2.6 | 0.55 | 16.1 | -75 | 0.04 | 0.5 | 1.3 | -1 | 0.4 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.7
| 617 | 2008-05-26 | 160000 | 71.4 | -2.5 | 0.55 | 16 | -71.8 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.09 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.7
| 618 | 2008-05-26 | 170000 | 71.4 | -2.7 | 0.55 | 16.3 | -81 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.09 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.63
| 619 | 2008-05-26 | 180000 | 71.5 | -2.6 | 0.55 | 17 | -79.1 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.08 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.71
| 620 | 2008-05-26 | 190000 | 71.4 | -2.4 | 0.55 | 17.9 | -78.8 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.07 | -0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.72
| 621 | 2008-05-26 | 200000 | 71.5 | -2.3 | 0.55 | 18.5 | -74.6 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.73
| 622 | 2008-05-26 | 210000 | 71.4 | -2.6 | 0.54 | 19.4 | -91.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.5 | 0.004 | 0 | 20.73
| 623 | 2008-05-26 | 220000 | 71.4 | -2.6 | 0.54 | 20.9 | -101.7 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.67
| 624 | 2008-05-26 | 230000 | 71.4 | -2.8 | 0.54 | 21.8 | -113.9 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.004 | 0 | 20.75
| 625 | 2008-05-27 | 0 | 71.4 | -2.7 | 0.54 | 21.7 | -102.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.004 | 0 | 20.75
| 626 | 2008-05-27 | 10000 | 71.3 | -2.8 | 0.54 | 22 | -115.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.08 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.75
| 627 | 2008-05-27 | 20000 | 71.4 | -2.4 | 0.53 | 21.7 | -102.4 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.08 | -0.2 | 0.01 | 0.5 | 0.004 | 0 | 20.68
| 628 | 2008-05-27 | 30000 | 71.5 | -2.7 | 0.53 | 22.2 | -109.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.08 | -0.2 | 0.01 | 0.3 | 0.004 | 0 | 20.76
| 629 | 2008-05-27 | 40000 | 71.5 | -2.6 | 0.53 | 22.7 | -121.2 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -0.2 | 0.02 | 0.5 | 0.004 | 0 | 20.76
| 630 | 2008-05-27 | 50000 | 71.5 | -2.5 | 0.53 | 23.6 | -112 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.08 | -0.2 | 0.01 | 0.3 | 0.004 | 0 | 20.76
| 631 | 2008-05-27 | 60000 | 71.4 | -2.5 | 0.54 | 24.7 | -113.9 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.2 | 0.01 | 0.5 | 0.005 | 0 | 20.77
| 632 | 2008-05-27 | 70000 | 71.4 | -2.5 | 0.55 | 25.5 | -112.2 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | -0.06 | -0.2 | 0.01 | 0.5 | 0.004 | 0 | 20.77
| 633 | 2008-05-27 | 80000 | 71.4 | -2.7 | 0.56 | 26.8 | -131.6 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | 0 | -0.06 | -0.2 | 0.01 | 0.3 | 0.005 | 0 | 20.78
| 634 | 2008-05-27 | 90000 | 71.4 | -2.4 | 0.57 | 27.6 | -119 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | 0 | 2.22 | -0.2 | 0.01 | 0.2 | 0.004 | 0 | 20.78
| 635 | 2008-05-27 | 100000 | 71.4 | -2.5 | 0.57 | 27.4 | -123.1 | 0.04 | 0.5 | 1.3 | 192.7 | 0.5 | 0 | -0.06 | -0.1 | 0.01 | 0.5 | 0.005 | 0 | 20.78
| 636 | 2008-05-27 | 110000 | 71.3 | -2.5 | 0.57 | 26.9 | -108.9 | 0.04 | 0.5 | 1.3 | 461.9 | 0.2 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.77
| 637 | 2008-05-27 | 120000 | 71.4 | -2.4 | 0.56 | 24.8 | -110.3 | 0.04 | 0.5 | 1.3 | 322.6 | 0.4 | 0 | -0.06 | -0.2 | 0.01 | 0.3 | 0.004 | 0 | 20.76
| 638 | 2008-05-27 | 130000 | 71.4 | -2.6 | 0.56 | 23 | -107.5 | 0.04 | 0.5 | 1.3 | 254.1 | 0.5 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0.004 | 0 | 20.76
| 639 | 2008-05-27 | 140000 | 71.4 | -2.7 | 0.55 | 21.7 | -107 | 0.04 | 0.5 | 1.3 | 31.9 | 0.5 | 0 | -0.07 | -0.2 | 0.01 | 0.4 | 0.004 | 0 | 20.67
| 640 | 2008-05-27 | 150000 | 71.4 | -2.8 | 0.55 | 19.2 | -94.2 | 0.04 | 0.5 | 1.3 | 21.7 | 0.5 | 0 | -0.07 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.65
| 641 | 2008-05-27 | 160000 | 72.3 | -2.6 | 0.55 | 16.8 | -81.7 | 0.04 | 0.5 | 1.3 | 217.7 | 0.3 | 0 | -0.07 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.71
| 642 | 2008-05-27 | 170000 | 72.7 | -2.8 | 0.54 | 15.6 | -80.8 | 0.04 | 0.5 | 1.3 | 455.8 | 0 | 0 | -0.09 | -0.1 | 0 | 0.1 | 0.002 | 0 | 20.69
| 643 | 2008-05-27 | 180000 | 72.8 | -2.7 | 0.54 | 15 | -76.9 | 0.04 | 0.5 | 1.3 | 308.3 | 0.3 | 0 | -0.09 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.69
| 644 | 2008-05-27 | 190000 | 72.7 | -2.7 | 0.54 | 15.2 | -79.7 | 0.04 | 0.5 | 1.3 | 439.5 | 0.1 | 0 | -0.09 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.69
| 645 | 2008-05-27 | 200000 | 72.7 | -2.4 | 0.54 | 15.4 | -67.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | 0 | -0.08 | -0.1 | 0.01 | 0.2 | 0.002 | 0 | 20.69
| 646 | 2008-05-27 | 210000 | 72.7 | -2.4 | 0.53 | 15.8 | -68.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | 0 | -0.08 | -0.1 | 0.01 | 0.2 | 0.003 | 0 | 20.7
| 647 | 2008-05-27 | 220000 | 72.8 | -2.6 | 0.53 | 16.1 | -76.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | 0 | -0.09 | -0.1 | 0 | 0.1 | 0.002 | 0 | 20.71
| 648 | 2008-05-27 | 230000 | 72.8 | -2.7 | 0.53 | 16.1 | -80.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.09 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.71
| 649 | 2008-05-28 | 0 | 72.8 | -2.6 | 0.53 | 16 | -80.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.7
| 650 | 2008-05-28 | 10000 | 72.7 | -2.4 | 0.53 | 16 | -73.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.09 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.7
| 651 | 2008-05-28 | 20000 | 72.8 | -2.6 | 0.53 | 16.1 | -78.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.09 | -0.2 | 0.02 | 0.4 | 0.003 | 0 | 20.7
| 652 | 2008-05-28 | 30000 | 72.8 | -2.5 | 0.53 | 15.9 | -79.8 | 0.04 | 0.5 | 1.3 | 461.9 | 0.2 | -0.01 | -0.09 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.7
| 653 | 2008-05-28 | 40000 | 72.3 | -2.4 | 0.53 | 15.2 | -68.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.08 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.62
| 654 | 2008-05-28 | 50000 | 71.4 | -2.6 | 0.53 | 15.5 | -76.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -0.2 | 0.01 | 0.1 | 0.003 | 0 | 20.7
| 655 | 2008-05-28 | 60000 | 71.4 | -2.6 | 0.53 | 15.9 | -76.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.08 | -0.2 | 0.01 | 0.2 | 0.003 | 0 | 20.7
| 656 | 2008-05-28 | 70000 | 71.4 | -2.6 | 0.53 | 16.1 | -79.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -0.2 | 0 | 0.1 | 0.003 | 0 | 20.7
| 657 | 2008-05-28 | 80000 | 71.4 | -2.8 | 0.53 | 16.5 | -80.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.71
| 658 | 2008-05-28 | 90000 | 71.3 | -2.4 | 0.54 | 17.5 | -79.7 | 0.04 | 0.5 | 1.2 | 463.2 | 0.3 | -0.01 | 2.22 | -0.1 | 0.01 | 0.3 | 0.003 | 0 | 20.72
| 659 | 2008-05-28 | 100000 | 71.4 | -2.7 | 0.54 | 17.6 | -88.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | 0 | -0.06 | -0.1 | 0 | 0.1 | 0.003 | 0 | 20.72
| 660 | 2008-05-28 | 110000 | 71.4 | -2.7 | 0.54 | 18.7 | -89.5 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | 0 | -0.06 | -0.2 | 0.01 | 0.3 | 0.003 | 0 | 20.73
| 661 | 2008-05-28 | 120000 | 71.3 | -2.4 | 0.53 | 19.3 | -84.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.3 | 0.01 | 0.2 | 0.003 | 0 | 20.74
| 662 | 2008-05-28 | 130000 | 71.4 | -2.5 | 0.54 | 19.7 | -91.3 | 0.04 | 98.6 | 99.7 | 462.9 | 0.2 | -0.01 | -0.07 | -0.3 | 0.01 | 0.1 | 0.003 | 0 | 20.66
| 663 | 2008-05-28 | 140000 | 71.4 | -2.7 | 0.54 | 20.2 | -100.4 | 0.04 | 210.3 | 210.7 | 453 | 0.2 | -0.01 | -0.06 | -0.3 | 0.01 | 0.2 | 0.003 | 0 | 20.74
| 664 | 2008-05-28 | 150000 | 71.4 | -2.5 | 0.54 | 21 | -95.5 | 0.04 | 0.5 | 1.3 | 454 | 0.2 | -0.01 | -0.07 | -0.3 | 0.01 | 0.3 | 0.004 | 0 | 20.75
| 665 | 2008-05-28 | 160000 | 71 | -2.7 | 0.54 | 21.3 | -105.6 | 0.04 | 0.5 | 1.3 | 463.1 | 0.1 | -0.01 | -0.08 | -0.3 | 0 | 0.1 | 0.003 | 0 | 20.75
| 666 | 2008-05-28 | 170000 | 69.6 | -2.5 | 0.54 | 22.9 | -108.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.08 | -0.3 | 0 | 0.1 | 0.004 | 0 | 20.76
| 667 | 2008-05-28 | 180000 | 69.4 | -2.5 | 0.54 | 24.6 | -117.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.09 | -0.3 | 0.01 | 0.2 | 0.004 | 0 | 20.77
| 668 | 2008-05-28 | 190000 | 69.3 | -2.7 | 0.54 | 26.6 | -134.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.09 | -0.3 | 0.01 | 0.2 | 0.004 | 0 | 20.78
| 669 | 2008-05-28 | 200000 | 69.4 | -2.5 | 0.54 | 29 | -136.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.09 | -0.4 | 0.01 | 0.6 | 0.005 | 0 | 20.79
| 670 | 2008-05-28 | 210000 | 69.4 | -2.7 | 0.54 | 32.6 | -163.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.09 | -0.4 | 0.01 | 0.2 | 0.005 | 0 | 20.8
| 671 | 2008-05-28 | 220000 | 69.4 | -2.7 | 0.54 | 33.5 | -169.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.09 | -0.4 | 0.01 | 0.7 | 0.006 | 0 | 20.8
| 672 | 2008-05-28 | 230000 | 69.5 | -2.6 | 0.54 | 36.1 | -172.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -0.5 | 0.01 | 0.6 | 0.007 | 0 | 20.81
| 673 | 2008-05-29 | 0 | 69.4 | -2.8 | 0.54 | 39.5 | -207.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.09 | -0.5 | 0.01 | 0.1 | 0.006 | 0 | 20.82
| 674 | 2008-05-29 | 10000 | 69.5 | -2.5 | 0.54 | 39.5 | -182.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.09 | -0.5 | 0.01 | 0.4 | 0.006 | 0 | 20.82
| 675 | 2008-05-29 | 20000 | 69.3 | -2.3 | 0.54 | 39.2 | -170.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.09 | -0.5 | 0 | 0.1 | 0.006 | 0 | 20.82
| 676 | 2008-05-29 | 30000 | 67.9 | -2.7 | 0.54 | 39.7 | -200.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.09 | -0.5 | 0.01 | 0.2 | 0.006 | 0 | 20.82
| 677 | 2008-05-29 | 40000 | 67.8 | -2.5 | 0.55 | 41.7 | -182.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.09 | -0.5 | 0.01 | 0.5 | 0.008 | 0 | 20.82
| 678 | 2008-05-29 | 50000 | 67.9 | -2.5 | 0.55 | 43.1 | -202.6 | 0.04 | 0.5 | 1.3 | 462 | 0.2 | -0.01 | -0.06 | -0.6 | 0 | 0 | 0.006 | 0 | 20.82
| 679 | 2008-05-29 | 60000 | 68 | -2.7 | 0.56 | 48.4 | -231.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.6 | 0.01 | 0.2 | 0.007 | 0 | 20.75
| 680 | 2008-05-29 | 70000 | 67.8 | -2.7 | 0.56 | 58.8 | -260.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.7 | 0.01 | 0.4 | 0.009 | 0 | 20.84
| 681 | 2008-05-29 | 80000 | 67.9 | -2.8 | 0.56 | 70.4 | -339.6 | 0.04 | 20.8 | 21.6 | 463.2 | 0.2 | -0.01 | -0.06 | -0.9 | 0.01 | -0.1 | 0.01 | 0 | 20.85
| 682 | 2008-05-29 | 90000 | 67.9 | -2.3 | 0.55 | 84.4 | -352.9 | 0.04 | 0.5 | 18.6 | 463.2 | 0.3 | -0.01 | 2.21 | -1 | 0.01 | 0.3 | 0.013 | 0 | 20.78
| 683 | 2008-05-29 | 100000 | 67.9 | -2.7 | 0.56 | 93.3 | -439.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -1.2 | 0.01 | -0.2 | 0.013 | 0 | 20.86
| 684 | 2008-05-29 | 110000 | 67.1 | -2.7 | 0.56 | 97.7 | -455.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -1.3 | 0.01 | 0.1 | 0.015 | 0 | 20.86
| 685 | 2008-05-29 | 120000 | 67.7 | -2.6 | 0.56 | 100.8 | -454.2 | 0.04 | 0.5 | 1.3 | 461.1 | 0.3 | -0.01 | -0.06 | -1.3 | 0.01 | 0.6 | 15.844 | 0 | 20.86
| 686 | 2008-05-29 | 130000 | 67.9 | -2.8 | 0.56 | 94.2 | -474.5 | 0.04 | 0.5 | 1.3 | 368.9 | 0.4 | -0.01 | -0.06 | -1.1 | 0.01 | -1.2 | 0.013 | 1.583 | 20.86
| 687 | 2008-05-29 | 140000 | 67.9 | -2.8 | 0.56 | 91.5 | -438.2 | 0.04 | 0.5 | 1.3 | 42.8 | 0.5 | -0.01 | -0.06 | -1.1 | 0.01 | 0.4 | 0.015 | 1.583 | 20.86
| 688 | 2008-05-29 | 150000 | 67.9 | -2.8 | 0.56 | 87.6 | -450.8 | 0.04 | 0.5 | 1.3 | 49.2 | 0.6 | -0.01 | -0.07 | -1.2 | 0.01 | 0.1 | 0.013 | 0 | 20.86
| 689 | 2008-05-29 | 160000 | 67.8 | -2.6 | 0.56 | 80.4 | -370.6 | 0.04 | 0.5 | 1.3 | 31.2 | 0.5 | -0.01 | -0.08 | -0.8 | 0.01 | -0.8 | 0.01 | 0 | 20.85
| 690 | 2008-05-29 | 170000 | 67.9 | -2.3 | 0.56 | 78.4 | -315.7 | 0.04 | 0.5 | 1.3 | 119.8 | 0.4 | -0.01 | -0.07 | -1 | 0.01 | 0.1 | 0.012 | 0 | 20.85
| 691 | 2008-05-29 | 180000 | 67.9 | -2.5 | 0.57 | 88.5 | -391.5 | 0.04 | 0.5 | 1.3 | 319.7 | 0.2 | -0.01 | -0.08 | -0.9 | 0.01 | -0.6 | 0.012 | 0 | 20.86
| 692 | 2008-05-29 | 190000 | 68 | -2.8 | 0.56 | 91.5 | -437.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | 0 | -0.06 | -0.8 | 0 | -0.5 | 0.011 | 0 | 20.86
| 693 | 2008-05-29 | 200000 | 67.8 | -2.7 | 0.56 | 87.6 | -411.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | 0 | -0.06 | -0.7 | 0.01 | 0.2 | 19.006 | 0 | 20.86
| 694 | 2008-05-29 | 210000 | 67.9 | -2.7 | 0.56 | 97.9 | -465.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -1 | 0.01 | -0.1 | 0.014 | 0 | 20.86
| 695 | 2008-05-29 | 220000 | 68 | -2.7 | 0.56 | 153.7 | -780.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.07 | -2 | 0.01 | 0.3 | 49.086 | 1.583 | 20.88
| 696 | 2008-05-29 | 230000 | 67.9 | -2.6 | 0.55 | 142.5 | -693.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -1.8 | 0.01 | 0.4 | 49.086 | 0 | 20.88
| 697 | 2008-05-30 | 0 | 68 | -2.7 | 0.55 | 144.2 | -701 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -1.7 | 0.01 | 2.5 | 69.667 | 0 | 20.88
| 698 | 2008-05-30 | 10000 | 67.9 | -2.6 | 0.55 | 146.9 | -712.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.08 | -2 | 0.01 | 0.3 | 55.416 | 0 | 20.88
| 699 | 2008-05-30 | 20000 | 66.4 | -2.5 | 0.54 | 134.8 | -665.6 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.09 | -1.9 | 0 | 0.2 | 50.669 | 0 | 20.8
| 700 | 2008-05-30 | 30000 | 65.7 | -2.8 | 0.55 | 140 | -668.8 | 0.04 | 0.5 | 1.2 | 463.2 | 0.1 | -0.01 | -0.07 | -1.8 | 0 | 0.9 | 82.323 | 0 | 20.88
| 701 | 2008-05-30 | 40000 | 65.7 | -2.8 | 0.55 | 121.1 | -534.7 | 0.04 | 0.5 | 1.2 | 463.2 | 0.1 | -0.01 | -0.06 | -1.4 | 0.01 | -0.3 | 55.414 | 0 | 20.87
| 702 | 2008-05-30 | 50000 | 65.8 | -2.4 | 0.55 | 124.1 | -540.6 | 0.04 | 0.5 | 1.2 | 463.2 | 0.1 | -0.01 | -0.06 | -1.8 | 0.01 | 0 | 17.427 | 0 | 20.87
| 703 | 2008-05-30 | 60000 | 66 | -2.8 | 0.56 | 128.5 | -635.6 | 0.04 | 0.5 | 1.2 | 463.2 | 0.1 | -0.01 | -0.06 | -2 | 0.01 | 1 | 49.084 | 1.583 | 20.87
| 704 | 2008-05-30 | 70000 | 65.9 | -2.1 | 0.55 | 146.8 | -594 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -1.8 | 0 | -0.4 | 56.999 | 4.748 | 20.88
| 705 | 2008-05-30 | 80000 | 66 | -3 | 0.56 | 144.5 | -811.5 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -1.7 | 0 | -0.6 | 30.09 | 0 | 20.88
| 706 | 2008-05-30 | 90000 | 66 | -2.8 | 0.67 | 160.8 | -652.7 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | 2.23 | -1.4 | 0 | 0.2 | 212.104 | 6.331 | 20.88
| 707 | 2008-05-30 | 100000 | 65.9 | -2.4 | 0.59 | 138.3 | -569.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | 0 | -0.06 | -1 | 0.01 | 0 | 50.666 | 0 | 20.88
| 708 | 2008-05-30 | 110000 | 67 | -2.5 | 0.57 | 149.5 | -632.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -1.7 | 0.01 | -0.5 | 7.932 | 0 | 20.87
| 709 | 2008-05-30 | 120000 | 67.9 | -2.6 | 0.57 | 124.3 | -580.4 | 0.04 | 0.5 | 1.3 | 180.6 | 0.5 | -0.01 | -0.06 | -1.6 | 0 | -0.7 | 0.016 | 0 | 20.87
| 710 | 2008-05-30 | 130000 | 68 | -2.6 | 0.56 | 103.7 | -473 | 0.04 | 0.5 | 1.3 | 162.2 | 0.4 | -0.01 | -0.06 | -1.4 | 0.01 | 1 | 30.089 | 0 | 20.87
| 711 | 2008-05-30 | 140000 | 67.9 | -2.8 | 0.55 | 84.2 | -418.2 | 0.04 | 0.5 | 1.3 | 102.6 | 0.4 | -0.01 | -0.06 | -1.1 | 0.01 | -0.4 | 0.01 | 0 | 20.86
| 712 | 2008-05-30 | 150000 | 67.9 | -2.5 | 0.55 | 62.3 | -275.1 | 0.04 | 0.5 | 1.3 | 36.8 | 0.5 | -0.01 | -0.06 | -0.9 | 0.01 | 0.3 | 0.009 | 0 | 20.84
| 713 | 2008-05-30 | 160000 | 68 | -2.9 | 0.55 | 50.5 | -263.1 | 0.04 | 0.5 | 1.3 | 62.5 | 0.4 | -0.01 | -0.06 | -0.6 | 0.01 | 0.2 | 0.007 | 0 | 20.83
| 714 | 2008-05-30 | 170000 | 68.8 | -2.7 | 0.55 | 42.4 | -202.6 | 0.04 | 0.5 | 1.3 | 128.4 | 0.4 | -0.01 | -0.05 | -0.6 | 0.01 | 0.2 | 0.007 | 0 | 20.82
| 715 | 2008-05-30 | 180000 | 69.5 | -2.8 | 0.56 | 38.1 | -180 | 0.04 | 0.5 | 1.3 | 303.2 | 0.1 | -0.01 | -0.06 | -0.5 | 0.01 | 0.1 | 0.006 | 0 | 20.81
| 716 | 2008-05-30 | 190000 | 69.4 | -2.6 | 0.56 | 38.1 | -187.1 | 0.04 | 0.5 | 1.3 | 461.8 | 0.2 | -0.01 | -0.06 | -0.5 | 0.01 | 0.2 | 0.006 | 0 | 20.81
| 717 | 2008-05-30 | 200000 | 69.3 | -2.6 | 0.56 | 42.6 | -195.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.06 | -0.5 | 0 | 0 | 0.006 | 0 | 20.82
| 718 | 2008-05-30 | 210000 | 69.4 | -2.9 | 0.56 | 54.4 | -291.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.7 | 0.01 | 0.4 | 0.009 | 0 | 20.84
| 719 | 2008-05-30 | 220000 | 69.4 | -2.6 | 0.57 | 70 | -296.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.9 | 0.01 | 0.9 | 0.011 | 0 | 20.85
| 720 | 2008-05-30 | 230000 | 69.4 | -2.7 | 0.57 | 74.3 | -350.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.9 | 0.01 | 1 | 0.012 | 0 | 20.85
| 721 | 2008-05-31 | 0 | 69.4 | -2.4 | 0.57 | 73.8 | -314 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.07 | -1 | 0.01 | 0 | 0.01 | 0 | 20.85
| 722 | 2008-05-31 | 10000 | 69.4 | -2.7 | 0.57 | 70.3 | -328.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -0.9 | 0.01 | 0.4 | 0.01 | 0 | 20.85
| 723 | 2008-05-31 | 20000 | 69.4 | -2.6 | 0.57 | 69.4 | -289.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.8 | 0.01 | 0.4 | 0.01 | 0 | 20.85
| 724 | 2008-05-31 | 30000 | 69.4 | -2.7 | 0.57 | 64.5 | -297.5 | 0.04 | 0.5 | 1.3 | 461.9 | 0.4 | -0.01 | -0.06 | -0.8 | 0.01 | 0.5 | 0.01 | 0 | 20.84
| 725 | 2008-05-31 | 40000 | 69.6 | -2.9 | 0.57 | 63.1 | -317.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.7 | 0.01 | 0.1 | 0.01 | 0 | 20.84
| 726 | 2008-05-31 | 50000 | 69.5 | -2.6 | 0.57 | 68.9 | -317.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.9 | 0.02 | 1.4 | 0.013 | 0 | 20.85
| 727 | 2008-05-31 | 60000 | 67.8 | -2.5 | 0.57 | 78.7 | -350.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -1.2 | 0.01 | 0.7 | 0.012 | 0 | 20.85
| 728 | 2008-05-31 | 70000 | 67.9 | -2.7 | 0.58 | 104.6 | -534 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -1.4 | 0.01 | 0.8 | 0.016 | 0 | 20.86
| 729 | 2008-05-31 | 80000 | 68.9 | -2.7 | 0.58 | 99.4 | -463.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -1.7 | 0.02 | 1.8 | 0.016 | 0 | 20.86
| 730 | 2008-05-31 | 90000 | 69.5 | -2.4 | 0.58 | 112.6 | -462.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | 2.24 | -1.8 | 0.01 | 1 | 0.016 | 0 | 20.86
| 731 | 2008-05-31 | 100000 | 69.4 | -2.8 | 0.59 | 118.1 | -552.8 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -1.8 | 0.01 | 1 | 6.348 | 0 | 20.87
| 732 | 2008-05-31 | 110000 | 69.4 | -2.9 | 0.59 | 95.2 | -476.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -1.6 | 0.01 | 0.3 | 0.013 | 0 | 20.86
| 733 | 2008-05-31 | 120000 | 69.4 | -2.5 | 0.59 | 76.6 | -301.5 | 0.04 | 0.5 | 1.3 | 133.7 | 0.4 | -0.01 | -0.06 | -1.3 | 0.02 | 1.3 | 0.013 | 0 | 20.85
| 734 | 2008-05-31 | 130000 | 69.3 | -2.5 | 0.59 | 63.6 | -275.5 | 0.04 | 0.5 | 1.3 | 145.7 | 0.5 | -0.01 | -0.06 | -1.1 | 0.01 | 1.3 | 0.011 | 0 | 20.84
| 735 | 2008-05-31 | 140000 | 70.4 | -2.8 | 0.6 | 57.8 | -272.7 | 0.04 | 0.5 | 1.3 | 108.3 | 0.5 | -0.01 | -0.06 | -1 | 0.01 | 0.9 | 0.01 | 0 | 20.84
| 736 | 2008-05-31 | 150000 | 71.4 | -2.8 | 0.59 | 52.5 | -238.7 | 0.04 | 0.5 | 1.3 | 203.9 | 0.3 | -0.01 | -0.06 | -0.9 | 0.02 | 1 | 0.01 | 0 | 20.83
| 737 | 2008-05-31 | 160000 | 71.3 | -2.5 | 0.59 | 50.5 | -227.3 | 0.04 | 0.5 | 1.3 | 183 | 0.4 | -0.01 | -0.06 | -0.9 | 0.02 | 1.4 | 0.01 | 0 | 20.83
| 738 | 2008-05-31 | 170000 | 71.4 | -2.9 | 0.59 | 56.7 | -266.9 | 0.04 | 0.5 | 1.3 | 231.2 | 0.4 | -0.01 | -0.07 | -0.9 | 0.01 | 0.9 | 0.01 | 0 | 20.84
| 739 | 2008-05-31 | 180000 | 71.3 | -2.7 | 0.59 | 66.5 | -296.3 | 0.04 | 0.5 | 1.3 | 377 | 0.3 | -0.01 | -0.06 | -0.9 | 0 | -0.3 | 0.008 | 0 | 20.84
| 740 | 2008-05-31 | 190000 | 71.3 | -2.4 | 0.59 | 92.7 | -386.4 | 0.04 | 0.5 | 1.3 | 461.6 | 0.1 | -0.01 | -0.06 | -1.5 | 0.01 | 0.7 | 0.013 | 0 | 20.86
| 741 | 2008-05-31 | 200000 | 72.4 | -3 | 0.58 | 121 | -624.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -1.9 | 0.01 | 0 | 0.018 | 0 | 20.87
| 742 | 2008-05-31 | 210000 | 71.6 | -2.9 | 0.59 | 144.2 | -674.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.07 | -2 | 0.01 | 1.2 | 36.425 | 0 | 20.88
| 743 | 2008-05-31 | 220000 | 71.4 | -2.7 | 0.58 | 153.4 | -703.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.08 | -2.1 | 0.01 | 4.3 | 288.087 | 0 | 20.81
| 744 | 2008-05-31 | 230000 | 71.3 | -2.6 | 0.57 | 149.6 | -691.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -2.7 | 0.01 | 4.1 | 96.575 | 0.001 | 20.89
| 745 | 2008-06-01 | 0 | 71.4 | -2.7 | 0.57 | 149.9 | -669.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -2.7 | 0.02 | 4.2 | 72.8 | 0 | 20.88
| 746 | / | /
| 747 | / | / | -9999 | 159.289 | -1.869 | 0.617 | 31.347 | -191.188 | 1.396 | 11.558 | 17.25 | -9999 | 8.506 | 0.257 | 1.034 | 0.039 | 0.619 | 1.326 | 68.868 | 2.13 | 20.332
[10 empty] | July Total MW-hr | 11607.9
 | [9 empty] | Excluding non-op hours
Used gas use column to confirm operation

## PEMS May
Rows highlighted in yellow indicate hours of start-up/shutdown/non-operating hours Bright yellow highlight indicates NH3 flow less than 1 lb/hour during these periods indicating not sufficient accuracy to provide reliable data
|  |  | Outlet | O2 | PNG | Inlet | NH3 |  |  |  |  | Gas | Gas Flow in scfm * HHV / 10^6 | HTIP * 8710 * (20.9 / 20.9 - O2dry) | NH3 Flow lb/hr * 379.43 / ( 60 * 17.03) | (nh3flow dscfm / flue gas flow dscfm ) * 10^6 | nh3flow fraction pppm * (20.9 / (20.9 -O2dry) | nh3flow fraction @ 15% O2 - (noxin - noxout @15% O2) | Correction Factor
|  |  | Nox | Dry | Flow | Nox | Flow |  |  |  |  | Flow |  |  | 17.03 lb / lb mole |  |  |  | 0.37763
|  |  | dry |  |  | dry | [5 empty] | scfm
DATE | TIME | GEN22 | NOX23 | OXY25 | GAS210 | NOX2I12 | NH3FLO216 | Constants | nox in | nox out corrected | noxin - noxout | fuel flow | heat input | flue gas flow | nh3 flow | nh3flow fraction | nh3flow fraction | nh3slip uncorrected | nh3slip | nh3slip | nh3slip | nh3slip W/OUT no flow and neg. data
|  | (MW) | ppm | % | lb/sec | ppm | lb/hour |  | ppm @15%O2 | ppm@15%O2 | ppm @15% O2 | scfm | mmbtu/min | dscfm | dscfm | ppm | ppm @15%O2 | ppm | ppm | lb/mmbtu | lb/hr | lb/hr
2008-05-01 | 0 | 1.3 | 0 | 20.95 | 0.35 | -0.05 | 0.171 |  | 5.9 | 0 | 5.9 | 478.3041 | 0.52613 | -1915540.101 | 0.063498 | -0.033149 | 3.9116 | -1.9884 | -0.75089 | 0.1206 | 3.8072
2008-05-01 | 10000 | 1.3 | 0 | 20.95 | 0.26 | -0.06 | 0.171 | Fd dscf/mmBtu | 7.08 | 0 | 7.08 | 355.3116 | 0.39084 | -1422972.6465 | 0.063498 | -0.044624 | 5.2656 | -1.8144 | -0.68518 | 0.11005 | 2.5807
2008-05-01 | 20000 | 1.3 | 0 | 20.96 | 0.26 | -0.06 | 0.171 | 8710 | 5.9 | 0 | 5.9 | 355.3116 | 0.39084 | -1185810.5387 | 0.063498 | -0.053548 | 5.2656 | -0.63441 | -0.23957 | 0.032065 | 0.75195
2008-05-01 | 30000 | 1.3 | 0.16 | 20.84 | 0.32 | 0.44 | 0.19 |  | 43.2667 | 15.7333 | 27.5333 | 437.3066 | 0.48104 | 1459459.1246 | 0.070554 | 0.048342 | 4.7537 | -22.7797 | -8.6023 | -1.1514 | -33.231
2008-05-01 | 40000 | 18.2 | 10.26 | 17.08 | 6.87 | 29.58 | 0.19 | HHV btu/scf | 45.6864 | 15.8466 | 29.8398 | 9388.4267 | 10.3273 | 492137.64 | 0.070554 | 0.14336 | 0.22142 | -29.6184 | -11.1848 | -0.023513 | -14.5698
2008-05-01 | 50000 | 120.8 | 7.94 | 14.84 | 13.71 | 25.26 | 11.267 | 1100 | 24.5931 | 7.7304 | 16.8627 | 18735.8559 | 20.6094 | 619096.0581 | 4.1838 | 6.758 | 6.5795 | -10.2832 | -3.8832 | -0.005146 | -6.3634
2008-05-01 | 60000 | 260 | 2.27 | 14 | 21.95 | 9.68 | 18.544 |  | 8.2771 | 1.941 | 6.3361 | 29996.5015 | 32.9962 | 870519.7768 | 6.886 | 7.9103 | 6.7638 | 0.42776 | 0.16153 | 0.000188 | 0.3722 | 0.3722
2008-05-01 | 70000 | 268.3 | 3.39 | 12.27 | 22.52 | 11.79 | 25.84 | Gas Specifc Gravity | 8.0604 | 2.3176 | 5.7428 | 30775.454 | 33.853 | 714086.4604 | 9.5953 | 13.4372 | 9.1865 | 3.4437 | 1.3005 | 0.0012101 | 2.458 | 2.458
2008-05-01 | 80000 | 267.8 | 2.46 | 13.84 | 22.5 | 11.99 | 25.346 | 0.584 | 10.02 | 2.0558 | 7.9642 | 30748.1223 | 33.8229 | 872109.5158 | 9.4119 | 10.7921 | 9.0189 | 1.0547 | 0.39828 | 0.00045304 | 0.91939 | 0.91939
2008-05-01 | 90000 | 268.4 | 2.45 | 13.77 | 22.53 | 12.94 | 27.911 |  | 10.7077 | 2.0273 | 8.6804 | 30789.1198 | 33.868 | 864698.8274 | 10.3643 | 11.9861 | 9.9183 | 1.238 | 0.4675 | 0.00052655 | 1.07 | 1.07
2008-05-01 | 100000 | 267.7 | 2.41 | 13.77 | 22.44 | 12.96 | 28.063 | Density of Air lb/cubic ft | 10.7243 | 1.9942 | 8.73 | 30666.1273 | 33.7327 | 861244.6377 | 10.4208 | 12.0997 | 10.0123 | 1.2823 | 0.48425 | 0.00054542 | 1.1039 | 1.1039
2008-05-01 | 110000 | 266.2 | 2.43 | 13.78 | 22.26 | 12.76 | 27.55 | 0.07518 | 10.5736 | 2.0136 | 8.56 | 30420.1423 | 33.4622 | 855536.1687 | 10.2303 | 11.9577 | 9.9088 | 1.3488 | 0.50936 | 0.00057451 | 1.1535 | 1.1535
2008-05-01 | 120000 | 264.4 | 2.43 | 13.81 | 22.23 | 12.47 | 26.543 |  | 10.377 | 2.0221 | 8.3549 | 30379.1448 | 33.4171 | 857998.3165 | 9.8563 | 11.4876 | 9.5595 | 1.2046 | 0.45491 | 0.00051526 | 1.0331 | 1.0331
2008-05-01 | 130000 | 264.6 | 2.43 | 13.79 | 22.21 | 12.79 | 27.626 |  | 10.6134 | 2.0165 | 8.5969 | 30351.8132 | 33.387 | 854815.0622 | 10.2585 | 12.0008 | 9.9585 | 1.3616 | 0.51418 | 0.00058076 | 1.1634 | 1.1634
2008-05-01 | 140000 | 264.8 | 2.43 | 13.77 | 22.24 | 12.98 | 28.063 |  | 10.7408 | 2.0108 | 8.73 | 30392.8107 | 33.4321 | 853568.6605 | 10.4208 | 12.2085 | 10.1024 | 1.3724 | 0.51825 | 0.00058371 | 1.1709 | 1.1709
2008-05-01 | 150000 | 264.3 | 2.44 | 13.77 | 22.15 | 12.96 | 27.968 |  | 10.7243 | 2.0191 | 8.7052 | 30269.8182 | 33.2968 | 850114.4708 | 10.3855 | 12.2166 | 10.1091 | 1.4039 | 0.53016 | 0.00059713 | 1.1929 | 1.1929
2008-05-01 | 160000 | 263.6 | 2.45 | 13.76 | 22.07 | 13.06 | 28.272 |  | 10.7919 | 2.0245 | 8.7674 | 30160.4915 | 33.1765 | 845857.7437 | 10.4984 | 12.4115 | 10.256 | 1.4887 | 0.56216 | 0.00063228 | 1.2586 | 1.2586
2008-05-01 | 170000 | 263.1 | 2.43 | 13.75 | 22.05 | 13.06 | 28.386 |  | 10.7768 | 2.0052 | 8.7716 | 30133.1599 | 33.1465 | 843909.2753 | 10.5407 | 12.4903 | 10.3067 | 1.5351 | 0.5797 | 0.0006511 | 1.2949 | 1.2949
2008-05-01 | 180000 | 262.6 | 2.44 | 13.75 | 22.05 | 13.09 | 28.481 |  | 10.8015 | 2.0134 | 8.7881 | 30133.1599 | 33.1465 | 843909.2753 | 10.576 | 12.5321 | 10.3412 | 1.5531 | 0.5865 | 0.00065873 | 1.3101 | 1.3101
2008-05-01 | 190000 | 263 | 2.44 | 13.73 | 22.05 | 13.05 | 28.158 |  | 10.7385 | 2.0078 | 8.7307 | 30133.1599 | 33.1465 | 841555.2745 | 10.456 | 12.4247 | 10.2239 | 1.4932 | 0.56389 | 0.00063158 | 1.2561 | 1.2561
2008-05-01 | 200000 | 264 | 2.44 | 13.71 | 22.08 | 12.99 | 27.93 |  | 10.6594 | 2.0022 | 8.6572 | 30174.1574 | 33.1916 | 840356.158 | 10.3714 | 12.3417 | 10.1274 | 1.4702 | 0.55519 | 0.00062011 | 1.2349 | 1.2349
2008-05-01 | 210000 | 261 | 2.35 | 13.75 | 21.91 | 12 | 25.213 |  | 9.9021 | 1.9392 | 7.9629 | 29941.8382 | 32.936 | 838551.1211 | 9.3625 | 11.1651 | 9.2131 | 1.2502 | 0.47211 | 0.00053026 | 1.0479 | 1.0479
2008-05-01 | 220000 | 20.6 | 2.43 | 19.4 | 2.3 | 6.43 | 0.418 |  | 25.2913 | 9.558 | 15.7333 | 3143.1414 | 3.4575 | 419594.4983 | 0.15522 | 0.36992 | 1.455 | -14.2783 | -5.3919 | -0.028867 | -5.9884
2008-05-05 | 10000 | 1.8 | 1.06 | 20.43 | 0.65 | 2.69 | 0.171 |  | 33.7681 | 13.3064 | 20.4617 | 888.2791 | 0.97711 | 378450.1719 | 0.063498 | 0.16779 | 2.1062 | -18.3555 | -6.9316 | -0.11844 | -6.9435
2008-05-05 | 20000 | 18.9 | 10.29 | 16.89 | 6.92 | 30.01 | 0.209 |  | 44.1544 | 15.1399 | 29.0145 | 9456.7558 | 10.4024 | 472231.4749 | 0.077609 | 0.16435 | 0.2418 | -28.7727 | -10.8654 | -0.02176 | -13.5812
2008-05-05 | 30000 | 20.8 | 10.29 | 16.8 | 7.06 | 30.01 | 8.607 |  | 43.1851 | 14.8076 | 28.3776 | 9648.0775 | 10.6129 | 471209.5161 | 3.1961 | 6.7827 | 9.7605 | -18.6171 | -7.0304 | -0.01377 | -8.7686
2008-05-05 | 40000 | 52.6 | 10.26 | 15.88 | 8.76 | 30.01 | 19.57 |  | 35.2707 | 12.0586 | 23.2122 | 11971.269 | 13.1684 | 477522.2335 | 7.267 | 15.2182 | 17.8859 | -5.3262 | -2.0113 | -0.0032176 | -2.5422
2008-05-05 | 50000 | 71.2 | 10.29 | 15.46 | 9.58 | 30.01 | 17.461 |  | 32.5476 | 11.1601 | 21.3875 | 13091.8672 | 14.4011 | 481903.2082 | 6.4839 | 13.4547 | 14.5924 | -6.7951 | -2.566 | -0.003788 | -3.2731
2008-05-05 | 60000 | 243.5 | 3.56 | 12.25 | 21.11 | 10.76 | 17.461 |  | 7.3392 | 2.4282 | 4.911 | 28848.5716 | 31.7334 | 667829.0922 | 6.4839 | 9.7089 | 6.6222 | 1.7113 | 0.64623 | 0.00059996 | 1.1423 | 1.1423
2008-05-05 | 70000 | 259.3 | 2.5 | 13.66 | 22.21 | 12.71 | 26.581 |  | 10.3576 | 2.0373 | 8.3203 | 30351.8132 | 33.387 | 839466.1729 | 9.8705 | 11.758 | 9.5818 | 1.2615 | 0.47638 | 0.0005284 | 1.0585 | 1.0585
2008-05-05 | 80000 | 260.3 | 2.45 | 13.66 | 22.05 | 12.3 | 25.479 |  | 10.0235 | 1.9965 | 8.0269 | 30133.1599 | 33.1465 | 833418.6904 | 9.4612 | 11.3523 | 9.2512 | 1.2243 | 0.46232 | 0.00051281 | 1.0199 | 1.0199
2008-05-05 | 90000 | 263.8 | 2.5 | 13.64 | 22.05 | 12.78 | 26.106 |  | 10.386 | 2.0317 | 8.3543 | 30133.1599 | 33.1465 | 831122.7711 | 9.6941 | 11.6638 | 9.4789 | 1.1246 | 0.42468 | 0.00046976 | 0.93426 | 0.93426
2008-05-05 | 100000 | 262.8 | 2.72 | 13.63 | 21.95 | 12.77 | 25.232 |  | 10.3635 | 2.2074 | 8.1561 | 29996.5015 | 32.9962 | 826215.469 | 9.3695 | 11.3403 | 9.2033 | 1.0471 | 0.39543 | 0.00043681 | 0.86477 | 0.86477
2008-05-05 | 110000 | 260.2 | 2.85 | 13.64 | 21.82 | 12.75 | 24.738 |  | 10.3616 | 2.3161 | 8.0455 | 29818.8457 | 32.8007 | 822453.4633 | 9.1861 | 11.1691 | 9.0768 | 1.0314 | 0.38948 | 0.00043082 | 0.84788 | 0.84788
2008-05-05 | 120000 | 258 | 2.84 | 13.64 | 21.61 | 12.6 | 24.282 |  | 10.2397 | 2.308 | 7.9317 | 29531.8633 | 32.485 | 814538.0083 | 9.0168 | 11.0698 | 8.9961 | 1.0644 | 0.40196 | 0.00044462 | 0.86662 | 0.86662
2008-05-05 | 130000 | 256.5 | 2.85 | 13.65 | 21.54 | 12.57 | 24.206 |  | 10.2294 | 2.3193 | 7.9101 | 29436.2024 | 32.3798 | 813019.3847 | 8.9885 | 11.0557 | 8.9971 | 1.087 | 0.41049 | 0.00045469 | 0.88337 | 0.88337
2008-05-05 | 140000 | 255.3 | 2.84 | 13.66 | 21.5 | 12.54 | 24.092 |  | 10.2191 | 2.3144 | 7.9047 | 29381.5391 | 32.3197 | 812630.4691 | 8.9462 | 11.0089 | 8.9714 | 1.0667 | 0.40281 | 0.0004468 | 0.86642 | 0.86642
2008-05-05 | 150000 | 253.9 | 2.84 | 13.66 | 21.32 | 12.51 | 24.054 |  | 10.1946 | 2.3144 | 7.8802 | 29135.5541 | 32.0491 | 805827.0512 | 8.9321 | 11.0844 | 9.0328 | 1.1526 | 0.43526 | 0.00048279 | 0.92838 | 0.92838
2008-05-05 | 160000 | 254 | 2.84 | 13.65 | 21.32 | 12.39 | 23.731 |  | 10.0829 | 2.3112 | 7.7717 | 29135.5541 | 32.0491 | 804715.5656 | 8.8121 | 10.9506 | 8.9116 | 1.1398 | 0.43043 | 0.00047678 | 0.91683 | 0.91683
2008-05-05 | 170000 | 255.6 | 2.84 | 13.66 | 21.53 | 12.52 | 24.168 |  | 10.2028 | 2.3144 | 7.8884 | 29422.5366 | 32.3648 | 813764.372 | 8.9744 | 11.0283 | 8.9871 | 1.0987 | 0.41492 | 0.00046023 | 0.89371 | 0.89371
2008-05-05 | 180000 | 257.6 | 2.77 | 13.66 | 21.61 | 12.74 | 25.213 |  | 10.382 | 2.2573 | 8.1247 | 29531.8633 | 32.485 | 816788.1133 | 9.3625 | 11.4625 | 9.341 | 1.2163 | 0.45931 | 0.00050947 | 0.99301 | 0.99301
2008-05-05 | 190000 | 258.2 | 2.58 | 13.7 | 21.71 | 12.34 | 24.795 |  | 10.1119 | 2.1142 | 7.9978 | 29668.5216 | 32.6354 | 825126.4999 | 9.2072 | 11.1586 | 9.1438 | 1.1461 | 0.43279 | 0.00048272 | 0.94522 | 0.94522
2008-05-05 | 200000 | 257.4 | 2.55 | 13.76 | 21.6 | 11.16 | 22.572 |  | 9.2218 | 2.1071 | 7.1147 | 29518.1974 | 32.47 | 827844.4614 | 8.3818 | 10.1248 | 8.3664 | 1.2517 | 0.47269 | 0.00053166 | 1.0358 | 1.0358
2008-05-05 | 210000 | 263.3 | 2.58 | 13.67 | 22.04 | 12.43 | 26.087 |  | 10.1434 | 2.1054 | 8.038 | 30119.494 | 33.1314 | 834192.9229 | 9.687 | 11.6124 | 9.4763 | 1.4382 | 0.54312 | 0.00060326 | 1.1992 | 1.1992
2008-05-05 | 220000 | 28.5 | 1.99 | 19.16 | 3 | 5.64 | 1.387 |  | 19.1241 | 6.7477 | 12.3764 | 4099.7496 | 4.5097 | 471807.9067 | 0.51504 | 1.0916 | 3.7015 | -8.6749 | -3.2759 | -0.015119 | -4.0911
2008-05-06 | 40000 | 2.3 | 1.13 | 20.37 | 0.76 | 3.43 | 0.171 |  | 38.183 | 12.5792 | 25.6038 | 1038.6032 | 1.1425 | 392401.7458 | 0.063498 | 0.16182 | 1.8014 | -23.8024 | -8.9885 | -0.1362 | -9.3359
2008-05-06 | 50000 | 51.4 | 10.06 | 15.91 | 9.11 | 29.31 | 6.726 |  | 34.6551 | 11.8946 | 22.7605 | 12449.5731 | 13.6945 | 499586.8972 | 2.4976 | 4.9993 | 5.911 | -16.8495 | -6.3629 | -0.01024 | -8.414
2008-05-06 | 60000 | 213.2 | 2.11 | 13.82 | 18.49 | 8.36 | 13.262 |  | 6.9667 | 1.7583 | 5.2083 | 25268.1236 | 27.7949 | 714655.6995 | 4.9246 | 6.8909 | 5.7424 | 0.53411 | 0.2017 | 0.00022878 | 0.38153 | 0.38153
2008-05-06 | 70000 | 264.9 | 3.62 | 12.11 | 22.26 | 12.77 | 26.961 |  | 8.5714 | 2.4298 | 6.1416 | 30420.1423 | 33.4622 | 692994.0297 | 10.0116 | 14.4468 | 9.697 | 3.5553 | 1.3426 | 0.0012266 | 2.4627 | 2.4627
2008-05-06 | 80000 | 265.5 | 2.58 | 13.7 | 22.16 | 12.79 | 26.695 |  | 10.4807 | 2.1142 | 8.3665 | 30283.484 | 33.3118 | 842229.5365 | 9.9128 | 11.7697 | 9.6446 | 1.2781 | 0.48264 | 0.00053832 | 1.076 | 1.076
2008-05-06 | 90000 | 265.3 | 2.59 | 13.66 | 22.07 | 12.84 | 26.429 |  | 10.4635 | 2.1106 | 8.3529 | 30160.4915 | 33.1765 | 834174.6257 | 9.814 | 11.7649 | 9.5874 | 1.2345 | 0.4662 | 0.00051711 | 1.0294 | 1.0294
2008-05-06 | 100000 | 265.5 | 2.53 | 13.72 | 21.92 | 11.87 | 24.054 |  | 9.7539 | 2.079 | 7.6749 | 29955.5041 | 32.9511 | 835428.5518 | 8.9321 | 10.6916 | 8.7856 | 1.1107 | 0.41942 | 0.00046911 | 0.92747 | 0.92747
2008-05-06 | 110000 | 264.4 | 2.58 | 13.76 | 21.72 | 11.37 | 22.8 |  | 9.3954 | 2.1319 | 7.2634 | 29682.1874 | 32.6504 | 832443.5973 | 8.4664 | 10.1706 | 8.4043 | 1.1408 | 0.43081 | 0.00048455 | 0.94924 | 0.94924
2008-05-06 | 120000 | 268.2 | 2.59 | 13.66 | 22.05 | 12.82 | 26.752 |  | 10.4472 | 2.1106 | 8.3366 | 30133.1599 | 33.1465 | 833418.6904 | 9.934 | 11.9195 | 9.7134 | 1.3768 | 0.51993 | 0.00057671 | 1.147 | 1.147
2008-05-06 | 130000 | 266.4 | 2.53 | 13.67 | 21.88 | 12.6 | 26.125 |  | 10.2822 | 2.0646 | 8.2176 | 29900.8407 | 32.8909 | 828137.0759 | 9.7011 | 11.7144 | 9.5595 | 1.3419 | 0.50674 | 0.00056286 | 1.1108 | 1.1108
2008-05-06 | 140000 | 191.6 | 2.46 | 13.89 | 16.4 | 7.97 | 9.899 |  | 6.708 | 2.0705 | 4.6375 | 22411.9647 | 24.6532 | 640204.9655 | 3.6758 | 5.7417 | 4.8325 | 0.19498 | 0.073632 | 8.4353e-05 | 0.12477 | 0.12477
2008-05-06 | 150000 | 190.8 | 2.48 | 13.88 | 16.4 | 7.97 | 10.336 |  | 6.6984 | 2.0843 | 4.6141 | 22411.9647 | 24.6532 | 639292.9926 | 3.8381 | 6.0037 | 5.0458 | 0.43173 | 0.16304 | 0.00018651 | 0.27588 | 0.27588
2008-05-06 | 160000 | 192.7 | 2.54 | 13.88 | 16.44 | 7.79 | 9.861 |  | 6.5472 | 2.1348 | 4.4124 | 22466.628 | 24.7133 | 640852.2438 | 3.6617 | 5.7138 | 4.8022 | 0.38985 | 0.14722 | 0.00016841 | 0.24972 | 0.24972
2008-05-06 | 170000 | 191.3 | 2.52 | 13.88 | 16.36 | 7.77 | 9.785 |  | 6.5303 | 2.1179 | 4.4124 | 22357.3014 | 24.593 | 637733.7414 | 3.6335 | 5.6975 | 4.7885 | 0.37614 | 0.14204 | 0.00016249 | 0.23977 | 0.23977
2008-05-06 | 180000 | 11.6 | 1.8 | 19.77 | 1.43 | 4.98 | 0.532 |  | 26.0018 | 9.3982 | 16.6035 | 1954.214 | 2.1496 | 346298.6529 | 0.19755 | 0.57046 | 2.9785 | -13.625 | -5.1452 | -0.036566 | -4.7162
[21 empty] | Total NH3 (lbs): | 44.4101
total aqueous ammonia flow
0.9
0.9
0.9
1
1
59.3
97.6
136
133.4
146.9
147.7
145
139.7
145.4
147.7
147.2
148.8
149.4
149.9
148.2
147
132.7
2.2
0.9
1.1
45.3
103
91.9
91.9
139.9
134.1
137.4
132.8
130.2
127.8
127.4
126.8
126.6
124.9
127.2
132.7
130.5
118.8
137.3
7.3
0.9
35.4
69.8
141.9
[7 empty] | 140.5 | [11 empty] | 0
[7 empty] | 139.1 | [11 empty] | 0
[7 empty] | 126.6 | [11 empty] | 0
[7 empty] | 120 | [11 empty] | 0
[7 empty] | 140.8 | [11 empty] | 0
[7 empty] | 137.5 | [11 empty] | 0
[7 empty] | 52.1 | [11 empty] | 0
[7 empty] | 54.4 | [11 empty] | 0
[7 empty] | 51.9 | [11 empty] | 0
[7 empty] | 51.5 | [11 empty] | 0
[7 empty] | 2.8 | [11 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## June CEMS data
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-01
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-02
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-03
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-04
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-05
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-06
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-07
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-08
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-09
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-10
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-11
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-12
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-13
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-14
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-15
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-16
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-17
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-18
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-19
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-20
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-21
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-22
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-23
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-24
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-25
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-26
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-27
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-28
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-29
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington
2008-06-30
|  | Nox | Nox | NOx | CO | CO | CO | NH3 | NH3 | Cat Tmp | Tmp | Load
| TM | ppmvd | 24hr | lbs/hr | ppmvd | lb/hr | Annual | ppmvd | lbs/hr | Deg F | F | MW
| 0 | Offline
| 1 | Offline
| 2 | Offline
| 3 | Offline
| 4 | Offline
| 5 | Offline
| 6 | Offline
| 7 | Offline
| 8 | Offline
| 9 | Offline
| 10 | Offline
| 11 | Offline
| 12 | Offline
| 13 | Offline
| 14 | Offline
| 15 | Offline
| 16 | Offline
| 17 | Offline
| 18 | Offline
| 19 | Offline
| 20 | Offline
| 21 | Offline
| 22 | Offline
| 23 | Offline
Legend
C | Out | of | Control | X | Cal | Expired
D | Out | of | Service | I | Insufficient | Data
M | Maintenance | Fault
Limits
NOx | 21.3 | lb/hr | 2.5 | ppmvd | 24 | hour | avg
CO | 31.1 | lb/hr | 6 | ppmvd | 1 | hour | avg | 2 | ppmvd | Annual | Avg
NH3 | 31.4 | lb/hr | 10 | ppmvd | 24 | hour | avg
Minimum | Catalyst | Operating | Temp | 563.4 | Deg F | F
Event | Codes
SD | - | Shutdown | OT | - | Other
CS | - | Cold | Startup | WS | - | Warm | Startup | HS | - | Hot | Startup
| Daily | Emissions | Report
| Mint | Farm | Energy | Center
CTG1
| Longview, | Washington

## June CEMS Raw data
This data is raw hourly CEMs database data which may include invalid data such as values obtained during calibration checks.
June | 2008
| Record# | DATE | TIME | CATTMP12 | COH13 | CO_14 | CO_COR15 | CO_HCOR16 | GAS17 | GEN18 | GEN29 | HGAS110 | NH3FLO112 | NOX113 | NOX1I14 | NOXCOR115 | NOXH116 | NOXHCOR117 | NOXHRT118 | NOXRT119 | OXY120
| 1 | 2008-06-01 | 0 | 71.4 | -2.7 | 0.57 | 149.9 | -669.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -2.7 | 0.02 | 4.2 | 72.8 | 0 | 20.88
| 2 | 2008-06-01 | 10000 | 71.4 | -2.8 | 0.57 | 151.2 | -727.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -2.6 | 0.01 | 2.6 | 93.4 | 0 | 20.88
| 3 | 2008-06-01 | 20000 | 71.4 | -2.5 | 0.56 | 143.2 | -648.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -2.5 | 0.01 | 2.4 | 66.5 | 0 | 20.81
| 4 | 2008-06-01 | 30000 | 71.4 | -2.3 | 0.56 | 142.1 | -638 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.05 | -2.8 | 0.01 | 2.4 | 101.3 | 1.6 | 20.88
| 5 | 2008-06-01 | 40000 | 71.4 | -2.6 | 0.56 | 142.4 | -692.4 | 0.04 | 0.5 | 1.2 | 463.2 | 0.3 | -0.01 | -0.06 | -2.5 | 0.01 | 3 | 80.7 | 0 | 20.88
| 6 | 2008-06-01 | 50000 | 71.4 | -2.6 | 0.56 | 139.2 | -632.6 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -2.5 | 0 | 3.1 | 120.3 | 1.6 | 20.81
| 7 | 2008-06-01 | 60000 | 71.4 | -2.7 | 0.56 | 153.8 | -783.5 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -2.8 | 0.01 | 4.7 | 246.9 | 0 | 20.89
| 8 | 2008-06-01 | 70000 | 71.4 | -2.7 | 0.56 | 125.9 | -609.5 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -2.3 | 0.01 | 4.9 | 283.3 | 1.6 | 20.89
| 9 | 2008-06-01 | 80000 | 70.9 | -2.8 | 0.57 | 113.8 | -660 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -2.4 | 0.01 | 5.7 | 449.5 | 1.6 | 20.89
| 10 | 2008-06-01 | 90000 | 69.4 | -2.9 | 0.57 | 71.8 | -396.6 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | 2.17 | -1.3 | 0.02 | 4.3 | 672.7 | 1.6 | 20.9
| 11 | 2008-06-01 | 100000 | 69.4 | -2.6 | 0.57 | 73.6 | -330.7 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -1.5 | 0.01 | 4.7 | 865.8 | 0 | 20.83
| 12 | 2008-06-01 | 110000 | 69.4 | -2.6 | 0.57 | 57.4 | -258.9 | 0.04 | 0.5 | 1.2 | 463.2 | 0.3 | -0.01 | -0.06 | -1.1 | 0.01 | 3.1 | 620.5 | 1.6 | 20.9
| 13 | 2008-06-01 | 120000 | 70.9 | -2.7 | 0.57 | 69.4 | -334 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.06 | -1.4 | 0.02 | 5.4 | 774 | 0 | 20.9
| 14 | 2008-06-01 | 130000 | 71.4 | -2.6 | 0.57 | 92.6 | -396 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -1.6 | 0.01 | 5.7 | 568.2 | 0 | 20.9
| 15 | 2008-06-01 | 140000 | 71.4 | -2.8 | 0.57 | 83.5 | -410.2 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -1.4 | 0.02 | 5 | 648.9 | 1.6 | 20.9
| 16 | 2008-06-01 | 150000 | 71.4 | -3.1 | 0.58 | 121.8 | -654.6 | 0.04 | 0.5 | 1.3 | 455.5 | 0.2 | -0.01 | -0.06 | -2.5 | 0.02 | 5.8 | 478 | 0 | 20.89
| 17 | 2008-06-01 | 160000 | 71.3 | -2.4 | 0.57 | 122.3 | -460.2 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -2.4 | 0.02 | 6.4 | 424.2 | 0 | 20.89
| 18 | 2008-06-01 | 170000 | 71.4 | -2.6 | 0.57 | 126.8 | -622.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -2.3 | 0.01 | 5.3 | 389.4 | 0 | 20.89
| 19 | 2008-06-01 | 180000 | 71.5 | -2.6 | 0.57 | 132.7 | -618.2 | 0.04 | 0.5 | 1.2 | 463.2 | 0.3 | -0.01 | -0.07 | -2.4 | 0.01 | 5.3 | 337.2 | 0 | 20.89
| 20 | 2008-06-01 | 190000 | 71.4 | -2.6 | 0.57 | 106.3 | -488.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -2 | 0.01 | 5.4 | 378.3 | 1.6 | 20.89
| 21 | 2008-06-01 | 200000 | 71.4 | -2.4 | 0.57 | 95.2 | -442.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -1.7 | 0.02 | 6.3 | 766.1 | 1.6 | 20.9
| 22 | 2008-06-01 | 210000 | 71.3 | -2.4 | 0.57 | 36.8 | -130.5 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -0.8 | 0.01 | 4.5 | 618.9 | 0 | 20.76
| 23 | 2008-06-01 | 220000 | 71.3 | -2.6 | 0.57 | 21.2 | -87.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -0.4 | 0.01 | 1.8 | 625.2 | 1.6 | 20.91
| 24 | 2008-06-01 | 230000 | 69.9 | -2.7 | 0.57 | 45.2 | -211.8 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.9 | 0.02 | 3.8 | 729.7 | 0 | 20.91
| 25 | 2008-06-02 | 0 | 69.4 | -2.4 | 0.57 | 75.3 | -366 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.06 | -1.6 | 0.02 | 7 | 838.9 | 3.2 | 20.83
| 26 | 2008-06-02 | 10000 | 69.3 | -2.8 | 0.58 | 70.8 | -419 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -1.3 | 0.01 | 3.6 | 786.6 | 0 | 20.9
| 27 | 2008-06-02 | 20000 | 69.4 | -2.7 | 0.58 | 86.1 | -436.4 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -1.7 | 0.01 | 5.5 | 520.7 | 0 | 20.9
| 28 | 2008-06-02 | 30000 | 69.5 | -2.6 | 0.58 | 120.3 | -479.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -2.4 | 0.01 | 4.4 | 417.9 | 0 | 20.89
| 29 | 2008-06-02 | 40000 | 69.3 | -2.6 | 0.59 | 148.1 | -649.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -2.6 | 0.01 | 4.5 | 265.9 | 1.6 | 20.89
| 30 | 2008-06-02 | 50000 | 69.4 | -2.8 | 0.59 | 142.2 | -643.1 | 0.04 | 0.5 | 1.3 | 462 | 0.2 | -0.01 | -0.06 | -2.4 | 0.02 | 5.2 | 389.4 | 0 | 20.89
| 31 | 2008-06-02 | 60000 | 69.4 | -2.6 | 0.61 | 134.5 | -580.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -2.4 | 0.01 | 5.4 | 400.5 | 1.6 | 20.89
| 32 | 2008-06-02 | 70000 | 69.4 | -2.7 | 0.68 | 141.7 | -593.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -1.8 | 0.02 | 4.4 | 408.4 | 4.7 | 20.89
| 33 | 2008-06-02 | 80000 | 69.4 | -2.7 | 0.65 | 169.2 | -670.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -2.3 | 0.01 | 4.3 | 74.4 | 0 | 20.88
| 34 | 2008-06-02 | 90000 | 69.4 | -2.6 | 0.62 | 168 | -724.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | 2.24 | -2.6 | 0.02 | 3.9 | 91.8 | 0 | 20.88
| 35 | 2008-06-02 | 100000 | 69.4 | -2.6 | 0.63 | 126.2 | -550.3 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -1.8 | 0.01 | 0.9 | 34.8 | 0 | 20.87
| 36 | 2008-06-02 | 110000 | 69.3 | -2.7 | 0.6 | 122.5 | -532.6 | 0.04 | 0.5 | 1.3 | 462.8 | 0.2 | -0.01 | -0.06 | -2 | 0.02 | 3 | 15.8 | 0 | 20.79
| 37 | 2008-06-02 | 120000 | 69.4 | -2.5 | 0.6 | 94.9 | -384.2 | 0.04 | 0.5 | 1.3 | 415.2 | 0.2 | -0.01 | -0.06 | -1.7 | 0.01 | 0.5 | 0 | 0 | 20.78
| 38 | 2008-06-02 | 130000 | 69.5 | -2.7 | 0.6 | 67.8 | -309 | 0.04 | 0.5 | 1.3 | 356.7 | 0.3 | -0.01 | -0.06 | -1.2 | 0.02 | 1.3 | 0 | 0 | 20.84
| 39 | 2008-06-02 | 140000 | 69.4 | -2.8 | 0.61 | 54.3 | -257.7 | 0.04 | 0.5 | 1.3 | 368.5 | 0.2 | -0.01 | -0.06 | -0.9 | 0.01 | 0.6 | 0 | 0 | 20.83
| 40 | 2008-06-02 | 150000 | 70.2 | -2.5 | 0.62 | 47.2 | -188.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.6 | 0.01 | 0.6 | 0 | 0 | 20.82
| 41 | 2008-06-02 | 160000 | 71.3 | -2.5 | 0.62 | 42.8 | -159.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -0.7 | 0.01 | 0.7 | 0 | 0 | 20.74
| 42 | 2008-06-02 | 170000 | 71.4 | -2.5 | 0.62 | 42.4 | -175.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.6 | 0.01 | 0.5 | 0 | 0 | 20.81
| 43 | 2008-06-02 | 180000 | 71.5 | -2.6 | 0.6 | 38.6 | -169.1 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -0.6 | 0.02 | 0.9 | 0 | 0 | 20.81
| 44 | 2008-06-02 | 190000 | 71.4 | -2.5 | 0.61 | 36.2 | -154 | 0.04 | 0.5 | 1.3 | 463.2 | 0.1 | -0.01 | -0.06 | -0.6 | 0.01 | 0.6 | 0 | 0 | 20.8
| 45 | 2008-06-02 | 200000 | 71.3 | -2.7 | 0.62 | 31.3 | -133.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.5 | 0.01 | 0.6 | 0 | 0 | 20.78
| 46 | 2008-06-02 | 210000 | 71.3 | -2.8 | 0.63 | 28.8 | -122 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.06 | -0.5 | 0.01 | 0.4 | 0 | 0 | 20.77
| 47 | 2008-06-02 | 220000 | 71.3 | -2.5 | 0.63 | 27.1 | -103.6 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -0.4 | 0 | 0 | 0 | 0 | 20.76
| 48 | 2008-06-02 | 230000 | 69.7 | -2.8 | 0.62 | 23.9 | -103.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -0.4 | 0.01 | 0.4 | 0 | 0 | 20.75
| 49 | 2008-06-03 | 0 | 69.4 | -2.6 | 0.64 | 22.2 | -91.8 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.09 | -0.3 | 0.01 | 0.4 | 0 | 0 | 20.73
| 50 | 2008-06-03 | 10000 | 69.4 | -2.7 | 0.64 | 20 | -87.6 | 0.04 | 0.5 | 1.3 | 459.4 | 0.2 | -0.01 | -0.09 | -0.3 | 0.02 | 0.5 | 0 | 0 | 20.71
| 51 | 2008-06-03 | 20000 | 69.3 | -2.4 | 0.63 | 18.4 | -67.5 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.08 | -0.3 | 0.01 | 0.2 | 0 | 0 | 20.7
| 52 | 2008-06-03 | 30000 | 69.3 | -2.7 | 0.62 | 16.7 | -71.2 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.68
| 53 | 2008-06-03 | 40000 | 69.4 | -2.7 | 0.62 | 15.3 | -66.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.2 | -0.01 | -0.07 | -0.2 | 0.01 | 0.3 | 0 | 0 | 20.66
| 54 | 2008-06-03 | 50000 | 69.4 | -2.6 | 0.62 | 14.5 | -60.7 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -0.2 | 0.01 | 0.2 | 0 | 0 | 20.65
| 55 | 2008-06-03 | 60000 | 69.4 | -2.7 | 0.63 | 14.2 | -62.9 | 0.04 | 0.5 | 1.3 | 463.2 | 0.3 | -0.01 | -0.06 | -0.2 | 0.02 | 0.4 | 0 | 0 | 20.64
| 56 | 2008-06-03 | 70000 | 69.4 | -2.5 | 0.64 | 14.5 | -56.2 | 0.04 | 0.5 | 1.3 | 462 | 0.2 | -0.01 | -0.06 | -0.2 | 0.01 | 0.2 | 0 | 0 | 20.64
| 57 | 2008-06-03 | 80000 | 69.4 | -2.3 | 0.64 | 14.7 | -52.7 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -0.2 | 0 | 0.1 | 0 | 0 | 20.64
| 58 | 2008-06-03 | 90000 | 69.4 | -2.5 | 0.63 | 14.6 | -59.6 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | 2.22 | -0.2 | 0.02 | 0.3 | 0 | 0 | 20.65
| 59 | 2008-06-03 | 100000 | 69.4 | -2.7 | 0.6 | 14.8 | -67.4 | 0.04 | 0.5 | 1.2 | 463.2 | 0.2 | -0.01 | -0.06 | -0.2 | 0.01 | 0.2 | 0 | 0 | 20.66
| 60 | 2008-06-03 | 110000 | 71 | -2.7 | 0.61 | 15.4 | -65.9 | 0.04 | 0.5 | 1.2 | 359.9 | 0.3 | -0.01 | -0.06 | -0.3 | 0.02 | 0.5 | 0 | 0 | 20.67
| 61 | 2008-06-03 | 120000 | 71.3 | -2.5 | 0.61 | 16.6 | -67.5 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 0.2 | 0 | 0 | 20.68
| 62 | 2008-06-03 | 130000 | 71.4 | -2.5 | 0.61 | 18.3 | -79 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.07 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.7
| 63 | 2008-06-03 | 140000 | 71.4 | -2.6 | 0.61 | 19.4 | -81 | 0.04 | 0.5 | 1.3 | -0.9 | 0.6 | -0.01 | -0.08 | -0.3 | 0.01 | 0.2 | 0 | 0 | 20.71
| 64 | 2008-06-03 | 150000 | 71.3 | -2.5 | 0.62 | 20 | -80.2 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.08 | -0.4 | 0.01 | 0.2 | 0 | 0 | 20.72
| 65 | 2008-06-03 | 160000 | 71.3 | -2.6 | 0.62 | 20.9 | -89.4 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.08 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.72
| 66 | 2008-06-03 | 170000 | 71.3 | -2.6 | 0.62 | 21.1 | -92.8 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.07 | -0.4 | 0.01 | 0.5 | 0 | 0 | 20.73
| 67 | 2008-06-03 | 180000 | 72.6 | -2.5 | 0.62 | 21.7 | -88.8 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.06 | -0.4 | 0.01 | 0.3 | 0 | 0 | 20.73
| 68 | 2008-06-03 | 190000 | 72.8 | -2.5 | 0.61 | 22 | -89.1 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.08 | -0.4 | 0.01 | 0.3 | 0 | 0 | 20.73
| 69 | 2008-06-03 | 200000 | 72.7 | -2.6 | 0.62 | 22.6 | -93 | 0.04 | 0.5 | 1.3 | -1 | 0.6 | -0.01 | -0.09 | -0.4 | 0.01 | 0.5 | 0 | 0 | 20.74
| 70 | 2008-06-03 | 210000 | 72.8 | -2.7 | 0.61 | 22.9 | -97.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.08 | -0.4 | 0.01 | 0.5 | 0 | 0 | 20.74
| 71 | 2008-06-03 | 220000 | 72.7 | -2.5 | 0.61 | 23.2 | -95.8 | 0.04 | 0.5 | 1.2 | -1 | 0.6 | -0.01 | -0.09 | -0.4 | 0 | 0 | 0 | 0 | 20.74
| 72 | 2008-06-03 | 230000 | 72.7 | -2.6 | 0.61 | 23.7 | -101.6 | 0.04 | 0.5 | 1.2 | -1 | 0.6 | -0.01 | -0.08 | -0.4 | 0.02 | 0.5 | 0 | 0 | 20.75
| 73 | 2008-06-04 | 0 | 72.8 | -2.9 | 0.6 | 23.7 | -111.5 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.06 | -0.4 | 0.01 | 0.5 | 0 | 0 | 20.75
| 74 | 2008-06-04 | 10000 | 72.8 | -2.6 | 0.6 | 23.9 | -103.3 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.06 | -0.4 | 0.01 | 0.7 | 0 | 0 | 20.75
| 75 | 2008-06-04 | 20000 | 71.7 | -2.7 | 0.6 | 24.8 | -111 | 0.04 | 0.5 | 1.2 | -1 | 0.6 | -0.01 | -0.06 | -0.4 | 0.01 | 0.2 | 0 | 0 | 20.76
| 76 | 2008-06-04 | 30000 | 71.3 | -2.6 | 0.6 | 26.2 | -112.2 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.06 | -0.4 | 0.01 | 0.3 | 0 | 0 | 20.76
| 77 | 2008-06-04 | 40000 | 71.4 | -2.7 | 0.6 | 28.1 | -124.9 | 0.04 | 0.5 | 1.3 | -1 | 0.5 | -0.01 | -0.05 | -0.5 | 0.01 | 0.6 | 0 | 0 | 20.77
| 78 | 2008-06-04 | 50000 | 71.3 | -2.7 | 0.61 | 31.9 | -135.7 | 0.04 | 0.5 | 1.3 | -1 | 0.7 | -0.01 | -0.06 | -0.6 | 0.01 | 0.5 | 0 | 0 | 20.71
| 79 | 2008-06-04 | 60000 | 71.3 | -2.5 | 0.63 | 36.1 | -145.3 | 0.04 | 0.5 | 1.3 | -6.9 | 0.6 | -0.01 | -0.06 | -0.6 | 0.02 | 0.8 | 0 | 0 | 20.8
| 80 | 2008-06-04 | 70000 | 71.3 | -2.9 | 0.64 | 41.2 | -188.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.7 | 0.02 | 0.9 | 0 | 0 | 20.81
| 81 | 2008-06-04 | 80000 | 71.3 | -2.7 | 0.62 | 46 | -208 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.8 | 0.01 | 0.5 | 0 | 0 | 20.82
| 82 | 2008-06-04 | 90000 | 72.1 | -2.7 | 0.62 | 50.7 | -218.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | 2.23 | -0.9 | 0.02 | 0.9 | 0 | 0 | 20.82
| 83 | 2008-06-04 | 100000 | 77.9 | -2.7 | 0.63 | 53.3 | -243.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.9 | 0.01 | 0.6 | 0 | 0 | 20.83
| 84 | 2008-06-04 | 110000 | 79.7 | -2.8 | 0.62 | 57.1 | -253.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -1 | 0.01 | 0.9 | 0 | 0 | 20.83
| 85 | 2008-06-04 | 120000 | 79.6 | -2.5 | 0.63 | 63.3 | -253.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1 | 0.02 | 1.4 | 0 | 0 | 20.84
| 86 | 2008-06-04 | 130000 | 79.6 | -2.7 | 0.62 | 61.6 | -264.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1 | 0.01 | 0.9 | 0 | 0 | 20.84
| 87 | 2008-06-04 | 140000 | 79.7 | -2.8 | 0.62 | 67.5 | -283.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.1 | 0.01 | 0.8 | 0 | 0 | 20.77
| 88 | 2008-06-04 | 150000 | 79.6 | -2.6 | 0.63 | 83.5 | -341 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.4 | 0.01 | 1.2 | 0 | 0 | 20.85
| 89 | 2008-06-04 | 160000 | 79.6 | -2.5 | 0.63 | 88.5 | -349.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.5 | 0.02 | 1.4 | 0 | 0 | 20.85
| 90 | 2008-06-04 | 170000 | 79.7 | -2.5 | 0.63 | 81.4 | -309.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.3 | 0 | -0.4 | 0 | 0 | 20.85
| 91 | 2008-06-04 | 180000 | 79 | -2.5 | 0.62 | 62.3 | -258.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.1 | 0.02 | 1.3 | 0 | 0 | 20.84
| 92 | 2008-06-04 | 190000 | 78.2 | -2.8 | 0.63 | 57.2 | -257.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1 | 0.02 | 1.1 | 0 | 0 | 20.76
| 93 | 2008-06-04 | 200000 | 78.2 | -2.6 | 0.62 | 54.2 | -232.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.9 | 0.01 | 0.8 | 0 | 0 | 20.83
| 94 | 2008-06-04 | 210000 | 78.2 | -2.9 | 0.62 | 53.3 | -242.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.9 | 0.01 | 0.6 | 0 | 0 | 20.83
| 95 | 2008-06-04 | 220000 | 77.9 | -2.7 | 0.62 | 51.3 | -211.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.8 | 0.01 | 0.7 | 0 | 0 | 20.83
| 96 | 2008-06-04 | 230000 | 76.3 | -2.5 | 0.64 | 45.6 | -183.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.7 | 0.01 | 0.2 | 0 | 0 | 20.81
| 97 | 2008-06-05 | 0 | 76.2 | -2.4 | 0.67 | 42.7 | -162.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.7 | 0.01 | 0.2 | 0 | 0 | 20.81
| 98 | 2008-06-05 | 10000 | 76.2 | -2.6 | 0.67 | 37.7 | -150 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.5 | 0.01 | 0.5 | 0 | 0 | 20.79
| 99 | 2008-06-05 | 20000 | 75.6 | -2.7 | 0.68 | 34.5 | -137 | 0.12 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.5 | 0.02 | 0.6 | 0 | 0 | 20.78
| 100 | 2008-06-05 | 30000 | 74.7 | -2.4 | 0.66 | 31.4 | -116 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.5 | 0.02 | 0.8 | 0 | 0 | 20.77
| 101 | 2008-06-05 | 40000 | 74.8 | -2.7 | 0.64 | 27.9 | -120 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.4 | 0.01 | 0.5 | 0 | 0 | 20.76
| 102 | 2008-06-05 | 50000 | 74.7 | -2.4 | 0.66 | 25.9 | -95.8 | 0.03 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.4 | 0.02 | 0.6 | 0 | 0 | 20.75
| 103 | 2008-06-05 | 60000 | 74.7 | -2.6 | 0.69 | 25.2 | -98.3 | 0.03 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 0.5 | 0 | 0 | 20.74
| 104 | 2008-06-05 | 70000 | 72.9 | -2.8 | 0.7 | 23.7 | -94.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.2 | 0.01 | 0.3 | 0 | 0 | 20.73
| 105 | 2008-06-05 | 80000 | 72.7 | -2.6 | 0.66 | 21.1 | -84.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.72
| 106 | 2008-06-05 | 90000 | 72.8 | -2.8 | 0.65 | 19.9 | -80.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | 2.23 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.7
| 107 | 2008-06-05 | 100000 | 72.7 | -2.7 | 0.68 | 19.5 | -81 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.2 | 0.01 | 0.1 | 0 | 0 | 20.69
| 108 | 2008-06-05 | 110000 | 72.8 | -2.8 | 0.7 | 20.6 | -80.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -0.2 | 0.01 | 0.2 | 0 | 0 | 20.7
| 109 | 2008-06-05 | 120000 | 72.8 | -2.5 | 0.7 | 19.9 | -72.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.2 | 0.01 | 0.3 | 0 | 0 | 20.69
| 110 | 2008-06-05 | 130000 | 72.7 | -2.7 | 0.67 | 18.5 | -71.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -0.2 | 0 | 0 | 0 | 0 | 20.69
| 111 | 2008-06-05 | 140000 | 72.7 | -2.3 | 0.66 | 17.3 | -63.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.2 | 0.02 | 0.3 | 0 | 0 | 20.67
| 112 | 2008-06-05 | 150000 | 72.8 | -2.3 | 0.65 | 16.8 | -59.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.05 | -0.2 | 0.01 | 0.3 | 0 | 0 | 20.67
| 113 | 2008-06-05 | 160000 | 72.8 | -2.3 | 0.64 | 16.7 | -60.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.2 | 0.02 | 0.5 | 0 | 0 | 20.67
| 114 | 2008-06-05 | 170000 | 72.7 | -2.7 | 0.65 | 16.5 | -69.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.2 | 0.01 | 0.1 | 0 | 0 | 20.67
| 115 | 2008-06-05 | 180000 | 72.8 | -2.6 | 0.62 | 16.1 | -64.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 0.4 | 0 | 0 | 20.67
| 116 | 2008-06-05 | 190000 | 72.7 | -2.6 | 0.61 | 16.7 | -69.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.05 | -0.3 | 0.01 | 0.2 | 0 | 0 | 20.68
| 117 | 2008-06-05 | 200000 | 72.8 | -2.8 | 0.62 | 18.5 | -77.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.7
| 118 | 2008-06-05 | 210000 | 71.8 | -2.4 | 0.61 | 19.3 | -74.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.4 | 0.01 | 0.4 | 0 | 0 | 20.64
| 119 | 2008-06-05 | 220000 | 71.4 | -2.7 | 0.62 | 20.6 | -93.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.4 | -0.01 | -0.06 | -0.3 | 0 | 0.2 | 0 | 0 | 20.72
| 120 | 2008-06-05 | 230000 | 71.4 | -2.6 | 0.61 | 20.4 | -84.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.07 | -0.3 | 0.01 | 0.2 | 0 | 0 | 20.65
| 121 | 2008-06-06 | 0 | 71.3 | -2.5 | 0.61 | 20.3 | -83.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.09 | -0.3 | 0 | 0.1 | 0 | 0 | 20.72
| 122 | 2008-06-06 | 10000 | 71.4 | -2.5 | 0.6 | 20 | -83.9 | 0.04 | 0.5 | 1.3 | -8.7 | 0.5 | -0.01 | -0.09 | -0.4 | 0.01 | 0.3 | 0 | 0 | 20.72
| 123 | 2008-06-06 | 20000 | 71.3 | -2.7 | 0.61 | 19.6 | -80.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.09 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.72
| 124 | 2008-06-06 | 30000 | 71.4 | -2.7 | 0.61 | 19.7 | -89.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.02 | 0.4 | 0 | 0 | 20.72
| 125 | 2008-06-06 | 40000 | 71.5 | -2.7 | 0.61 | 19.6 | -84.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.72
| 126 | 2008-06-06 | 50000 | 71.3 | -2.7 | 0.62 | 19.4 | -79.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.3 | 0.01 | 0.2 | 0 | 0 | 20.71
| 127 | 2008-06-06 | 60000 | 69.5 | -2.6 | 0.62 | 20 | -84.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -0.2 | 0.01 | 0.3 | 0 | 0 | 20.71
| 128 | 2008-06-06 | 70000 | 69.4 | -2.7 | 0.63 | 21 | -94.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.65
| 129 | 2008-06-06 | 80000 | 69.5 | -2.6 | 0.62 | 21.5 | -89.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.3 | 0.02 | 0.6 | 0 | 0 | 20.73
| 130 | 2008-06-06 | 90000 | 69.4 | -2.6 | 0.63 | 23.3 | -94.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | 2.25 | -0.3 | 0.01 | 0.4 | 0 | 0 | 20.74
| 131 | 2008-06-06 | 100000 | 69.4 | -2.6 | 0.63 | 24.4 | -102.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.75
| 132 | 2008-06-06 | 110000 | 69.4 | -2.6 | 0.63 | 25.1 | -101.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.75
| 133 | 2008-06-06 | 120000 | 69.5 | -2.5 | 0.64 | 26.2 | -106.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 0.4 | 0 | 0 | 20.76
| 134 | 2008-06-06 | 130000 | 69.4 | -2.3 | 0.62 | 27 | -107.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.5 | 0.02 | 0.7 | 0 | 0 | 20.76
| 135 | 2008-06-06 | 140000 | 69.4 | -2.7 | 0.62 | 28.6 | -129.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.05 | -0.5 | 0.01 | 0.5 | 0 | 0 | 20.77
| 136 | 2008-06-06 | 150000 | 69.4 | -2.4 | 0.62 | 31.2 | -121.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.5 | 0.02 | 0.7 | 0 | 0 | 20.78
| 137 | 2008-06-06 | 160000 | 69.5 | -2.5 | 0.62 | 33.1 | -134.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.6 | 0.01 | 0.6 | 0 | 0 | 20.71
| 138 | 2008-06-06 | 170000 | 69.4 | -2.4 | 0.62 | 36 | -134.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.6 | 0.02 | 0.9 | 0 | 0 | 20.8
| 139 | 2008-06-06 | 180000 | 69.3 | -2.7 | 0.62 | 41.3 | -182.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.7 | 0.01 | 0.3 | 0 | 0 | 20.81
| 140 | 2008-06-06 | 190000 | 69.4 | -2.7 | 0.62 | 51.8 | -220.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.9 | 0.02 | 1.1 | 0 | 0 | 20.83
| 141 | 2008-06-06 | 200000 | 69.3 | -2.8 | 0.62 | 68.2 | -303.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -1.2 | 0.01 | 0.5 | 0 | 0 | 20.84
| 142 | 2008-06-06 | 210000 | 69.3 | -2.5 | 0.62 | 76.6 | -305.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -1.2 | 0.01 | 0.7 | 0 | 0 | 20.85
| 143 | 2008-06-06 | 220000 | 69.4 | -2.6 | 0.63 | 113.1 | -446.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -2 | 0.01 | 1 | 6.3 | 0 | 20.86
| 144 | 2008-06-06 | 230000 | 69.4 | -2.6 | 0.63 | 144.4 | -584 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -2.4 | 0.01 | 1.7 | 87.1 | 0 | 20.87
| 145 | 2008-06-07 | 0 | 69.4 | -2.7 | 0.63 | 158.9 | -736.8 | 0.04 | 0.5 | 1.3 | -8.7 | 0.6 | -0.01 | -0.05 | -2.6 | 0.02 | 3.5 | 115.6 | 0 | 20.88
| 146 | 2008-06-07 | 10000 | 69.3 | -2.5 | 0.63 | 162.8 | -675.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -2.9 | 0.01 | 5.1 | 182 | 0 | 20.88
| 147 | 2008-06-07 | 20000 | 69.4 | -2.6 | 0.62 | 147.4 | -574 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -2.5 | 0.01 | 6 | 373.6 | 0 | 20.89
| 148 | 2008-06-07 | 30000 | 69.3 | -2.9 | 0.62 | 103.2 | -475.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -2 | 0.02 | 6 | 642.6 | 0 | 20.9
| 149 | 2008-06-07 | 40000 | 69.4 | -2.7 | 0.62 | 49.3 | -199.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.8 | 0.02 | 3.2 | 978.1 | 0 | 20.91
| 150 | 2008-06-07 | 50000 | 69.3 | -2.5 | 0.63 | 16.3 | -94.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 1.7 | 568.2 | 1.6 | 20.92
| 151 | 2008-06-07 | 60000 | 69.4 | -2.8 | 0.62 | 1.5 | -4.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0.1 | 324.5 | 0 | 20.85
| 152 | 2008-06-07 | 70000 | 69.4 | -2.5 | 0.63 | 5.2 | -16.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.1 | 0.02 | 0.6 | 234.3 | 0 | 20.93
| 153 | 2008-06-07 | 80000 | 69.4 | -2.5 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.7 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 49.1 | 0 | 20.94
| 154 | 2008-06-07 | 90000 | 69.4 | -2.5 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | 2.26 | 0 | 0.01 | 0 | 11.1 | 0 | 20.87
| 155 | 2008-06-07 | 100000 | 69.5 | -2.8 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 26.9 | 0 | 20.95
| 156 | 2008-06-07 | 110000 | 69.5 | -2.6 | 0.62 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 26.9 | 0 | 20.94
| 157 | 2008-06-07 | 120000 | 69.4 | -2.6 | 0.62 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.95
| 158 | 2008-06-07 | 130000 | 69.4 | -2.3 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.95
| 159 | 2008-06-07 | 140000 | 69.4 | -3.1 | 0.62 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.95
| 160 | 2008-06-07 | 150000 | 69.5 | -2.7 | 0.63 | 0 | 0 | 0.05 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.02 | 0 | 0 | 0 | 20.95
| 161 | 2008-06-07 | 160000 | 69.3 | -2.1 | 0.62 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 162 | 2008-06-07 | 170000 | 69.5 | -2.6 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.88
| 163 | 2008-06-07 | 180000 | 70 | -2.6 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 164 | 2008-06-07 | 190000 | 69.6 | -2.7 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 165 | 2008-06-07 | 200000 | 69.5 | -2.6 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.88
| 166 | 2008-06-07 | 210000 | 69.4 | -2.5 | 0.64 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 167 | 2008-06-07 | 220000 | 69.4 | -2.6 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.89
| 168 | 2008-06-07 | 230000 | 69.4 | -2.7 | 0.62 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.89
| 169 | 2008-06-08 | 0 | 69.4 | -2.6 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 170 | 2008-06-08 | 10000 | 69.5 | -2.6 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 171 | 2008-06-08 | 20000 | 69.4 | -2.6 | 0.62 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 172 | 2008-06-08 | 30000 | 69.4 | -2.6 | 0.62 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.95
| 173 | 2008-06-08 | 40000 | 69.4 | -2.8 | 0.62 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | 0 | 0.01 | 0 | 26.9 | 0 | 20.87
| 174 | 2008-06-08 | 50000 | 69.4 | -2.6 | 0.62 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.02 | 0 | 53.8 | 0 | 20.87
| 175 | 2008-06-08 | 60000 | 69.4 | -2.7 | 0.62 | 1.9 | 7.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0.4 | 128.2 | 0 | 20.94
| 176 | 2008-06-08 | 70000 | 69.4 | -2.4 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 22.2 | 0 | 20.94
| 177 | 2008-06-08 | 80000 | 69.4 | -2.7 | 0.63 | 1.6 | -9.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0.3 | 52.2 | 0 | 20.94
| 178 | 2008-06-08 | 90000 | 69.4 | -2.7 | 0.63 | 1 | -4.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | 2.26 | 0 | 0.01 | 0.1 | 169.4 | 0 | 20.94
| 179 | 2008-06-08 | 100000 | 69.5 | -2.5 | 0.63 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 188.4 | 0 | 20.86
| 180 | 2008-06-08 | 110000 | 69.5 | -2.6 | 0.62 | 8.2 | -40.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | -0.1 | 0.01 | 0.6 | 246.9 | 0 | 20.93
| 181 | 2008-06-08 | 120000 | 69.5 | -2.8 | 0.63 | 6.8 | -29.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.2 | 0.01 | 1.1 | 466.9 | 3.2 | 20.92
| 182 | 2008-06-08 | 130000 | 69.4 | -2.7 | 0.64 | 5.2 | -28.7 | 0.1 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.1 | 0.01 | 1.1 | 457.4 | 1.6 | 20.92
| 183 | 2008-06-08 | 140000 | 69.4 | -2.8 | 0.64 | 52.3 | -204.2 | 0.21 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.9 | 0.01 | 3.7 | 807.2 | 0 | 20.91
| 184 | 2008-06-08 | 150000 | 69.5 | -2.6 | 0.64 | 100.6 | -381.2 | 0.12 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.6 | 0 | 2.9 | 497 | 0 | 20.9
| 185 | 2008-06-08 | 160000 | 69.4 | -2.5 | 0.64 | 164.8 | -652.8 | 0.09 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -2.9 | 0.01 | 2.4 | 117.1 | 0 | 20.88
| 186 | 2008-06-08 | 170000 | 70.1 | -2.5 | 0.65 | 120.6 | -449.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -1.9 | 0.01 | 0.3 | 0 | 0 | 20.86
| 187 | 2008-06-08 | 180000 | 71.4 | -2.5 | 0.65 | 83.2 | -319.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -1.3 | 0.01 | 1.3 | 0 | 0 | 20.78
| 188 | 2008-06-08 | 190000 | 71.3 | -2.7 | 0.65 | 71.7 | -302.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.2 | 0.02 | 1.1 | 0 | 0 | 20.84
| 189 | 2008-06-08 | 200000 | 71.4 | -2.6 | 0.65 | 63.7 | -253.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.1 | 0.01 | 0.5 | 0 | 0 | 20.84
| 190 | 2008-06-08 | 210000 | 71.4 | -2.4 | 0.65 | 58.1 | -217.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1 | 0.02 | 1 | 0 | 0 | 20.76
| 191 | 2008-06-08 | 220000 | 71.3 | -2.5 | 0.66 | 61.2 | -234.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1 | 0.02 | 1.1 | 0 | 0 | 20.83
| 192 | 2008-06-08 | 230000 | 69.4 | -2.5 | 0.65 | 49.3 | -190.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.7 | 0.01 | 0.8 | 0 | 0 | 20.82
| 193 | 2008-06-09 | 0 | 69.3 | -2.6 | 0.65 | 46.2 | -188.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.7 | 0.01 | 0.8 | 0 | 0 | 20.81
| 194 | 2008-06-09 | 10000 | 69.4 | -2.5 | 0.65 | 41.5 | -154.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.6 | 0.01 | 0.8 | 0 | 0 | 20.73
| 195 | 2008-06-09 | 20000 | 69.4 | -2.6 | 0.65 | 42.2 | -169.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -0.7 | 0.01 | 0.6 | 0 | 0 | 20.81
| 196 | 2008-06-09 | 30000 | 69.4 | -2.6 | 0.65 | 40.4 | -165 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -0.7 | 0.01 | 0.3 | 0 | 0 | 20.8
| 197 | 2008-06-09 | 40000 | 69.4 | -2.5 | 0.65 | 37.1 | -141.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.6 | 0.01 | 0.4 | 0 | 0 | 20.79
| 198 | 2008-06-09 | 50000 | 69.4 | -2.7 | 0.65 | 33.8 | -135.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.5 | 0.01 | 0.4 | 0 | 0 | 20.78
| 199 | 2008-06-09 | 60000 | 69.4 | -2.7 | 0.67 | 31.2 | -130 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.5 | 0.01 | 0.4 | 0 | 0 | 20.77
| 200 | 2008-06-09 | 70000 | 69.3 | -2.6 | 0.69 | 29.6 | -122.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.05 | -0.4 | 0.01 | 0.4 | 0 | 0 | 20.76
| 201 | 2008-06-09 | 80000 | 69.4 | -2.6 | 0.67 | 27 | -99.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.4 | 0.02 | 0.6 | 0 | 0 | 20.75
| 202 | 2008-06-09 | 90000 | 69.4 | -2.8 | 0.68 | 25.3 | -102.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | 2.24 | -0.4 | 0.01 | 0.4 | 0 | 0 | 20.67
| 203 | 2008-06-09 | 100000 | 69.4 | -2.7 | 0.68 | 23.9 | -90.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.66
| 204 | 2008-06-09 | 110000 | 69.4 | -2.5 | 0.68 | 22.9 | -80.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.3 | 0.01 | 0.4 | 0 | 0 | 20.72
| 205 | 2008-06-09 | 120000 | 69.4 | -2.6 | 0.69 | 22.2 | -87.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.02 | 0.5 | 0 | 0 | 20.72
| 206 | 2008-06-09 | 130000 | 69.4 | -2.5 | 0.69 | 21.1 | -81.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.3 | 0.01 | 0.2 | 0 | 0 | 20.71
| 207 | 2008-06-09 | 140000 | 69.4 | -2.8 | 0.66 | 19.6 | -82.2 | 0.05 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 0.2 | 0 | 0 | 20.7
| 208 | 2008-06-09 | 150000 | 69.5 | -2.7 | 0.63 | 17.7 | -76 | 0.18 | 0.5 | 1.2 | -8.6 | 0.4 | -0.01 | -0.06 | -0.3 | 0.01 | 0.2 | 0 | 0 | 20.69
| 209 | 2008-06-09 | 160000 | 69.5 | -2.5 | 0.62 | 17.9 | -70.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.4 | -0.01 | -0.07 | -0.3 | 0.01 | 0.3 | 0 | 0 | 20.69
| 210 | 2008-06-09 | 170000 | 69.4 | -2.6 | 0.62 | 18 | -74.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.02 | 0.4 | 0 | 0 | 20.69
| 211 | 2008-06-09 | 180000 | 69.5 | -2.7 | 0.63 | 19 | -79.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.02 | 0.4 | 0 | 0 | 20.63
| 212 | 2008-06-09 | 190000 | 69.4 | -2.6 | 0.64 | 23 | -90.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.09 | -0.4 | 0.01 | 0.3 | 0 | 0 | 20.73
| 213 | 2008-06-09 | 200000 | 69.4 | -2.5 | 0.64 | 25 | -98.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.09 | -0.4 | 0.01 | 0.5 | 0 | 0 | 20.75
| 214 | 2008-06-09 | 210000 | 69.4 | -2.7 | 0.64 | 26.4 | -107.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.09 | -0.5 | 0.01 | 0.1 | 0 | 0 | 20.75
| 215 | 2008-06-09 | 220000 | 69.3 | -2.5 | 0.64 | 28.3 | -110.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.08 | -0.4 | 0.02 | 0.6 | 0 | 0 | 20.77
| 216 | 2008-06-09 | 230000 | 69.4 | -2.2 | 0.63 | 26.8 | -98 | 0.22 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.5 | 0.01 | 0.5 | 0 | 0 | 20.76
| 217 | 2008-06-10 | 0 | 69.4 | -2.5 | 0.64 | 24.5 | -100.1 | 0.21 | 0.5 | 1.2 | -8.6 | 0.4 | -0.01 | -0.06 | -0.4 | 0.01 | 0.4 | 0 | 0 | 20.74
| 218 | 2008-06-10 | 10000 | 69.3 | -2.6 | 0.63 | 23 | -93.5 | 0.11 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | -0.4 | 0.01 | 0.3 | 0 | 0 | 20.74
| 219 | 2008-06-10 | 20000 | 68.5 | -2.9 | 0.63 | 22.7 | -105 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | -0.4 | 0.01 | 0.2 | 0 | 0 | 20.66
| 220 | 2008-06-10 | 30000 | 67.9 | -2.7 | 0.64 | 23.7 | -104.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.08 | -0.4 | 0.01 | 0.2 | 0 | 0 | 20.74
| 221 | 2008-06-10 | 40000 | 67.9 | -2.8 | 0.64 | 26.1 | -117.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.3 | -0.01 | -0.08 | -0.4 | 0.01 | 0.6 | 0 | 0 | 20.75
| 222 | 2008-06-10 | 50000 | 68 | -2.6 | 0.64 | 28.6 | -114.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.09 | -0.5 | 0.01 | 0.3 | 0 | 0 | 20.77
| 223 | 2008-06-10 | 60000 | 67.8 | -2.4 | 0.64 | 33.6 | -126.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.09 | -0.5 | 0.01 | 0.5 | 0 | 0 | 20.78
| 224 | 2008-06-10 | 70000 | 67.8 | -2.6 | 0.64 | 38.9 | -149.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.09 | -0.6 | 0.01 | 0.6 | 0 | 0 | 20.8
| 225 | 2008-06-10 | 80000 | 67.9 | -2.8 | 0.65 | 40.6 | -170.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.08 | -0.7 | 0.01 | 0.6 | 0 | 0 | 20.8
| 226 | 2008-06-10 | 90000 | 67.9 | -2.7 | 0.64 | 45.4 | -188.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | 2.23 | -0.7 | 0.01 | 0.4 | 0 | 0 | 20.81
| 227 | 2008-06-10 | 100000 | 67.9 | -2.8 | 0.64 | 55.8 | -250.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.9 | 0.01 | 0.3 | 0 | 0 | 20.83
| 228 | 2008-06-10 | 110000 | 67.9 | -2.8 | 0.65 | 77.5 | -335.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -1.2 | 0.01 | 1 | 0 | 0 | 20.85
| 229 | 2008-06-10 | 120000 | 67.9 | -2.7 | 0.65 | 115.3 | -503.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -2 | 0.01 | 0.5 | 0 | 0 | 20.86
| 230 | 2008-06-10 | 130000 | 67.9 | -2.4 | 0.64 | 148.3 | -552.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | -2.5 | 0.01 | 1.4 | 79.2 | 0 | 20.87
| 231 | 2008-06-10 | 140000 | 67.9 | -2.7 | 0.64 | 135.3 | -573.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -2.2 | 0.01 | 3.7 | 349.8 | 3.2 | 20.89
| 232 | 2008-06-10 | 150000 | 67.9 | -2.6 | 0.65 | 76.3 | -311.5 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.5 | 0.02 | 4.8 | 775.6 | 0 | 20.9
| 233 | 2008-06-10 | 160000 | 67.9 | -2.6 | 0.65 | 30.1 | -161.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.5 | 0.01 | 1.7 | 557.1 | 1.6 | 20.91
| 234 | 2008-06-10 | 170000 | 68.2 | -2.4 | 0.66 | 4.4 | -16.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.05 | -0.1 | 0.01 | 0.4 | 264.3 | 0 | 20.86
| 235 | 2008-06-10 | 180000 | 67.9 | -2.6 | 0.66 | 1.6 | -12.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0.1 | 170.9 | 0 | 20.94
| 236 | 2008-06-10 | 190000 | 68 | -2.8 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.07 | 0 | 0.01 | 0 | 53.8 | 0 | 20.94
| 237 | 2008-06-10 | 200000 | 67.9 | -2.7 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.5 | 0.6 | -0.01 | -0.08 | 0 | 0.02 | 0 | 15.8 | 0 | 20.95
| 238 | 2008-06-10 | 210000 | 67.8 | -2.8 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 239 | 2008-06-10 | 220000 | 67.8 | -2.4 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | 0 | 0.01 | 0 | 0 | 0 | 20.97
| 240 | 2008-06-10 | 230000 | 67.8 | -2.5 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.02 | 0 | 0 | 0 | 20.97
| 241 | 2008-06-11 | 0 | 67.8 | -2.6 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | 0 | 0.02 | 0 | 0 | 0 | 20.98
| 242 | 2008-06-11 | 10000 | 67.9 | -2.5 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.99
| 243 | 2008-06-11 | 20000 | 67.9 | -2.6 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.05 | 0 | 0.01 | 0 | 0 | 0 | 20.99
| 244 | 2008-06-11 | 30000 | 67.8 | -2.6 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.02 | 0 | 0 | 0 | 20.98
| 245 | 2008-06-11 | 40000 | 67.9 | -2.6 | 0.65 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 246 | 2008-06-11 | 50000 | 67.9 | -2.7 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.99
| 247 | 2008-06-11 | 60000 | 67.8 | -2.7 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.99
| 248 | 2008-06-11 | 70000 | 67.9 | -2.6 | 0.71 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.99
| 249 | 2008-06-11 | 80000 | 67.9 | -2.5 | 0.72 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 21
| 250 | 2008-06-11 | 90000 | 67.8 | -2.6 | 0.71 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | 2.3 | 0 | 0.01 | 0 | 0 | 0 | 20.92
| 251 | 2008-06-11 | 100000 | 67.9 | -2.8 | 0.7 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 21
| 252 | 2008-06-11 | 110000 | 67.9 | -2.4 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 21
| 253 | 2008-06-11 | 120000 | 67.9 | -2.8 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.05 | 0 | 0.01 | 0 | 0 | 0 | 21
| 254 | 2008-06-11 | 130000 | 67.8 | -2.5 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -7.7 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 21
| 255 | 2008-06-11 | 140000 | 67.9 | -2.6 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.99
| 256 | 2008-06-11 | 150000 | 67.9 | -2.7 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.99
| 257 | 2008-06-11 | 160000 | 67.9 | -2.8 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.4 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 258 | 2008-06-11 | 170000 | 67.9 | -2.5 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 259 | 2008-06-11 | 180000 | 67.8 | -2.2 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.97
| 260 | 2008-06-11 | 190000 | 67.9 | -2.8 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.97
| 261 | 2008-06-11 | 200000 | 68 | -2.5 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.97
| 262 | 2008-06-11 | 210000 | 67.9 | -2.8 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.4 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.97
| 263 | 2008-06-11 | 220000 | 68 | -2.6 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 264 | 2008-06-11 | 230000 | 67.9 | -2.6 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.4 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 265 | 2008-06-12 | 0 | 67.9 | -2.6 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 266 | 2008-06-12 | 10000 | 67.8 | -2.6 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 267 | 2008-06-12 | 20000 | 67.9 | -2.5 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.97
| 268 | 2008-06-12 | 30000 | 67.9 | -2.8 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.97
| 269 | 2008-06-12 | 40000 | 67.9 | -2.4 | 0.66 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.9
| 270 | 2008-06-12 | 50000 | 67.9 | -2.8 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.9
| 271 | 2008-06-12 | 60000 | 67.9 | -2.5 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 272 | 2008-06-12 | 70000 | 67.9 | -2.7 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 273 | 2008-06-12 | 80000 | 68 | -2.5 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 274 | 2008-06-12 | 90000 | 67.8 | -2.8 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | 2.27 | 0 | 0.01 | 0 | 0 | 0 | 20.91
| 275 | 2008-06-12 | 100000 | 68 | -2.5 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0 | 0 | 0 | 0 | 20.98
| 276 | 2008-06-12 | 110000 | 67.8 | -2.7 | 0.67 | 0 | 0 | 0.05 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.98
| 277 | 2008-06-12 | 120000 | 67.9 | -2.5 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.97
| 278 | 2008-06-12 | 130000 | 67.9 | -2.7 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 279 | 2008-06-12 | 140000 | 68.1 | -2.6 | 0.67 | 0 | 0 | 0.21 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.02 | 0 | 3.2 | 0 | 20.87
| 280 | 2008-06-12 | 150000 | 69.5 | -2.6 | 0.67 | 0 | 0 | 0.17 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 23.7 | 0 | 20.94
| 281 | 2008-06-12 | 160000 | 69.4 | -2.9 | 0.67 | 15.5 | -44.5 | 0.05 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -0.3 | 0.01 | 1.2 | 288.1 | 0 | 20.92
| 282 | 2008-06-12 | 170000 | 69.5 | -2.8 | 0.67 | 17.5 | -80.6 | 0.16 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.3 | 0.01 | 1.1 | 554 | 0 | 20.91
| 283 | 2008-06-12 | 180000 | 69.4 | -2.7 | 0.68 | 94.4 | -389.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.07 | -1.6 | 0.01 | 3.6 | 493.8 | 0 | 20.9
| 284 | 2008-06-12 | 190000 | 70.5 | -2.6 | 0.67 | 121.5 | -422.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -2.1 | 0.01 | 5.5 | 455.9 | 0 | 20.9
| 285 | 2008-06-12 | 200000 | 71.2 | -2.5 | 0.68 | 45.9 | -167.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.7 | 0.02 | 3.5 | 867.4 | 0 | 20.91
| 286 | 2008-06-12 | 210000 | 71.4 | -2.6 | 0.68 | 14.1 | -83.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.3 | 0.01 | 1.4 | 438.4 | 0 | 20.92
| 287 | 2008-06-12 | 220000 | 71.4 | -2.6 | 0.68 | 4.4 | -24.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.1 | 0 | 0.6 | 262.7 | 0 | 20.93
| 288 | 2008-06-12 | 230000 | 71.3 | -2.5 | 0.68 | 3.8 | -30.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0.2 | 305.5 | 0 | 20.93
| 289 | 2008-06-13 | 0 | 70.2 | -2.5 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | 0 | 0.01 | 0 | 163 | 0 | 20.86
| 290 | 2008-06-13 | 10000 | 69.4 | -2.4 | 0.68 | 5 | -14.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.05 | -0.1 | 0.01 | 1 | 307.1 | 0 | 20.93
| 291 | 2008-06-13 | 20000 | 69.4 | -2.6 | 0.68 | 4.8 | -24.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 335.6 | 0 | 20.92
| 292 | 2008-06-13 | 30000 | 69.3 | -2.4 | 0.68 | 9 | -12.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.1 | 0.01 | 0.5 | 547.6 | 0 | 20.92
| 293 | 2008-06-13 | 40000 | 69.4 | -2.5 | 0.68 | 15 | -57.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.3 | 0.01 | 2.2 | 462.2 | 0 | 20.92
| 294 | 2008-06-13 | 50000 | 69.4 | -2.5 | 0.68 | 3.9 | -22.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 341.9 | 0 | 20.92
| 295 | 2008-06-13 | 60000 | 69.3 | -2.5 | 0.69 | 6.9 | -15.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.1 | 0.01 | 0.4 | 573 | 0 | 20.92
| 296 | 2008-06-13 | 70000 | 69.3 | -2.6 | 0.7 | 5.8 | -19.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.1 | 0.01 | 0.1 | 436.8 | 0 | 20.93
| 297 | 2008-06-13 | 80000 | 69.4 | -2.6 | 0.7 | 1.2 | -3.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0.1 | 106.1 | 0 | 20.93
| 298 | 2008-06-13 | 90000 | 69.4 | -2.7 | 0.69 | 0.5 | -4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | 2.27 | 0 | 0.02 | 0.1 | 126.6 | 1.6 | 20.93
| 299 | 2008-06-13 | 100000 | 70.8 | -2.6 | 0.69 | 2.2 | -8.8 | 0.1 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0.3 | 258 | 0 | 20.93
| 300 | 2008-06-13 | 110000 | 71.4 | -2.7 | 0.68 | 3.3 | -2.3 | 0.06 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.02 | 0.1 | 509.7 | 0 | 20.92
| 301 | 2008-06-13 | 120000 | 71.5 | -2.6 | 0.67 | 12.6 | -53.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -0.3 | 0.01 | 1.2 | 598.3 | 0 | 20.92
| 302 | 2008-06-13 | 130000 | 71.4 | -2.6 | 0.67 | 59.4 | -236.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -1.1 | 0 | 2.7 | 588.8 | 0 | 20.91
| 303 | 2008-06-13 | 140000 | 71.3 | -2.9 | 0.67 | 57.8 | -293.7 | 0.24 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.9 | 0.02 | 3.1 | 891.1 | 0 | 20.9
| 304 | 2008-06-13 | 150000 | 71.3 | -2.5 | 0.66 | 67.7 | -260.4 | 0.17 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.3 | 0.01 | 4.3 | 666.4 | 0 | 20.9
| 305 | 2008-06-13 | 160000 | 71.4 | -2.7 | 0.67 | 68.7 | -315.5 | 0.09 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.2 | 0.01 | 3.1 | 702.8 | 0 | 20.83
| 306 | 2008-06-13 | 170000 | 71.6 | -2.6 | 0.68 | 89.7 | -374.5 | 0.05 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.5 | 0.01 | 2.6 | 789.8 | 0 | 20.82
| 307 | 2008-06-13 | 180000 | 72.7 | -2.3 | 0.68 | 121.5 | -399.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.05 | -1.9 | 0.02 | 4.4 | 593.5 | 0 | 20.89
| 308 | 2008-06-13 | 190000 | 72.7 | -2.7 | 0.68 | 78.6 | -281 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.3 | 0.01 | 2.2 | 702.8 | 0 | 20.9
| 309 | 2008-06-13 | 200000 | 72.7 | -2.5 | 0.68 | 17.6 | -73.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.08 | -0.3 | 0.01 | 0.7 | 398.9 | 1.6 | 20.84
| 310 | 2008-06-13 | 210000 | 72.7 | -2.6 | 0.69 | 1.2 | -1.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.08 | 0 | 0.01 | 0.4 | 155.1 | 0 | 20.93
| 311 | 2008-06-13 | 220000 | 71.4 | -2.7 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.08 | 0 | 0.01 | 0 | 185.2 | 0 | 20.86
| 312 | 2008-06-13 | 230000 | 71.4 | -2.5 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.08 | 0 | 0.01 | 0 | 19 | 0 | 20.94
| 313 | 2008-06-14 | 0 | 71.4 | -2.6 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.08 | 0 | 0.01 | 0 | 63.3 | 0 | 20.87
| 314 | 2008-06-14 | 10000 | 71.5 | -2.6 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.08 | 0 | 0.01 | 0 | 26.9 | 0 | 20.94
| 315 | 2008-06-14 | 20000 | 71.4 | -2.7 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.07 | 0 | 0.01 | 0 | 3.2 | 0 | 20.94
| 316 | 2008-06-14 | 30000 | 71.4 | -2.5 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0.01 | 0 | 7.9 | 0 | 20.94
| 317 | 2008-06-14 | 40000 | 71.3 | -2.5 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 69.6 | 0 | 20.94
| 318 | 2008-06-14 | 50000 | 69.8 | -2.6 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.05 | 0 | 0.01 | 0 | 0 | 0 | 20.94
| 319 | 2008-06-14 | 60000 | 69.4 | -2.5 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.95
| 320 | 2008-06-14 | 70000 | 69.5 | -2.7 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | 0 | 0 | 0 | 0 | 0 | 20.96
| 321 | 2008-06-14 | 80000 | 69.5 | -2.7 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 0 | 0 | 20.96
| 322 | 2008-06-14 | 90000 | 69.4 | -2.6 | 0.68 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | 2.24 | 0 | 0 | 0 | 0 | 0 | 20.96
| 323 | 2008-06-14 | 100000 | 70.5 | -2.6 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.05 | 0 | 0 | 0 | 0 | 0 | 20.95
| 324 | 2008-06-14 | 110000 | 71.3 | -2.6 | 0.67 | 0 | 0 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.05 | 0 | 0.01 | 0 | 3.2 | 0 | 20.94
| 325 | 2008-06-14 | 120000 | 71.4 | -2.4 | 0.67 | 0 | 0 | 0.19 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 85.5 | 0 | 20.93
| 326 | 2008-06-14 | 130000 | 71.4 | -2.6 | 0.67 | 5.9 | -21.4 | 0.12 | 0.5 | 1.2 | -7.8 | 0.6 | -0.01 | -0.06 | -0.1 | 0.01 | 0.5 | 406.8 | 0 | 20.85
| 327 | 2008-06-14 | 140000 | 71.3 | -2.8 | 0.68 | 24.5 | -100.6 | 0.24 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.05 | -0.4 | 0.01 | 1.6 | 620.5 | 0 | 20.91
| 328 | 2008-06-14 | 150000 | 71.5 | -2.3 | 0.69 | 47.8 | -169.4 | 0.16 | 0.5 | 1.2 | -8.6 | 0.4 | -0.01 | -0.06 | -0.9 | 0.01 | 2.8 | 761.3 | 0 | 20.91
| 329 | 2008-06-14 | 160000 | 71.4 | -2.5 | 0.68 | 106.6 | -438.4 | 0.1 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -2 | 0 | 3.1 | 379.9 | 1.6 | 20.9
| 330 | 2008-06-14 | 170000 | 71.4 | -2.8 | 0.68 | 165 | -668.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -2.8 | 0.01 | 3.1 | 158.3 | 0 | 20.89
| 331 | 2008-06-14 | 180000 | 72.6 | -2.7 | 0.69 | 193.2 | -748.9 | 0.04 | 0.5 | 1.3 | -7.8 | 0.5 | -0.01 | -0.06 | -3 | 0 | -0.5 | 77.6 | 1.6 | 20.88
| 332 | 2008-06-14 | 190000 | 72.8 | -2.8 | 0.69 | 172.1 | -725 | 0.04 | 0.5 | 1.2 | -6.9 | 0.5 | -0.01 | -0.05 | -2.6 | 0.01 | 1.6 | 66.5 | 0 | 20.88
| 333 | 2008-06-14 | 200000 | 72.8 | -2.8 | 0.69 | 171.2 | -707.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.07 | -2.8 | 0 | -0.5 | 186.8 | 1.6 | 20.81
| 334 | 2008-06-14 | 210000 | 72.8 | -2.7 | 0.69 | 172.1 | -697.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -2.6 | 0.01 | 3.7 | 177.3 | 0 | 20.89
| 335 | 2008-06-14 | 220000 | 71.8 | -2.4 | 0.69 | 124.6 | -496.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.8 | 0.01 | 4.7 | 324.5 | 0 | 20.9
| 336 | 2008-06-14 | 230000 | 71.5 | -2.7 | 0.69 | 108.9 | -418.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.8 | 0.01 | 3.8 | 455.8 | 1.6 | 20.9
| 337 | 2008-06-15 | 0 | 71.4 | -2.8 | 0.7 | 52.8 | -222.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.1 | 0.01 | 3.6 | 793 | 0 | 20.91
| 338 | 2008-06-15 | 10000 | 71.4 | -2.7 | 0.7 | 30.6 | -151.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -0.5 | 0 | 1.2 | 634.7 | 0 | 20.91
| 339 | 2008-06-15 | 20000 | 71.4 | -2.4 | 0.7 | 42.7 | -132.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -0.6 | 0.01 | 2.8 | 652.1 | 0 | 20.91
| 340 | 2008-06-15 | 30000 | 71.4 | -2.9 | 0.69 | 62.4 | -279.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.1 | 0.01 | 2.4 | 736 | 0 | 20.9
| 341 | 2008-06-15 | 40000 | 71.4 | -2.7 | 0.7 | 61.9 | -223.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1 | 0.01 | 3.6 | 857.9 | 0 | 20.91
| 342 | 2008-06-15 | 50000 | 71.4 | -2.6 | 0.7 | 48.2 | -189.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.8 | 0 | 2.2 | 528.7 | 0 | 20.91
| 343 | 2008-06-15 | 60000 | 71.4 | -2.4 | 0.71 | 27.9 | -75.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.5 | 0.01 | 1.8 | 506.5 | 0 | 20.91
| 344 | 2008-06-15 | 70000 | 71.5 | -2.9 | 0.72 | 31.8 | -115.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.5 | 0.01 | 1.8 | 617.3 | 0 | 20.91
| 345 | 2008-06-15 | 80000 | 71.4 | -2.8 | 0.71 | 42 | -142 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -0.8 | 0.01 | 2.5 | 743.9 | 1.6 | 20.91
| 346 | 2008-06-15 | 90000 | 71.3 | -2.6 | 0.71 | 53.4 | -204.6 | 0.1 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | 2.26 | -0.9 | 0.01 | 2.9 | 648.9 | 0 | 20.91
| 347 | 2008-06-15 | 100000 | 71.3 | -2.6 | 0.72 | 88.1 | -305.2 | 0.07 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.4 | 0 | 3.5 | 615.7 | 0 | 20.9
| 348 | 2008-06-15 | 110000 | 71.4 | -2.5 | 0.72 | 140.5 | -494.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -2.3 | 0.01 | 4.6 | 397.3 | 0 | 20.89
| 349 | 2008-06-15 | 120000 | 71.4 | -2.3 | 0.71 | 193.8 | -605.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -3 | 0.01 | 2.9 | 248.5 | 0 | 20.81
| 350 | 2008-06-15 | 130000 | 71.8 | -2.7 | 0.71 | 184.6 | -696.8 | 0.06 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -2.9 | 0 | 0 | 52.3 | 0 | 20.88
| 351 | 2008-06-15 | 140000 | 72.7 | -2.6 | 0.72 | 150.7 | -524 | 0.26 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -2.2 | 0.01 | 0.2 | 15.8 | 0 | 20.79
| 352 | 2008-06-15 | 150000 | 72.7 | -2.7 | 0.72 | 129.2 | -482.8 | 0.17 | 0.5 | 1.3 | -7.1 | 0.5 | -0.01 | -0.06 | -2 | 0.01 | -0.2 | 0 | 0 | 20.86
| 353 | 2008-06-15 | 160000 | 72.7 | -2.6 | 0.72 | 100.9 | -367.3 | 0.09 | 0.5 | 1.3 | -8.6 | 0.5 | -0.01 | -0.06 | -1.5 | 0.01 | 0.5 | 0 | 0 | 20.85
| 354 | 2008-06-15 | 170000 | 72.8 | -2.8 | 0.71 | 81 | -324.7 | 0.09 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.3 | 0.01 | 0.6 | 0 | 0 | 20.77
| 355 | 2008-06-15 | 180000 | 72.8 | -2.4 | 0.71 | 76.1 | -279.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.2 | 0.01 | 0.1 | 0 | 0 | 20.84
| 356 | 2008-06-15 | 190000 | 72.7 | -2.7 | 0.72 | 74.4 | -277.5 | 0.04 | 0.5 | 1.3 | -7.1 | 0.7 | -0.01 | -0.06 | -1.2 | 0.01 | 0.9 | 0 | 0 | 20.84
| 357 | 2008-06-15 | 200000 | 72.7 | -2.9 | 0.72 | 78.3 | -306.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.05 | -1.3 | 0.01 | -0.1 | 0 | 0 | 20.84
| 358 | 2008-06-15 | 210000 | 72.7 | -2.5 | 0.72 | 98.5 | -333.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.5 | 0.01 | 0.6 | 0 | 0 | 20.85
| 359 | 2008-06-15 | 220000 | 72.8 | -2.4 | 0.72 | 101.8 | -315.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.6 | 0.01 | 1 | 0 | 0 | 20.78
| 360 | 2008-06-15 | 230000 | 72.7 | -2.5 | 0.72 | 102.7 | -400.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -1.4 | 0.01 | 0.4 | 0 | 0 | 20.85
| 361 | 2008-06-16 | 0 | 72.8 | -2.7 | 0.71 | 103.9 | -393.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.07 | -1.5 | 0.01 | 0.9 | 0 | 0 | 20.86
| 362 | 2008-06-16 | 10000 | 72.8 | -2.7 | 0.71 | 94.9 | -369.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -1.4 | 0 | -0.5 | 0 | 0 | 20.85
| 363 | 2008-06-16 | 20000 | 72.8 | -2.9 | 0.7 | 80.3 | -328.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.4 | 0.01 | 0.8 | 0 | 0 | 20.84
| 364 | 2008-06-16 | 30000 | 72.5 | -2.8 | 0.7 | 76.7 | -304.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | -1.1 | 0.01 | -0.3 | 0 | 0 | 20.84
| 365 | 2008-06-16 | 40000 | 71.3 | -2.4 | 0.7 | 80 | -273.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.2 | 0.01 | 0.5 | 0 | 0 | 20.77
| 366 | 2008-06-16 | 50000 | 71.3 | -2.8 | 0.7 | 90.2 | -331.6 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | -1.4 | 0.01 | 0.7 | 0 | 0 | 20.85
| 367 | 2008-06-16 | 60000 | 71.3 | -2.7 | 0.7 | 102.7 | -388.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.06 | -1.6 | 0.01 | 0.3 | 0 | 0 | 20.85
| 368 | 2008-06-16 | 70000 | 71.3 | -2.5 | 0.71 | 94 | -337.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.4 | 0.01 | 1.1 | 0 | 0 | 20.85
| 369 | 2008-06-16 | 80000 | 71.3 | -2.7 | 0.7 | 94.9 | -373.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -1.4 | 0.01 | 0.6 | 0 | 0 | 20.85
| 370 | 2008-06-16 | 90000 | 71.3 | -2.8 | 0.71 | 89.8 | -348.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | 2.24 | -1.4 | 0.01 | 0.5 | 0 | 0 | 20.85
| 371 | 2008-06-16 | 100000 | 71.4 | -2.6 | 0.71 | 89.5 | -325.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.3 | 0 | -0.3 | 0 | 0 | 20.77
| 372 | 2008-06-16 | 110000 | 71.5 | -2.7 | 0.71 | 72.3 | -276.8 | 0.08 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.2 | 0.01 | 0 | 0 | 0 | 20.84
| 373 | 2008-06-16 | 120000 | 71.4 | -2.6 | 0.71 | 61.7 | -218.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -0.9 | 0.01 | 0.6 | 0 | 0 | 20.83
| 374 | 2008-06-16 | 130000 | 71.3 | -2.7 | 0.71 | 56.1 | -214.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -0.9 | 0.01 | 0.5 | 0 | 0 | 20.82
| 375 | 2008-06-16 | 140000 | 71.9 | -2.4 | 0.72 | 53.1 | -171.2 | 0.23 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -0.8 | 0.01 | 0.3 | 0 | 0 | 20.82
| 376 | 2008-06-16 | 150000 | 72.8 | -2.8 | 0.71 | 50.6 | -202.5 | 0.16 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.7 | 0.01 | 0.5 | 0 | 0 | 20.81
| 377 | 2008-06-16 | 160000 | 72.8 | -2.5 | 0.71 | 48.4 | -166.9 | 0.1 | 0.5 | 1.3 | -8.6 | 0.4 | -0.01 | -0.06 | -0.8 | 0.02 | 1 | 0 | 0 | 20.81
| 378 | 2008-06-16 | 170000 | 72.8 | -2.4 | 0.71 | 49.2 | -178.4 | 0.04 | 0.5 | 1.3 | -6.9 | 0.6 | -0.01 | -0.06 | -0.7 | 0.01 | 0.1 | 0 | 0 | 20.81
| 379 | 2008-06-16 | 180000 | 72.8 | -2.5 | 0.71 | 52 | -179.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -0.8 | 0 | -0.1 | 0 | 0 | 20.82
| 380 | 2008-06-16 | 190000 | 72.8 | -2.6 | 0.71 | 56.8 | -207.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -0.9 | 0 | 0 | 0 | 0 | 20.75
| 381 | 2008-06-16 | 200000 | 72.9 | -2.6 | 0.7 | 74 | -272.5 | 0.04 | 0.5 | 1.2 | -8.6 | 0.5 | -0.01 | -0.05 | -1.2 | 0.02 | 1.5 | 0 | 0 | 20.84
| 382 | 2008-06-16 | 210000 | 72.7 | -2.5 | 0.7 | 104.4 | -392.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -1.7 | 0.01 | 0.7 | 0 | 0 | 20.86
| 383 | 2008-06-16 | 220000 | 72.7 | -2.7 | 0.7 | 159.7 | -601.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.08 | -2.5 | 0.01 | 0.7 | 22.2 | 0 | 20.87
| 384 | 2008-06-16 | 230000 | 72.8 | -2.6 | 0.71 | 172.8 | -612.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.09 | -2.6 | 0.01 | 4 | 164.6 | 0 | 20.88
| 385 | 2008-06-17 | 0 | 72.7 | -2.6 | 0.71 | 148.4 | -486.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.09 | -2.5 | 0.01 | 4.6 | 297.6 | 0 | 20.89
| 386 | 2008-06-17 | 10000 | 72.7 | -2.6 | 0.7 | 106.5 | -374.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.09 | -1.6 | 0.02 | 5.3 | 615.7 | 0 | 20.9
| 387 | 2008-06-17 | 20000 | 72.5 | -2.5 | 0.7 | 48.4 | -201.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -0.8 | 0.01 | 3.3 | 723.3 | 1.6 | 20.91
| 388 | 2008-06-17 | 30000 | 71.4 | -2.2 | 0.7 | 15 | -65.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.07 | -0.3 | 0.01 | 1.1 | 460.6 | 0 | 20.92
| 389 | 2008-06-17 | 40000 | 71.3 | -2.4 | 0.71 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.01 | 0 | 64.9 | 0 | 20.94
| 390 | 2008-06-17 | 50000 | 71.4 | -2.4 | 0.7 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | 0 | 0.02 | 0 | 0 | 0 | 20.95
| 391 | 2008-06-17 | 60000 | 71.4 | 89.4 | 3.5 | 13.9 | 17.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | 0.71 | -0.06 | 0.6 | 0.7 | 1.5 | 31.7 | 9.5 | 17.39
| 392 | 2008-06-17 | 70000 | 71.4 | -1.1 | 0.35 | 10.5 | -238.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | 0 | -0.06 | -0.7 | 0.03 | 1.9 | 41.2 | 11.1 | 20.87
| 393 | 2008-06-17 | 80000 | 71.4 | -2.6 | 0.09 | 18.6 | -498.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.05 | -1.6 | 0.01 | 0.8 | 0 | 0 | 20.87
| 394 | 2008-06-17 | 90000 | 71.4 | -2.3 | 0.06 | 12.6 | -511.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | 2.26 | -2.1 | 0.02 | 1.6 | 42.8 | 0 | 20.87
| 395 | 2008-06-17 | 100000 | 71.3 | -2.3 | -0.02 | 2.4 | -83.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.5 | 0.02 | 0.1 | 72.8 | 0 | 20.93
| 396 | 2008-06-17 | 110000 | 71.3 | 259.2 | 9.18 | 13.8 | 57.4 | 0.04 | 0.5 | 1.3 | -8.5 | 0.6 | 4.26 | -0.06 | 2.6 | 16.94 | 5.2 | 197.9 | 213.7 | 9.06
| 397 | 2008-06-17 | 120000 | 71.3 | 297.5 | 9.83 | 496.4 | 422.1 | 0.04 | 0.5 | 1.2 | -8.5 | 0.6 | 3.32 | -0.06 | 43.1 | 25.62 | 47.8 | 280.3 | 283.5 | 14.95
| 398 | 2008-06-17 | 130000 | 71.4 | -2.2 | 0.09 | 0 | 0 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | 0.02 | -0.06 | 0 | 0.04 | 0 | 23.7 | 4.7 | 20.88
| 399 | 2008-06-17 | 140000 | 71.3 | -262.9 | -2.59 | -76.9 | -7684.6 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | 0.01 | -0.06 | 0.1 | 0.02 | 0.3 | 0 | 0 | 20.82
| 400 | 2008-06-17 | 150000 | 71.5 | -499.5 | -5 | -128.2 | -12805.2 | 0.04 | 0.5 | 1.3 | -8.5 | 0.8 | 0.01 | -0.06 | 0.2 | 0.03 | 0.6 | 0 | 0 | 20.67
| 401 | 2008-06-17 | 160000 | 72.7 | -499.5 | -5 | -109.2 | -10906.9 | 0.04 | 0.5 | 1.3 | -8.5 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.3 | 0 | 0 | 20.63
| 402 | 2008-06-17 | 170000 | 72.6 | -499.5 | -5 | -132.7 | -13259.6 | 0.04 | 0.5 | 1.3 | -8.5 | 0.9 | 0 | -0.06 | -0.1 | 0.02 | 0.5 | 0 | 0 | 20.67
| 403 | 2008-06-17 | 180000 | 72.7 | -499.5 | -5 | -140.1 | -13996.9 | 0.04 | 0.5 | 1.2 | -8.5 | 0.9 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.69
| 404 | 2008-06-17 | 190000 | 72.8 | -499.5 | -5 | -142.6 | -14242 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.4 | 0 | 0 | 20.69
| 405 | 2008-06-17 | 200000 | 72.7 | -499.5 | -5 | -144.4 | -14422.6 | 0.04 | 0.5 | 1.2 | -8.5 | 0.7 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.69
| 406 | 2008-06-17 | 210000 | 72.7 | -499.5 | -5 | -148.1 | -14793.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.7 | 0 | 0 | 20.7
| 407 | 2008-06-17 | 220000 | 72.9 | -499.5 | -5 | -147.8 | -14759.2 | 0.04 | 0.5 | 1.3 | -8.5 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.5 | 0 | 0 | 20.7
| 408 | 2008-06-17 | 230000 | 72.8 | -499.5 | -5 | -141.4 | -14120.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.5 | 0 | 0 | 20.62
| 409 | 2008-06-18 | 0 | 72.7 | -499.5 | -5 | -137.7 | -13756 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.68
| 410 | 2008-06-18 | 10000 | 71.6 | -499.5 | -5 | -132.2 | -13202.3 | 0.04 | 0.5 | 1.3 | -8.5 | 0.7 | -0.01 | -0.06 | -0.2 | 0.02 | 0.4 | 0 | 0 | 20.68
| 411 | 2008-06-18 | 20000 | 71.3 | -499.5 | -5 | -131 | -13082.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | -0.01 | -0.06 | -0.2 | 0.02 | 0.5 | 0 | 0 | 20.67
| 412 | 2008-06-18 | 30000 | 71.4 | -499.5 | -5 | -132.5 | -13231.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | -0.06 | -0.2 | 0.02 | 0.5 | 0 | 0 | 20.68
| 413 | 2008-06-18 | 40000 | 71.3 | -499.5 | -5 | -132.8 | -13269.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -0.2 | 0.02 | 0.5 | 0 | 0 | 20.68
| 414 | 2008-06-18 | 50000 | 71.4 | -499.5 | -5 | -129.8 | -12963.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | -0.01 | -0.06 | -0.2 | 0.02 | 0.4 | 0 | 0 | 20.67
| 415 | 2008-06-18 | 60000 | 71.3 | -499.5 | -5 | -125.5 | -12530.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.66
| 416 | 2008-06-18 | 70000 | 71.4 | -499.5 | -5 | -123.6 | -12349.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.07 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.66
| 417 | 2008-06-18 | 80000 | 71.3 | -499.5 | -5 | -123.6 | -12349.5 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.07 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.66
| 418 | 2008-06-18 | 90000 | 71.3 | -499.5 | -5 | -124.5 | -12431.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | 0 | 2.28 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.66
| 419 | 2008-06-18 | 100000 | 71.6 | -499.5 | -5 | -122 | -12182.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.05 | -0.2 | 0.02 | 0.6 | 0 | 0 | 20.66
| 420 | 2008-06-18 | 110000 | 71.4 | -499.5 | -5 | -125.3 | -12510.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.2 | 0.01 | 0.2 | 0 | 0 | 20.66
| 421 | 2008-06-18 | 120000 | 71.3 | -499.5 | -5 | -126.8 | -12663.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -0.2 | 0.02 | 0.4 | 0 | 0 | 20.67
| 422 | 2008-06-18 | 130000 | 71.2 | -499.5 | -5 | -126.4 | -12626.8 | 0.17 | 0.5 | 1.2 | -8.6 | 0.6 | -0.01 | -0.06 | -0.2 | 0.01 | 0.3 | 0 | 0 | 20.67
| 423 | 2008-06-18 | 140000 | 72.3 | -499.5 | -5 | -124.6 | -12448.6 | 0.23 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.07 | -0.2 | 0.01 | 0.3 | 0 | 0 | 20.66
| 424 | 2008-06-18 | 150000 | 72.7 | -499.5 | -5 | -120.6 | -12049.5 | 0.16 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.2 | 0.02 | 0.4 | 0 | 0 | 20.66
| 425 | 2008-06-18 | 160000 | 72.8 | -499.5 | -5 | -114.9 | -11477.2 | 0.09 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.2 | 0.02 | 0.4 | 0 | 0 | 20.64
| 426 | 2008-06-18 | 170000 | 72.7 | -499.5 | -5 | -112.2 | -11203.1 | 0.04 | 0.5 | 1.3 | -7.8 | 0.7 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.64
| 427 | 2008-06-18 | 180000 | 72.7 | -499.5 | -5 | -111.5 | -11139.3 | 0.04 | 0.5 | 1.2 | -6.7 | 0.6 | -0.01 | -0.05 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.64
| 428 | 2008-06-18 | 190000 | 72.8 | -499.5 | -5 | -109.3 | -10911.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.63
| 429 | 2008-06-18 | 200000 | 72.7 | -499.5 | -5 | -108.8 | -10867.4 | 0.04 | 0.5 | 1.2 | -7.8 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.63
| 430 | 2008-06-18 | 210000 | 72.7 | -499.5 | -5 | -109.3 | -10916.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | 0 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.63
| 431 | 2008-06-18 | 220000 | 72.8 | -499.5 | -5 | -107.6 | -10745.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | 0 | -0.05 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.63
| 432 | 2008-06-18 | 230000 | 72.8 | -499.5 | -5 | -106.2 | -10608.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.05 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.62
| 433 | 2008-06-19 | 0 | 72.7 | -499.5 | -5 | -104.8 | -10466.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | 0.01 | -0.06 | 0.2 | 0.03 | 0.5 | 0 | 0 | 20.62
| 434 | 2008-06-19 | 10000 | 72.7 | -499.5 | -5 | -102.5 | -10235.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | 0 | -0.06 | 0 | 0.01 | 0.3 | 0 | 0 | 20.61
| 435 | 2008-06-19 | 20000 | 72.7 | -499.5 | -5 | -102.4 | -10223 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.61
| 436 | 2008-06-19 | 30000 | 72.8 | -499.5 | -5 | -99.3 | -9921.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.05 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.6
| 437 | 2008-06-19 | 40000 | 72.2 | -499.5 | -5 | -99.4 | -9927 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.6
| 438 | 2008-06-19 | 50000 | 71.4 | -499.5 | -5 | -98.4 | -9832.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.02 | 0.4 | 0 | 0 | 20.6
| 439 | 2008-06-19 | 60000 | 71.4 | -499.5 | -5 | -99.1 | -9904.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.6
| 440 | 2008-06-19 | 70000 | 71.4 | -499.5 | -5 | -100.9 | -10081.9 | 0.04 | 0.5 | 1.3 | -8.5 | 0.8 | 0.02 | -0.06 | 0.4 | 0.03 | 0.7 | 0 | 0 | 20.61
| 441 | 2008-06-19 | 80000 | 71.4 | -499.5 | -5 | -101.7 | -10160.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0.01 | -0.06 | 0.2 | 0.02 | 0.4 | 0 | 0 | 20.61
| 442 | 2008-06-19 | 90000 | 72.3 | -499.5 | -5 | -101.3 | -10120.5 | 0.05 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | 2.23 | 0 | 0.02 | 0.4 | 0 | 0 | 20.61
| 443 | 2008-06-19 | 100000 | 72.7 | -499.5 | -5 | -99.2 | -9909.4 | 0.06 | 0.5 | 1.3 | -8.5 | 0.8 | 0 | -0.06 | 0 | 0.02 | 0.3 | 0 | 0 | 20.6
| 444 | 2008-06-19 | 110000 | 72.7 | -499.5 | -5 | -89.7 | -8956.4 | 0.05 | 0.5 | 1.3 | -8.5 | 0.8 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.57
| 445 | 2008-06-19 | 120000 | 72.7 | -499.5 | -5 | -92.1 | -9201.4 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | 0 | -0.06 | 0 | 0.02 | 0.4 | 0 | 0 | 20.58
| 446 | 2008-06-19 | 130000 | 72.7 | -499.5 | -5 | -91.1 | -9102.6 | 0.04 | 0.5 | 1.3 | -8.5 | 0.7 | 0 | -0.06 | 0 | 0.02 | 0.4 | 0 | 0 | 20.58
| 447 | 2008-06-19 | 140000 | 72.8 | -499.5 | -5 | -91.2 | -9113.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.02 | 0.4 | 0 | 0 | 20.58
| 448 | 2008-06-19 | 150000 | 74.3 | -499.5 | -5 | -90.8 | -9072.4 | 0.04 | 0.5 | 1.3 | -8.5 | 0.6 | 0 | -0.05 | 0 | 0.02 | 0.3 | 0 | 0 | 20.57
| 449 | 2008-06-19 | 160000 | 74.7 | -499.5 | -5 | -88.1 | -8799.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0 | 0 | 20.56
| 450 | 2008-06-19 | 170000 | 74.7 | -499.5 | -5 | -86 | -8586.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.6 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.56
| 451 | 2008-06-19 | 180000 | 74.7 | -499.5 | -5 | -84.7 | -8457 | 0.07 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.55
| 452 | 2008-06-19 | 190000 | 74.7 | -499.5 | -5 | -83.9 | -8378.4 | 0.12 | 0.5 | 1.3 | -8.5 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.55
| 453 | 2008-06-19 | 200000 | 75.4 | -499.5 | -5 | -83.5 | -8338.2 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | 0 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.55
| 454 | 2008-06-19 | 210000 | 76.2 | -499.5 | -5 | -84.2 | -8410 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | 0 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.55
| 455 | 2008-06-19 | 220000 | 75 | -499.5 | -5 | -82.7 | -8264.2 | 0.04 | 0.5 | 1.2 | -8.5 | 0.7 | -0.01 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.54
| 456 | 2008-06-19 | 230000 | 74.7 | -499.5 | -5 | -81.7 | -8167.5 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.54
| 457 | 2008-06-20 | 0 | 74.7 | -499.5 | -5 | -80.6 | -8058 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.53
| 458 | 2008-06-20 | 10000 | 74.7 | -499.5 | -5 | -80 | -7998.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | 0 | -0.07 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.53
| 459 | 2008-06-20 | 20000 | 74.8 | -499.5 | -5 | -78.4 | -7830.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.52
| 460 | 2008-06-20 | 30000 | 74.7 | -499.5 | -5 | -77.1 | -7704.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.52
| 461 | 2008-06-20 | 40000 | 74.6 | -499.5 | -5 | -76 | -7594.1 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.51
| 462 | 2008-06-20 | 50000 | 74.7 | -499.5 | -5 | -76.5 | -7639.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | -0.1 | 0.01 | 0.1 | 0 | 0 | 20.51
| 463 | 2008-06-20 | 60000 | 74.7 | -499.5 | -5 | -76.5 | -7646.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.06 | 0 | 0.02 | 0.3 | 0 | 0 | 20.51
| 464 | 2008-06-20 | 70000 | 74.7 | -499.5 | -5 | -76.6 | -7654.7 | 0.04 | 0.5 | 1.2 | -8.5 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0 | 0 | 20.51
| 465 | 2008-06-20 | 80000 | 74.6 | -499.5 | -5 | -77 | -7692.6 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.07 | 0 | 0.02 | 0.3 | 0 | 0 | 20.52
| 466 | 2008-06-20 | 90000 | 74.6 | -499.5 | -5 | -75.1 | -7499.4 | 0.06 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | 2.25 | 0 | 0.01 | 0.2 | 0 | 0 | 20.51
| 467 | 2008-06-20 | 100000 | 75 | -499.5 | -5 | -72.7 | -7258.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.6 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.49
| 468 | 2008-06-20 | 110000 | 76.2 | -499.5 | -5 | -71.1 | -7106.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.48
| 469 | 2008-06-20 | 120000 | 76.1 | -499.5 | -5 | -69.8 | -6970.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0 | 0 | 20.48
| 470 | 2008-06-20 | 130000 | 76.1 | -499.5 | -5 | -68 | -6794.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0.01 | -0.06 | 0.2 | 0.02 | 0.3 | 0 | 0 | 20.47
| 471 | 2008-06-20 | 140000 | 76.2 | -499.5 | -5 | -66.3 | -6626.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0 | 0 | 20.45
| 472 | 2008-06-20 | 150000 | 76.2 | -499.5 | -5 | -63.4 | -6328.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.43
| 473 | 2008-06-20 | 160000 | 76.1 | -499.5 | -5 | -63 | -6288.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.43
| 474 | 2008-06-20 | 170000 | 77.6 | -499.5 | -5 | -63.1 | -6302.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -0.1 | 0.02 | 0.2 | 0 | 0 | 20.43
| 475 | 2008-06-20 | 180000 | 78.2 | -499.5 | -5 | -63.1 | -6305.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.05 | 0 | 0.02 | 0.2 | 0 | 0 | 20.43
| 476 | 2008-06-20 | 190000 | 78.2 | -499.5 | -5 | -63.1 | -6300.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -0.1 | 0.02 | 0.2 | 0 | 0 | 20.43
| 477 | 2008-06-20 | 200000 | 78.2 | -499.5 | -5 | -63.1 | -6304.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.43
| 478 | 2008-06-20 | 210000 | 78.2 | -499.5 | -5 | -64.1 | -6405.5 | 0.04 | 0.5 | 1.2 | -8.5 | 0.7 | 0 | -0.06 | 0 | 0.02 | 0.3 | 0 | 0 | 20.44
| 479 | 2008-06-20 | 220000 | 78.2 | -499.5 | -5 | -64.5 | -6443.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0 | 0 | 20.44
| 480 | 2008-06-20 | 230000 | 78.3 | -499.5 | -5 | -63.7 | -6357.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0 | 0 | 20.44
| 481 | 2008-06-21 | 0 | 78.2 | -499.5 | -5 | -63 | -6291.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.02 | 0.3 | 0 | 0 | 20.43
| 482 | 2008-06-21 | 10000 | 78.2 | -499.5 | -5 | -62.2 | -6214.7 | 0.04 | 0.5 | 1.2 | -8.5 | 0.6 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0 | 0 | 20.43
| 483 | 2008-06-21 | 20000 | 76.1 | -499.5 | -5 | -61.3 | -6117.4 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.42
| 484 | 2008-06-21 | 30000 | 76.2 | -499.5 | -5 | -59.5 | -5940.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0 | 0 | 20.4
| 485 | 2008-06-21 | 40000 | 76.2 | -499.5 | -5 | -58.8 | -5873.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0 | 0 | 20.4
| 486 | 2008-06-21 | 50000 | 76.2 | -499.5 | -5 | -58.3 | -5824.6 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.39
| 487 | 2008-06-21 | 60000 | 76.2 | -499.5 | -5 | -57.7 | -5761 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.39
| 488 | 2008-06-21 | 70000 | 76.2 | -499.5 | -5 | -57.5 | -5748 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.2 | 0 | 0 | 20.39
| 489 | 2008-06-21 | 80000 | 76.2 | -499.5 | -5 | -58 | -5791 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0 | 0 | 20.39
| 490 | 2008-06-21 | 90000 | 76.2 | -499.5 | -5 | -58 | -5790.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.02 | 2.25 | 0.2 | 0.03 | 0.3 | 0 | 0 | 20.39
| 491 | 2008-06-21 | 100000 | 76.1 | -499.5 | -5 | -57.9 | -5787.4 | 0.08 | 0.5 | 1.3 | -8.6 | 0.8 | 0.01 | -0.06 | 0.1 | 0.01 | 0.1 | 0 | 0 | 20.39
| 492 | 2008-06-21 | 110000 | 77.4 | -499.5 | -5 | -59.5 | -5947.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.4
| 493 | 2008-06-21 | 120000 | 78.2 | -499.5 | -5 | -58.5 | -5845.1 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 0 | -0.06 | 0 | 0.01 | 0.1 | 0 | 0 | 20.4
| 494 | 2008-06-21 | 130000 | 78.2 | -499.5 | -5 | -54.6 | -5455.6 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.36
| 495 | 2008-06-21 | 140000 | 78.2 | -499.5 | -5 | -53 | -5295.9 | 0.06 | 0.5 | 1.2 | -8.5 | 0.9 | 0 | -0.06 | 0 | 0.02 | 0.2 | 0 | 0 | 20.34
| 496 | 2008-06-21 | 150000 | 78.1 | -499.5 | -5 | -54.2 | -5418.7 | 0.17 | 0.5 | 1.3 | -8.5 | 0.9 | -0.01 | -0.06 | -0.1 | 0.02 | 0.2 | 0 | 0 | 20.36
| 497 | 2008-06-21 | 160000 | 78.1 | -499.5 | -5 | -55.9 | -5586.4 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | -0.01 | -0.06 | -0.1 | 0.01 | 0.1 | 0 | 0 | 20.37
| 498 | 2008-06-21 | 170000 | 78.2 | -499.5 | -5 | -56.9 | -5683 | 0.04 | 0.5 | 1.3 | -8.5 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.2 | 0 | 0 | 20.38
| 499 | 2008-06-21 | 180000 | 78.2 | -499.5 | -5 | -62.1 | -6201.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.1 | 0 | 0 | 20.42
| 500 | 2008-06-21 | 190000 | 79.3 | -499.5 | -5 | -64.7 | -6456 | 0.04 | 0.5 | 1.3 | -8.5 | 1 | -0.01 | -0.06 | -0.1 | 0.02 | 0.2 | 0 | 0 | 20.44
| 501 | 2008-06-21 | 200000 | 79.6 | -499.5 | -5 | -68.4 | -6835.3 | 0.04 | 0.5 | 1.3 | -8.5 | 1 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.47
| 502 | 2008-06-21 | 210000 | 79 | -499.5 | -5 | -71.8 | -7174.9 | 0.04 | 0.5 | 1.3 | -8.5 | 0.9 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.49
| 503 | 2008-06-21 | 220000 | 78.1 | -499.5 | -5 | -74.2 | -7416 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.2 | 0 | 0 | 20.5
| 504 | 2008-06-21 | 230000 | 78.2 | -499.5 | -5 | -77.6 | -7753.5 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | -0.01 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.52
| 505 | 2008-06-22 | 0 | 78.2 | -499.5 | -5 | -78.9 | -7887.3 | 0.04 | 0.5 | 1.3 | -8.5 | 1.1 | 0 | -0.06 | -0.1 | 0.02 | 0.2 | 0 | 0 | 20.53
| 506 | 2008-06-22 | 10000 | 78.3 | -499.5 | -5 | -80.9 | -8087.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0 | 0.02 | 0.3 | 0 | 0 | 20.53
| 507 | 2008-06-22 | 20000 | 78.2 | -499.5 | -5 | -83.8 | -8372.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.55
| 508 | 2008-06-22 | 30000 | 78.2 | -499.5 | -5 | -85.2 | -8512.7 | 0.04 | 0.5 | 1.3 | -8.5 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.1 | 0 | 0 | 20.55
| 509 | 2008-06-22 | 40000 | 78.3 | -499.5 | -5 | -87.7 | -8759.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.56
| 510 | 2008-06-22 | 50000 | 78.2 | -499.5 | -5 | -92.5 | -9237 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.58
| 511 | 2008-06-22 | 60000 | 76.9 | -499.5 | -5 | -93.9 | -9377.2 | 0.04 | 0.5 | 1.3 | -8.5 | 1 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.59
| 512 | 2008-06-22 | 70000 | 76.1 | -499.5 | -5 | -95 | -9484 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.59
| 513 | 2008-06-22 | 80000 | 76.1 | -499.5 | -5 | -97.7 | -9755 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.5 | 0 | 0 | 20.6
| 514 | 2008-06-22 | 90000 | 76.2 | -499.5 | -5 | -97.3 | -9718.1 | 0.04 | 0.5 | 1.2 | -8.5 | 0.9 | -0.01 | 2.27 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.6
| 515 | 2008-06-22 | 100000 | 76.1 | -499.5 | -5 | -97.8 | -9772.4 | 0.04 | 0.5 | 1.3 | -8.5 | 0.8 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.6
| 516 | 2008-06-22 | 110000 | 77.2 | -499.5 | -5 | -99.7 | -9957.5 | 0.05 | 0.5 | 1.3 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.6
| 517 | 2008-06-22 | 120000 | 78.2 | -499.5 | -5 | -99.9 | -9977.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.6
| 518 | 2008-06-22 | 130000 | 78.2 | -499.5 | -5 | -98.3 | -9816.4 | 0.06 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | -0.05 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.6
| 519 | 2008-06-22 | 140000 | 78.2 | -499.5 | -5 | -97.9 | -9778.3 | 0.24 | 0.5 | 1.3 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.6
| 520 | 2008-06-22 | 150000 | 78.2 | -499.5 | -5 | -94.1 | -9401.7 | 0.19 | 0.5 | 1.3 | -8.6 | 0.8 | -0.01 | -0.06 | -0.2 | 0.01 | 0.2 | 0 | 0 | 20.59
| 521 | 2008-06-22 | 160000 | 78.2 | -499.5 | -5 | -88.4 | -8833.4 | 0.09 | 0.5 | 1.3 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.57
| 522 | 2008-06-22 | 170000 | 78.1 | -499.5 | -5 | -84 | -8388.1 | 0.05 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.55
| 523 | 2008-06-22 | 180000 | 78.3 | -499.5 | -5 | -78.8 | -7871.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.1 | 0 | 0 | 20.53
| 524 | 2008-06-22 | 190000 | 78.2 | -499.5 | -5 | -86.4 | -8627.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.56
| 525 | 2008-06-22 | 200000 | 78.1 | -499.5 | -5 | -91.8 | -9170.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.58
| 526 | 2008-06-22 | 210000 | 78.3 | -499.5 | -5 | -91.9 | -9181.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.58
| 527 | 2008-06-22 | 220000 | 78.2 | -499.5 | -5 | -91.6 | -9153.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.58
| 528 | 2008-06-22 | 230000 | 78.2 | -499.5 | -5 | -90.4 | -9027.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.57
| 529 | 2008-06-23 | 0 | 78.3 | -499.5 | -5 | -89.3 | -8918.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.57
| 530 | 2008-06-23 | 10000 | 76.6 | -499.5 | -5 | -88.9 | -8879.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.05 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.57
| 531 | 2008-06-23 | 20000 | 76.2 | -499.5 | -5 | -88.5 | -8843.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.57
| 532 | 2008-06-23 | 30000 | 76.2 | -499.5 | -5 | -88.3 | -8817.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.57
| 533 | 2008-06-23 | 40000 | 76.2 | -499.5 | -5 | -87.5 | -8739.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.56
| 534 | 2008-06-23 | 50000 | 76.1 | -499.5 | -5 | -87.7 | -8754.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.56
| 535 | 2008-06-23 | 60000 | 76.2 | -499.5 | -5 | -88.7 | -8857 | 0.09 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.57
| 536 | 2008-06-23 | 70000 | 76.2 | -499.5 | -5 | -88.2 | -8805.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.56
| 537 | 2008-06-23 | 80000 | 76.2 | -499.5 | -5 | -86.9 | -8678 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.56
| 538 | 2008-06-23 | 90000 | 76.1 | -499.5 | -5 | -86.6 | -8649.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | 2.23 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.56
| 539 | 2008-06-23 | 100000 | 76.1 | -499.5 | -5 | -85.7 | -8559.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.2 | 0 | 0 | 20.56
| 540 | 2008-06-23 | 110000 | 76.1 | -499.5 | -5 | -85.1 | -8500.8 | 0.08 | 0.5 | 1.3 | -8.6 | 0.8 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.55
| 541 | 2008-06-23 | 120000 | 76.3 | -499.5 | -5 | -84.9 | -8484.5 | 0.18 | 0.5 | 1.3 | -8.5 | 0.6 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.55
| 542 | 2008-06-23 | 130000 | 76.3 | -499.5 | -5 | -83.3 | -8324.2 | 0.03 | 0.5 | 1.3 | -8.5 | 0.7 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.55
| 543 | 2008-06-23 | 140000 | 76.2 | -499.5 | -5 | -81.4 | -8135.4 | 0.04 | 0.5 | 1.3 | -8.5 | 0.8 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.54
| 544 | 2008-06-23 | 150000 | 76.2 | -499.5 | -5 | -82.9 | -8282 | 0.03 | 0.5 | 1.2 | -8.6 | 0.7 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.54
| 545 | 2008-06-23 | 160000 | 76.2 | -499.5 | -5 | -84.4 | -8434 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.55
| 546 | 2008-06-23 | 170000 | 76.3 | -499.5 | -5 | -86.3 | -8625.2 | 0.1 | 0.5 | 1.2 | -8.5 | 0.8 | -0.01 | -0.05 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.56
| 547 | 2008-06-23 | 180000 | 76.3 | -499.5 | -5 | -91.4 | -9125.9 | 0.03 | 0.5 | 1.2 | -8.5 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.58
| 548 | 2008-06-23 | 190000 | 76 | -499.5 | -5 | -106.8 | -10668.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.2 | 0.02 | 0.4 | 0 | 0 | 20.62
| 549 | 2008-06-23 | 200000 | 76 | -499.5 | -5 | -103.5 | -10337.8 | 0.04 | 0.5 | 1.2 | -8.5 | 0.9 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.61
| 550 | 2008-06-23 | 210000 | 76.1 | -499.5 | -5 | -106.7 | -10654.5 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.62
| 551 | 2008-06-23 | 220000 | 76.1 | -499.5 | -5 | -106.6 | -10644.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | -0.01 | -0.07 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.62
| 552 | 2008-06-23 | 230000 | 76.1 | -499.5 | -5 | -104.1 | -10400.1 | 0.04 | 0.5 | 1.2 | -8.5 | 0.9 | 0 | -0.07 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.62
| 553 | 2008-06-24 | 0 | 76.2 | -499.5 | -5 | -102.9 | -10278.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.61
| 554 | 2008-06-24 | 10000 | 76.1 | -499.5 | -5 | -101.4 | -10132.4 | 0.03 | 0.5 | 1.2 | -8.5 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.61
| 555 | 2008-06-24 | 20000 | 74.7 | -499.5 | -5 | -103.3 | -10321.8 | 0.04 | 0.5 | 1.3 | -8.5 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.61
| 556 | 2008-06-24 | 30000 | 74.7 | -499.5 | -5 | -108.5 | -10836.9 | 0.03 | 0.5 | 1.2 | -8.5 | 1 | -0.01 | -0.05 | -0.1 | 0.01 | 0.2 | 0 | 0 | 20.63
| 557 | 2008-06-24 | 40000 | 74.5 | -499.5 | -5 | -108.6 | -10850.8 | 0.03 | 0.5 | 1.2 | -8.5 | 0.9 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.63
| 558 | 2008-06-24 | 50000 | 74.8 | -499.5 | -5 | -107.3 | -10720.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.06 | 0 | 0.01 | 0.3 | 0 | 0 | 20.62
| 559 | 2008-06-24 | 60000 | 74.7 | -499.5 | -5 | -106.5 | -10633.7 | 0.03 | 0.5 | 1.3 | -8.5 | 0.9 | 0 | -0.06 | 0 | 0.02 | 0.3 | 0 | 0 | 20.62
| 560 | 2008-06-24 | 70000 | 74.6 | -499.5 | -5 | -105.9 | -10577.7 | 0.04 | 0.5 | 1.2 | -8.5 | 0.8 | 0 | -0.06 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.62
| 561 | 2008-06-24 | 80000 | 74.6 | -499.5 | -5 | -106.9 | -10677.9 | 0.04 | 0.5 | 1.3 | -8.5 | 1 | -0.01 | -0.06 | -0.1 | 0.02 | 0.3 | 0 | 0 | 20.62
| 562 | 2008-06-24 | 90000 | 74.7 | -499.5 | -5 | -107.8 | -10764.1 | 0.03 | 0.5 | 1.3 | -8.5 | 0.9 | -0.01 | 2.28 | -0.1 | 0.02 | 0.4 | 0 | 0 | 20.63
| 563 | 2008-06-24 | 100000 | 74.6 | -499.5 | -5 | -107.9 | -10775.3 | 0.05 | 0.5 | 1.2 | -8.5 | 0.9 | -0.01 | -0.06 | -0.1 | 0.01 | 0.3 | 0 | 0 | 20.62
| 564 | 2008-06-24 | 110000 | 75.1 | -217.8 | -1.7 | 14 | -5443.7 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | -0.01 | -0.06 | -0.7 | 0.02 | 1.7 | 17.4 | 0 | 20.77
| 565 | 2008-06-24 | 120000 | 76.2 | 55.8 | 2.01 | 38.7 | -254.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0.98 | 1.68 | 1.9 | 4.93 | 4.9 | 655.3 | 357.7 | 18.86
| 566 | 2008-06-24 | 130000 | 76.1 | -4.2 | 0.06 | 8.4 | -361.8 | 0.11 | 0.5 | 1.2 | -8.6 | 0.8 | 0.02 | -0.06 | 2 | 0.02 | 2.3 | 71.2 | 38 | 20.77
| 567 | 2008-06-24 | 140000 | 76.2 | -2.7 | -0.03 | -2.4 | -236.9 | 0.25 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.7 | 0.01 | 0.7 | 0 | 0 | 20.83
| 568 | 2008-06-24 | 150000 | 76.2 | -2.2 | -0.04 | -3.3 | -155.5 | 0.22 | 0.5 | 1.2 | -8.6 | 0.8 | 0.01 | -0.07 | 0.5 | 0.01 | 0.2 | 0 | 0 | 20.82
| 569 | 2008-06-24 | 160000 | 76.1 | -2.6 | -0.07 | -4 | -155.7 | 0.05 | 0.5 | 1.2 | -8.6 | 0.7 | 0 | -0.06 | 0.3 | 0.01 | 0.7 | 0 | 0 | 20.8
| 570 | 2008-06-24 | 170000 | 76.2 | -2.6 | -0.09 | -4.5 | -129.6 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.06 | 0.2 | 0.02 | 0.9 | 0 | 0 | 20.71
| 571 | 2008-06-24 | 180000 | 77.3 | -2.5 | -0.1 | -4.6 | -115.8 | 0.03 | 0.5 | 1.3 | -8.6 | 0.5 | 0.01 | -0.06 | 0.3 | 0.01 | 0.6 | 0 | 0 | 20.77
| 572 | 2008-06-24 | 190000 | 78.3 | -2.7 | -0.11 | -4.9 | -124.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0.01 | -0.06 | 0.3 | 0.02 | 0.7 | 0 | 0 | 20.77
| 573 | 2008-06-24 | 200000 | 78.2 | -2.5 | -0.12 | -5.3 | -112 | 0.04 | 0.5 | 1.2 | -8.6 | 0.7 | 0.01 | -0.06 | 0.3 | 0.01 | 0.7 | 0 | 0 | 20.77
| 574 | 2008-06-24 | 210000 | 78.3 | -2.5 | -0.12 | -5.6 | -128.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0.01 | -0.06 | 0.2 | 0.01 | 0.5 | 0 | 0 | 20.77
| 575 | 2008-06-24 | 220000 | 77.6 | -2.7 | -0.13 | -6.4 | -135.5 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.05 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.78
| 576 | 2008-06-24 | 230000 | 76.1 | -2.9 | -0.14 | -7.1 | -147.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.2 | 0.01 | 0.6 | 0 | 0 | 20.78
| 577 | 2008-06-25 | 0 | 76.2 | -2.6 | -0.14 | -7.1 | -133 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.2 | 0.01 | 0.5 | 0 | 0 | 20.78
| 578 | 2008-06-25 | 10000 | 76.1 | -2.6 | -0.15 | -7.4 | -129.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.06 | 0.2 | 0.02 | 0.9 | 0 | 0 | 20.78
| 579 | 2008-06-25 | 20000 | 76.2 | -2.8 | -0.15 | -7.7 | -138.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0.01 | -0.06 | 0.3 | 0.02 | 0.9 | 0 | 0 | 20.78
| 580 | 2008-06-25 | 30000 | 76.1 | -2.5 | -0.16 | -8.4 | -126.3 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.2 | 0.02 | 0.7 | 0 | 0 | 20.78
| 581 | 2008-06-25 | 40000 | 76.2 | -2.6 | -0.17 | -8.6 | -139.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.06 | 0.2 | 0.01 | 0.6 | 0 | 0 | 20.78
| 582 | 2008-06-25 | 50000 | 76.1 | -2.5 | -0.17 | -8.6 | -124.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | 0 | -0.06 | 0.2 | 0.02 | 0.7 | 0 | 0 | 20.78
| 583 | 2008-06-25 | 60000 | 74.9 | -2.6 | -0.17 | -9.3 | -139.9 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.2 | 0.01 | 0.7 | 0 | 0 | 20.79
| 584 | 2008-06-25 | 70000 | 74.7 | -2.7 | -0.17 | -10 | -157.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | 0 | -0.06 | 0.3 | 0.01 | 0.6 | 0 | 0 | 20.8
| 585 | 2008-06-25 | 80000 | 74.7 | -2.5 | -0.17 | -10.2 | -146.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.06 | 0.2 | 0.02 | 1.1 | 0 | 0 | 20.72
| 586 | 2008-06-25 | 90000 | 74.7 | -2.4 | -0.17 | -10.3 | -139.4 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | 0 | 2.07 | 0.3 | 0.02 | 0.9 | 0 | 0 | 20.8
| 587 | 2008-06-25 | 100000 | 74.8 | 84.2 | 2.79 | 12.6 | -166.4 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 1.61 | -0.06 | 3 | 7.54 | 6.4 | 0 | 0 | 17.46
| 588 | 2008-06-25 | 110000 | 75.2 | -2.5 | 0.42 | 21 | -141.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.03 | -0.07 | 1.7 | 0.04 | 2 | 0 | 0 | 20.79
| 589 | 2008-06-25 | 120000 | 76.1 | -2.6 | 0.07 | 3.7 | -134.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.4 | 0.01 | 0.6 | 0 | 0 | 20.79
| 590 | 2008-06-25 | 130000 | 76.2 | -2.6 | 0.07 | 3.2 | -129.6 | 0.07 | 0.5 | 1.3 | -8.6 | 0.8 | 0.01 | -0.05 | 0.3 | 0.01 | 0.8 | 0 | 0 | 20.78
| 591 | 2008-06-25 | 140000 | 76.2 | -2.7 | 0.06 | 2.9 | -125.2 | 0.25 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.3 | 0.01 | 0.5 | 0 | 0 | 20.77
| 592 | 2008-06-25 | 150000 | 76.2 | -2.5 | 0.06 | 2.7 | -117.8 | 0.21 | 0.5 | 1.2 | -8.6 | 0.9 | 0.01 | -0.06 | 0.3 | 0.01 | 0.2 | 0 | 0 | 20.77
| 593 | 2008-06-25 | 160000 | 76.1 | -2.5 | 0.05 | 2.3 | -107.7 | 0.05 | 0.5 | 1.3 | -8.6 | 0.8 | 0 | -0.06 | 0.2 | 0.02 | 0.6 | 0 | 0 | 20.69
| 594 | 2008-06-25 | 170000 | 76.2 | -2.4 | 0.05 | 2 | -106.4 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.2 | 0.01 | 0.3 | 0 | 0 | 20.76
| 595 | 2008-06-25 | 180000 | 76.1 | -2.5 | 0.05 | 2.4 | -108.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.2 | 0.02 | 0.7 | 0 | 0 | 20.69
| 596 | 2008-06-25 | 190000 | 76.5 | -2.5 | 0.06 | 3.2 | -128.7 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 0.01 | -0.06 | 0.3 | 0.01 | 0.5 | 0 | 0 | 20.71
| 597 | 2008-06-25 | 200000 | 77.5 | -2.5 | 0.06 | 3.9 | -155.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0.01 | -0.06 | 0.4 | 0.02 | 1 | 0 | 0 | 20.8
| 598 | 2008-06-25 | 210000 | 76.2 | -2.8 | 0.06 | 4.7 | -207 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.3 | 0.02 | 1.1 | 0 | 0 | 20.82
| 599 | 2008-06-25 | 220000 | 76.2 | -2.6 | 0.06 | 5.7 | -225.2 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.4 | 0.01 | 0.9 | 0 | 0 | 20.83
| 600 | 2008-06-25 | 230000 | 76.2 | -2.7 | 0.06 | 5.6 | -260.6 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 0.01 | -0.06 | 0.5 | 0.01 | 1 | 0 | 0 | 20.84
| 601 | 2008-06-26 | 0 | 76.2 | -2.9 | 0.06 | 5.4 | -271.8 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 0 | -0.06 | 0.5 | 0.02 | 1.1 | 0 | 0 | 20.84
| 602 | 2008-06-26 | 10000 | 76.1 | -2.5 | 0.07 | 7.3 | -275.5 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 0 | -0.05 | 0.5 | 0.02 | 0.6 | 0 | 0 | 20.84
| 603 | 2008-06-26 | 20000 | 76.1 | -2.6 | 0.06 | 7.6 | -346.9 | 0.04 | 0.5 | 1.2 | -8.6 | 1.1 | 0 | -0.06 | 0.6 | 0.02 | 2 | 0 | 0 | 20.85
| 604 | 2008-06-26 | 30000 | 74.6 | -2.6 | 0.05 | 8.7 | -419.5 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.05 | 0.6 | 0.01 | 1.4 | 0 | 0 | 20.86
| 605 | 2008-06-26 | 40000 | 74.7 | -2.7 | 0.05 | 8.5 | -460.2 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.7 | 0.02 | 2.3 | 0 | 0 | 20.86
| 606 | 2008-06-26 | 50000 | 74.8 | -2.1 | 0.05 | 9 | -431.2 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.06 | 0.9 | 0.01 | 1.6 | 19 | 4.8 | 20.87
| 607 | 2008-06-26 | 60000 | 74.7 | -2.6 | 0.06 | 11.9 | -592.3 | 0.04 | 0.5 | 1.3 | -8.6 | 1.2 | 0 | -0.06 | 1 | 0.01 | 1.2 | 3.2 | 1.6 | 20.87
| 608 | 2008-06-26 | 70000 | 74.8 | -2.7 | 0.06 | 16.8 | -735.5 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.07 | 1.2 | 0.01 | 3.4 | 60.2 | 41.2 | 20.88
| 609 | 2008-06-26 | 80000 | 74.7 | -2.5 | 0.05 | 14.7 | -742.3 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.06 | 1.1 | 0.02 | 6.6 | 193.1 | 55.4 | 20.88
| 610 | 2008-06-26 | 90000 | 74.8 | -2.6 | 0.05 | 9.5 | -541.3 | 0.04 | 0.5 | 1.2 | -8.6 | 1.1 | 0 | 2.11 | 1 | 0.01 | 3.9 | 487.5 | 88.6 | 20.89
| 611 | 2008-06-26 | 100000 | 74.7 | -2.3 | 0.03 | 5.2 | -402.9 | 0.04 | 0.5 | 1.2 | -8.6 | 1.1 | 0 | -0.06 | 0.4 | 0.01 | 2.9 | 372 | 87.1 | 20.89
| 612 | 2008-06-26 | 110000 | 74.4 | -2.3 | 0 | 0.7 | -359.4 | 0.19 | 0.5 | 1.1 | -8.6 | 0.9 | 0 | -0.06 | 0.7 | 0.01 | 1.1 | 0 | 0 | 20.86
| 613 | 2008-06-26 | 120000 | 74.5 | -2.6 | -0.01 | -0.7 | -332.9 | 0.08 | 0.5 | 1.2 | -8.6 | 1 | 0 | -0.06 | 0.5 | 0.01 | 1.7 | 0 | 0 | 20.85
| 614 | 2008-06-26 | 130000 | 75.8 | -2.6 | -0.01 | -0.7 | -248.8 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.3 | 0.01 | 0.9 | 0 | 0 | 20.84
| 615 | 2008-06-26 | 140000 | 76.1 | -2.5 | -0.01 | -0.8 | -211.8 | 0.12 | 1.8 | 2.5 | -8.6 | 1 | 0 | -0.06 | 0.4 | 0.01 | 0.5 | 0 | 0 | 20.83
| 616 | 2008-06-26 | 150000 | 76.2 | -2.7 | -0.01 | -0.7 | -205.1 | 0.12 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.06 | 0.3 | 0.01 | 0.8 | 0 | 0 | 20.75
| 617 | 2008-06-26 | 160000 | 76.1 | -2.5 | -0.01 | -1.1 | -186.1 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.3 | 0.01 | 0.6 | 0 | 0 | 20.82
| 618 | 2008-06-26 | 170000 | 76 | -2.6 | -0.02 | -1.3 | -199.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.06 | 0.4 | 0.01 | 0.3 | 0 | 0 | 20.82
| 619 | 2008-06-26 | 180000 | 76.1 | -2.5 | -0.02 | -1.2 | -155 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.2 | 0.02 | 1 | 0 | 0 | 20.8
| 620 | 2008-06-26 | 190000 | 76.1 | -2.6 | -0.02 | -1.3 | -165.9 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.06 | 0.3 | 0.01 | 0.3 | 0 | 0 | 20.81
| 621 | 2008-06-26 | 200000 | 77.8 | -2.5 | -0.02 | -1.3 | -155.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.3 | 0.01 | 0.5 | 0 | 0 | 20.8
| 622 | 2008-06-26 | 210000 | 77.7 | -2.4 | -0.03 | -1.6 | -158.7 | 0.04 | 0.5 | 1.2 | -8.6 | 0.8 | 0 | -0.06 | 0.3 | 0.01 | 0.6 | 0 | 0 | 20.73
| 623 | 2008-06-26 | 220000 | 76 | -2.7 | -0.02 | -1.5 | -193.5 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 0 | -0.06 | 0.3 | 0.01 | 0.5 | 0 | 0 | 20.81
| 624 | 2008-06-26 | 230000 | 76.1 | -2.6 | -0.01 | -0.6 | -163.3 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | 0 | -0.06 | 0.3 | 0.01 | 0.6 | 0 | 0 | 20.8
| 625 | 2008-06-27 | 0 | 76.1 | -2.4 | -0.01 | -0.7 | -145 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.06 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.8
| 626 | 2008-06-27 | 10000 | 76 | -2.3 | -0.02 | -1.6 | -136.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.4 | 0.01 | 0.4 | 0 | 0 | 20.8
| 627 | 2008-06-27 | 20000 | 76.1 | -2.7 | -0.02 | -1.3 | -161.5 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.4 | 0.01 | 0.4 | 0 | 0 | 20.8
| 628 | 2008-06-27 | 30000 | 76 | -2.3 | -0.02 | -1.4 | -134.7 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.05 | 0.3 | 0.01 | 0.3 | 0 | 0 | 20.8
| 629 | 2008-06-27 | 40000 | 76 | -2.6 | -0.02 | -1.3 | -148.9 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.2 | 0.01 | 0.5 | 0 | 0 | 20.79
| 630 | 2008-06-27 | 50000 | 76 | -2.6 | -0.02 | -1.1 | -140 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.2 | 0 | 0.3 | 0 | 0 | 20.79
| 631 | 2008-06-27 | 60000 | 76 | -2.6 | -0.01 | -0.3 | -146.8 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0.01 | -0.06 | 0.4 | 0.01 | 0.6 | 0 | 0 | 20.79
| 632 | 2008-06-27 | 70000 | 76.1 | -2.5 | 0 | -0.1 | -137.4 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0.01 | -0.06 | 0.4 | 0.01 | 0.3 | 0 | 0 | 20.71
| 633 | 2008-06-27 | 80000 | 76.1 | -2.7 | 0 | -0.1 | -130.2 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0.01 | -0.06 | 0.4 | 0.01 | 0.4 | 0 | 0 | 20.78
| 634 | 2008-06-27 | 90000 | 76.1 | -2.4 | 0.01 | 0.6 | -115.1 | 0.04 | 0.5 | 1.2 | -8.6 | 1.2 | 0.01 | 2.1 | 0.3 | 0.01 | 0.5 | 0 | 0 | 20.78
| 635 | 2008-06-27 | 100000 | 76 | -2.6 | 0.05 | 2.8 | -154.7 | 0.03 | 0.4 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.4 | 0.01 | 0.6 | 0 | 0 | 20.72
| 636 | 2008-06-27 | 110000 | 76.2 | -2.5 | 0.06 | 3.6 | -135.1 | 0.03 | 0.4 | 1.2 | -8.6 | 1.3 | 0.01 | -0.06 | 0.4 | 0.02 | 0.8 | 0 | 0 | 20.8
| 637 | 2008-06-27 | 120000 | 76.1 | -2.7 | 0.05 | 2.8 | -154.8 | 0.03 | 0.4 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.3 | 0.01 | 0.8 | 0 | 0 | 20.79
| 638 | 2008-06-27 | 130000 | 77.7 | -2.4 | 0.05 | 2.5 | -120 | 0.03 | 0.5 | 1.2 | -8.6 | 1 | 0 | -0.06 | 0.2 | 0.01 | 0.6 | 0 | 0 | 20.78
| 639 | 2008-06-27 | 140000 | 78.3 | -2.5 | 0.05 | 2.3 | -97.4 | 0.12 | 0.4 | 1.2 | -8.6 | 1.1 | 0 | -0.05 | 0.2 | 0.01 | 0.6 | 0 | 0 | 20.77
| 640 | 2008-06-27 | 150000 | 78.4 | -2.6 | 0.05 | 2.2 | -110.4 | 0.16 | 0.5 | 1.2 | -8.6 | 1.3 | 0 | -0.06 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.76
| 641 | 2008-06-27 | 160000 | 78.3 | -2.2 | 0.05 | 1.9 | -85.1 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0 | -0.06 | 0.1 | 0.02 | 0.6 | 0 | 0 | 20.74
| 642 | 2008-06-27 | 170000 | 78.2 | -2.5 | 0.05 | 1.8 | -88 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.2 | 0.01 | 0.3 | 0 | 0 | 20.65
| 643 | 2008-06-27 | 180000 | 79.3 | -2.3 | 0.06 | 2 | -75.2 | 0.03 | 0.5 | 1.2 | -8.6 | 1.3 | 0.01 | -0.06 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.72
| 644 | 2008-06-27 | 190000 | 79.6 | -2.6 | 0.06 | 1.9 | -84.7 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.64
| 645 | 2008-06-27 | 200000 | 79.7 | -2.3 | 0.06 | 1.7 | -72.2 | 0.03 | 0.5 | 1.2 | -8.6 | 1 | 0.01 | -0.06 | 0.2 | 0.02 | 0.4 | 0 | 0 | 20.71
| 646 | 2008-06-27 | 210000 | 79.6 | -2.3 | 0.05 | 1.7 | -71.1 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.71
| 647 | 2008-06-27 | 220000 | 79.7 | -2.4 | 0.06 | 1.9 | -79.5 | 0.03 | 0.5 | 1.2 | -8.6 | 1.2 | 0.01 | -0.06 | 0.2 | 0.02 | 0.5 | 0 | 0 | 20.72
| 648 | 2008-06-27 | 230000 | 79.7 | -2.4 | 0.07 | 2.2 | -83.5 | 0.03 | 0.5 | 1.2 | -8.6 | 1.2 | 0.01 | -0.06 | 0.2 | 0.01 | 0.5 | 0 | 0 | 20.72
| 649 | 2008-06-28 | 0 | 79.6 | -2.5 | 0.07 | 2.3 | -80.5 | 0.03 | 0.5 | 1.2 | -8.6 | 1.2 | 0.01 | -0.06 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.73
| 650 | 2008-06-28 | 10000 | 79.7 | -2.7 | 0.07 | 2.4 | -85.4 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.2 | 0.01 | 0.5 | 0 | 0 | 20.72
| 651 | 2008-06-28 | 20000 | 79.7 | -2.5 | 0.06 | 2 | -81.1 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.2 | 0.02 | 0.4 | 0 | 0 | 20.71
| 652 | 2008-06-28 | 30000 | 79.7 | -2.4 | 0.07 | 2.1 | -76.8 | 0.03 | 0.5 | 1.2 | -8.6 | 0.9 | 0.01 | -0.06 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.63
| 653 | 2008-06-28 | 40000 | 79.7 | -2.7 | 0.08 | 2.2 | -88.3 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.2 | 0.02 | 0.5 | 0 | 0 | 20.7
| 654 | 2008-06-28 | 50000 | 79.6 | -2.7 | 0.08 | 2.4 | -85.7 | 0.04 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.2 | 0.01 | 0.5 | 0 | 0 | 20.71
| 655 | 2008-06-28 | 60000 | 79.7 | -2.5 | 0.09 | 2.8 | -76.2 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.64
| 656 | 2008-06-28 | 70000 | 79.6 | -2.7 | 0.1 | 3.2 | -86.4 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.2 | 0.01 | 0.1 | 0 | 0 | 20.71
| 657 | 2008-06-28 | 80000 | 79.7 | -2.6 | 0.1 | 3.3 | -80.7 | 0.03 | 0.5 | 1.2 | -8.6 | 1 | 0.01 | -0.06 | 0.2 | 0.01 | 0.3 | 0 | 0 | 20.72
| 658 | 2008-06-28 | 90000 | 79.8 | -2.7 | 0.11 | 3.4 | -81.9 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | 2.12 | 0.4 | 0.01 | 0.5 | 0 | 0 | 20.71
| 659 | 2008-06-28 | 100000 | 80.3 | -2.5 | 0.12 | 3.6 | -78 | 0.04 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.4 | 0.01 | 0.1 | 0 | 0 | 20.71
| 660 | 2008-06-28 | 110000 | 81.7 | -2.6 | 0.09 | 2.8 | -79.3 | 0.04 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | -0.06 | 0.3 | 0.01 | 0.2 | 0 | 0 | 20.7
| 661 | 2008-06-28 | 120000 | 81.5 | -2.6 | 0.06 | 1.5 | -64.6 | 0.03 | 0.5 | 1.2 | -8.6 | 0.9 | 0.01 | -0.06 | 0.2 | 0.01 | 0.3 | 0 | 0 | 20.66
| 662 | 2008-06-28 | 130000 | 81.6 | -2.5 | 0.05 | 1.2 | -53.5 | 0.04 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.64
| 663 | 2008-06-28 | 140000 | 81.5 | -2.6 | 0.05 | 1 | -51.8 | 0.07 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.62
| 664 | 2008-06-28 | 150000 | 81.6 | -2.5 | 0.04 | 0.8 | -51.7 | 0.14 | 0.5 | 1.2 | -8.6 | 0.9 | 0 | -0.05 | 0.1 | 0 | 0 | 0 | 0 | 20.61
| 665 | 2008-06-28 | 160000 | 82 | -2.6 | 0.03 | 0.5 | -51.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.6
| 666 | 2008-06-28 | 170000 | 83 | -2.5 | 0.02 | 0.4 | -49.5 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0.01 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.59
| 667 | 2008-06-28 | 180000 | 83.2 | -2.4 | 0.03 | 0.5 | -44.2 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0.01 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.58
| 668 | 2008-06-28 | 190000 | 83.3 | -2.5 | 0.03 | 0.5 | -46.1 | 0.04 | 0.5 | 1.3 | -7.7 | 1 | 0.01 | -0.06 | 0.1 | 0.01 | 0.1 | 0 | 0 | 20.58
| 669 | 2008-06-28 | 200000 | 83.5 | -2.7 | 0.02 | 0.4 | -50 | 0.04 | 0.5 | 1.3 | -8.6 | 0.7 | 0.01 | -0.06 | 0.1 | 0.01 | 0.1 | 0 | 0 | 20.58
| 670 | 2008-06-28 | 210000 | 85.2 | -2.8 | 0.02 | 0.3 | -52.1 | 0.04 | 0.5 | 1.3 | -8.6 | 0.8 | 0.01 | -0.05 | 0.1 | 0 | 0 | 0 | 0 | 20.59
| 671 | 2008-06-28 | 220000 | 85.3 | -2.5 | 0 | 0 | -47.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.05 | 0.1 | 0.01 | 0.1 | 0 | 0 | 20.6
| 672 | 2008-06-28 | 230000 | 85.2 | -2.6 | -0.01 | -0.2 | -57.4 | 0.05 | 0.5 | 1.3 | -8.6 | 1 | 0.01 | -0.05 | 0.2 | 0.01 | 0.2 | 0 | 0 | 20.61
| 673 | 2008-06-29 | 0 | 83.5 | -2.6 | -0.02 | -0.4 | -56.8 | 0.06 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.64
| 674 | 2008-06-29 | 10000 | 83.2 | -2.3 | -0.02 | -0.6 | -56.8 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.66
| 675 | 2008-06-29 | 20000 | 83.3 | -2.5 | -0.03 | -0.8 | -66.4 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.69
| 676 | 2008-06-29 | 30000 | 83.4 | -2.6 | -0.04 | -1 | -63.2 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.07 | 0.1 | 0 | 0.1 | 0 | 0 | 20.66
| 677 | 2008-06-29 | 40000 | 83.4 | -2.7 | -0.03 | -0.7 | -60.6 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.63
| 678 | 2008-06-29 | 50000 | 83.4 | -2.5 | -0.04 | -0.8 | -60.8 | 0.04 | 0.5 | 1.3 | -8.6 | 0.9 | 0.01 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.64
| 679 | 2008-06-29 | 60000 | 83.3 | -2.4 | -0.03 | -0.6 | -57.9 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0 | 0.2 | 0 | 0 | 20.65
| 680 | 2008-06-29 | 70000 | 83.4 | -2.4 | -0.03 | -0.6 | -59.7 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.65
| 681 | 2008-06-29 | 80000 | 83.4 | -2.3 | 0 | -0.2 | -60.8 | 0.05 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.01 | 0.4 | 0 | 0 | 20.67
| 682 | 2008-06-29 | 90000 | 83.3 | -2.6 | 0 | -0.1 | -69.3 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | 2.11 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.68
| 683 | 2008-06-29 | 100000 | 83.2 | -2.4 | 0 | 0 | -67.3 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.68
| 684 | 2008-06-29 | 110000 | 83.2 | -2.8 | 0 | 0 | -71.6 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.01 | 0.4 | 0 | 0 | 20.68
| 685 | 2008-06-29 | 120000 | 83.4 | -2.4 | 0 | 0.1 | -64.3 | 0.04 | 0.5 | 1.3 | -8.6 | 1.2 | 0 | -0.06 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.67
| 686 | 2008-06-29 | 130000 | 83.4 | -2.6 | 0.01 | 0.3 | -63.2 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0.01 | -0.06 | 0.1 | 0.02 | 0.4 | 0 | 0 | 20.65
| 687 | 2008-06-29 | 140000 | 83.7 | -2.5 | 0.02 | 0.4 | -54 | 0.18 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.64
| 688 | 2008-06-29 | 150000 | 85.2 | -2.5 | 0.03 | 0.6 | -55.1 | 0.12 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.63
| 689 | 2008-06-29 | 160000 | 85.4 | -2.7 | 0.02 | 0.5 | -58.5 | 0.04 | 0.5 | 1.3 | -8.6 | 1.2 | 0 | -0.06 | 0.1 | 0.02 | 0.4 | 0 | 0 | 20.63
| 690 | 2008-06-29 | 170000 | 85.3 | -2.3 | 0.02 | 0.4 | -52.1 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0.01 | -0.06 | 0.1 | 0.02 | 0.3 | 0 | 0 | 20.63
| 691 | 2008-06-29 | 180000 | 85.4 | -2.5 | 0.01 | 0.4 | -65.8 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.68
| 692 | 2008-06-29 | 190000 | 85.2 | -2.2 | 0.02 | 0.5 | -58.2 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.06 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.68
| 693 | 2008-06-29 | 200000 | 84.9 | -2.5 | 0.01 | 0.4 | -81.8 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.06 | 0.1 | 0.02 | 0.5 | 0 | 0 | 20.72
| 694 | 2008-06-29 | 210000 | 83.2 | -2.2 | 0.02 | 0.5 | -63.6 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.05 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.69
| 695 | 2008-06-29 | 220000 | 83.2 | -2.9 | 0.02 | 0.5 | -82.2 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.69
| 696 | 2008-06-29 | 230000 | 83.3 | -2.6 | 0.02 | 0.5 | -81.2 | 0.04 | 0.5 | 1.2 | -8.6 | 1.2 | 0 | -0.06 | 0.1 | 0.01 | 0.2 | 0 | 0 | 20.71
| 697 | 2008-06-30 | 0 | 83.2 | -2.5 | 0.02 | 0.5 | -77.7 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.02 | 0.5 | 0 | 0 | 20.71
| 698 | 2008-06-30 | 10000 | 83.2 | -2.6 | 0.02 | 0.6 | -77 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.06 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.7
| 699 | 2008-06-30 | 20000 | 83.2 | -2.7 | 0.02 | 0.8 | -78.8 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.05 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.71
| 700 | 2008-06-30 | 30000 | 83.2 | -2.3 | 0.02 | 0.7 | -69.3 | 0.04 | 0.5 | 1.3 | -8.6 | 1 | 0 | -0.05 | 0.1 | 0.01 | 0.4 | 0 | 0 | 20.7
| 701 | 2008-06-30 | 40000 | 81.6 | -2.4 | 0.02 | 0.7 | -70.8 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.02 | 0.4 | 0 | 0 | 20.7
| 702 | 2008-06-30 | 50000 | 81.7 | -2.6 | 0.03 | 0.8 | -80 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 0.01 | -0.06 | 0.2 | 0.02 | 0.5 | 0 | 0 | 20.7
| 703 | 2008-06-30 | 60000 | 81.7 | -2.6 | 0.03 | 1 | -78.5 | 0.04 | 0.5 | 1.3 | -8.6 | 1.1 | 0 | -0.06 | 0.1 | 0.02 | 0.6 | 0 | 0 | 20.64
| 704 | 2008-06-30 | 70000 | 81.6 | -2.1 | 0.05 | 1.8 | -70.8 | 0.04 | 0.5 | 1.2 | -8.6 | 1.1 | 0 | -0.06 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.72
| 705 | 2008-06-30 | 80000 | 81.6 | -2.3 | 0.08 | 2.9 | -82.7 | 0.03 | 0.5 | 1.2 | -8.6 | 1 | 0 | -0.06 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.73
| 706 | 2008-06-30 | 90000 | 81.5 | 91.9 | 3.31 | 9.1 | -33.4 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 1.74 | 2.15 | 2.5 | 8.09 | 5 | 0 | 0 | 17.2
| 707 | 2008-06-30 | 100000 | 81.7 | -2.8 | 0.18 | 4.9 | -75.3 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.02 | 0 | 0.5 | 0.02 | 0.6 | 0 | 0 | 20.69
| 708 | 2008-06-30 | 110000 | 81.6 | -2.6 | 0.17 | 4.5 | -68.4 | 0.04 | 0.5 | 1.2 | -8.6 | 1 | 0.01 | -0.01 | 0.2 | 0.01 | 0.3 | 0 | 0 | 20.67
| 709 | 2008-06-30 | 120000 | 81.6 | -2.6 | 0.18 | 4.6 | -69.3 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | 0 | 0.2 | 0.01 | 0.2 | 0 | 0 | 20.67
| 710 | 2008-06-30 | 130000 | 82.5 | -2.4 | 0.19 | 4.7 | -57.8 | 0.03 | 0.5 | 1.2 | -8.6 | 1.2 | 0.01 | 0 | 0.2 | 0.01 | 0.3 | 0 | 0 | 20.66
| 711 | 2008-06-30 | 140000 | 83.1 | -2.8 | 0.2 | 4.9 | -69.5 | 0.2 | 0.5 | 1.2 | -8.6 | 1 | 0 | 0 | 0.1 | 0.02 | 0.3 | 0 | 0 | 20.66
| 712 | 2008-06-30 | 150000 | 83.1 | -2.5 | 0.21 | 5.2 | -62.7 | 0.17 | 0.5 | 1.2 | -8.6 | 1.1 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.66
| 713 | 2008-06-30 | 160000 | 82.9 | -2.5 | 0.2 | 4.8 | -59.5 | 0.03 | 0.5 | 1.2 | -8.6 | 1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 20.66
| 714 | 2008-06-30 | 170000 | 83 | -2.5 | 0.16 | 4 | -56.9 | 0.03 | 0.5 | 1.2 | -8.6 | 1.2 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.66
| 715 | 2008-06-30 | 180000 | 83.1 | -2.8 | 0.14 | 3.4 | -70.9 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0 | 0 | 0.1 | 0.02 | 0.4 | 0 | 0 | 20.67
| 716 | 2008-06-30 | 190000 | 83 | -2.4 | 0.12 | 3.3 | -66.8 | 0.03 | 0.5 | 1.2 | -8.6 | 1.2 | 0 | 0 | 0.1 | 0.02 | 0.4 | 0 | 0 | 20.68
| 717 | 2008-06-30 | 200000 | 83 | -2.7 | 0.11 | 3.3 | -78.9 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0 | 0 | 0.1 | 0.01 | 0.3 | 0 | 0 | 20.69
| 718 | 2008-06-30 | 210000 | 83 | -2.3 | 0.1 | 3.1 | -73 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | 0 | 0.2 | 0.02 | 0.5 | 0 | 0 | 20.71
| 719 | 2008-06-30 | 220000 | 82.9 | -2.5 | 0.09 | 2.8 | -79.3 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0.01 | 0 | 0.2 | 0.01 | 0.4 | 0 | 0 | 20.63
| 720 | 2008-06-30 | 230000 | 82.5 | -2.6 | 0.09 | 2.8 | -79.6 | 0.03 | 0.5 | 1.2 | -8.6 | 1.1 | 0 | 0 | 0.1 | 0.02 | 0.6 | 0 | 0 | 20.64
| 721 | 2008-07-01 | 0 | 81.5 | -2.6 | 0.09 | 2.7 | -82.4 | 0.03 | 0.5 | 1.2 | -8.593 | 1.1 | 0 | 0 | 0.1 | 0.01 | 0.4 | 0.003 | 0 | 20.71
| 722 | / | /
| 723 | / | / | -9999 | 73.611 | -115.038 | -0.744 | 4.279 | -2236.171 | 0.049 | 0.501 | 1.264 | -9999 | 0.686 | 0.012 | 0.037 | -0.288 | 0.101 | 0.891 | 75.974 | 1.731 | 20.714
[10 empty] | July Total MW-hr | 0
 | [9 empty] | Excluding non-op hours
Used gas use column to confirm operation

## PEMS June
The Combustion Turbine did not operate during June
| Total NH3 (lbs): | 0

## Monthly Emissions Report
==============================================================================
| Monthly | Emissions | Report
| Plant: | MINT | FARM | ENERGY | CTR
| Unit: | Unit | 1
==============================================================================
Report | Dates: | 2008-04-01 | - | 2008-06-30
| Month | NOx | Heat Input | SO2 | CO2 | Megawatts | CO
|  | tons | mmBtu | tons | tons | MW-hours | tons
| April | 6 | 1115872 | 0.3 | 66308.4 | 155679 | 1
| May | 0.9 | 84402 | 0 | 5016 | 11643 | 0.5
| June | 0 | 0 | 0 | 0 | 0 | 0
Report | Totals | 6.9 | 1200274 | 0.3 | 71324.4 | 167322 | 1.5

## CEM INCIDENTS
Turbine CEMS Downtime
NOx ppm @15% O2 NOx lb/hr CO ppm @15% O2 and CO lb/hr CEMS Downtime for 4/1/2008 thru 6/30/2008
Parameter | Date/Time | Duration | Duration (minutes) | Reason |  | Action
CO/NOx | 4/24/08 1300 | 1.75 hrs | 105 | Quarterly QA audit |  | Complete
Turbine Excess Emissions
NOx ppm @15% O2 24-Hr Rolling NOx lb/hr CO ppm @15% O2 and CO lb/hr Excess Emissions for 4/1/2008 thru 6/30/2008
Parameter | Date/Time | Duration | Duration (minutes) | Average | Min | Max | Limit | Reason | Action
No Excess emissions this period. Start-up and shutdown periods are indicated in the monthly "CEMS data" tabs. These periods are excluded from short term emission limits

## CEM Qrtly QA
Quarterly Linearity Check Form
Mint Farm Energy Center
| Date: | 2008-04-24 |  |  | Initials: | RL
| Time: | 10:34 |  |  | Analyzer: | O2
|  | Reference |  | Monitor |  | Monitor | Linearity
|  | Value |  | Response |  | Average | Error *
1 | Low-Level | 5.496 |  | 5.54
2 | Low-Level | 5.496 |  | 5.57 |  | 5.5533 | 1.0432
3 | Low-Level | 5.496 |  | 5.55
1 | Mid-Level | 11.51 |  | 11.5
2 | Mid-Level | 11.51 |  | 11.57 |  | 11.5467 | 0.31856
3 | Mid-Level | 11.51 |  | 11.57
1 | High-Level | 20.89 |  | 20.96
2 | High-Level | 20.89 |  | 20.95 |  | 20.9567 | 0.31913
3 | High-Level | 20.89 |  | 20.96
* The percent error is based on the reference value of the cylinder gas concentration.
Linearity error for pollutant and diluent analyzers is determined as follows:
¦ R - A ¦
| LE = | ---------------- | * 100
R
Where:
LE = Percent linearity error, based on the reference value
R = Reference value of cylinder gas
A = Average of three monitoring system responses
Quarterly Linearity Check Form
Mint Farm Energy Center
| Date: | 2008-04-24 |  |  | Initials: | RL
| Time: | 14:15 |  |  | Analyzer: | CO (Low Range)
|  | Reference |  | Monitor |  | Monitor | Linearity
|  | Value |  | Response |  | Average | Error *
1 | Low-Level | 5.597 |  | 5.52
2 | Low-Level | 5.597 |  | 5.47 |  | 5.4733 | 2.2095
3 | Low-Level | 5.597 |  | 5.43
1 | Mid-Level | 11.21 |  | 10.93
2 | Mid-Level | 11.21 |  | 10.91 |  | 10.9 | 2.7654
3 | Mid-Level | 11.21 |  | 10.86
1 | High-Level | N/A |  | N/A
2 | High-Level | N/A |  | N/A |  | N\A | N\A
3 | High-Level | N/A |  | N/A
* The percent error is based on the reference value of the cylinder gas concentration.
Linearity error for pollutant and diluent analyzers is determined as follows:
¦ R - A ¦
| LE = | ---------------- | * 100
R
Where:
LE = Percent linearity error, based on the reference value
R = Reference value of cylinder gas
A = Average of three monitoring system responses
Quarterly Linearity Check Form
Mint Farm Energy Center
| Date: | 2008-04-24 |  |  | Initials: | RL
| Time: | 13:34 |  |  | Analyzer: | CO (High Range)
|  | Reference |  | Monitor |  | Monitor | Linearity
|  | Value |  | Response |  | Average | Error *
1 | Low-Level | 513.65 |  | 579.1
2 | Low-Level | 513.65 |  | 572.8 |  | 577 | 12.3333
3 | Low-Level | 513.65 |  | 579.1
1 | Mid-Level | 1107 |  | 1095.2
2 | Mid-Level | 1107 |  | 1085.9 |  | 1089.5 | 1.5808
3 | Mid-Level | 1107 |  | 1087.4
1 | High-Level | N/A |  | N/A
2 | High-Level | N/A |  | N/A |  | N\A | N\A
3 | High-Level | N/A |  | N/A
* The percent error is based on the reference value of the cylinder gas concentration.
Linearity error for pollutant and diluent analyzers is determined as follows:
¦ R - A ¦
| LE = | ---------------- | * 100
R
Where:
LE = Percent linearity error, based on the reference value
R = Reference value of cylinder gas
A = Average of three monitoring system responses
Quarterly Linearity Check Form
Mint Farm Energy Center
| Date: | 2008-04-24 |  |  | Initials: | RL
| Time: | 12:21 |  |  | Analyzer: | NOx
|  | Reference |  | Monitor |  | Monitor | Linearity
|  | Value |  | Response |  | Average | Error *
1 | Low-Level | 25.49 |  | 24.66
2 | Low-Level | 25.49 |  | 24.88 |  | 24.7567 | 2.8769
3 | Low-Level | 25.49 |  | 24.73
1 | Mid-Level | 54.874 |  | 53.76
2 | Mid-Level | 54.874 |  | 53.76 |  | 53.76 | 2.0301
3 | Mid-Level | 54.874 |  | 53.76
1 | High-Level | 89.62 |  | 89.82
2 | High-Level | 89.62 |  | 89.18 |  | 89.3867 | 0.26036
3 | High-Level | 89.62 |  | 89.16
* The percent error is based on the reference value of the cylinder gas concentration.
Linearity error for pollutant and diluent analyzers is determined as follows:
¦ R - A ¦
| LE = | ---------------- | * 100
R
Where:
LE = Percent linearity error, based on the reference value
R = Reference value of cylinder gas
A = Average of three monitoring system responses

## Cooling Tower Emissions
TDS Sampling
Cooling Tower Discharge Samples
Date Taken |  | Value (ppm)
2008-04-30 |  | 430
2008-05-05 |  | 370
2008-05-05 |  | 448
| Avg: | 416 | ppmw
PM Emission Rate
100% PM is PM10
|  | 5e-06 | Max drift rate (0.0005%)
|  | 8.34 | weight of water (lb/gal)
|  | 77000 | Water circulation rate (gpm)
| PM/PM10 = | 0.080144 | lb/hr
PM/PM10 Emissions
| Month | Hours | Emissions
| Apr | 638.93 | 51.2064 | lbs
| May | 52.18 | 4.1819 | lbs
| Jun | 0 | 0 | lbs
|  | Total PM/PM10: | 0.027694 | tons

## PM & VOC factors
Mint Farm Energy Center
Emission Factor Calculations for Total PM and VOC
Calculations are derived from results of emission testing conducted on February 19-20, 2008.
Total Particulate Matter |  |  |  | VOC
| Emission Rate | Heat Input |  |  | Emission Rate | Heat Input
Run # | lb/hr | MMBtuH | lb/MMBtu | Run # | lb/hr | MMBtuH | lb/MMBtu
1 | 11.1 | 2338.5 | 0.0047466 | 1 | 1.9 | 2338.5 | 0.00081249
2 | 8.6 | 2288.9 | 0.0037573 | 2 | 0 | 2288.9 | 0
3 | 10.1 | 2322 | 0.0043497 | 3 | 0 | 2322 | 0
Average | 9.9333 | 2316.4667 | 0.0042845 | Average | 0.63333 | 2316.4667 | 0.00027083
Filterable Particulate Matter
| Emission Rate | Heat Input
Run # | lb/hr | MMBtuH | lb/MMBtu
1 | 1.8 | 2338.5 | 0.00076972
2 | 1.9 | 2288.9 | 0.00083009
3 | 0.72 | 2322 | 0.00031008
Average | 1.4733 | 2316.4667 | 0.00063663
Condensable Particulate Matter
| Emission Rate | Heat Input
Run # | lb/hr | MMBtuH | lb/MMBtu
1 | 9.3 | 2338.5 | 0.0039769
2 | 6.8 | 2288.9 | 0.0029709
3 | 9.3 | 2322 | 0.0040052
Average | 8.4667 | 2316.4667 | 0.003651

## Diesel Calcs
Mint Farm Generation |  |  |  | Facility ID # | 2111
Diesel Generator
| Operation: | 4 | Hours
Pollutant | Emission Factor |  |  | Emissions
NOx | 14.57 | lb/hr |  | 0.02914 | tons
CO | 0.55 | lb/hr |  | 0.0011 | tons
SOx | 0.29 | lb/hr |  | 0.00058 | tons
PM/PM10/PM2.5 | 0.68 | lb/hr |  | 0.00136 | tons
VOC | 0.06 | lb/hr |  | 0.00012 | tons
Emission Factors per ADP 04-2571R1 TSD, Section 6.e