COLUMBIA CREST ESTATES WATER SYSTEM

COWLITZ COUNTY, ID 07200P, Group A – Community

COLIFORM MCL HISTORY JANUARY 2009 – FEBRUARY 2011

| COMPLIANCEMONTH | WAC 246-290-310 Maximum Contaminant Levels (MCLs) | WAC 246-290-320 Follow-up Action | WAC 246-290-320 (2)(c) Refers to WAC 246-300 Monitoring Requirements Table 2* Minimum Monthly Routine Coliform Sampling Requirements - Last Column – When Any Samples with a Coliform Presence Were Collected During the Previous Month | RECORDKEEPING AND REPORTING WAC 246-290-480 (2)(n) and Part 7 – Reporting Subpart A - Public Notification and Consumer Information WAC 246-290-71001 – Public Notification (1)(b) and 40 CFR 141.203.(a) – Tier 2 Public Notice |
| --- | --- | --- | --- | --- |
| 2/11 |  |  |  |  |
| 1/11 |  |  |  |  |
| 12/10 |  |  | Only three of the required five routine samples were collected and analyzed. These three routine samples had satisfactory results. |  |
| 11/10 | Nonacute MCL WAC 246-290-310 (1)(a) and (2) (a)(b) and (d) (i) and (c)(i) (A)(B) | - Four repeat samples were collected and analyzed as required by WAC 246-290-320 (2) (a) and (b). - Not known if the customers were notified of the Nonacute MCL as required by WAC 246-290-320 (1) (b) (ii). - Not known what follow-up action was done to determine the cause or to correct the contamination problem as required by WAC 246-290-320. |  | Was a Certification received by ODW- No Was a copy of the Tier 2 Nonacute MCL notice received by ODW - No |
| 10/10 |  |  |  |  |
| 9/10 |  |  |  |  |
| 8/10 |  |  |  |  |
| 7/10 |  |  |  |  |
| 6/10 |  |  |  |  |
| 5/10 |  |  |  |  |
| 4/10 |  |  |  |  |
| 3/10 |  |  | Five of the required five routine samples were collected and analyzed. All five routine samples had satisfactory results. |  |
| 2/10 | Nonacute MCL WAC 246-290-310 (1)(a) and (2) (a)(b) and (d) (i) and (c)(i) (A)(B) | - Five repeat samples were collected and analyzed as required by WAC 246-290-320 (2) (a) and (b). (Four samples are required; OK that five were collected.) - Not known if customers were notified of the Nonacute MCL as required by WAC 246-290-320 (1)(b)(ii). - Not known what follow-up action was done to determine the cause or to correct the contamination problem as required by WAC 246-290-320. |  | Was a Certification received by ODW - Yes Was a copy of the Tier 2 Nonacute MCL notice received by ODW - Yes |
| 1/10 |  |  |  |  |
| 12/09 |  |  |  |  |
| 11/09 |  |  |  |  |
| 10/09 |  |  |  |  |
| 9/09 |  |  |  |  |
| 8/09 |  |  |  |  |
| 7/09 |  |  |  |  |
| 6/09 |  |  |  |  |
| 5/09 |  |  |  |  |
| 4/09 |  |  |  |  |
| 3/09 |  |  | The five required routine samples and one extra routine sample were collected and analyzed. All six routine samples had satisfactory results. |  |
| 2/09 | Nonacute MCL WAC 246-290-310 (1)(a) and (2) (a)(b) and (d) (i) and (c)(i) (A)(B) | - Three of the required four repeat samples were collected as required by WAC 246-20-320(2) (a) and (b). - Not known if customers were notified of the Nonacute MCL as required by WAC 246-290-320 (1) (b) (ii). - Not known what follow-up action was done to determine the cause or to correct the contamination problem as required by WAC 246-290-320. |  | Was a Certification received by ODW - Yes Was a copy of the Tier 2 Nonacute MCL notice received by ODW - Yes |
| 1/09 |  |  |  |  |

WAC 246-290-320 Follow-Up Action:

246-2990-320(a)(i) -  The sample is analyzed for fecal coliform or E. coli.  When a sample with a coliform presence is not analyzed for E. coli or fecal coliform, the sample shall be considered having a fecal coliform presence for MCL compliance purposes.   (The samples were fully analyzed as required.  The samples were satisfactory or unsatisfactory - total coliform positive, E. coli absent.)

*Table incorrectly labeled as Table 1 in WAC 246-290 – Revised 12/10.

Do not know if ODW was notified in all situations of the unsatisfactory samples by the owner or operator.  ODW receives copies of the sample results from the laboratory that analyzed the samples.