Proposed Rule:

###### WAC  480-93-015  Odorization of gas

(1)  All gas that is transported by pipeline and all gas consumed by an end use customer must be odorized in accordance with CFR 49, Part 192 section 625 excluding paragraphs (b)(1) and (b)(3).

(2)  Operator’s must use odorant testing instrumentation when conducting  odorant  level checks (sniff tests).  Sniff tests must be performed at least monthly.

Comment: Cascade Natural Gas would like to know why sniff tests must be performed at least monthly.

(3)  Instruments used to detect odorant concentration must be calibrated in accordance with the manufactures recommendation.  When there is no manufacturers recommendation calibration must be done at least once each calendar year.

(4)  All records of odorant usage, sniff tests performed, and equipment calibration must be kept for five years.

Comment: Cascade Natural Gas would like to know why five years of record storage is deemed necessary.

Proposed Rule:

###### WAC     480-93-018  Maps, drawings, and records of gas facilities

(1)  Each gas company must prepare, maintain, and make available to the commission or its designated representatives all maps, drawings, and records of the company's gas facilities.  The maps, drawings, and records must show the size and type of material of all facilities, corrosion control, and the maximum allowable operating pressure.  The maps and drawings must indicate the location of all district regulator and gate stations and location of all valves, identifying the emergency valves specified in the company's emergency plan.  The gas company must provide key sheets for ready reference as needed.

Comment: In order to support the industry’s heightened security efforts subsequent to September 11, 2001, NW Natural strongly suggests that all documents pertaining to the exact location of pipeline facilities must not be provided to the public or any public agency. These documents are, however, available for review by Staff.

- Each gas company must make books, records, reports, and other information available to the commission, so the commission or its authorized representatives can determine whether the gas company is in compliance with state and federal regulations.

(3)  All construction records, revision to maps and operating history made available to appropriate operations personnel must be updated every 6 months.

Comment: NW Natural, Cascade Natural Gas and Avista Utilities suggest deleting this requirement or limiting it to transmission lines and mains. Updating all the documentation for the thousands of services added within the 6-month time frame would be excessively burdensome, particularly if there have been no changes to the records.

Proposed Rule:

WAC     480-93-080  Welder  and Joiner identification and qualification certificates

(1)  All welding procedures and welders must be qualified to API Standard 1104 or section IX of the ASME Boiler and Pressure Vessel Code.  Each welder qualification test result must be recorded and kept for a period of 5 years

Comments: Avista Utilities suggests that Appendix C of part 192 be included in this proposed rule since it is an acceptable procedure under federal pipeline safety code. Cascade Natural Gas requests that Staff elaborate why the 49 CFR 192 Appendix C requirements are not acceptable for pipelines operating with a hoop stress under 20% SMYS.

(a) Operators must use testing equipment necessary to measure the essential variables during welder qualification or requalification, and also for procedure qualification or requalification.  All essential variables must be recorded as performed during the welding qualification.

Cascade Natural Gas requests that Staff defines “essential variables.”

(b)  Qualified welding procedures must be on site where welding is being performed.

(2)  Each operator must have qualified written procedures for the joining of gas pipelines by means other than welding.

- Qualified joining procedures must be on site where joining is being performed.

Comment: Please define joining procedures. Are they limited to fusing or do they include mechanical joining techniques?

- Personnel qualified to join gas pipeline facilities must be requalified each calendar year not to exceed 15 months.

(c) Each joiner qualification test result must be recorded and kept for a period of 5 years.

(3)  Welders and joiners must carry appropriate identification and qualification cards showing the name of welder or joiner, their qualifications, date of qualification expiration, and the company whose procedures were followed for the qualification.  Welders and joiners qualification cards will be subject to commission inspection at all times when qualified personnel are working on facilities subject to Commission jurisdiction.

Proposed Rule:

###### WAC     480-93-082  Qualification of employees

Staff recommends deleting this rule

Proposed Rule:

WAC     480-93-120   Aboveground facilities

(1)  All exposed pipelines and associated equipment must have pipeline markers and other protective measures taken at any point where gas pipelines and any associated equipment are exposed.

Comment: The term "protective measures" is unclear. The issue of marking pipelines is included in WAC 480-93-124. Suggest deleting this rule.

Proposed Rule:

###### WAC     480-93-124  line markers for mains and transmission lines

Comment: Line markers for mains and transmission lines is the title of 49 CFR part 192 section 707. This is referenced in paragraph (1) of the proposed rule.

(1) Line markers must be placed at all railroad, road, irrigation, and drainage ditch crossings, and at all fence lines where a line crosses private property.  Line markers must be placed approximately 500 yards apart, if practical, and   where the angle of the line changes direction.  Exceptions to this rule must conform to 49 CFR, Part 192.707(b).

Comment: The term “ deflection” infers unsatisfactory loading of the pipe to cause direction away from its normal course. Application of this rule to all fence lines would be disruptive, impractical and expensive.

(2) All gas pipelines attached to bridges or otherwise spanning an area must have line markers at both ends of the suspended pipeline.  Each gas company must annually inspect and maintain the markers to ensure they are visible and legible.  Markers that are reported damaged and missing must be replaced within 30 days.

Comments: NW Natural and Avista Utilities suggest revising the timeframe for replacing line markers to 45 days. Consistency throughout the proposed rules would be beneficial. Cascade Natural Gas requests Staff to comment on why a prescribed replacement schedule is deemed necessary.  Avista Utilities and Cascade Natural Gas would like to know what the basis is for proposing a separate annual marker survey program.

- line marker survey must be conducted every three years and the recorded results must be kept for a minimum of 6 years.

Comment:  CFR part 192 section 709(c) requires that similar records be kept for a minimum of 5 years. Six years could cause a duplication of efforts by staff inspecting records in two cycles. Suggest keeping records for 5 years for consistency and inspection efficiency.

###### Proposed Rule:

###### WAC     480-93-155  Increasing maximum operating pressure

Each gas company must submit to the commission for approval, complete written plans and drawings at least 45 days before uprating to a maximum allowable operating pressure (MAOP) greater than  60 psig.  The plan must include a review of the following:

(1) 	All affected gas facilities, including pipe, fittings, valves, and other affected equipment, with their manufactured design operating pressure and specifications;

(2) 	Original design and construction standards;

(3) 	All previous operating pressures and length of time at that pressure;

(4) 	All leaks, regardless of cause, and the date and method of repair;

(5) 	All upstream and downstream regulators and relief valves;

(6) 	All cathodic protection readings on mains for the past three years or three most recent inspections, whichever is longer, and the most recent inspection on each attached service line, which is electrically isolated; and

(7) 	Additional records deemed necessary to evaluate the pressure increase.(8)       Uprates must be based on a previous strength test that would substantiate the  proposed MAOP.   When there is no documented history of strength tests, one must be conducted in conjunction with the uprate.

Comment: Uprates are generally performed while pipelines are in operation and it is not feasible or desirable to take them out of service to test. Pressure testing a pipeline with natural gas to 1½ times the new MAOP may not be in the best interest of public safety. Suggest deleting statement (8).

Proposed Rule:

WAC     480-93-180  Plan of operations and maintenance procedures; emergency policy; reporting requirements

Each gas company must have written operation, maintenance, emergency, and inspection plans and procedures in compliance with the provisions and general intent of the federal “Natural Gas Pipeline Safety Act.”   Such plans and procedures, and amendments, must be practicable and designed to enhance safety and must be filed with the commission for review.  The commission may, after notice and opportunity for hearing, require such plans and procedures be revised in accordance with Title 49, Part 192 and 480-93 WAC.

Comment: Inspection is included in 49 CFR Part 192, subparts I, L and M. Suggest deleting this term or defining where the term exceeds Part 192 requirements.

Proposed Rule:

WAC     480-93-190  Being aware of construction work near gas company facilities

Staff recommends deleting  this rule

(1) Each gas company must subscribe to the available "one call locating service" in every area their facilities are located.

(2) Each gas company must establish procedures for notification of all construction work in close proximity to gathering lines, mains, service lines, transmission lines, and other gas facilities.

#### LEAKS

Staff recommends deleting this rule

WAC 480-93-184  Gas leak responsibility.

Each gas company shall designate personnel who shall be responsible for pipeline and service line patrolling; leak survey practices, procedures, and operations; and

leak classification and repairs within its respective areas of operation (i.e. division, district, etc.).

Proposed Rule:

WAC     480-93-185   Failure investigation

- Each gas company must promptly investigate any notification of a leak, explosion, or fire, which may involve gas pipelines or other gas facilities, received from any outside source.  .  . Where the investigation reveals a leak, the leak must graded in accordance with WAC 480-93-186 and appropriate action must be taken in accordance with these rules.

Comments: The above statement designating authority to the WUTC is contradictory to federal regulation. 49 CFR part 192 section 617 states:

“Each operator shall establish procedures for analyzing accidents and failures, including the selection of samples of the failed facility or equipment for laboratory examination, where appropriate, for the purpose of determining the causes of the failure and minimizing the possibility of recurrence.”

This definition of jurisdiction may prevent the operator from complying with the requirements of §192.617.

There is also a legal concern regarding preservation of evidence at the site until the Commission authorizes the release of the gas facility for failure analysis.

The leak grading requirements belong in §480-93-186. Suggest this language be struck out. Under some circumstances, improved or additional information will legitimately support changing a grade 1 or 2 leak to a grade 3 leak without a physical repair having been made to the pipeline facility.

(2)  When leak indications are found to originate from a foreign source or facility, such as gasoline vapors, sewer or marsh gas, or customer-owned piping, prompt action must be taken, to protect life and property.  All Leaks that represent an ongoing, potentially hazardous situation must be reported promptly to the owner or operator of the source facility and, where appropriate, to the police department, or other appropriate governmental agency.  In all cases, the property owner or the adult person occupying the premises must be notified of the leak conditions.

If no methane (or propane) indication is found, the gas company employee on-site must inform the property owner or the adult person occupying the premises, and must request the adult person occupying the premises to sign the gas company work order.  The gas company employee must provide the adult person occupying the premises an odor sniff card that identifies the odor of gas (or propane) and indicates the name, address, and telephone number of the gas company representative to be contacted if the leak indications are again noticed.

Comments: NW Natural and Avista Utilities suggest deleting the odor sniff card requirement. Problems have occurred with the customer disposing of the card and creating false odor calls based on these cards. We also suggest deleting the requirement of having the adult person occupying the premises to sign the gas company work order based on legal counsel’s suggestion given that the customer is not usually aware of what they are signing and why.

If the property owner or an adult person occupying the premises is not available, the gas company must, within  24 hours of the leak notification, send by first-class mail addressed to the person occupying the premises, a letter explaining the results of the investigation.  A copy of the letter must be retained by the gas company and kept with the leak report.  A leak investigation report form must be maintained in the gas company's leak report files for all leaks investigated, indicating gas company employee making the initial leak evaluation.

Proposed Rule:

WAC     480-93-186  Leakage classification and action criteria

(1)  Based on an evaluation of the location and/or magnitude of a leak, one of the following leak grades shall be assigned, thereby establishing the leak repair priority. A gas company may utilize an alphabetical grade classification, i.e. Grade A for Grade 1, Grade B for Grade 2, and Grade C for Grade 3 if it has historically utilized such a grading designation.  The same criteria for initial leak grading must be applied to re-inspected leaks.

(2)  Gas leak classification and repair.  Each gas company must establish a procedure for evaluating the concentration and extent of gas leakage.  When evaluating any leak, the perimeter of the leak area must be determined and documented.  If the perimeter of the leak extends to a building wall, the investigation must extend inside the building.

(3)   Leak grades.

(a)  Grade 1 - Grade 1 means a leak that represents an existing or probable hazard to persons or property and requiring immediate repair or continuous action until conditions are no longer hazardous.

- Grade 2 - Grade 2 means a leak recognized as being nonhazardous at the time of detection but requiring scheduled repair based on probable future hazard.

(c)  Grade 3 - Grade 3 means a leak that is non-hazardous at the time of   detection and can reasonably be expected to remain non-hazardous.

Leakage classification and control requirements are provided in Table 1.  The examples of leakage provided in the table are guidelines and are not exclusive.

(4)   Follow-up inspections.   The perimeter of the leak area must be checked with a Combustible Gas Indicator.  Grade 1 leaks with residual gas in the ground must be re-inspected as soon as practical and no later than one month following the repair.  In the case of Grade 2 or Grade 3 leaks which have been repaired, the need for a follow-up inspection must be determined by  qualified personnel employed or retained by the gas company.

Proposed Rule:

WAC 480-93-18601   Table 1--Leak classification and action criteria--Grade--Definition--Priority of leak repair--Examples

| TABLE 1--LEAK CLASSIFICATION AND ACTION CRITERIA |
| --- |
| GRADE 1 DEFINITION A leak that represents an existing or probable hazard to persons or property and requires immediate repair or continuous action until the conditions are no longer hazardous. |
| PRIORITY OF LEAK REPAIR Comment: Placing this table in table format will keep the margins aligned correctly. | EXAMPLES Comment: Examples become prescriptive when performance language is used, such as 80% LEL or six months. Suggest removing specific values from the examples in this column. |
|  | Leaks requiring prompt action: |
| Requires prompt action* to protect life and property and continuous action until the conditions are no longer hazardous. *The prompt action in some instances may require one or more of the following: | Any leak which, in the judgment of operating personnel at the scene, is regarded as an immediate hazard. 2. Escaping gas that has ignited unintentionally |
| Implementation of company emergency plan (192.615). Evacuating premises. | 3. Any indication of gas, which has migrated into or under a building or tunnel. |
| Blocking off an area. Rerouting traffic. Eliminating sources of ignition Venting the area, or Stopping the flow of gas by closing valves or other means. Notifying police and fire department | 4. Any reading at the outside wall of a building or where the gas would likely could potentially migrate to the outside wall of a building. 5. Any high reading in a confined space. |
|  | 6. Any reading in small substructures not associated with gas facilities where the gas would likely could potentially migrate to the outside wall of a building. 7. Any leak that can be seen, heard, or felt and which is in a location that may endanger the general public or property. |

GRADE 2

DEFINITION

A leak that is recognized as being nonhazardous at the time of detection but justifies scheduled repair based on probable future hazard.

PRIORITY OF LEAK REPAIR 		EXAMPLES

Comments: Placing this table in table format will keep the margins aligned correctly. Examples become prescriptive when performance language is used, such as 80% LEL or six months. Suggest removing specific values from the examples in this column.

Leaks should be repaired or			A. Leaks requiring action ahead of

cleared in 1 year but shall		ground freezing or other

not exceed 15 months from		adverse changes in venting

the date reported.  If a Grade			conditions:

2 leak occurs in a segment of

pipeline which is under			1. Any leak, which under frozen

consideration for replacement,		or other adverse soil

an additional 6 months may be		conditions, would likely could potentially

added to the 15 months maximum		migrate to the outside of a

time for repair noted above.  In		building.

determining the repair priority,

criteria such as the following			B. Leaks requiring

should be considered:				:

Comment: The example indicates a shorter response time (6 months) than the proposed code requirement in column 1 (1 year).

a. Amount and migration of		1. Any reading

gas,					under a sidewalk in

b. Proximity of gas to			a wall-to-wall paved area

buildings and subsurface			that does not qualify as a

structures,					Grade 1 leak and where gas

c. Extent of pavement, and		is likely   could potentially to migrate to

the outside wall of a building.

d. Soil type and conditions,

such as frost cap, moisture

and natural venting.			2. Any high reading

under a street in a

Grade 2 leaks shall be re-			wall-to-wall paved area that

evaluated at least once every six		does not qualify as a Grade

months until cleared.  The			1 leak and where the gas is

frequency of reevaluation should be		likely could potentially to migrate to the

determined by the location and		outside wall of a building.

magnitude of the leakage

condition.					3. Any high reading

in small substructures

not associated with gas

facilities where gas would

.			likely could potentially migrate creating a

probable future hazard.

4. Any reading 		 in a confined

space that causes concern.

5. Any reading on a pipeline

operating at 30% SMYS or

greater in Class 3 or 4

locations that does not

.			qualify as a Grade 1 leak.

Comment: The above statement is unnecessary.

On the other hand, there will be		6. Any leak which in the

many Grade 2 leaks, which because		judgment of operating

of their location and magnitude,		personnel at the scene is of

can be scheduled for repair on a		sufficient magnitude to

normal routine basis with			justify scheduled repair.

periodic reinspection as necessary.

GRADE 3

DEFINITION

A leak that is nonhazardous at the time of detection and can reasonably be expected to remain nonhazardous.

PRIORITY OF LEAK REPAIR		EXAMPLES

Comments: Placing this table in table format will keep the margins aligned correctly. Examples become prescriptive when performance language is used, such as 80% LEL or six months. Suggest removing specific values from the examples in this column.

Grade 3 leaks should be re-		Leaks requiring reevaluation at

evaluated during the next			periodic intervals:

scheduled survey, or within 15

months of the reporting date,			1. Any reading of less than 80%

whichever occurs first, until			LEL in small gas associated

the leak is regraded or no			substructures such as small

longer results in a reading.			meter boxes or gas valve boxes.

2. Any reading under a street in

areas without wall-to-wall paving

where it is unlikely the gas could

migrate to the outside wall of a

building.

3. Any low reading

in a confined space.

[Statutory Authority:  RCW 80.01.040.  92-16-100 (Order R-375, Docket No. UG-911261), § 480-93-18601, filed 8/5/92, effective 9/5/92; Order R-103, Table 1 (codified as WAC 480-93-18601), filed 5/18/77.]

Proposed Rule:

WAC     480-93-187 Gas Leak records and self audit

(1) 	Gas leak records.  Each gas company must prepare and maintain permanent gas leak repair records.  The leak repair records must contain sufficient data and information to permit the commission to assess the adequacy of the company maintenance programs and to provide the data and information required by RSPA F-7100.1, F-7100.1-1, F-7100.2, and F-7100.2-1 leak report.

(2) 	Gas Leak Reports.  Data and information which cannot reasonably be expected to be available under the particular circumstances of a leak situation need not be reported immediately, but at a minimum must include the following:

(a) 	Date and time detected, investigated, and reported and the name of employees conducting the detection, investigation and report;

(b) 	Date and time the leak was reevaluated before repair, and the name of the employee involved;

(c) 	Date and time of repair, when a Grade 1 leak is involved, and the name of the employee in charge of the repair;

(d) 	Date and time the leak was rechecked after repair and the employee involved;

(e) 	Location of leak (sufficiently described to allow ready location by other qualified personnel);

(f) 	Leak grade;

(g) 	Pipeline classification (distribution, transmission, etc.);

(h) 	Method of leak detection (if reported by outside party, list name and address);

(i) 	Part of system where leak(s) occurred  (main, service, etc.);

(j) 	Location on the system where leaked  (pipe, valve, fitting, compressor or regulator station, etc.);

(k) 	Material which leaked (steel, plastic, cast iron, etc.);

(l) 	Origin of leak;

(m) 	Pipe description;

(n) 	Type repair;

(o) 	Leak cause;

(p) 	Date pipe installed (if known);

- Corrosion control method;

- Magnitude of Combustible Gas Indicator readings and relative location to leak; and

- Unique identification numbers (such as serial numbers) of leak detection equipment.

(3) 	Self audits.  Each gas company must ensure:

(a) 	All repairs are made within the time required;

(b) 	All leak repairs are effective; and

(c) 	Records are accurate.

Proposed Rule:

WAC     480-93-188  Gas leak surveys

(1)	Types of gas leak surveys and test methods.

Each gas company must have a leak detection program.  A gas leak survey must be conducted using a gas detection instrument covering:

(a)  	all mains and services, including the testing of the atmosphere near utility (gas, electric, telephone, sewer, water) and other underground structures;

(b)  	cracks in paving, and in wall-to-wall paved areas, the cracks in sidewalks;

(c)  	building walls; and

(d)  	other areas where gas can migrate.

(2) 	Maintenance and calibration of instruments.  All instruments used in leak detection and evaluation shall must be maintained, calibrated, and operated in accordance with the recommended latest manufacturers' specifications and methods.  If there is no manufacture’s recommendation, calibration must be done once each calendar year.

(3) 	Frequency of surveys in designated areas.  Gas leakage surveys must be conducted according to the following specified frequencies:

(a) 	Business areas - once each calendar year, not exceeding fifteen months;

(b) 	Residential areas - as frequently as necessary, not exceeding five years;

(c) 	Buildings of public assembly - once each calendar year, not exceeding fifteen months;

(d) 	Special surveys such as floods, earthquake, land movement- as required; and

(e) 	Where the gas system has cast iron, wrought iron, or ductile iron, or noncathodically protected bare steel, galvanized steel, or coated steel pipe - twice each calendar year not exceeding eight months.

(4) 	Business areas and buildings of public assembly.  Gas leakage surveys of business areas and public buildings must be conducted on the following basis:

(a) 	Where gas service lines exist, a survey must be conducted at the building wall at the point of entrance, using a bar hole where necessary;

(b) 	Surveys must be conducted within all buildings where gas leakage has been detected at the outside wall at all points and where escaping gas potentially migrate into and accumulate inside the building; and

(c) 	Service piping, riser piping and meter(s) must be checked with gas detection instrument or with a soap solution.

Comments:  Paragraphs (4)(b) and (c) should be moved to 480-93-186. Cascade Natural Gas requests that Staff define “building of public assembly” and which of them are required to be surveyed.

(5) 	Special surveys.  Special leakage surveys must be conducted in the following circumstances:

(a) 	Prior to resurfacing, repairs, or  street alterations, where gas facilities are under the area to be paved, and where there is a potential that damage occurred to gas facilities, a gas survey, including manholes and other street openings, must be made;

(b) 	In areas where substructure construction adjacent to underground gas facilities occurs, where there is a potential that damage could have occurred to the gas facilities, an appropriate gas detection survey must be made following the completion of installation but prior to paving;

(c) 	Unstable soil areas where active gas lines could be affected;

(d) 	Special surveys must be made annually of places of public assembly when an active gas service line serves the building or where active gas service lines or mains are located with such close proximity as to present a possible hazard should leakage occur, for example, churches; schools; and hospitals;

(e) 	In areas of unusual activity, such as, earthquake, and explosions.

(6) 	Leak survey records.  The current and immediately preceding survey of an area records, must be maintained:

(a) 	Description of system and area surveyed (this could include maps and leak survey logs);

(b) 	Survey results;

(c) 	Survey method;

(d) 	Name of employees making survey; and

(e) 	Survey dates

(8) 	Self audits.  Each gas company is required to perform self audits of the effectiveness of their leak detection program.  The following self audits must be performed as frequently as necessary, not exceeding three years:

(a) 	Leak survey schedule must assure that it is commensurate with the minimum federal safety standards for gas pipelines, Subpart M-Maintenance, and the general condition of the pipeline system as required by other applicable regulations;

(b) 	Survey effectiveness - evaluate survey results to assure that a consistent evaluation of leaks is being made throughout the system; and

(c) 	Check the adequacy of records.

[Statutory Authority:  RCW 80.01.040 and 80.04.160.  01-11-003 (Docket No. UG-990294, General Order No. R-484), § 480-90-999, filed 5/3/01, effective 6/3/01.]