A completed Standard Inspection Checklist, OQ Field Validation Protocol form and Cover Letter/Field Report are to be submitted to the Senior Engineer within 30 days from completion of the inspection.

| Inspection Report |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Docket Number |  | PG-060217 |  |  |  |
| Inspector/Submit Date |  | Patti Johnson/05-19-2006 |  |  |  |
| Sr. Eng Review/Date |  | Dave Lykken/05-25-2006 |  |  |  |
| Operator Information |  |  |  |  |  |
| Name of Operator: | Cascade Corporation |  |  | OP ID #: |  |
| Name of Unit(s): | Aberdeen District |  |  |  |  |
| Records Location: | 713 W. Wishkah, Aberdeen |  |  |  |  |
| Date(s) of Last (unit) Inspection: | October 4 – 8, 2004 |  | Inspection Date(s): | April 18 – 21, 2006 Exit meeting 5-16-2006 |  |

Inspection Summary:

Six probable violations, as noted in the enclosed report and one area of concern. The revised O&M manual has been will be in effect by June and will be providing training on all updated and new procedures to its field personal in the coming months. CNG expects to ensure more accurate record keeping and better field practices.

| HQ Address: |  |  | System/Unit Name & Address: |  |
| --- | --- | --- | --- | --- |
| 222 Fairview Ave N Seattle, WA 98109 |  |  | 713 W Wishkah Aberdeen, WA 98520 |  |
| Co. Official: Phone No.: Fax No.: Emergency Phone No.: | Dan Meredith |  | Phone No.: Fax No.: Emergency Phone No.: | (360) -532-0400 |
|  | (206) 654-4069 |  |  |  |
|  | (206) 654-4069 |  |  | (360) 532 2541 |
|  | (206) 381-6720 |  |  |  |
| Persons Interviewed |  | Title |  | Phone No. |
| John Hubler |  | General Manager |  | (360) 532-2541 & (360) 532-0400 |
| Joe Maxwell |  | Manager Corrosion Control |  | (360) 532-2541 & (360) 532-0400 |
| Sam Hicks |  | Pipeline Safety Specialist |  | (360) 532-2541 & (360) 532-0400 |
| Pat Bradford |  | Aberdeen/Longview Office Manager |  | (360) 532-2541 & (360) 532-0400 |
| Terry Melton |  | Utility A |  | (360) 532-0400 |
| Dick Emile |  | Service Mechanic A |  | (360) 532-0400 |

| WUTC staff conducted an abbreviated procedures inspection on 192 O&M and WAC items that changed since the last inspection. This checklist focuses on Records and Field items per a routine standard inspection. (check one below and enter appropriate date) |  |  |  |
| --- | --- | --- | --- |
|  | Team inspection was performed (Within the past five years.) or, | Date: | NA |
|  | Other WUTC Inspector reviewed the O & M Manual (Since the last yearly review of the manual by the operator.) | Date: | May 2-5-, 2005 Longview/Kelso Inspection |

| GAS SYSTEM OPERATIONS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Gas Supplier |  | Williams |  |  |  |
| Services: Total is approximately 6,347. Residential 5,258 Commercial 144 Industrial 29 Other 0 |  |  |  |  |  |
| Number of reportable safety related conditions last year 5 in 2005 |  |  |  | Number of deferred leaks in system 0 |  |
| Number of non-reportable safety related conditions last year 12 |  |  |  | Number of third party hits last year 14 in 2005, 0 to April, 2006 |  |
| Miles of transmission pipeline within unit (total miles and miles in class 3 & 4 areas) 18.49 miles, designed to class 4 |  |  |  | Miles of main within inspection unit(total miles and miles in class 3 & 4 areas) 83.04 miles of HP main, 184.89 miles of main all designed to class 4 |  |
| Operating Pressure(s): |  |  |  | MAOP (Within last year) | Actual Operating Pressure (At time of Inspection) |
| Feeder: | Regulator Station 01, Wishkah Rd |  |  | 150 | 138 |
| Town: | Aberdeen/Hoquiam Montesano El\ma McCleary Shelton system 1 Shelton system 2 |  |  | 60 psig 25 25 25 27 25 | 55 psig 20 20 20 24 21 |
| Other: | 8 inch Kitsap line |  |  | 400 psig MAOP | 250 psig |
| Does the operator have any transmission pipelines? |  |  | yes |  |  |
| Compressor stations? Use Attachment 4. |  |  | None in Aberdeen District |  |  |

| Pipe Specifications: |  |  |  |
| --- | --- | --- | --- |
| Year Installed (Range) | 1962 to Present | Pipe Diameters (Range) | ½ “ to 12 inch |
| Material Type | pe, steel wrap | Line Pipe Specification Used | PE-ASTM D-2513 PE 3408 ½"-4" Steel-API 5L ½"-12" Grade B X-42 |
| Mileage | 286.42 miles of main | SMYS % | 12% |

Operator Qualification Field Validation

Important: Per OPS, the OQ Field Inspection Protocol Form (Rev 2, Feb 06) shall be used by the inspector as part of this standard inspection. When completed, the inspector will upload this information into the PHMSA OQ Database located at http://primis.phmsa.dot.gov/oqdb/home Date Completed/Database updated 4-21-2006

| REPORTING RECORDS |  | S | U | N/A | N/C |
| --- | --- | --- | --- | --- | --- |
| 191.5 | Telephonic reports to NRC (800-424-8802) Note: none | X |  |  |  |
| 480-93-200(1) | Telephonic Reports to UTC Pipeline Safety Incident Notification 1-888-321-9146 (Within 2 hours) for events which; (eff 6/02/05) Note: none |  |  | X |  |
| 480-93-200(1)(a) | Result in a fatality or personal injury requiring hospitalization; Note: none |  |  | X |  |
| 480-93-200(1)(b) | Results in damage to property of the operator and others of a combined total exceeding fifty thousand dollars; Note: none |  |  | X |  |
| 480-93-200(1)(c) | Results in the evacuation of a building, or high occupancy structures or areas; (eff 6/02/05) Note: none |  |  | X |  |
| 480-93-200(1)(d) | Results in the unintentional ignition of gas; Note: none |  |  | X |  |
| 480-93-200(1)(e) | Results in the unscheduled interruption of service furnished by any operator to twenty five or more distribution customers; Note: none |  |  | X |  |
| 480-93-200(1)(f) | Results in a pipeline or system pressure exceeding the MAOP plus ten percent or the maximum pressure allowed by proximity considerations outlined in WAC 480-93-020; (eff 6/02/05) Note: none |  |  | X |  |
| 480-93-200(1)(g) | Is significant, in the judgment of the operator, even though it does not meet the criteria of (a) through (e) of this subsection; or Note: none |  |  | X |  |
| 480-93-200(1)(h) | Results in the news media reporting the occurrence, even though it does not meet the criteria of (a) through (e) of this subsection. | X |  |  |  |
| 480-93-200(2) | Telephonic Reports to UTC Pipeline Safety Incident Notification 1-888-321-9146 (Within 24 hours) for; | X |  |  |  |
| 480-93-200(2)(a) | The uncontrolled release of gas for more than two hours; (eff 6/02/05) Note: none |  |  | X |  |
| 480-93-200(2)(b) | The taking of a high pressure supply or transmission pipeline or a major distribution supply pipeline out of service; (eff 6/02/05) Note: none |  |  | X |  |
| 480-93-200(2)(c) | A pipeline or system operating at low pressure dropping below the safe operating conditions of attached appliances and gas equipment; or (eff 6/02/05) Note: none |  |  | X |  |
| 480-93-200(2)(d) | A pipeline or system pressure exceeding the MAOP (eff 6/02/05) | X |  |  |  |
| 191.15 | Annual (federal) reports; supplemental incident reports (DOT Form F 7100.2) | X |  |  |  |
| 480-93-200(4) | Written incident reports (within 30 days); supplemental incident reports | X |  |  |  |
| 480-93-200(5) | Written report within 45 days of receiving the failure analysis of any incident or hazardous condition due to construction defects or material failure (eff 6/02/05) Note: none |  |  | X |  |
| 191.17(a) | Annual Report (DOT Form PHMSA F-7100.2-1) Note: none |  |  | X |  |
| 480-93-200(6)(a) | To the Commission a copy of PHMSA F-7100.1-1 and F-7100.2-1 annual report required by U.S. Department of Transportation, Office of Pipeline Safety (eff 6/02/05) | X |  |  |  |
| 480-93-200(6)(b) | Annual Damage Prevention Statistics Report (eff 6/02/05) | X |  |  |  |
| 480-93-200(6)(c) | Annual report on construction defects or material failures (eff 6/02/05) Note: none |  |  | X |  |
| 480-93-200(7) | Providing updated emergency contact information to the Commission and appropriate officials | X |  |  |  |
| 480-93-200(8) | Providing daily construction and repair activities reports (eff 6/02/05) | X |  |  |  |
| 480-93-200(9) | Submitting copy of DOT Drug and Alcohol Testing MIS Data Collection Form when required (eff 6/02/05) | X |  |  |  |
| 191.23 | Safety related condition reports Note: none |  |  | X |  |
| 191.25 | Filing the SRCR within 5 days of determination, but not later than 10 days after discovery Note: none |  |  | X |  |
| 192.727(g) | Abandoned facilities offshore, onshore crossing commercially navigable waterways reports Note: none |  |  | X |  |

| Documentation Reviewed: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Document Title | Document Number | Revision Date | Date Range Reviewed | Pct of Data Reviewed |
| Annual Report |  |  | 2005 |  |

Comments:

| CUSTOMER and EXCESS FLOW VALVE INSTALLATION NOTIFICATION |  | S | U | N/A | N/C |
| --- | --- | --- | --- | --- | --- |
| 192.16 | New customers notified, within 90 days, of their responsibility for those service lines not maintained by the operator | X |  |  |  |
| 192.381 | Does the excess flow valve meet the performance standards prescribed under §192.381? | X |  |  |  |
| 192.383 | Does the operator have a voluntary installation program for excess flow valves and does the program meet the requirements outlined in §192.383? Are records adequate? Note: no voluntary program |  |  | X |  |
| 192.383 | If no voluntary program for EFV installations, are customers notified in accordance with §192.383? Are records adequate? | X |  |  |  |

| Documentation Reviewed: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Document Title | Document Number | Revision Date | Date Range Reviewed | Pct of Data Reviewed |
| New Customer Letter | CNG 453 | 03/05 |  |  |
| Customer Commitment Contract |  |  |  |  |
| Comments: |  |  |  |  |

| CONSTRUCTION RECORDS |  | S | U | N/A | N/C |
| --- | --- | --- | --- | --- | --- |
| 192.225 | Test Results to Qualify Welding Procedures note: reviewed previously |  |  |  | X |
| 192.227 | Welder Qualification | X |  |  |  |
| 480-93-013 | OQ records for personnel performing New Construction covered tasks (eff 6/02/05) | X |  |  |  |
| 480-93-080(1)(a)(iv) | Appendix C Welders re-qualified 2/Yr (7.5Months) (eff 6/02/05) | X |  |  |  |
| 480-93-080(1)(b) | Use of testing equipment to record and document essential variables (eff 6/02/05) note: reviewed previously |  |  |  | X |
| 480-93-080(2) | Plastic pipe joiners re-qualified 1/Yr (15 Months) (eff 6/02/05) | X |  |  |  |
| 480-93-080(2)(b) | Plastic pipe joiners re-qualified if no production joints made during any 12 month period (eff 6/02/05) | X |  |  |  |
| 480-93-080(2)(c) | Tracking Production Joints or Re-qualify joiners 1/Yr (12Months) (eff 6/02/05) | X |  |  |  |
| 480-93-115(2) | Test leads on casings (without vents) installed after 9/05/1992 note: none |  |  | X |  |
| 480-93-115(3) | Sealing ends of casings or conduits on transmission lines and mains (eff 6/02/05) Note: none |  |  | X |  |
| 480-93-115(4) | Sealing ends (nearest building wall) of casings or conduits on services (eff 6/02/05) Note: none, do not do, in new O&M to be adopted |  |  | X |  |
| 192.241(a) | Visual Weld Inspector Training/Experience Note: part of weld procedure, CP 760, Training in Yakima, no construction in area to verify |  |  | X |  |
| 192.243(b)(2) | Nondestructive Technician Qualification Note: No construction in area to verify |  |  | X |  |
| 192.243(c) | NDT procedures Note: No construction in area to verify |  |  | X |  |
| 192.243(f) | Total Number of Girth Welds Note: No construction in area to verify |  |  | X |  |
| 192.243(f) | Number of Welds Inspected by NDT Note: No construction in area to verify |  |  | X |  |
| 192.243(f) | Number of Welds Rejected Note: No construction in area to verify |  |  | X |  |
| 192.243(f) | Disposition of each Weld Rejected Note: No construction in area to verify |  |  | X |  |
| 192.303 | Construction Specifications Note: No construction in area to verify |  |  | X |  |
| 192.325 | Underground Clearance Note: No construction in area to verify |  |  | X |  |
| 192.327 | Amount, location, cover of each size of pipe installed Note: No construction in area to verify |  |  | X |  |
| 480-93-160(1) | Report filed 45 days prior to construction or replacement of transmission pipelines ≥ 100 feet in length (eff 6/2/05) Note: No construction |  |  | X |  |
| 480-93-170(1) | Commission notified 2 day’s prior to pressure testing pipelines with an MAOP producing a hoop stress ≥ 20% SMYS? (eff 6/02/05) Note: None |  |  | X |  |
| 480-93-170(7) | Pressure tests records at a minimum include required information listed under 480-93-170(a-h) (eff 6/02/05) | X |  |  |  |
| 480-93-170(9) | Individual pressure test records maintained for single installations where multiple pressure tests were performed? Note: No construction in area to verify |  |  | X |  |
| 480-93-170(10) | Pressure Testing Equipment checked for accuracy/intervals (Manufacturers Rec or Operators schedule) eff 6/2/05 | X |  |  |  |
| 480-93-175(1) | Study prepared and approved prior to moving and lowering of metallic pipelines > 60 psig (eff 6/2/05) Note: None |  |  | X |  |
| 480-93-175(4) | Leak survey within 30 days of moving or lowering pipelines ≤ 60 psig (eff 6/2/05) Note: None |  |  | X |  |
| 192.455 | Cathodic Protection | X |  |  |  |

| Documentation Reviewed: |  |  |  |
| --- | --- | --- | --- |
| Document Title | Document Number | Revision Date | Date Range Reviewed |
| [192.227, 480-93-080(1)(a)(iv), 480-93-080(2), 480-93-080(2)(b), 480-93-080(2)(c)] Welding Permit – Kevin Berner |  |  | 12/21/05-06/19/06 |
| [192.605(b)(8), 192.615(b)(3), 192.751] District Construction Inspectors Checklist |  |  | 2005 100 % reviewed (20/20) 2006 100% reviewed to date. (5/5) |
| [480-93-170(10)] Aberdeen District Gauge Calibrations | CNG 300 | 1/05 | 11/15/05 SN A01-A23 10/28/04 19 gauges calibrated |
| Energy WorldNet: Cascade Natural Gas Corporation Employee Task Status | Emele, Richard P/S Qualified – 1320DOT Evaluation Date 10/28/01 Regulator Inspect and Test Qualified – 1620DOT Evaluation Date 5/15/01 |  | Activity Report from Database 4/14/2000 -4/14/2006 |
| Energy WorldNet: Cascade Natural Gas Corporation Employee Task Status | Melton, Terry P/S Qualified – 1320DOT Evaluation Date 12/13/06 |  | Activity Report from Database Up to 4/20/2006 |

Comments:

| OPERATIONS and MAINTENANCE RECORDS |  |  |  | S | U | N/A | N/C |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 192.605(a) |  | Procedural Manual Review – Operations and Maintenance (1 per yr/15 months) Note: New O&M will include new documentation procedures for annual O&M review |  | X |  |  |  |
| 192.605(b)(3) |  | Availability of construction records, maps, operating history to operating personnel |  | X |  |  |  |
| 192.517(a) |  | Pressure Testing (operates at or above 100 psig) – useful life of pipeline |  | X |  |  |  |
| 192.517(b) |  | Pressure Testing (operates below 100 psig, service lines, plastic lines) – 5 years CNG retains records for life of line |  | X |  |  |  |
| 192.605(b)(8) |  | Periodic review of personnel work – effectiveness of normal O&M procedures Note: CNG performs crew construction reviews. In 2005, 20 were conducted and in 2006, 5 have been conducted |  | X |  |  |  |
| 192.605(c) |  | Abnormal Operations – Transmission Lines |  | X |  |  |  |
| 192.605(c)(4) |  | Periodic review of personnel work – effectiveness of abnormal operation procedures Note: reviewed at every safety meeting. Reviewed Safety Meeting minute notes. |  | X |  |  |  |
| 192.615(b)(1) |  | Location Specific Emergency Plan Note: each district, each neighboring district, each RD, Engineering and each gas construction truck. |  | X |  |  |  |
| 192.615(b)(2) |  | Emergency Procedure training, verify effectiveness of training |  | X |  |  |  |
| 192.615(b)(3) |  | Employee Emergency activity review, determine if procedures were followed. |  | X |  |  |  |
| 192.615(c) |  | Liaison Program with Public Officials note: with officials (city public works, 9 fire departments, Weyerhaeuser, Grays Harbor College and PUD) a one hour film is watched, then discussion on incident command, responsibilities and general information is conducted |  | X |  |  |  |
| 192.616 |  | Public Awareness Note: Written plan not required until 6-06. Will be adopted in new O&M in CP 925.04 |  |  |  | X |  |
| 192.614 |  | Damage Prevention (Miscellaneous) Note: One call membership #22317 |  | X |  |  |  |
| 192.609 |  | Class Location Study (If Applicable) note: everything designed to class 4 except KB pipeline which is a class 3 |  | X |  |  |  |
| 192.619 |  | Maximum Allowable Operating Pressure (MAOP) Note: MAOP in district varies from 250 psig to 25 psig. Did not review a complete pipeline in this inspection. |  |  |  |  | X |
| 192.625 |  | Odorization of Gas |  | X |  |  |  |
| 480-93-015(2) |  | Monthly Odorant Testing (eff 6/02/05) note: field sniff test conducted as OQ test, records reviewed |  | X |  |  |  |
| 480-93-015(3) |  | Odorant Testing Equipment Calibration/Intervals (Annually or Manufacturers Recommendation) eff 6/02/05 |  | X |  |  |  |
| 480-93-018(3) |  | Records, including maps and drawings updated within 6 months of completion of construction activity? (eff 6/02/05) Note: red line maps in each district up to date. Having formal CNG maps updated every 6 months is CNG goal. Markers are not yet being mapped |  | X |  |  |  |
| 480-93-124(3) |  | Pipeline markers attached to bridges or other spans inspected? 1/yr(15 months) eff 6/02/05 Note: no current record of bridge markers or documentation of inspection in new O&M CP 610 there is |  | X |  |  |  |
| 480-93-124(4) |  | Markers reported missing or damaged replaced within 45 days? eff 6/02/05 Note: doing and documenting on quarterly patrol, reg maint sheets and in comments on leak survey sheets. New O&M will have different procedure |  | X |  |  |  |
| 480-93-140(2) |  | Service regulators and associated safety devices tested during initial turn-on eff 6/02/05 Note: reviewed Service Request to set meter , Form 305, service regulator test noted. Testing service regulator is part of procedure but it is not always noted as being preformed. |  | X |  |  |  |
| 480-93-155(1) |  | Up-rating of system MAOP to >60 psig? Procedures and specifications submitted 45 days prior? (eff 6/02/05) Note: none in the Aberdeen district |  |  |  | X |  |
| 480-93-185(1) |  | Reported gas leaks investigated promptly graded. Records retained? Note: found a leak during field inspection, repair made and have documentation of the immediate repair. Reviewed leaks. When CNG fixes a leak due to a service call the leak may not be included in the number of leaks on the annual reports. When leaks are found they are graded as a one and immediately fixed. No deferred leaks in Aberdeen |  | X |  |  |  |
| 480-93-185(3) |  | Leaks originating from a foreign source reported promptly/notification by mail. Records retained? Note: CNG Records Center does mailings when required, no documentation in district |  | X |  |  |  |
| 480-93-186(3) |  | Leak evaluations: Are follow-up inspections performed within 30 days of a leak repair? eff 6/02/05 |  | X |  |  |  |
| 480-93-186(\4) |  | Leak evaluations: Grade 1 and 2 leaks (if any), downgraded once to a grade 3 without physical repair? eff 6/02/05 note: in Aberdeen district all leaks grades as 1 and repaired |  | X |  |  |  |
| 480-93-187 |  | Gas leak records: at a minimum include required information listed under 480-93-187(1-13) (eff 6/02/05) |  | X |  |  |  |
| 480-93-188(1) |  | Gas leak surveys |  | X |  |  |  |
| 480-93-188(2) |  | Gas detection instruments tested for accuracy/intervals (Mfct rec or monthly not to exceed 45 days) eff 6/2/05 |  | X |  |  |  |
| 480-93-188(3) |  | Leak survey frequency (Refer to Table Below) note: flame paks calibrated daily and reviewed 2004 and 2005 CGI calibration records |  | X |  |  |  |
| Business Districts (implement by 6/02/07); 1/yr (15 months). High Occupancy Structures; 1/yr (15 months). Pipelines Operating ≥ 250 psig; 1/yr (15 months). Other Mains: CI, WI, copper, unprotected steel; 2/yr (7.5 months). |
| 480-93-188(4)(a) |  |  | Special leak surveys - Prior to paving or resurfacing, following street alterations or repairs Note: none in area |  |  | X |  |
| 480-93-188(4)(b) |  |  | Special leak surveys - areas where substructure construction occurs adjacent to underground gas facilities, and damage could have occurred Note: none in area |  |  | X |  |
| 480-93-188(4)(c) |  |  | Special leak surveys - Unstable soil areas where active gas lines could be affected Note: none in area |  |  | X |  |
| 480-93-188(4)(d) |  |  | Special leak surveys - areas and at times of unusual activity, such as earthquake, floods, and explosions Note: none in area. However an earthquake survey was conducted documented on 3/5/01 |  |  | X |  |
| 480-93-188(4)(e) |  |  | Special leak surveys - After third-party excavation damage to services, operators must perform a gas leak survey from the point of damage to the service tie-in Note: reviewed substructures damage report. currently doing pressure test to meter set, did not review if leak survey conducted back to main |  |  |  | X |
| 480-93-188(4)(e) |  |  | Gas Surveys/Self Audits | X |  |  |  |
| 480-93-188(5) |  |  | Gas Survey Records | X |  |  |  |
| 192.709 |  |  | Patrolling (Transmission Lines) (Refer to Table Below) .705 CNG has a right of way covered with blackberries, walking a serpentine path with leak detection equipment is difficult at best. Right of way located in McCleary at Old Snad Creek Rd near Knight Rd | X |  |  |  |
| Class Location; At Highway and Railroad Crossings; At All Other Places. 1 and 2; 2/yr (7½ months); 1/yr (15 months). 3; 4/yr (4½ months); 2/yr (7½ months). 4; 4/yr (4½ months); 4/yr (4½ months). |
| 192.709 | Leak Surveys (Transmission Lines) (Refer to Table Below) .706 |  |  | X |  |  |  |
| Class Location; Required; Not Exceed. 1 and 2; 1/yr; 15 months. 3; 2/yr; 7½ months. 4; 4/yr; 4½ months. |
| 192.721(b)(1) |  | Patrolling Business District (4 per yr/4½ months) |  | X |  |  |  |
| 192.721(b)(2) |  | Patrolling Outside Business District (2 per yr/7½ months) note: Outside business districts are patrolled every 4 months and documented on the patrol forms |  | X |  |  |  |
| 192 .723(b)(1) |  | Leakage Survey - Outside Business District (5 years) |  | X |  |  |  |
| 192.725 |  | Tests for Reinstating Service Lines |  | X |  |  |  |
| 192.727(g) |  | Abandoned Pipelines; Underwater Facility Reports Note no abandoned underwater pipelines |  |  |  | X |  |
| 192.739 |  | Pressure Limiting and Regulating Stations (1 per yr/15 months) .739 Tests are conducted in a timely manner however at R1 in Aberdeen a 5 pound increment , 600 pound dura gauge is used to conduct the relief test. A five pound increment gauge makes in difficult to determine if it relieved at the correct pressure. |  | X |  |  |  |
| 192.743 |  | Pressure Limiting and Regulator Stations – Capacity (1 per yr/15 months) .743 |  | X |  |  |  |
| 192.745 |  | Valve Maintenance (1 per yr/15 months) .745 |  | X |  |  |  |
| 480-93-100(3) |  | Service valve maintenance (1 per yr/15 months) (eff. 06/02/05) Note: not fully implemented will be in new O&M(inspection in April) |  |  |  | X |  |
| 480-93-100(4) |  | Service valve installation and maintenance program fully implemented by 6/01/07? (eff. 06/02/05) Note: Will be by 6-1-07, in new O&M(inspection in April) |  |  |  | X |  |
| 192.749 |  | Vault maintenance (200 cubic feet)(1 per yr/15 months) .749 note: all vaults less than 200 feet |  | X |  |  |  |
| 192.751 |  | Prevention of Accidental Ignition (hot work permits) .751 Note No crew work to observe |  |  |  | X |  |
| 192.225(b) |  | Welding – Procedure Note No crew work to observe |  |  |  | X |  |
| 192.227/.229 |  | Welding – Welder Qualification Note No crew work to observe |  |  |  | X |  |
| 192.243(b)(2) |  | NDT – NDT Personnel Qualification .243(b)(2) Note No crew work to observe |  |  |  | X |  |
| 192.243(f) |  | NDT Records (pipeline life) .243(f) Note No crew work to observe |  |  |  | X |  |
| 192.709 |  | Repair: pipe (pipeline life); Other than pipe (5 years) Note No crew work to observe |  |  |  | X |  |

| Documentation Reviewed: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Document Title | Document Number | Revision Date | Date Range Reviewed |  |
| Substructure Damage/Leak Report | CNG 293 |  | 2005, Reviewed 15/15 records, 100% |  |
| Substructure Damage/Leak Report | CNG 293 |  | 2006, Reviewed 2/2 records, 100% to date |  |
| Substructure Damage /Leak 192.725 Report for reinstating service |  |  | 9/10/04 |  |
| Operations & Maintenance Request for 480-93-186 (3) for 30 day recheck of a substructure damage report |  |  | 9/10/04 |  |
| Operations & Maintenance request, document stand by on digs near HP lines - 3/20/06 dug over Kitsap line, 3/22/06 dug over Kitsap line, 3/23/2006 augured by 4” line, 4/6/2006 walked project with contractor, , 1/31/06 contractor installed culvert over 4”, 2/1/06 dug over 4”, |  |  |  |  |
| Operations and Maintenance Request generated because of wood supporting meter that was seen during pre inspection. |  |  |  |  |
| 480-93-186 (4) Service Request created during inspection. Found leak on meter regulator at 101 E Market St, Aberdeen. Regulator was replace. Relit not done at that time. |  |  |  |  |
| Operation & Maintenance Request created because of RS5 violation. Order to install new cap and do maintenance to remove all liquid. | CNG 330A |  | #0014053 & 0014054, Date Ordered 4/20/06 |  |
| Service Request to verify 480-93-140(2) meter pressure tested |  |  |  |  |
| Valve maintenance 192.745 Transmission and 192.747 Distribution |  |  | 71 2005 valve records |  |
| R5 Facility Maintenance and Inspection Record for 2005 maintenance. NOTE this is the one with the bad flap and water in relief vent |  |  |  |  |
| 4/20/06 Operation & Maintenance Request to replace cap |  |  |  |  |
| [192.605(c)(4)]Safety Meeting Report |  |  | 12/20/2005 |  |
| Gas Odorization Test Report | CNG 350 | 7/00 | 2005, 100% 2006, 100% to date. |  |
| [192.743]Annual Regulator Station Relief Valve Check - Capacity |  |  | 12/30/05 |  |
| [192.614] Excavating Contractors Grays Harbor County |  |  | January 2006 |  |
| [192.614] Excavation Contractors Mason County |  |  | 2006 |  |
| [480-93-188(1)] System Surveillance Record | CNG 286 | 01/96 | 1/17/06, 2/21/01, 3/05/01 |  |
| [480-93-188(2)] Flamepack Calibration Log S/N 9900 |  |  | 11/12/02 – 4/21/06 (Example, calibration logs kept with equipment) |  |
| [480-93-188(2)] 2005 (CGI) Calibration Log Sheet |  |  | 2005 - 4 instruments calibrated every month. |  |
| [480-93-188(2)] 2006 (CGI) Calibration Log Sheet |  |  | 2006 – 4 instruments calibrated for 4 months. |  |
| [480-93-188(2)] Pyrometer Calibration - Aberdeen |  |  | 2005, 10/7 and 12/20 2006, 3/7/ |  |
| [480-93-188(2)] Recorder Reading Checks - Aberdeen |  |  | 03/25/2005 |  |
| Substructure Damage/Leak Report | CNG 293 |  | 2005, Reviewed 15/15 records, 100% |  |
| [192.709, 192.721(b)(1)] System Surveillance Record | CNG 286 | 01/96 | 2/22/06-2/28/06 (First quarter and high water follow-up. |  |
| 2004 and 2005 patrolling records |  |  |  |  |
| 2004 and 2005 leak survey records |  |  |  |  |
| District construction Inspection checklist |  |  |  |  |
| Aberdeen Incident Command and shut down |  |  |  |  |
| Regulator Set Point List |  |  | 2005 and 2006 | 100% |

Comments:

| CORROSION CONTROL RECORDS |  | S | U | N/A | N/C |
| --- | --- | --- | --- | --- | --- |
| 192.491 | Maps or Records .491(a) Note: Maps in Seattle did not review |  |  | X |  |
| 192.491 | Examination of Buried Pipe when Exposed .459 | X |  |  |  |
| 480-93-110(8) | CP test reading on all exposed facilities where coating has been removed (eff 6/02/05) note: reviewed substructure damage records and installs | X |  |  |  |
| 192.491 | Annual Pipe-to-soil Monitoring (1 per yr/15 months) .465(a) | X |  |  |  |
| 192.491 | Rectifier Monitoring (6 per yr/2½ months) .465(b) note: reviewed Bi monthly reports. There are 2 rectifier system in Aberdeen, 2 in Hoquiam, 2 in Montesano, one in Elma, Shelton and McCleary and one galvanic system in Aberdeen | X |  |  |  |
| 192.491 | Interference Bond Monitoring – Critical (6 per yr/2½ months) .465(c) Note: none |  |  | X |  |
| 192.491 | Interference Bond Monitoring – Non-critical (1 per yr/15 months) .465(c) Note: none |  |  | X |  |
| 480-93-110(2) | Remedial action taken within 90 days ( Up to 30 additional days if other circumstances. Must document) .465(d) note: reviewed test site surveys | X |  |  |  |
| 192.491 | Unprotected Pipeline Surveys, CP active corrosion areas (1 per 3 cal yr/39 months) .465(e) Note: none |  |  | X |  |
| 192.491 | Electrical Isolation (Including Casings) .467 | X |  |  |  |
| 480-93-110(5) | Casings inspected/tested annually not to exceed fifteen months (eff 6/02/05) note: reviewed casing documentation | X |  |  |  |
| 480-93-110(5)(a) | Casings w/no test leads installed prior to 9/05/1992. Demonstrate other acceptable test methods (eff 6/02/05) note: CNG uses a Tinker Razor to determine if these casings are shorted. | X |  |  |  |
| 480-93-110(5)(b) | Possible shorted conditions – Perform confirmatory follow-up inspection within 90 days (eff 6/02/05) note: currently no shorted casings | X |  |  |  |
| 480-93-110(5)(c) | Casing shorts cleared when practical (eff 6/02/05) note: see CP 755 | X |  |  |  |
| 480-93-110(5)(d) | Shorted conditions leak surveyed within 90 days of discovery. Twice annually/7.5 months (eff 6/02/05) | X |  |  |  |
| 192.491 | Test Stations – Sufficient Number .469 note: there are 319 in Aberdeen district | X |  |  |  |
| 192.491 | Test Lead Maintenance .471 | X |  |  |  |
| 192.491 | Interference Currents .473 note: none | X |  |  |  |
| 192.491 | Internal Corrosion; Corrosive Gas Investigation .475(a) note: have gramograph from Williams | X |  |  |  |
| 192.491 | Internal Corrosion; Internal Surface Inspection; Pipe Replacement .475(b) note: use the substructure damage report for both internal and external corrosion. Mark same box for both. Informed CNG this does not adequately address internal and external corrosion inspectionn. | X |  |  |  |
| 192.491 | Internal Corrosion Control Coupon Monitoring (2 per yr/7½ months) .477 Note: none |  |  | X |  |
| 192.491 | Atmospheric Corrosion Control Monitoring (1 per 3 cal yr/39 months onshore; 1 per yr/15 months offshore) .481 note: New procedure started in 2003. In 2004, Shelton area inspected, 2005 towns between Shelton and Aberdeen were inspected. Aberdeen’s atmospheric corrosion inspection is scheduled to be conducted in 2006. Aberdeen district performed inspections but did not perform remedial action as required in the new procedures. The new procedure timeframe allows 6 months for painting and 90 days for wall loss repairs or replacement. Also reviewed 2003 and 2004 atmospheric corrosion records and verified that meterless risers are being checked. Specifically the meterless risers in McCleary behind the Select Market and at 1402 W Main CNG procedure in both old and new manual requires an atmospheric corrosion inspection during every regulator station annual maintenance. CNG does not document that that is done, they do not conduct an inspection under pipe and straps and they do not mark the box for paint condition accurately |  | X |  |  |
| 192.491 | Remedial: Replaced or Repaired Pipe; coated and protected; corrosion evaluation and actions .483/.485 | X |  |  |  |
| 480-93-110(3) | CP Test Equipment and Instruments checked for accuracy/intervals (Mfct Rec or Opr Sched) (eff 6/02/05) | X |  |  |  |

| Documentation Reviewed: |  |  |  |
| --- | --- | --- | --- |
| Document Title | Document Number | Revision Date | Date Range Reviewed |
| Cathodic Protection System (Rectifier and P/S Reads) | CNG 294A |  | 2005, Reviewed 6/6 records. 100% |
| Bi-Monthly Monitoring Report (Rectifier and P/S Reads) |  | 04/15/03 | 2006, Review 2/2 records. 100% to date. |
| [192.491] Cathodic Protection Data Sheet | CNG 283 | 4/89 | 4-29-05 to 5-11-05(2005) |
| For 480-93-110(8) reviewed substructure damage records and installs for 2004 and 2005 |  |  |  |
| 480-93-110(5) 2004 and 2005 reviewed casing documentation |  |  |  |

Comments:

- No isolated services or mains in Aberdeen

| PIPELINE INSPECTION (Field) |  | S | U | N/A | N/C |
| --- | --- | --- | --- | --- | --- |
| 192.161 | Support and anchors |  | x |  |  |
| 192.179 | Valve Protection from Tampering or Damage | X |  |  |  |
| 480-93-080(1)(d) | Welding procedures located on site where welding is performed? Note welding procedures would be on site but no construction to observe |  |  | X |  |
| 480-93-080(2)(a) | Plastic procedures located on site where welding is performed? (eff 6/02/05) Note: pe procedures would be on site but no construction to observe |  |  | X |  |
| 480-93-080(3) | Identification and qualification cards/certificates w/name of welder/joiner, their qualifications, date of qualification and operator whose qualification procedures were followed. (eff 6/02/05) | X |  |  |  |
| 480-93-013 | Personnel performing “New Construction” covered tasks OQ qualified? (eff 6/02/05) Note: Included in new O&M to be adopted |  |  | X |  |
| 480-93-015(1) | Odorization | X |  |  |  |
| 480-93-018(3) | Updated records, including maps and drawings made available to appropriate operations personnel? (eff 6/02/05) | X |  |  |  |
| 192.463 | Levels of Cathodic Protection Note: found one impressed current system with low p/s reads |  | X |  |  |
| 192.465 | Rectifiers | X |  |  |  |
| 192.467 | CP - Electrical Isolation Note: none |  |  | X |  |
| 192.469 | Test Stations (Sufficient Number) | X |  |  |  |
| 192.479 | Pipeline Components Exposed to the Atmosphere | X |  |  |  |
| 192.481 | Atmospheric corrosion control: Monitoring | x |  |  |  |
| 480-93-115(2) | Casings – Test Leads (casings w/o vents installed after 9/05/1992) eff. 6/02/05 Note: none | X |  |  |  |
| 480-93-115(2) | Mains or transmission lines in installed in casings/conduit. Are casing ends sealed? eff 6/02/05 Note: since 1977 all casing have been designed to hold line pressure. | X |  |  |  |
| 480-93-115(4) | Service lines installed in casings/conduit. Are casing ends nearest to building walls sealed? eff. 6/02/05 Note: yes, procedure in new O&M |  |  | X |  |
| 192.605(a) | Appropriate parts of manuals kept at locations where O&M activities are conducted | X |  |  |  |
| 192.605 | Knowledge of Operating Personnel | X |  |  |  |
| 480-93-124 | Pipeline markers installed eff 6/02/05 Note: markers in place, procedure in new O&M | X |  |  |  |
| 480-93-124(4) | Markers reported missing or damaged replaced within 45 days? eff 6/02/05 Note: markers replaced, procedure in new O&M. Documentation currently on quarterly patrols, leak surveys, work orders. | X |  |  |  |
| 192.707 | Warning Signs | X |  |  |  |
| 192.719 | Pre-pressure Tested Pipe (Markings and Inventory) Note: Aberdeen has a piece of 12 Kitsap line in the yard, rest of pre pressure tested pipe is in Yakima and ordered as needed |  |  | X |  |
| 192.739 | Pressure Limiting and Regulating Devices (Mechanical) During the pressure relief test at R5 in Montesano water was blown out of the stack under the test pressure was discontinued. And at 4,5, and 10 Hoffman Rd in Aberdeen the farm tap was a district regulator (per definition) and was not being inspected annually. |  | X |  |  |
| 192.743 | Pressure Limiting and Regulating Devices (Capacities) | X |  |  |  |
| 480-93-140 | Service Regulators installed, operated and maintained per state/fed regs and manufacturers recommended practices? eff 6/02/05 | X |  |  |  |
| 192.745 | Valve Maintenance (Transmission) Note: none observed |  |  | X |  |
| 192.747 | Valve Maintenance (Distribution) Note: none observed |  |  | X |  |

| Facility Sites Visited: |  |  |
| --- | --- | --- |
| Facility Type and ID Number | Location | Comment |
| Casing | Maple and Adams at RR crossing | p/s -.59 ok |
| Casing | 28th and John Stevens, and house at 718 28th | p/s -.336 on casing, -1.020 at house |
| Antique store meter | 22nd and Simpson | Meter to have 3 year atmospheric corrosion inspection in 2006, ultra sonic thickness gauge used to determine if any wall loss. No wall loss |
| Regulator Station R1 | Aberdeen | Used 5 pound increment, 600 pound Dura gauge. Set to relieve at 156 psig, could not tell with 5 pound increment gauge. Refused to remove straps and inspection for atmospheric corrosion. Atmospheric corrosion and atmospheric corrosion not properly noted on form |
| Regulator Station R5 | Aberdeen | During pre field inspection observed vent cap open and no signs in area. During relief test it Spit water. Chart pen had stopped for a day and a half, atmospheric corrosion not properly noted on form. Signs installed in area |
| Regulator Station R4 | Aberdeen | Sing installed between pre field inspection and inspection |
| Regulator Station 24 |  | Bad address for regulator station. Across street from station is a farm tap sitting next to mobile home. No distance requirement |
| Farm tap | Next to 3117 Wishkah | 3 service on Hoffman Rd (addressed 4, 5 and 10) make this farm tap a district regulator |
| Farm tap | 2809 Wishkah | ok |
| Farm Tap | 2801 Wishkah | Ok, new vent extender installed |
| Farm Tap | 2801 Wishkah |  |
| Farm Tap | Monte and Camp Creek | Looked it up on map. The map did not have an update date |
| Farm Tap at 80 Fairground Rd. |  | Appeared to be district reg. It was not because there was a second farm tap in a vault |
| Vault R3 |  | p/s inside -1.150 |
| Valve 65 on line to satsop |  | Is above ground and the Wasser paint not holding up like expected. |
| Odormeter test | At Aberdeen office | Ok. An odormeter test in every town and two in Shelton all done monthly. |
| Rectifier | Cascade Lane and W Satsop Valley Rd | Far west Corrosion Control Co, Model ASAI, AC volts 115/230, DC volts 40, Amp tem 50 degree C, Serial # 051977, AC Amps 59/29, DC Amps 12, phase 1 HZ 60. |
| Bridge crossing signs | Line to Satsop | Ok, under bridge, moving supports good, coating good, signs good, |
| Right of way | In McCleary, on McKnight Rd and Old Sand Creek Rd. | 30 foot by 40 foot section of RW covered with blackberries. |
| Fairground Super Storage | Fairground and Menzo-Haverly Rd | Side vent during pre inspection corrected before inspection |
| Low p/s reads in Hoquiam | Low reads in area from down town Hoquiam to Hwy 109 and Hwy 101 | CNG determined that a rectifier system was down. Investigation showed that a metal cable chain was wrapped around a meter set. |
| 3 blocks of alley on either side of Hwy 12 from Broadway Street east |  | We walked the alleys, took random p/s reads, and I pointed out atmospheric corrosion, where side way vents had been. They removed wood blocks that were not required. |
| NOT FIELDED WITH COMPANY BUT ASKED THE CNG ABOUT |  |  |
| Casing in Aberdeen at Perry Street and River Street |  | There was a zero p/s read on casing during pre field inspection. During inspection asked about this and it was an abandoned line. Verified on CNG map |
| Right of Way | In Elma, on Batstone between Brockdale and Johns Prairie Rd | From road in one direction there were waist deep weeds and in other direction looked like a building might be on top of line . Asked during the inspection. Weeds are waist deep but walk able and in the other direction the r/w turns before building. |
| Farm taps in Elma at 8, 28, 31, 36, 166, and 243 Stampler; In Montesano farm tap at Lough head and Camp creek, In Shelton at Aero Controls, In Aberdeen at 2741, 3117, 2801 Wishkah and at Bartech Rd and Wishkah |  | During pre inspection all farm taps had sideway vents. They were replaced before the inspection. Followed up on ones in Elma, Montesano and Aberdeen. Also, signs were missing and they were installed before the inspection. |
| Markers on Hwy 101 at Hwy 102 and on the Monte Elma Rd near Schouweiler Rd |  | No markers. I asked during the inspection and markers have been installed. |
| McCleary behind the Select Market and at 1402 W Main |  | Verified that meterless are included in atmospheric corrosion inspection |
| High p/s reads in McCleary |  | In McCleary, p/s reads in one two block long section ranged from 02.17 to -1.17. It had been raining for days. CNG felt the reads were high because it was so wet during the pre inspection |
| Pre Inspection fielded sites not fielded with company |  |  |
| R 37 vault at Shelton Fred Meyers Parking lot. Has 6’ vent in grass area |  |  |
| R38 by Burger master in Shelton, iced up atmos corr |  |  |
| R 15 Wallace Knee land and Shelton Springs, atmos corrosion |  |  |
| R 34 Shelton Springs Rd and Wallace Blvd |  |  |
| R 16 Shelton Springs Rd |  | Primer on some of it, no paint in accordance with CNG standard |
| R 2 Wishkah Rd and N B Street |  |  |
| McCleary Hospital, Lumber Mill at Simpson Hwy and 3rd in Elma, Fir Lane & Alpine Retirement meter 6027653, Grays Haror Community Hospital in Aberdeen, Grays Harbor Health and Reb Center in Aberdeen, |  | These might be a master meter. |
| Casing in Elma near 8 Stampler, at RR tracks near W Martin St and N 3rd St, in Shelton in R 38, on Batstone between Brockdale and Johns Prairie Rd, Hwy 102 and Sanderson Way West, In Aberdeen O St and 5th, Near McDonalds on main road into town, John Stevens Way and 28th, W first and Maple, Montesano at RR tracks near S Main and Broomfield |  | All casing reads were good. |
| Brehmer’s Collision Center, meter 5657090 |  | Has his equipment regulators by gas meter, ok but looks strange from road |
| p/s reads in Shelton, Elma and Aberdeen |  | Multiply reads and all were ok |

Comments:

New Construction activities are testing of new and replace lines, locating , inspection of excavations, stabilization.

Pipeline Safety Advisory Bulletins:

OPS, PHMSA ADB-06-01 dated 1/17/06 Integrate Operator Qualification Regulations into Excavation Activities

Although excavation is not explicitly addressed in 49 CFR parts 192 and 195, excavation is considered a covered task under the pipeline operator qualifications regulations. These regulations require that pipeline operators and contractors be qualified to perform pipeline excavation activities. This advisory reminds operators to ensure all procedures and processes to perform excavation and backfilling are followed. Only qualified personnel must oversee all marking, trenching, and backfilling operations. Y/N YES

OPS, PHMSA ADB-05-06 dated 8/05/05 Counter Measures to Prevent Human Fatigue in the Control Room

The purpose of this advisory is to help operators ensure that controllers are not assigned to shift duties while fatigued, to advise pipeline operators on considerations which could cause a reduction of mental alertness or decision making ability, and to encourage safe management practices. Y/N Yes, SCADA

OPS, PHMSA ADB-05-03 dated 5/17/05  Pipeline Safety: Planning for Coordination of Emergency Response to Pipeline Emergencies

Concerns alerting pipeline operators about the need to preplan for emergency response with utilities whose proximity to the pipeline may impact the response. Coordination with electric and other utilities may be critical in responding to a pipeline emergency. Preplanning would facilitate actions that may be needed for safety, such as removing sources of ignition or reducing the amount of combustible material. Y/N YES, LDC MUTUAL ASSISTANCE PROGRAM

WUTC PSS AB 04-01 dated 10/24/04 Maintenance of Impressed Current Cathodic Protection Systems

Is the operator aware of the advisory bulletin, and has the operator reviewed their Plans and Procedures to determine whether adequate processes are in pace to ensure that impressed current cathodic protection systems are configured and labeled correctly?  Y/N YES, LEADS MARKED

OPS, PHMSA ADB-99-02 dated 3/03/99 Potential Failures Due to Brittle-Like Cracking of Older Plastic Pipe in Natural Gas Distribution Systems

Certain plastic pipe used in natural gas distribution service may be susceptible to brittle-like cracking. The standards used to rate the long-term strength of plastic pipe may have overrated the strength and resistance to brittle-like cracking of much of the plastic pipe manufactured and used for gas service from the 1960s through the early 1980s. Has the operator identified and/or taking steps to identify all pre-1982 plastic pipe installations, analyze leak histories, and evaluate any conditions that may impose high stresses on the pipe? Is appropriate remedial action, including replacement, being taken to mitigate any risks to public safety?  No pre 1982 Aldyl A and all pe reviewed

Comments:

| .605(b) | COMPRESSOR STATION PROCEDURES | S | U | N/A | N/C |
| --- | --- | --- | --- | --- | --- |
|  | .605(b)(6) Maintenance procedures, including provisions for isolating units or sections of pipe and for purging before returning to service |  |  |  | X |
|  | .605(b)(7) Starting, operating, and shutdown procedures for gas compressor units |  |  |  | X |
|  | .731 Inspection and testing procedures for remote control shutdowns and pressure relieving devices (1 per yr/15 months), prompt repair or replacement |  |  |  | X |
|  | .735 (a) Storage of excess flammable or combustible materials at a safe distance from the compressor buildings |  |  |  | X |
|  | (b) Tank must be protected according to NFPA #30 |  |  |  | X |
|  | .736 Compressor buildings in a compressor station must have fixed gas detection and alarm systems (must be performance tested), unless: |  |  |  | X |
|  | - 50% of the upright side areas are permanently open, or |  |  |  | X |
|  | - It is an unattended field compressor station of 1000 hp or less |  |  |  | X |

| Documentation Reviewed: |  |  |
| --- | --- | --- |
| Document Title | Document/Section Number | Revision Date |

Comments:

No compressor station in the CNG Aberdeen District

| COMPRESSOR STATION O&M RECORDS |  | S | U | N/A | N/C |
| --- | --- | --- | --- | --- | --- |
| .709 | .731(a) Compressor Station Relief Devices (1 per yr/15 months) |  |  |  | X |
|  | .731(c) Compressor Station Emergency Shutdown (1 per yr/15 months) |  |  |  | X |
|  | .736(c) Compressor Stations – Detection and Alarms (Performance Test) |  |  |  | X |

| Documentation Reviewed: |  |  |  |
| --- | --- | --- | --- |
| Document Title | Document Number | Revision Date | Date Range Reviewed |

Comments:

No compressor station in the CNG Aberdeen District

| COMPRESSOR STATIONS INSPECTION (Field) (Note: Facilities may be “Grandfathered”) |  | S | U | N/A | N/C |
| --- | --- | --- | --- | --- | --- |
| .163 (c) | Main operating floor must have (at least) two (2) separate and unobstructed exits |  |  |  | X |
|  | Door latch must open from inside without a key |  |  |  | X |
|  | Doors must swing outward |  |  |  | X |
| (d) | Each fence around a compressor station must have (at least) 2 gates or other facilities for emergency exit |  |  |  | X |
|  | Each gate located within 200 ft of any compressor plant building must open outward |  |  |  | X |
|  | When occupied, the door must be opened from the inside without a key |  |  |  | X |
| (e) | Does the equipment and wiring within compressor stations conform to the National Electric Code, ANSI/NFPA 70? |  |  |  | X |
| .165 (a) | If applicable, are there liquid separator(s) on the intake to the compressors? |  |  |  | X |
| (b) | Do the liquid separators have a manual means of removing liquids? |  |  |  | X |
|  | If slugs of liquid could be carried into the compressors, are there automatic dumps on the separators, Automatic compressor shutdown devices, or high liquid level alarms? |  |  |  | X |
| .167 (a) | ESD system must: |  |  |  |  |
|  | - Discharge blowdown gas to a safe location |  |  |  | X |
|  | - Block and blow down the gas in the station |  |  |  | X |
|  | - Shut down gas compressing equipment, gas fires, electrical facilities in compressor building and near gas headers |  |  |  | X |
|  | - Maintain necessary electrical circuits for emergency lighting and circuits needed to protect equipment from damage |  |  |  | X |
|  | ESD system must be operable from at least two locations, each of which is: |  |  |  |  |
|  | - Outside the gas area of the station |  |  |  | X |
|  | - Not more than 500 feet from the limits of the station |  |  |  | X |
|  | - ESD switches near emergency exits? |  |  |  | X |
| (b) | For stations supplying gas directly to distribution systems, is the ESD system configured so that the LDC will not be shut down if the ESD is activated? |  |  |  | X |
| (c) | Are ESDs on platforms designed to actuate automatically by… |  |  |  |  |
|  | - For unattended compressor stations, when: |  |  |  |  |
|  | - The gas pressure equals MAOP plus 15%? |  |  |  | X |
|  | - An uncontrolled fire occurs on the platform? |  |  |  | X |
|  | - For compressor station in a building, when |  |  |  |  |
|  | - An uncontrolled fire occurs in the building? |  |  |  | X |
|  | - Gas in air reaches 50% or more of LEL in a building with a source of ignition (facility conforming to NEC Class 1, Group D is not a source of ignition)? |  |  |  | X |
| .171 (a) | Does the compressor station have adequate fire protection facilities? If fire pumps are used, they must not be affected by the ESD system. |  |  |  | X |
| (b) | Do the compressor station prime movers (other than electrical movers) have over-speed shutdown? |  |  |  | X |
| (c) | Do the compressor units alarm or shutdown in the event of inadequate cooling or lubrication of the unit(s)? |  |  |  | X |
| (d) | Are the gas compressor units equipped to automatically stop fuel flow and vent the engine if the engine is stopped for any reason? |  |  |  | X |
| (e) | Are the mufflers equipped with vents to vent any trapped gas? |  |  |  | X |
| .173 | Is each compressor station building adequately ventilated? |  |  |  | X |
| .457 | Is all buried piping cathodically protected? |  |  |  | X |
| .481 | Atmospheric corrosion of aboveground facilities |  |  |  | X |
| .603 | Does the operator have procedures for the start-up and shut-down of the station and/or compressor units? |  |  |  | X |
|  | Are facility maps current/up-to-date? |  |  |  | X |
| .615 | Emergency Plan for the station on site? |  |  |  | X |
| .619 | Review pressure recording charts and/or SCADA |  |  |  | X |
| .707 | Markers |  |  |  | X |
| .731 | Overpressure protection – relief’s or shutdowns |  |  |  | X |
| .735 | Are combustible materials in quantities exceeding normal daily usage, stored a safe distance from the compressor building? |  |  |  | X |
|  | Are aboveground oil or gasoline storage tanks protected in accordance with NFPA standard No. 30? |  |  |  | X |
| .736 | Gas detection – location |  |  |  | X |

| Documentation Reviewed: |  |  |  |
| --- | --- | --- | --- |
| Document Title | Document Number | Revision Date | Date Range Reviewed |

Comments:

No compressor station in the CNG Aberdeen District