| WN U-74 |  |  | First Revision of Sheet No. J.2 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Canceling Original Sheet No. J.2 |  |  |  |  |  |  |  |  |  |  |
| PACIFIC POWER & LIGHT COMPANY |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | FOR COMMISSION’S RECEIPT STAMP |  |  |
|  | GENERAL RULES AND REGULATIONS 8. METERING: (continued) (M) pg j1 (M) pg j1 (K) pg j3 (K) pg j3 B. METER TEST PROCEDURES: (As of the effective date of this tariff.) 1. Certified Meter Testing of New Meters. The Company purchases meters with accuracy certified by the manufacturer to be in compliance with The American National Standard Code for Electricity Metering (ANSI C12.1). The test results of the manufacturer are identified by each meter's individual serial number. These records will be maintained for the three most recent years. 2. In-Service Meter Performance Testing. The Company performs an in-service meter test program to ensure the accuracy of meters throughout their service life. Meters are tested on full load, light load and power factor to meet the following standards: - Mechanical and Hybrid +/- 1.0% accuracy - Solid State +/- 0.5% accuracy Meters that meet acceptable standards of accuracy will remain in service, subject to random sampling and scheduled testing. The Company's schedule testing will occur: - Every 8 years for all electro-mechanical meters without surge proof magnets. - Every 16 years for all other electro-mechanical meters. |  |  |  |  |  |  |  |  |  |  |  |  |
| (Continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Issued |  |  |  |  | February 6, 2008 |  | Effective |  |  | March 7, 2008 |  |  |  |
| Issued by |  |  |  | PACIFIC POWER & LIGHT COMPANY |  |  |  |  |  |  |  |  |  |
| By |  | Andrea L. Kelly |  |  |  |  |  | Title | Vice President, Regulation |  |  |  |  |
|  |  | TF2 J.2REV |  |  |  | Case No. |  |  |  |  |  | UE- |  |
| Form F |  |  |  |  |  |  |  |  |  |  |  |  |  |