Proposed Rule:

###### WAC  480-93-015  Odorization of gas

(1)  All gas that is transported by pipeline and all gas consumed by an end use customer must be odorized in accordance with CFR 49, Part 192.625 (a), except those pipeline segments excluded under the provisions of  paragraphs (b)(2) and (b)(4).

Comment:  Paragraphs (b)(1) and (b)(3) are used by DOT to exclude pipeline sections.   PSE recommends the above changes to make clear that the UTC does not allow the exclusions granted by DOT in paragraphs (b)(1) and (b)(3).

(2)  Operator’s must use odorant testing instrumentation when conducting  odorant  level checks (sniff tests).  Sniff tests must be performed at least monthly.

(3)  Instruments used to detect odorant concentration must be calibrated in accordance with the manufactures recommendation.  When there is no manufacturers recommendation calibration must be done at least once each calendar year.

(4)  All records of odorant usage, sniff tests performed, and equipment calibration must be kept for five years.

Proposed Rule:

###### WAC     480-93-018  Maps, drawings, and records of gas facilities

(1)  Each gas company must prepare, maintain, and make available for review to the commission or commission staff all maps, drawings, and records of the company's gas facilities.  The maps, drawings, and records must show the size and type of material of all facilities, corrosion control, and the maximum allowable operating pressure.  The maps and drawings must indicate the location of all district regulator and gate stations and location of all valves, identifying the emergency valves specified in the company's emergency plan.

Comment: In order to support the industry’s heightened security efforts subsequent to September 11, 2001, all documents pertaining to the exact location of pipeline facilities must not be provided to the public or any public agency. We recommends the above changes for clarity.

- Each gas company must make books, records, reports, and other information available for review by the commission, so the commission can determine whether the gas company is in compliance with state and federal regulations.

Comment:  PSE would like to discuss how paragraph (2) relates to this section (480-93-018) on maps, drawings, and records.  It appears to have come out of rule 480-93-180.  We recommend deleting this section here and making it a separate rule.

(3)  Every company shall establish a standard that specifies a frequency for distributing updates of maps, drawings and records and that identifies which maps, drawings and records are provided to appropriate operations personnel.

Comment: PSE would like to discuss this with UTC staff.

Proposed Rule:

WAC     480-93-080  Welder  and Joiner qualification

(1) Each welder qualification test result must be recorded and kept for a period of 5 years

Comment: If the intent is to disallow Appendix C of Part 192  PSE strongly disagrees and would like to discuss with the commission staff.   There is no value added by the proposed language of the first sentence since DOT 192.227 stipulates welder qualification requirements and welding procedures are covered in 192.225.  Qualifying a welder under 192.227 requires a qualified welding procedure as explicitly stated in API 1104 Section 2 and Article II of Section IX of the ASME Boiler and Pressure Vessel Code.

(2)Operators must use appropriate testing equipment to measure the essential variables during welder qualification or requalification, and also for procedure qualification or requalification.  All essential variables must be recorded during these processes.

Comment:  PSE recommends the above changes for clarity..

(3)  Qualified welding procedures must be on site where welding is being performed.

Comment:  Duplicate of DOT 192.273(b).  No value added.

(5)Qualified joining procedures must be on site where joining is being performed.

Comment: Please define joining.  Does this include everything covered under 192 Subpart F -Joining of Materials Other Than by Welding, just plastic pipe (all joining methods), or just plastic pipe heat fusion method?

Comment:  DOT 192.285(c) covers requalification for plastic pipe joining and the operator qualification requirements specified in 192.805(b) cover requalification for all non-welded pipe joining.  The proposed language would disallow performance history review for plastic pipe joining, as allowed by the federal rule in 192.285(c).

(3) Each joiner qualification test result must be recorded and kept for a period of 5 years.

(5)  Welders and joiners must carry appropriate identification and qualification cards showing the name of welder or joiner, their qualifications, date of qualification expiration, and the company whose procedures were followed for the qualification.  Welder and joiner qualification cards will be subject to commission inspection at all times when qualified personnel are working on facilities subject to Commission jurisdiction.

Proposed Rule:

###### WAC     480-93-082  Qualification of employees

Staff recommends deleting this rule

Proposed Rule:

WAC     480-93-120   Marking Aboveground facilities

- All exposed pipelines and associated equipment whose location presents an unusually hazardous situation must have a pipeline marker.

- All gas pipelines attached to bridges or otherwise spanning an area must have line markers at both ends of the suspended pipeline.

(a)Each gas company must annually inspect and maintain the markers to ensure they are visible and legible.

(b) Markers that are reported damaged and missing must be replaced within 45 days

Comment: We would like to discuss the intent paragraph (1) of the proposed rule.  We believe paragraph (2) should be part of this rule not 480-93-124 for clarity.

Proposed Rule:

###### WAC     480-93-124  Line markers for buried pipelines

- Line markers required by 192.707 must be placed:

- at all railroad, road, irrigation, and drainage ditch crossings;

- at all fence lines where a line crosses private property;

- approximately 500 yards apart, if practical; and

- where the line changes direction.

Exceptions to this rule must conform to 49 CFR, Part 192.707(b).

Comment: We recommend the above changes for clarity.

(2) All gas pipelines attached to bridges or otherwise spanning an area must have line markers at both ends of the suspended pipeline.  Each gas company must annually inspect and maintain the markers to ensure they are visible and legible.  Markers that are reported damaged and missing must be replaced within 45 days.

Comment: We recommend combining this paragraph with 480-93-120.

- (2)Each company must establish a frequency for line marker surveys and include this in their Operations and Maintenance plan.  Line marker survey records must be kept for a minimum of 5years.

Comment:  Operators need the flexibility to combine line marker surveys with other required surveys (i.e. leak surveys) for efficiency.  Also, a records retention of 5 years would be consistent with CFR part 192 section 709(c).

###### Proposed Rule:

###### WAC     480-93-155  Increasing maximum allowable operating pressure

(1)Each gas company must submit to the commission for review, complete written plans and drawings at least 45 days before uprating to a maximum allowable operating pressure (MAOP) greater than  60 psig.  The plan must include a review of the following:

(a) 	All affected gas facilities, including pipe, fittings, valves, and other affected equipment, with their manufactured design operating pressure and specifications;

(b) 	Original design and construction standards;

(c) 	All previous operating pressures and length of time at that pressure;

(d) 	All leaks, regardless of cause, and the date and method of repair;

(e) 	All upstream and downstream regulators and relief valves;

(f) 	All cathodic protection readings on mains for the past three years or three most recent inspections, whichever is longer, and the most recent inspection on each attached service line, which is electrically isolated; and

(g) 	Additional records deemed necessary to evaluate the pressure increase.

(2)     The proposed MAOP of the pipeline must be substantiated by a previous  test. When a previous test does not substantiate the proposed MAOP, a new test must be conducted before or in conjuction with the uprate.

Comment: We recommend the above changes for clarity.

Proposed Rule:

WAC     480-93-180  Operations , maintenance, emergency, and inspection plans and procedures

Each gas company must have written operation, maintenance, emergency, and inspection plans and procedures in compliance with the provisions and general intent of the federal “Natural Gas Pipeline Safety Act.”   Such plans and procedures, and amendments, must be practicable and designed to enhance safety and must be filed with the commission for review.  The commission may, after notice and opportunity for hearing, require such plans and procedures be revised in accordance with Title 49, Part 192 and 480-93 WAC.

Proposed Rule:

WAC     480-93-190  Being aware of construction work near gas company facilities

Staff recommends deleting  this rule

(1) Each gas company must subscribe to the available "one call locating service" in every area their facilities are located.

(2) Each gas company must establish procedures for notification of all construction work in close proximity to gathering lines, mains, service lines, transmission lines, and other gas facilities.

#### LEAKS

Staff recommends deleting this rule

WAC 480-93-184  Gas leak responsibility.

Each gas company shall designate personnel who shall be responsible for pipeline and service line patrolling; leak survey practices, procedures, and operations; and

leak classification and repairs within its respective areas of operation (i.e. division, district, etc.).

Proposed Rule:

WAC     480-93-185  Gas leak investigation

- Each gas company must promptly investigate any notification of a leak, explosion, or fire, which may involve gas pipelines or other gas facilities, received from any outside source such as a police or fire department, other utility, contractor, customer, or the general public.  .  .

(a)Where the investigation reveals a gas leak, the leak must graded in accordance with WAC 480-93-186 and appropriate action must be taken in accordance with these rules.

:

Comment:  CFR 192.617 requires operators to establish procedures for analyzing accidents and failures.  PSE believes it is more appropriate for such procedures to specify how a company works with the commission during such incidents.  Preservation of evidence is an important issue but the prescriptive language of the proposed rule is counterproductive and could hinder a company’s ability to properly respond to an emergency.

PSE also believes the final sentence is more appropriately placed in 480-93-186.

(b)  When leak indications are found to originate from a foreign source or facility, such as gasoline vapors, sewer or marsh gas, or customer-owned piping, prompt action must be taken, to protect life and property.

(i)All Leaks that represent an ongoing, potentially hazardous situation must be reported promptly to the owner or operator of the source facility and, where appropriate, to the police department, or other appropriate governmental agency.  In all cases, the property owner or the adult person occupying the premises must be notified of the leak conditions.

(ii)If no methane (or propane) indication is found, the gas company employee on-site must inform the property owner or the adult person occupying the premises, and must request the adult person occupying the premises to sign the gas company work order.  The gas company employee must provide the adult person occupying the premises an odor sniff card that identifies the odor of gas (or propane) and indicates the name, address, and telephone number of the gas company representative to be contacted if the leak indications are again noticed.

(iii)If the property owner or an adult person occupying the premises is not available, the gas company must, within  24 hours of the leak notification, send by first-class mail addressed to the person occupying the premises, a letter explaining the results of the investigation.  A copy of the letter must be retained by the gas company and kept with the leak report.  A leak investigation report form must be maintained in the gas company's leak report files for all leaks investigated, indicating gas company employee making the initial leak evaluation.

Proposed Rule:

WAC     480-93-186  Leakage classification and action criteria

(1)  Each gas company must establish a procedure for evaluating the concentration and extent of gas leakage.  When evaluating any leak, the perimeter of the leak area must be determined and documented.  If the perimeter of the leak extends to a building wall, the investigation must extend inside the building.

(2)  Based on an evaluation of the location and/or magnitude of a leak, one of the following leak grades shall be assigned, thereby establishing the leak repair priority. A gas company may utilize an alphabetical grade classification, i.e. Grade A for Grade 1, Grade B for Grade 2, and Grade C for Grade 3 if it has historically utilized such a grading designation.

(a)  Grade 1 - Grade 1 means a leak that represents an existing or probable hazard to persons or property and requires immediate repair or continuous action until conditions are no longer hazardous.

- Grade 2 - Grade 2 means a leak recognized as being nonhazardous at the time of detection but justifies scheduled repair based on probable future hazard.

(c)  Grade 3 - Grade 3 means a leak that is non-hazardous at the time of   detection and can reasonably be expected to remain non-hazardous.

(3)  The same criteria for initial leak grading must be applied to re-inspected leaks.  However, Grade 1 or Grade 2 leaks may not be downgraded to a Grade 3 leak without a physical repair having been made to the pipeline facility.

(4)  Leak repair priority and re-evaluation requirements are provided in Table 1.  The examples of leakage provided in the table are guidelines and are not exclusive.

() Immediately following a leak repair, the perimeter of the leak area must be checked with a Combustible Gas Indicator.  Grade 1 leaks with residual gas in the ground must be re-inspected as soon as practical and no later than one month following the repair.  In the case of Grade 2 or Grade 3 leaks which have been repaired, the need for a follow-up inspection must be determined by  qualified personnel employed or retained by the gas company.

Proposed Rule:

WAC 480-93-18601  Table 1-- Priority of leak repair--Examples

| TABLE 1--LEAK CLASSIFICATION AND ACTION CRITERIA |  |
| --- | --- |
| Comment: Definitions are given above. Duplicating here adds no value. |  |
| PRIORITY OF LEAK REPAIR | EXAMPLES |
|  | Leaks requiring prompt action: |
| Requires prompt action* to protect life and property and continuous action until the conditions are no longer hazardous. *The prompt action in some instances may require one or more of the following: | - Any leak which, in the judgment of operating personnel at the scene, is regarded as an immediate hazard. 2. Escaping gas that has ignited unintentionally |
| - Implementation of company emergency plan (192.615). - Evacuating premises. | 3. Any indication of gas, which has migrated into or under a building or tunnel. |
| - Blocking off an area. - Rerouting traffic. - Eliminating sources of ignition - Venting the area, or - Stopping the flow of gas by closing valves or other means. - Notifying police and fire department | 4. Any reading at the outside wall of a building or where the gas would likely would likely migrate to the outside wall of a building. 5. Any reading of 80% LEL or greater in a confined space. |
|  | 6. Any reading of 80% LEL, or greater in small substructures not associated with gas facilities where the gas would likely would likelymigrate to the outside wall of a building. 7. Any leak that can be seen, heard, or felt and which is in a location that may endanger the general public or property. |

Comment:  PSE prefers the current language of “would likely” since ANY leak “could potentially” migrate.

GRADE 2

PRIORITY OF LEAK REPAIR 		EXAMPLES

Leaks should be repaired or		A. Leaks requiring action ahead of

cleared in one year but shall		ground freezing or other

not exceed fifteen months from		adverse changes in venting

the date reported.  If a Grade		conditions:

2 leak occurs in a segment of

pipeline which is under			1. Any leak, which under frozen

consideration for replacement,		or other adverse soil

an additional 6 months may be		conditions, would likely would likely

added to the 15 months maximum	migrate to the outside of a

time for repair noted above.  In		building.

determining the repair priority,

criteria such as the following		B. Leaks requiring action within

should be considered:			six months:

a. Amount and migration of		1. Any reading of 40% LEL or

gas,					greater under a sidewalk in

b. Proximity of gas to			a wall-to-wall paved area

buildings and subsurface		that does not qualify as a

structures,				Grade 1 leak and where gas

c. Extent of pavement, and		is likely   is likely to migrate to

the outside wall of a building.

d. Soil type and conditions,

such as frost cap, moisture

and natural venting.			2. Any reading of 100% LEL or

greater under a street in a

Grade 2 leaks shall be re-			wall-to-wall paved area that

evaluated at least once every six		does not qualify as a Grade

months until cleared.  The			1 leak and where the gas is

frequency of reevaluation should be	likely is likely to to migrate to the

determined by the location and		outside wall of a building.

magnitude of the leakage

condition.					3. Any reading less than 80%

LEL in small substructures

It should be recognized that		not associated with gas

Grade 2 leaks will vary greatly		facilities where gas would

in degree of potential hazard.		likely would likely  migrate creating a

There will be some Grade 2		probable future hazard.

leaks, which when evaluated by

the above criteria, will justify		4. Any reading between 20% LEL

scheduled repair within the next		and 80% LEL in a confined

5 working days.  Others will		space.

justify repair within 30 days.

These situations shall be brought		5. Any reading on a pipeline

to the attention of the			operating at 30% SMYS or

individual responsible for			greater in Class 3 or 4

scheduling leakage repair at the		locations that does not

end of the working day.			qualify as a Grade 1 leak.

On the other hand, there will be		6. Any leak which in the

many Grade 2 leaks, which because	judgment of operating

of their location and magnitude,		personnel at the scene is of

can be scheduled for repair on a		sufficient magnitude to

normal routine basis with			justify scheduled repair.

periodic reinspection as necessary.

GRADE 3

PRIORITY OF LEAK REPAIR		EXAMPLES

Grade 3 leaks should be re-		Leaks requiring re-evaluation at

evaluated during the next			periodic intervals:

scheduled survey, or within 15

months of the reporting date,		1. Any reading of less than 80%

whichever occurs first, until		LEL in small gas associated

the leak is regraded or no			substructures such as small

longer results in a reading.			meter boxes or gas valve boxes.

2. Any reading under a street in

areas without wall-to-wall paving

where it is unlikely the gas could

migrate to the outside wall of a

building.

3. Any reading of less than 20% LEL

in a confined space.

[Statutory Authority:  RCW 80.01.040.  92-16-100 (Order R-375, Docket No. UG-911261), § 480-93-18601, filed 8/5/92, effective 9/5/92; Order R-103, Table 1 (codified as WAC 480-93-18601), filed 5/18/77.]

Proposed Rule:

WAC     480-93-187 Leak records and self audit

(1) 	Each gas company must prepare and maintain permanent gas leak repair records.  The leak repair records must contain sufficient data and information to permit the commission to assess the adequacy of the company maintenance programs and to provide the data and information required by RSPA F-7100.1, F-7100.1-1, F-7100.2, and F-7100.2-1 leak report.

(2) 	The following information must be recorded and maintained to the extent the information is available.  Data and information which cannot reasonably be expected to be available under the particular circumstances of a leak situation need not be recorded immediately:

(a) 	Date and time detected, investigated, and reported and the name of employees conducting the detection, investigation and report;

(b) 	Date and time the leak was reevaluated before repair, and the name of the employee involved;

(c) 	Date and time of repair, when a Grade 1 leak is involved, and the name of the employee in charge of the repair;

(d) 	Date and time the leak was rechecked after repair and the employee involved;

(e) 	Location of leak (sufficiently described to allow ready location by other qualified personnel);

(f) 	Leak grade;

(g) 	Pipeline classification (distribution, transmission, etc.);

(h) 	Method of leak detection (if reported by outside party, list name and address);

(i) 	Part of system where leak(s) occurred  (main, service, etc.);

(j) 	Location on the system where leak occured  (pipe, valve, fitting, compressor or regulator station, etc.);

(k) 	Material which leaked (steel, plastic, cast iron, etc.);

(l) 	Origin of leak;

(m) 	Pipe description;

(n) 	Type repair;

(o) 	Leak cause;

(p) 	Date pipe installed (if known);

- Whether under cathodic protection;

- Location and magnitude of Combustible Gas Indicator readings taken inside and outside of the leak perimeter.

Comment:  (s) is not necessary given the calibration requirements set forth in Rule 480-93-188(2)

(3) 	Self audits.  Each gas company must ensure:

(a) 	All repairs are made within the time required;

(b) 	All leak repairs are effective; and

(c) 	Records are accurate.

Proposed Rule:

WAC     480-93-188  Gas leak surveys

(1)  Each gas company must have a leak detection program.  A gas leak survey must be conducted using a gas detection instrument.  The leak survey must be conducted at:

(a)  	all mains and services, including the testing of the atmosphere in utility (gas, electric, telephone, sewer, water) and other underground structures;

(b)  	cracks in paving, and the cracks in sidewalks in wall-to-wall paved areas;

(c)  	building walls; and

(d)  	other areas where gas can migrate.

(2) 	All instruments used in leak detection and evaluation shall must be maintained, calibrated, and operated in accordance with the recommended latest manufacturers' specifications and methods.  If there is no manufacture’s recommendation, calibration must be done once each calendar year.

(3) 	Gas leakage surveys must be conducted according to the following specified frequencies:

(a) 	Business areas - once each calendar year, not exceeding fifteen months;

(b) 	Residential areas - as frequently as necessary, not exceeding five years;

(c) 	Buildings of public assembly (such as churches, schools, and hospitals)- once each calendar year, not exceeding fifteen months;

(d) 	Special surveys (such as after floods, earthquake, land movement and unstable soil areas) - as deemed appropriate by the gas company; and

(e) 	Where the gas system has cast iron, wrought iron, or ductile iron, or noncathodically protected bare steel, galvanized steel, or coated steel pipe - twice each calendar year not exceeding eight months.

(4) 	Gas leakage surveys of business areas and public buildings must be conducted on the following basis:

(a) 	Where gas service lines exist, a survey must be conducted at the building wall at the point of entrance, using a bar hole where necessary;

(b) 	Surveys must be conducted within all buildings, where gas leakage has been detected at the outside wall, at all points where escaping gas could potentially migrate into and accumulate inside the building; and

(c) 	Service piping, riser piping and meter(s) must be checked with gas detection instrument or with a soap solution.

(5)  Prior to resurfacing, repairs, or  street alterations, where gas facilities are under the area to be paved, and where there is substantial probability that damage occurred to gas facilities as a result of the road work, a gas survey, including manholes and other street openings, must be made;

(6)In areas where substructure construction adjacent to underground gas facilities occurs, where there is substantial probability that damage could have occurred to the gas facilities, an appropriate gas detection survey must be made following the completion of installation but prior to paving;

Comment: Move to (3)

(d) 	  Comment:  Already covered in paragraph (3)

(7) 	Records of the current and immediately preceding survey of an area must be maintained and must include the following:

(a) 	Description of system and area surveyed (this could include maps and leak survey logs);

(b) 	Survey results;

(c) 	Survey method;

(d) 	Name of person making survey; and

(e) 	Survey dates.

(8) 	Each gas company is required to perform self audits of the effectiveness of their leak detection program as frequently as necessary, not exceeding three years.

(a) 	Leak survey schedule must assure that it is commensurate with the minimum federal safety standards for gas pipelines, Subpart M-Maintenance, and the general condition of the pipeline system as required by other applicable regulations;

(b) 	Survey effectiveness - evaluate survey results to assure that a consistent evaluation of leaks is being made throughout the system; and

(c) 	Check the adequacy of records.

[Statutory Authority:  RCW 80.01.040 and 80.04.160.  01-11-003 (Docket No. UG-990294, General Order No. R-484), § 480-90-999, filed 5/3/01, effective 6/3/01.]