## Energy Efficiency
Energy Efficiency Customer Benefits
There are two principal areas of energy efficiency savings enabled by the deployment of advanced meters, efficiency measures undertaken by the customer as a result of better understanding their patterns of energy use, and energy savings associated with the utility’s management of the electric distribution system.
| CVR Energy usage reduction | [6 empty] | Source or Reference
|  | 1 | Avoided Energy Purchased in kWh (from Utility CVR spreadsheet) |  |  |  | 13798937.34 | See Appendix Benefits CVR tab to see how this value was determined
|  | 2 | Avista average cost per kWh |  |  |  | 0.086 | Avg of Tier 2 for residential and Tier 2 for Schedule 21
|  | 3 | Total |  |  |  | 1186708.6112 | Calculation
| Energy Savings due to better understanding of energy usage | [8 empty] | x
Model 1
Immediate direct feedback could be extremely valuable, especially for savings from daily behaviour in non-heating end-uses. In the longer term and on a larger scale, informative billing and annual energy reports can promote investment as well as influencing behaviour. Savings have been shown in the region of 5-15% and 0-10% for direct and indirect feedback respectively.
Caluclation of total kWh by the customer groups modeled
[5 empty] | Number | kWh
|  | Commercial Customers |  |  | 23385 | 1804801283
|  | Residential Customers |  |  | 212659 | 2482493050
|  |  | Under 500 kWh/Mo |  | 46061 | 154446492
|  |  | 500 - 1000 kWh/Mo |  | 85416 | 762768267
|  |  | Over 1000 kWh/Mo |  | 81121 | 1564546291
|  | Total |  |  |  | 6769055383
[5 empty] | Customers | % Participating | kWh Savings | 3% | * Based on an assumption of 3% percent reduction in energy use. References 1-10 (Reviewed literature to estimate a reasonable reduction)
|  | Commercial Customers |  |  | 23385 | 5% | 2707201.9245
|  | Residential Customers |  |  | 212659 |  |  |  | * Customer counts obtained from Customer Information System
|  |  | Under 500 kWh/Mo |  | 46061 | 1% | 46333.9476 |  | * % Participating estimates were based on qualitative assessments from literature and Avista Experience
|  |  | 500 - 1000 kWh/Mo |  | 85416 | 3% | 686491.4403 |  | * Based on a weighted average retail electric rate of $0.085 per kWh
|  |  | Over 1000 kWh/Mo |  | 81121 | 5% | 2346819.4365
|  |  | Total |  |  |  | 5786846.7489 | 491881.9737 | Monetary savings to customers
[8 empty] | 0.08549% | <- Estimated reduction in retail load for these customer groups
References
| 1 | 6% | http://www.slideshare.net/breakingnews/unlocking-energy-efficiency-in-the-us-economy-1789726
| 2 |  | http://www.eci.ox.ac.uk/research/energy/downloads/smart-metering-report.pdf
| 3 | 1-4% | http://finance-commerce.com/2014/09/sustainable-reducing-energy-use-through-behavioral-science/
| 4 |  | http://opower.com/uploads/library/file/24/Opower_WP_Effective_Customer_Engagement.pdf
| 5 |  | http://www.elp.com/articles/2013/07/study-utility-customer-engagement-programs-are-worth-it.html
| 6 |  | https://www.energystar.gov/buildings/program-administrators/state-and-local-governments/campaigns
| 7 | 2% | http://www.energyvortex.com/pages/headlinedetails.cfm?id=4857
| 8 | 2% | http://www.intelligentutility.com/article/12/02/behavioral-approaches-energy-conservation-pay&utm_medium=eNL&utm_campaign=IU_DAILY2&utm_term=Original-Member
| 9 | 4% | http://www.bchydro.com/content/dam/BCHydro/customer-portal/documents/projects/smart-metering/smi-program-business-case.pdf
| 10 | 3% | http://www.utilitydive.com/news/could-reducing-peak-demand-5-be-as-simple-as-asking/329102/
|  |  |  | REV_CLASS_CDE | CountOfUSAGE_PT_KY | SumOfACCUM_USAGE_QTY
|  |  |  | 01 | 212659 | 2482493050
|  |  |  | 21 | 23385 | 1804801283
|  |  |  | 39 | 570 | 80159
|  |  |  | 31 | 359 | 205546579
|  |  |  | 80 | 56 | 12095526
|  |  |  | 51 | 1 | 2875
Value represented above includes benefits to Avista's customers, not Avista.

## Appendix Benefits CVR
AMI can increase CVR savings 1 is based on voltage alarming. Avista has 70 feeders with Integrated Volt Var Control (IVVC) which is an application that implements CVR for energy savings based on power flow and primary measurement points. Using power flow (IVVC) provides a good estimate of voltage, but requires us to assume a conservative minimum voltage at each meter since we don’t know the exact characteristics/loading of each transformer and secondary circuit. With voltage alarming at the meter level, we could set the IVVC system to a lower setpoint and verify each customer receives the appropriate voltage. Our estimation is that this could provide at least 0.5% additional energy savings over the 2% 2IVVC is achieving today. The cost savings below are based on the same method used for SGIG/SGDP cost savings for CVR.
Benefits Description
Source or Reference
Component Estimate
| Annual Usage on Feeders with IVVC (kWh) | 1667139240 | Used ArcGis to associate meters to feeders and summed up usage for trailing 12 months (Nov 2013 - Oct 2014)
| Annual Usage on Feeders with IVVC installed over time (kWh) | 1092648228 | Assume balance of feeders upgraded over the life of the meters (15 years) = 50% of remaining
| Estimated Reduction in voltage (CVR) 1-2 | 0.5% | Qualitative estimate of reduction on buffer that could exist with AMI alarming
| Energy Reduction kWh | 13798937.34 | Calculation
| Weighted Average Cost of Energy | 0.086
| Savings due to Avoided cost of energy | 1186708.6112 | Calculation |  |  | * 6% based on EIA estimate
Table 1: Shows which feeders have IVVC today, and the energy they use:
|  | Feeders | Usage_PTs | Accum_Usage | % Feeders | % Usage_PTs | % Accum_Usage
| All | 206 | 229320 | 3852435696 | 100% | 100% | 100%
| No IVVC | 136 | 127188 | 2185296456 | 66.02% | 55.46% | 56.73%
| IVVC | 70 | 102132 | 1667139240 | 33.98% | 44.54% | 43.27%
References
1 | Low-Cost CVR May Pay for Your AMI System. Jerry Jackson, Ph.D., Smart Grid Research Consortium
2 | Navigant Research, Avista Utilities’ Conservation Voltage Reduction Program (April 2014) - Reference No.: 164638
Table 2
| Feeder | Meters
| 3HT12F1 | 624
| 3HT12F2 | 1871
| 3HT12F3 | 1008
| 3HT12F4 | 2310
| 3HT12F5 | 1941
| 3HT12F6 | 556
| 3HT12F8 | 5
| 3HT12F7 | 414
| 9CE12F2 | 2350
| AIR12F3 | 477
| ARD12F1 | 1
| ARD12F2 | 923
| BEA12F1 | 1579
| BEA12F2 | 2947
| BEA12F3 | 239
| BEA12F4 | 334
| BEA12F5 | 514
| BEA12F6 | 653
| BEA13T09 | 2
| BKR12F1 | 1878
| BKR12F2 | 1311
| BKR12F3 | 1178
| BLA311 | 2
| C&W12F1 | 2089
| C&W12F2 | 2407
| C&W12F3 | 1573
| C&W12F4 | 1715
| C&W12F5 | 2042
| C&W12F6 | 1965
| CFD1210 | 1744
| CFD1211 | 1114
| CHE12F1 | 1758
| CHE12F2 | 1567
| CHE12F3 | 2126
| CHE12F4 | 1565
| CHW12F2 | 1031
| CHW12F3 | 703
| CHW12F4 | 501
| CLA56 | 3
| CLV12F1 | 864
| CLV12F2 | 1459
| CLV12F3 | 1
| CLV12F4 | 1453
| CLV34F1 | 1626
| COB12F1 | 2280
| COB12F2 | 1759
| DEP12F1 | 2259
| DEP12F2 | 1057
| DIA231 | 610
| DIA232 | 384
| DRY1208 | 1161
| DRY1209 | 545
| DVP12F1 | 947
| DVP12F2 | 197
| ECL221 | 570
| ECL222 | 1462
| EFM12F1 | 1550
| EFM12F2 | 788
| EWN241 | 436
| F&C12F1 | 3054
| F&C12F2 | 2056
| F&C12F3 | 1344
| F&C12F4 | 2513
| F&C12F5 | 1763
| F&C12F6 | 1873
| FOR12F1 | 601
| FOR2.3 | 1
| FWT12F1 | 2361
| FWT12F2 | 1720
| FWT12F3 | 1464
| FWT12F4 | 1093
| GAR461 | 607
| GIF34F1 | 1540
| GIF34F2 | 965
| GLN12F1 | 2636
| GLN12F2 | 2435
| GRN12F1 | 1456
| GRN12F2 | 568
| GRV1272 | 1
| H&W12F2 | 555
| HAR4F1 | 168
| HAR4F2 | 189
| INT12F1 | 1878
| INT12F2 | 1195
| KET12F1 | 84
| KET12F2 | 845
| L&R511 | 346
| L&R512 | 411
| L&S12F1 | 796
| L&S12F2 | 3404
| L&S12F3 | 2538
| L&S12F4 | 1811
| L&S12F5 | 894
| LAT421 | 489
| LAT422 | 259
| LEO611 | 1
| LEO612 | 573
| LF34F1 | 468
| LIB12F1 | 1989
| LIB12F2 | 2696
| LIB12F3 | 1741
| LIB12F4 | 84
| LIN711 | 404
| LL12F1 | 433
| LOO12F1 | 1046
| LOO12F2 | 728
| M15515 | 13
| MEA12F1 | 1159
| MEA12F2 | 2190
| MIL12F1 | 1782
| MIL12F2 | 1696
| MIL12F3 | 1842
| MIL12F4 | 1608
| MLN12F1 | 875
| MLN12F2 | 817
| NE12F1 | 2581
| NE12F2 | 697
| NE12F3 | 1264
| NE12F4 | 2141
| NE12F5 | 878
| NEZ1267 | 1
| NMO521 | 19
| NW12F1 | 1782
| NW12F2 | 1391
| NW12F3 | 1767
| NW12F4 | 2009
| ODS12F1 | 718
| OPT12F1 | 1748
| OPT12F2 | 531
| ORI12F1 | 660
| ORI12F2 | 174
| ORI12F3 | 1176
| OTH501 | 1132
| OTH502 | 2
| OTH503 | 4
| OTH505 | 1
| PAL311 | 699
| PAL312 | 46
| PDL1201 | 1642
| PDL1202 | 2060
| PDL1203 | 1612
| PDL1204 | 282
| POT322 | 1
| PST12F1 | 454
| PVW241 | 3
| RDN12F1 | 555
| RDN12F2 | 329
| RIT731 | 694
| RIT732 | 481
| ROK451 | 326
| ROS12F1 | 3143
| ROS12F2 | 985
| ROS12F3 | 2352
| ROS12F4 | 983
| ROS12F5 | 2024
| ROS12F6 | 2462
| ROX751 | 74
| RSA431 | 668
| SE12F1 | 1856
| SE12F2 | 2943
| SE12F3 | 2028
| SE12F4 | 2161
| SE12F5 | 2226
| SIP12F1 | 1
| SIP12F2 | 215
| SIP12F3 | 171
| SIP12F4 | 1984
| SIP12F5 | 112
| SLK12F1 | 1652
| SLK12F2 | 916
| SLK12F3 | 241
| SLW1368 | 691
| SOT521 | 1144
| SOT522 | 716
| SOT523 | 673
| SPA442 | 238
| SPI12F1 | 805
| SPI12F2 | 372
| SPR761 | 480
| SPU121 | 2058
| SPU122 | 2
| SPU123 | 1558
| SPU124 | 2
| SPU125 | 3
| SUN12F1 | 3080
| SUN12F2 | 2108
| SUN12F3 | 2603
| SUN12F4 | 1281
| SUN12F5 | 545
| SUN12F6 | 1655
| TKO411 | 554
| TKO412 | 316
| TUR111 | 18
| TUR112 | 2165
| TUR113 | 1829
| TUR115 | 157
| TUR116 | 2242
| TUR117 | 2484
| TVW131 | 1
| TVW132 | 1789
| VAL12F1 | 1059
| VAL12F2 | 374
| VAL12F3 | 699
| WAK12F1 | 1734
| WAK12F2 | 1505
| WAK12F3 | 1507
| WAK12F4 | 1266
| WAS781 | 242
| WIL12F1 | 629
| WIL12F2 | 697
Note on B27: EnergyEfficiency_05.pdf